## SUMMARY
B10639 - 130 Queen St W - Toronto
\\
| Source | CBRE - BAS |  |  | Note
IOPS continues to manage the MAG portfolio within owned and leased buildings according to applicable ASHRAE and industry standards and codes. Landlords are responsible to operate all buildings in accordance with their lease agreements and the applicable ASHRAE industry standards and codes. Buildings are operated in accordance with the applicable standards outlined by the following: 1. Ontario Building Code; 2. American Society of Heating, Refrigerating and Air-Conditioning Engineers (ASHRAE); and 3. Building Owners and Managers Association (BOMA) Canada. With respect to COVID-19, IOPS will continue to monitor and respond to best practices from accredited organizations and make the necessary building operational adjustments, as practical and when required at owned buildings. IOPS will continue to work with landlords to incorporate identified best practices from accredited organizations.
Thresholds
| Metric |  | High | Low
| Temperature (oC) |  | 26
| RH (%) |  | 60 | 40
| CO2 (ppm) |  | 800
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.

## Calc Pivot (hidden)
B#-ADDRESS-CITY | B10639 - 130 Queen St W - Toronto |  | B#-ADDRESS-CITY | B10639 - 130 Queen St W - Toronto |  |  | B#-ADDRESS-CITY | B10639 - 130 Queen St W - Toronto
LOCATION | (All) |  | LOCATION | (All) |  |  | LOCATION | (All)
Row Labels | Average of Temperature (C) for Graphs | Sum of HighTempLimit | Row Labels | Average of RH (%) for Graphs | Sum of HumidityLimit | Sum of HumidityLowerLimit | Row Labels | Average of CO2 (ppm) for Graphs | Sum of CO2Limit
16-Sep | 21 | 26 | 16-Sep | 55.4194 | 60 | 40 | 16-Sep | 456.3871 | 800
9 AM | 21 | 26 | 9 AM | 54.8571 | 60 | 40 | 9 AM | 461.5 | 800
12 PM | 21 | 26 | 12 PM | 55.8571 | 60 | 40 | 12 PM | 456.4286 | 800
3 PM | 21 | 26 | 3 PM | 56 | 60 | 40 | 3 PM | 432.3333 | 800
17-Sep | 21.0465 | 26 | 17-Sep | 50.7907 | 60 | 40 | 17-Sep | 474.4186 | 800
9 AM | 20.7857 | 26 | 9 AM | 54.4286 | 60 | 40 | 9 AM | 493.2143 | 800
12 PM | 21.2143 | 26 | 12 PM | 49.7857 | 60 | 40 | 12 PM | 461.1429 | 800
3 PM | 21.1333 | 26 | 3 PM | 48.3333 | 60 | 40 | 3 PM | 469.2667 | 800
18-Sep | 20.8525 | 26 | 18-Sep | 28.3934 | 60 | 40 | 18-Sep | 466.5902 | 800
9 AM | 20.8788 | 26 | 9 AM | 31.5152 | 60 | 40 | 9 AM | 479.7273 | 800
12 PM | 21.2143 | 26 | 12 PM | 23.5714 | 60 | 40 | 12 PM | 457.6429 | 800
3 PM | 20.4286 | 26 | 3 PM | 25.8571 | 60 | 40 | 3 PM | 444.5714 | 800
21-Sep | 20.881 | 26 | 21-Sep | 37.3571 | 60 | 40 | 21-Sep | 464.1429 | 800
9 AM | 20.0714 | 26 | 9 AM | 38 | 60 | 40 | 9 AM | 479.7143 | 800
12 PM | 20.5 | 26 | 12 PM | 38.0714 | 60 | 40 | 12 PM | 464.9286 | 800
3 PM | 22.0714 | 26 | 3 PM | 36 | 60 | 40 | 3 PM | 447.7857 | 800
22-Sep | 21 | 26 | 22-Sep | 42 | 60 | 40 | 22-Sep | 529.5854 | 800
9 AM | 20.7857 | 26 | 9 AM | 41.9286 | 60 | 40 | 9 AM | 532.4286 | 800
12 PM | 21 | 26 | 12 PM | 40.3571 | 60 | 40 | 12 PM | 532.5 | 800
3 PM | 21.2308 | 26 | 3 PM | 43.8462 | 60 | 40 | 3 PM | 523.3846 | 800
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.
This shape represents a slicer. Slicers are supported in Excel 2010 or later. If the shape was modified in an earlier version of Excel, or if the workbook was saved in Excel 2003 or earlier, the slicer cannot be used.

## DAA (hidden)
Site |  | 15-Sep | 16-Sep | 17-Sep | 18-Sep | 19-Sep | 21-Sep | Grand Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Source | (All) | [11 empty] | Check | Check | Check |  |  | Check |  |  |  |  | Check
|  | 15-Sep | 16-Sep | 17-Sep | 18-Sep | 19-Sep | 21-Sep | Grand Total | 0 | 0
Count of B# | Column Labels
| 14-Sep | 15-Sep | 16-Sep | 17-Sep | 18-Sep | 19-Sep | 21-Sep | Grand Total
Row Labels
B10000 - 426 Queen St E - Sault Ste. Marie | 30 | 30 | 30 | 60 | 32 |  | 33 | 215
B10639 - 130 Queen St W - Toronto | 45 | 46 | 34 | 92 | 65 |  | 45 | 327
B10644 - 361 University Ave - Toronto | 56 | 48 | 61 | 102 | 54 |  | 66 | 387
B10991 - 440 Kent St W - Lindsay | 48 | 48 | 48 | 48 | 48 | 48 | 48 | 336
B11589 - 155 Elm St - Sudbury | 42 | 42 | 37 | 82 | 42 |  | 37 | 282
B12948 - 297 Pembroke St E - Pembroke | 53 | 54 | 52 | 110 | 53 |  | 54 | 376
B14164 - 311 Jarvis St - Toronto | 45 | 45 | 45 | 90 | 44 |  | 47 | 316
B15646 - 245 Windsor Ave - Windsor | 96 | 96 | 96 | 96 | 96 | 96 | 96 | 672
B18343 - 80 Dundas Street East - London | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 1344
B18784 - 491 Steeles Ave E - Milton | 192 | 192 | 192 | 192 | 192 | 192 | 192 | 1344
B19512 - 70 Wellington St - Brantford | 13 | 12 | 12 | 26 | 13 |  | 11 | 87
B20022 - 470 Water St - Peterborough | 76 | 78 | 62 | 78 | 82 |  | 82 | 458
B20080 - 700 Christina Street North - Sarnia | 18 | 21 | 21 | 42 | 22 |  | 18 | 142
B20265 - 60 Queen St W - Toronto | 61 | 64 | 40 | 118 | 61 |  | 60 | 404
B20289 - 47 SHEPPARD AVE E - Willowdale | 44 | 45 | 44 | 90 | 44 |  | 45 | 312
B20390 - 102 East Main St - Welland | 77 | 76 | 75 | 75 | 75 |  | 76 | 454
B20474 - 74 Woolwich St - Guelph | 65 | 63 | 63 | 61 | 57 |  | 57 | 366
B20478 - 5 Court St - Kingston | 40 | 38 | 38 | 40 | 45 |  | 45 | 246
B20616 - 50 Eagle St W - Newmarket | 21 | 21 | 21 | 40 | 20 |  | 19 | 142
B20619 - 59 Church St - St. Catharines | 6 | 6 | 6 | 12 | 4 |  | 4 | 38
B20705 - 161 Elgin St - Ottawa |  |  | 62 | 126 | 56 | 8 | 66 | 318
B20893 - 75 Mulcaster St. - Barrie | 3 | 3 | 4 | 6 | 3 |  | 3 | 22
B20979 - 1000 Finch Ave W - Toronto | 45 | 46 | 47 | 98 | 48 |  | 48 | 332
B21128 - 1911 Eglinton Ave E - Scarborough | 36 | 35 | 51 | 55 | 55 |  | 51 | 283
B21554 - 36 Wyndham St S - Guelph | 31 | 32 | 29 | 33 | 34 |  | 33 | 192
B24638 - 55 Main St W - Hamilton | 9 | 9 | 9 | 18 | 9 |  | 10 | 64
B25165 - 45 Main Street East - Hamilton | 33 | 30 | 30 | 72 | 42 |  | 33 | 240
B25479 - 44 Queen St - Brantford | 36 | 33 | 36 | 32 | 46 |  | 35 | 218
B25602 - 29 Second St W - Cornwall | 25 | 24 | 23 | 48 | 24 |  | 24 | 168
B25671 - 425 Grand Ave W - Chatham | 15 | 9 | 9 | 18 |  |  | 9 | 60
B25683 - 200 Chatham St - Windsor | 9 | 9 | 9 | 12 | 6 |  |  | 45
B70003 - 444 Yonge St - Toronto |  | 206 | 45 | 136 | 60 |  | 58 | 505
B70235 - 70-110 Simcoe St - Peterborough | 98 | 97 | 96 | 99 | 104 |  | 104 | 598
B70451 - 393 University Ave - Toronto | 60 | 60 | 40 | 120 | 57 |  | 59 | 396
B70496 - 10 Louisa St - Orangeville | 15 | 15 | 37 | 49 | 49 |  | 47 | 212
B90009 - 7755 HURONTARIO ST - Brampton | 72 | 72 | 72 | 72 | 72 | 72 | 72 | 504
B90558 - 49 Place D'Armes - Kingston | 29 | 28 | 30 | 29 | 30 |  | 30 | 176
B90636 - 2201 Finch Ave W - Toronto | 45 | 45 | 45 | 94 | 45 |  | 45 | 319
B90838 - 611 9th Ave E - Owen Sound | 6 | 9 | 4 | 12 | 6 |  | 9 | 46
B91122 - 330 University Ave - Toronto | 51 | 72 | 49 | 148 | 89 |  | 90 | 499
B92347 - 75 Mulcaster Street - Barrie | 3 | 3 | 2 | 6 | 3 |  | 3 | 20
B24968 - 159 Cedar St - Sudbury | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 168
B20226 - 38 Pine St N - Timmins | 18 | 18 | 18 | 36 | 18 |  | 19 | 127
B70050 - 48 Spruce St N - Timmins | 21 | 22 | 20 | 42 | 22 |  | 21 | 148
B10002 - 445 Albert St E - Sault Ste. Marie | 18 | 18 | 18 | 36 | 18 |  | 18 | 126
B13049 - 216 Water St - Kenora | 24 | 25 | 13 | 48 | 23 |  | 25 | 158
B70740 - 2021 Plains Rd - Burlington | 46 | 55 | 60 | 46 | 45 |  | 44 | 296
B10246 - 393 Main St - Haileybury |  | 43 | 41 | 84 | 42 |  | 41 | 251
B20772 - 7765 Hurontario St - Brampton | 150 | 113 | 109 | 116 | 114 |  | 119 | 721
B14895 - 149 Fourth Ave - Cochrane |  |  | 39 | 78 | 36 |  | 39 | 192
B14209 - 89 James St - Parry Sound | 75 | 76 | 74 | 152 | 77 |  | 80 | 534
B10577 - 55 Munsee St N - Cayuga | 69 | 69 | 75 | 75 | 77 |  | 74 | 439
B19570 - 860 William St - Cobourg | 91 | 93 | 93 | 92 | 94 |  | 93 | 556
B16187 - 3 Dominion St - Bracebridge | 75 | 76 | 75 | 75 | 75 |  | 76 | 452
B21030 - 479 Government St - Dryden | 15 | 18 | 17 | 36 | 18 |  | 18 | 122
B17477 - 50 Frederick Hobson VC Dr - Simcoe | 90 | 99 | 98 | 114 | 81 |  | 93 | 575
B11228 - 44 Union St - Picton | 30 | 31 | 29 | 30 | 39 |  | 45 | 204
B19652 - 1 Courthouse Sq - Goderich | 77 | 75 | 77 | 148 | 75 |  | 75 | 527
B20367 - 207 Cayley St - Walkerton | 59 | 60 | 75 | 63 | 62 |  | 62 | 381
B11586 - 27 Phipps St - Gore Bay | 33 | 33 | 33 | 68 | 33 |  | 30 | 230
B12955 - 333 Church St - Fort Frances | 6 | 17 | 18 | 36 | 18 |  | 12 | 107
B25477 - 97 Thomas St E - Napanee | 31 | 25 | 27 | 28 | 31 |  | 30 | 172
B19890 - 41 Dundas St W - Napanee | 29 | 35 | 29 | 29 | 30 |  | 30 | 182
B20550 - 469 Montreal St - Kingston | 30 | 31 | 21 | 19 | 23 |  | 24 | 148
B19523 - 41 Court House Sq - Brockville | 104 | 106 | 106 | 208 | 106 |  | 104 | 734
B20016 - 43 Drummond St E - Perth | 26 | 31 | 30 | 66 | 32 |  | 30 | 215
B20494 - 415 Hunter St - Woodstock | 71 | 80 | 113 | 90 | 92 |  | 78 | 524
B20489 - 1 Huron St - Stratford | 26 | 34 | 29 | 29 | 30 |  | 30 | 178
B20151 - 100 St. Patrick St - Stratford | 27 | 25 | 30 | 31 | 30 |  | 30 | 173
B14660 - 700 Memorial Ave - Orillia | 90 | 90 | 92 | 95 | 95 |  | 94 | 556
B25039 - 590 Rossland Rd E - Whitby | 75 | 84 | 75 | 75 |  |  |  | 309
B20603 - 119 King St W - Hamilton | 145 | 141 | 87 | 56 | 128 |  | 156 | 713
B25548 - 301 St. Paul St - St. Catharines | 137 | 138 | 137 | 135 | 136 |  | 149 | 832
B10578 - 10 Echo St W - Cayuga |  | 1 | [5 empty] | 1
B90631 - 215 Cayley St - Walkerton | 30 | 31 | 21 | 32 | 33 |  | 34 | 181
B70277 - 34 Simcoe St - Barrie | 80 | 79 | 78 | 79 | 79 |  | 79 | 474
B13095 - 220 Main St S - Kenora | 8 | 7 | 3 | 16 | 8 |  | 7 | 49
B70510 - 150 Dufferin Ave - London | 89 | 93 | 91 | 180 | 91 |  | 92 | 636
B21858 - 5 Huron St - Stratford | 7 | [6 empty] | 7
B70151 - 400 Pembroke St E - Pembroke | 1 | [6 empty] | 1
B25398 - 655 BAY ST - Toronto | 48 | 46 | 39 | 96 | 48 |  | 52 | 329
B70485 - 255 Albert St - Ottawa | 57 | 57 | 57 | 114 | 60 |  | 59 | 404
B10003 - 444 Queen St E - Sault Ste. Marie |  | 12 | 12 | 24 | 12 |  | 12 | 72
B18359 - 25 Grosvenor St - Toronto |  |  | 102 | 186 | 138 |  | 105 | 531
Pearson Centre - 2638 Steeles Ave E |  |  |  | 90 | 63 |  | 90 | 243
B92624 - 222 Bremner Blvd - Toronto |  |  |  | 152 | 75 |  | 76 | 303
Grand Total | 3873 | 4165 | 4083 | 6158 | 4410 | 632 | 4425 | 27746

## MASTER DATA
Date | Time | Source | B# | B#-ADDRESS-CITY | LOCATION | COURTROOM | OCCUPANCY | Outdoor baseline reading: Air Temp | Outdoor baseline reading: RH (%) | Outdoor baseline reading: CO2 (ppm) | Temperature (C) | RH (%) | CO2 (ppm) | COMMENT | Date and Time for Graphs | Time for Graphs | Temperature (C) for Graphs | RH (%) for Graphs | CO2 (ppm) for Graphs | Temp Flag | RH Flag | Week Flag | Key
2020-09-16 05:21 | 44090.2229 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 4 | 18.7 | 44.6 | 366 | 23.5 | 40.4 | 877 |  | 2020-09-16 05:21 | 44090.2229 | 23.5 | 40.4 | 877 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 05:21
2020-09-16 08:19 | 44090.3468 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 20 | 40 | 450 | 24 | 44 | 610 |  | 2020-09-16 08:19 | 44090.3468 | 24 | 44 | 610 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 08:19
2020-09-16 08:22 | 44090.3488 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 3 | 14 | 77 | 430 | 17.4 | 66 | 502 |  | 2020-09-16 08:22 | 44090.3488 | 17.4 | 66 | 502 |  | high | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:22
2020-09-16 08:24 | 44090.3497 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 17 | 77 | 430 | 18 | 63 | 470 |  | 2020-09-16 08:24 | 44090.3497 | 18 | 63 | 470 |  | caution | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:23
2020-09-16 08:25 | 44090.3504 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 17 | 77 | 430 | 18.3 | 61 | 451 |  | 2020-09-16 08:25 | 44090.3504 | 18.3 | 61 | 451 |  | caution | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:24
2020-09-16 08:26 | 44090.3512 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 17 | 77 | 430 | 18.5 | 60 | 431 |  | 2020-09-16 08:26 | 44090.3512 | 18.5 | 60 | 431 |  | caution | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:25
2020-09-16 08:27 | 44090.352 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 17 | 77 | 430 | 18.5 | 60.5 | 420 |  | 2020-09-16 08:27 | 44090.352 | 18.5 | 60.5 | 420 |  | caution | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:26
2020-09-16 08:28 | 44090.3528 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 14 | 77 | 430 | 18.7 | 59.4 | 426 |  | 2020-09-16 08:28 | 44090.3528 | 18.7 | 59.4 | 426 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:28
2020-09-16 08:29 | 44090.3535 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 14 | 77 | 430 | 18.7 | 60 | 453 |  | 2020-09-16 08:29 | 44090.3535 | 18.7 | 60 | 453 |  | caution | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:29
2020-09-16 08:30 | 44090.3539 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 16.3 | 67.7 | 375 | 23.4 | 40.6 | 446 |  | 2020-09-16 08:30 | 44090.3539 | 23.4 | 40.6 | 446 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 08:29
2020-09-16 08:30 | 44090.3544 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 14 | 77 | 430 | 19 | 57.8 | 446 |  | 2020-09-16 08:30 | 44090.3544 | 19 | 57.8 | 446 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:30
2020-09-16 08:32 | 44090.3553 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 14 | 77 | 430 | 19.5 | 56 | 440 |  | 2020-09-16 08:32 | 44090.3553 | 19.5 | 56 | 440 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:31
2020-09-16 08:33 | 44090.3561 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 14 | 77 | 430 | 19.8 | 57 | 440 |  | 2020-09-16 08:33 | 44090.3561 | 19.8 | 57 | 440 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:32
2020-09-16 08:34 | 44090.357 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 14 | 77 | 430 | 20 | 54 | 440 |  | 2020-09-16 08:34 | 44090.357 | 20 | 54 | 440 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:34
2020-09-16 08:36 | 44090.3584 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 14 | 77 | 430 | 19.6 | 55 | 455 |  | 2020-09-16 08:36 | 44090.3584 | 19.6 | 55 | 455 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:36
2020-09-16 08:36 | 44090.3585 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 69 | 450 | 22 | 53 | 610 |  | 2020-09-16 08:36 | 44090.3585 | 22 | 53 | 610 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 08:36
2020-09-16 08:37 | 44090.3593 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 14 | 77 | 430 | 19.4 | 55.5 | 456 |  | 2020-09-16 08:37 | 44090.3593 | 19.4 | 55.5 | 456 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:37
2020-09-16 08:39 | 44090.3603 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 14 | 77 | 430 | 19.5 | 55 | 450 |  | 2020-09-16 08:39 | 44090.3603 | 19.5 | 55 | 450 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:38
2020-09-16 08:39 | 44090.3604 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 17.2 | 62.9 | 449 |  | 2020-09-16 08:39 | 44090.3604 | 17.2 | 62.9 | 449 |  | caution | 2020-09-14 | B16187¦¦¦Sep-16-2020 08:39
2020-09-16 08:40 | 44090.361 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 14 | 77 | 430 | 19.7 | 55 | 450 |  | 2020-09-16 08:40 | 44090.361 | 19.7 | 55 | 450 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:39
2020-09-16 08:41 | 44090.3615 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 20.1 | 58.8 | 371 |  | 2020-09-16 08:41 | 44090.3615 | 20.1 | 58.8 | 371 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:40
2020-09-16 08:41 | 44090.3621 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 20.2 | 57.9 | 372 |  | 2020-09-16 08:41 | 44090.3621 | 20.2 | 57.9 | 372 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:41
2020-09-16 08:41 | 44090.3621 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 3 | 15 | 67 | 400 | 20.2 | 55.1 | 632 |  | 2020-09-16 08:41 | 44090.3621 | 20.2 | 55.1 | 632 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 08:41
2020-09-16 08:42 | 44090.3622 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 22.7 | 40.9 | 398 |  | 2020-09-16 08:42 | 44090.3622 | 22.7 | 40.9 | 398 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 08:41
2020-09-16 08:42 | 44090.3628 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 3 | 15 | 67 | 400 | 20.6 | 52.8 | 588 |  | 2020-09-16 08:42 | 44090.3628 | 20.6 | 52.8 | 588 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 08:42
2020-09-16 08:43 | 44090.3629 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 20.6 | 56.3 | 374 |  | 2020-09-16 08:43 | 44090.3629 | 20.6 | 56.3 | 374 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:42
2020-09-16 08:43 | 44090.3633 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 20.7 | 55.9 | 373 |  | 2020-09-16 08:43 | 44090.3633 | 20.7 | 55.9 | 373 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:43
2020-09-16 08:43 | 44090.3635 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 3 | 15 | 67 | 400 | 20.8 | 51.5 | 565 |  | 2020-09-16 08:43 | 44090.3635 | 20.8 | 51.5 | 565 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 08:43
2020-09-16 08:44 | 44090.3641 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 22.4 | 51 | 590 |  | 2020-09-16 08:44 | 44090.3641 | 22.4 | 51 | 590 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 08:44
2020-09-16 08:44 | 44090.3641 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 2 | 18.6 | 65.3 | 394 | 20.4 | 55.8 | 471 |  | 2020-09-16 08:44 | 44090.3641 | 20.4 | 55.8 | 471 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 08:44
2020-09-16 08:44 | 44090.3641 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 21.1 | 53.7 | 372 |  | 2020-09-16 08:44 | 44090.3641 | 21.1 | 53.7 | 372 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:44
2020-09-16 08:45 | 44090.3643 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 21.1 | 51.3 | 540 |  | 2020-09-16 08:45 | 44090.3643 | 21.1 | 51.3 | 540 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 08:44
2020-09-16 08:45 | 44090.3646 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 21.4 | 53 | 371 |  | 2020-09-16 08:45 | 44090.3646 | 21.4 | 53 | 371 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:44
2020-09-16 08:46 | 44090.365 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 22.7 | 40.9 | 402 |  | 2020-09-16 08:46 | 44090.365 | 22.7 | 40.9 | 402 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 08:45
2020-09-16 08:46 | 44090.365 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 2 | 15 | 67 | 400 | 21.4 | 48.9 | 502 |  | 2020-09-16 08:46 | 44090.365 | 21.4 | 48.9 | 502 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 08:45
2020-09-16 08:46 | 44090.3653 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 21.6 | 52.6 | 377 |  | 2020-09-16 08:46 | 44090.3653 | 21.6 | 52.6 | 377 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:46
2020-09-16 08:46 | 44090.3656 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 18 | 60 | 388 | No | 2020-09-16 08:46 | 44090.3656 | 18 | 60 | 388 |  | caution | 2020-09-14 | B14660¦¦¦Sep-16-2020 08:46
2020-09-16 08:47 | 44090.3656 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 21.4 | 48.5 | 466 |  | 2020-09-16 08:47 | 44090.3656 | 21.4 | 48.5 | 466 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 08:46
2020-09-16 08:47 | 44090.3661 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 21.7 | 52.3 | 377 |  | 2020-09-16 08:47 | 44090.3661 | 21.7 | 52.3 | 377 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:47
2020-09-16 08:47 | 44090.3661 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 50 | 590 |  | 2020-09-16 08:47 | 44090.3661 | 23 | 50 | 590 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 08:47
2020-09-16 08:48 | 44090.3664 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 22.2 | 40.9 | 398 |  | 2020-09-16 08:48 | 44090.3664 | 22.2 | 40.9 | 398 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 08:47
2020-09-16 08:48 | 44090.3664 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 21.6 | 47.2 | 482 |  | 2020-09-16 08:48 | 44090.3664 | 21.6 | 47.2 | 482 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 08:47
2020-09-16 08:49 | 44090.3673 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 22.3 | 47.4 | 470 |  | 2020-09-16 08:49 | 44090.3673 | 22.3 | 47.4 | 470 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 08:48
2020-09-16 08:49 | 44090.3674 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 20 | 55 | 415 | No | 2020-09-16 08:49 | 44090.3674 | 20 | 55 | 415 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 08:49
2020-09-16 08:50 | 44090.368 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 1 | 15.7 | 68.9 | 383 | 20 | 53 | 436 | No | 2020-09-16 08:50 | 44090.368 | 20 | 53 | 436 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 08:49
2020-09-16 08:50 | 44090.3681 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 22.2 | 46 | 447 |  | 2020-09-16 08:50 | 44090.3681 | 22.2 | 46 | 447 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 08:50
2020-09-16 08:50 | 44090.3683 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 22.2 | 41.8 | 455 |  | 2020-09-16 08:50 | 44090.3683 | 22.2 | 41.8 | 455 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 08:50
2020-09-16 08:51 | 44090.3685 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 0 | 18.6 | 65.3 | 394 | 19.9 | 54.2 | 431 |  | 2020-09-16 08:51 | 44090.3685 | 19.9 | 54.2 | 431 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 08:50
2020-09-16 08:51 | 44090.3689 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 49 | 610 |  | 2020-09-16 08:51 | 44090.3689 | 23 | 49 | 610 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 08:51
2020-09-16 08:51 | 44090.3689 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 21.6 | 52.7 | 418 |  | 2020-09-16 08:51 | 44090.3689 | 21.6 | 52.7 | 418 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:51
2020-09-16 08:52 | 44090.3694 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 21.6 | 49.5 | 422 | No | 2020-09-16 08:52 | 44090.3694 | 21.6 | 49.5 | 422 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 08:51
2020-09-16 08:52 | 44090.3695 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 21.7 | 52.3 | 398 |  | 2020-09-16 08:52 | 44090.3695 | 21.7 | 52.3 | 398 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:52
2020-09-16 08:53 | 44090.3701 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 14 | 77 | 430 | 20.2 | 53.5 | 435 |  | 2020-09-16 08:53 | 44090.3701 | 20.2 | 53.5 | 435 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:52
2020-09-16 08:53 | 44090.3702 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 22.2 | 45.3 | 468 |  | 2020-09-16 08:53 | 44090.3702 | 22.2 | 45.3 | 468 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 08:53
2020-09-16 08:53 | 44090.3702 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22 | 51.4 | 388 |  | 2020-09-16 08:53 | 44090.3702 | 22 | 51.4 | 388 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:53
2020-09-16 08:53 | 44090.3702 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 22.5 | 47.5 | 411 | No | 2020-09-16 08:53 | 44090.3702 | 22.5 | 47.5 | 411 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 08:53
2020-09-16 08:54 | 44090.3706 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.1 | 51.5 | 387 |  | 2020-09-16 08:54 | 44090.3706 | 22.1 | 51.5 | 387 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:53
2020-09-16 08:54 | 44090.3707 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 7 | 15 | 67 | 400 | 21.9 | 47.1 | 484 |  | 2020-09-16 08:54 | 44090.3707 | 21.9 | 47.1 | 484 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 08:53
2020-09-16 08:54 | 44090.3709 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 1 | 16 | 69 | 383 | 21 | 51 | 441 | No | 2020-09-16 08:54 | 44090.3709 | 21 | 51 | 441 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 08:54
2020-09-16 08:54 | 44090.3711 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 22.6 | 48.2 | 412 | No | 2020-09-16 08:54 | 44090.3711 | 22.6 | 48.2 | 412 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 08:54
2020-09-16 08:55 | 44090.3712 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.1 | 51.1 | 383 |  | 2020-09-16 08:55 | 44090.3712 | 22.1 | 51.1 | 383 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:54
2020-09-16 08:55 | 44090.3713 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 3 | 17 | 72 | 430 | 20 | 52 | 514 |  | 2020-09-16 08:55 | 44090.3713 | 20 | 52 | 514 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 08:54
2020-09-16 08:55 | 44090.3713 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 580 |  | 2020-09-16 08:55 | 44090.3713 | 23 | 48 | 580 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 08:54
2020-09-16 08:55 | 44090.3717 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 22.9 | 40.8 | 423 |  | 2020-09-16 08:55 | 44090.3717 | 22.9 | 40.8 | 423 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 08:55
2020-09-16 08:55 | 44090.3718 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 1 | 17 | 72 | 430 | 20 | 48 | 505 |  | 2020-09-16 08:55 | 44090.3718 | 20 | 48 | 505 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 08:55
2020-09-16 08:55 | 44090.3718 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 1 | 18.6 | 65.3 | 394 | 20.4 | 53.2 | 425 |  | 2020-09-16 08:55 | 44090.3718 | 20.4 | 53.2 | 425 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 08:55
2020-09-16 08:56 | 44090.372 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 21.8 | 45.8 | 464 |  | 2020-09-16 08:56 | 44090.372 | 21.8 | 45.8 | 464 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 08:55
2020-09-16 08:56 | 44090.3723 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 17 | 72 | 430 | 20 | 42 | 532 |  | 2020-09-16 08:56 | 44090.3723 | 20 | 42 | 532 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 08:56
2020-09-16 08:56 | 44090.3725 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 22.8 | 46.4 | 425 | No | 2020-09-16 08:56 | 44090.3725 | 22.8 | 46.4 | 425 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 08:56
2020-09-16 08:57 | 44090.3728 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 17 | 72 | 430 | 21 | 45 | 535 |  | 2020-09-16 08:57 | 44090.3728 | 21 | 45 | 535 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 08:56
2020-09-16 08:57 | 44090.3729 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 22.2 | 51.2 | 457 |  | 2020-09-16 08:57 | 44090.3729 | 22.2 | 51.2 | 457 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 08:56
2020-09-16 08:57 | 44090.3729 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.2 | 51 | 378 |  | 2020-09-16 08:57 | 44090.3729 | 22.2 | 51 | 378 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:57
2020-09-16 08:57 | 44090.3731 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 23 | 40.5 | 425 |  | 2020-09-16 08:57 | 44090.3731 | 23 | 40.5 | 425 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 08:57
2020-09-16 08:57 | 44090.3732 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 17 | 72 | 430 | 21 | 43 | 537 |  | 2020-09-16 08:57 | 44090.3732 | 21 | 43 | 537 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 08:57
2020-09-16 08:58 | 44090.3733 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 23.3 | 44.1 | 425 | No | 2020-09-16 08:58 | 44090.3733 | 23.3 | 44.1 | 425 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 08:57
2020-09-16 08:58 | 44090.3734 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 5 | 14 | 77 | 430 | 20 | 53 | 489 |  | 2020-09-16 08:58 | 44090.3734 | 20 | 53 | 489 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:57
2020-09-16 08:58 | 44090.3735 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.1 | 49.6 | 378 |  | 2020-09-16 08:58 | 44090.3735 | 22.1 | 49.6 | 378 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:57
2020-09-16 08:59 | 44090.3741 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22 | 50.8 | 376 |  | 2020-09-16 08:59 | 44090.3741 | 22 | 50.8 | 376 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:58
2020-09-16 08:59 | 44090.3744 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 17 | 72 | 430 | 21 | 49 | 494 |  | 2020-09-16 08:59 | 44090.3744 | 21 | 49 | 494 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 08:59
2020-09-16 08:59 | 44090.3745 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 14 | 77 | 430 | 19.6 | 53 | 470 |  | 2020-09-16 08:59 | 44090.3745 | 19.6 | 53 | 470 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 08:59
2020-09-16 09:00 | 44090.3747 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22 | 50.6 | 371 |  | 2020-09-16 09:00 | 44090.3747 | 22 | 50.6 | 371 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 08:59
2020-09-16 09:00 | 44090.3748 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 0 | 18.6 | 65.3 | 394 | 20.7 | 50.4 | 429 |  | 2020-09-16 09:00 | 44090.3748 | 20.7 | 50.4 | 429 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 08:59
2020-09-16 09:00 | 44090.3749 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 22 | 46.4 | 447 |  | 2020-09-16 09:00 | 44090.3749 | 22 | 46.4 | 447 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 08:59
2020-09-16 09:00 | 44090.3749 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 19.7 | 61.5 | 432 |  | 2020-09-16 09:00 | 44090.3749 | 19.7 | 61.5 | 432 |  | caution | 2020-09-14 | B20390¦¦¦Sep-16-2020 08:59
2020-09-16 09:00 | 44090.3753 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 22.5 | 40.5 | 435 |  | 2020-09-16 09:00 | 44090.3753 | 22.5 | 40.5 | 435 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:00
2020-09-16 09:00 | 44090.3753 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 605 |  | 2020-09-16 09:00 | 44090.3753 | 23 | 48 | 605 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 09:00
2020-09-16 09:00 | 44090.3753 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 21.8 | 51.7 | 370 |  | 2020-09-16 09:00 | 44090.3753 | 21.8 | 51.7 | 370 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:00
2020-09-16 09:01 | 44090.3754 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 17 | 72 | 430 | 22 | 47 | 480 | Couldn't get into courtroom 1,3 and 4 | 2020-09-16 09:01 | 44090.3754 | 22 | 47 | 480 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 09:00
2020-09-16 09:01 | 44090.3756 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 14 | 77 | 430 | 19.5 | 55.3 | 450 |  | 2020-09-16 09:01 | 44090.3756 | 19.5 | 55.3 | 450 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 09:00
2020-09-16 09:01 | 44090.3756 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 3 | 15 | 67 | 400 | 22.2 | 46.9 | 461 |  | 2020-09-16 09:01 | 44090.3756 | 22.2 | 46.9 | 461 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 09:00
2020-09-16 09:01 | 44090.3758 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 21.6 | 52.1 | 373 |  | 2020-09-16 09:01 | 44090.3758 | 21.6 | 52.1 | 373 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:01
2020-09-16 09:01 | 44090.3759 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 17 | 72 | 430 | 22 | 45 | 472 |  | 2020-09-16 09:01 | 44090.3759 | 22 | 45 | 472 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 09:01
2020-09-16 09:01 | 44090.376 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 22 | 48 | 418 | No | 2020-09-16 09:01 | 44090.376 | 22 | 48 | 418 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 09:01
2020-09-16 09:02 | 44090.3762 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 0 | 17.5 | 63.4 | 369 | 21 | 48 | 431 | H17 keys would not open the doors | 2020-09-16 09:02 | 44090.3762 | 21 | 48 | 431 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:01
2020-09-16 09:02 | 44090.3763 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 2 | 15 | 67 | 400 | 22.1 | 47 | 460 |  | 2020-09-16 09:02 | 44090.3763 | 22.1 | 47 | 460 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 09:01
2020-09-16 09:02 | 44090.3763 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 2 | 17 | 72 | 430 | 22 | 44 | 479 |  | 2020-09-16 09:02 | 44090.3763 | 22 | 44 | 479 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 09:01
2020-09-16 09:02 | 44090.3765 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 5 | 19 | 64.7 | 393 | 20.7 | 57.1 | 460 |  | 2020-09-16 09:02 | 44090.3765 | 20.7 | 57.1 | 460 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:02
2020-09-16 09:02 | 44090.3765 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 21.7 | 51.7 | 377 |  | 2020-09-16 09:02 | 44090.3765 | 21.7 | 51.7 | 377 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:02
2020-09-16 09:02 | 44090.3766 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 0 | 18.6 | 65.3 | 394 | 20.9 | 50 | 413 |  | 2020-09-16 09:02 | 44090.3766 | 20.9 | 50 | 413 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 09:02
2020-09-16 09:03 | 44090.3768 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 17 | 72 | 430 | 22 | 46 | 478 |  | 2020-09-16 09:03 | 44090.3768 | 22 | 46 | 478 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 09:02
2020-09-16 09:03 | 44090.377 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 21 | 48 | 392 |  | 2020-09-16 09:03 | 44090.377 | 21 | 48 | 392 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:02
2020-09-16 09:03 | 44090.3772 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 14 | 77 | 430 | 19.5 | 56 | 534 |  | 2020-09-16 09:03 | 44090.3772 | 19.5 | 56 | 534 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 09:03
2020-09-16 09:03 | 44090.3773 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 22.2 | 45.4 | 448 |  | 2020-09-16 09:03 | 44090.3773 | 22.2 | 45.4 | 448 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 09:03
2020-09-16 09:03 | 44090.3773 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 21.8 | 51.4 | 380 |  | 2020-09-16 09:03 | 44090.3773 | 21.8 | 51.4 | 380 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:03
2020-09-16 09:03 | 44090.3774 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 3 | 19 | 64.7 | 393 | 21 | 55.7 | 474 |  | 2020-09-16 09:04 | 44090.3774 | 21 | 55.7 | 474 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:03
2020-09-16 09:04 | 44090.3777 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 21.8 | 51.1 | 379 |  | 2020-09-16 09:04 | 44090.3777 | 21.8 | 51.1 | 379 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:03
2020-09-16 09:04 | 44090.378 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 3 | 17 | 72 | 430 | 22 | 47 | 548 |  | 2020-09-16 09:04 | 44090.378 | 22 | 47 | 548 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 09:04
2020-09-16 09:04 | 44090.3781 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 22.7 | 41.2 | 410 |  | 2020-09-16 09:04 | 44090.3781 | 22.7 | 41.2 | 410 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:04
2020-09-16 09:05 | 44090.3782 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 21 | 48 | 388 |  | 2020-09-16 09:05 | 44090.3782 | 21 | 48 | 388 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:04
2020-09-16 09:05 | 44090.3783 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 2 | 15 | 70 | 390 | 24 | 42.8 | 456 | No | 2020-09-16 09:05 | 44090.3783 | 24 | 42.8 | 456 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:04
2020-09-16 09:05 | 44090.3783 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 21.9 | 51.2 | 375 |  | 2020-09-16 09:05 | 44090.3783 | 21.9 | 51.2 | 375 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:04
2020-09-16 09:05 | 44090.3783 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 17 | 72 | 430 | 22 | 43 | 557 |  | 2020-09-16 09:05 | 44090.3783 | 22 | 43 | 557 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 09:04
2020-09-16 09:05 | 44090.3785 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 19 | 64.7 | 393 | 21.1 | 55 | 450 |  | 2020-09-16 09:05 | 44090.3785 | 21.1 | 55 | 450 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:05
2020-09-16 09:05 | 44090.3788 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 21.9 | 51.4 | 376 |  | 2020-09-16 09:05 | 44090.3788 | 21.9 | 51.4 | 376 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:05
2020-09-16 09:06 | 44090.3789 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 23 | 40.8 | 432 |  | 2020-09-16 09:06 | 44090.3789 | 23 | 40.8 | 432 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:05
2020-09-16 09:06 | 44090.3791 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 14 | 77 | 430 | 19.6 | 54.5 | 461 |  | 2020-09-16 09:06 | 44090.3791 | 19.6 | 54.5 | 461 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 09:05
2020-09-16 09:06 | 44090.3791 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 14 | 77 | 430 | 19.6 | 54.5 | 461 |  | 2020-09-16 09:06 | 44090.3791 | 19.6 | 54.5 | 461 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 09:05
2020-09-16 09:06 | 44090.3791 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 19 | 64.7 | 393 | 21.2 | 54.2 | 445 |  | 2020-09-16 09:06 | 44090.3791 | 21.2 | 54.2 | 445 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:05
2020-09-16 09:06 | 44090.3792 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 22.2 | 44.9 | 453 |  | 2020-09-16 09:06 | 44090.3792 | 22.2 | 44.9 | 453 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 09:06
2020-09-16 09:06 | 44090.3792 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 23.6 | 42.5 | 433 | No | 2020-09-16 09:06 | 44090.3792 | 23.6 | 42.5 | 433 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:06
2020-09-16 09:06 | 44090.3792 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22 | 50.9 | 376 |  | 2020-09-16 09:06 | 44090.3792 | 22 | 50.9 | 376 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:06
2020-09-16 09:06 | 44090.3793 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 21 | 48 | 384 |  | 2020-09-16 09:06 | 44090.3793 | 21 | 48 | 384 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:06
2020-09-16 09:06 | 44090.3794 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.5 | 47 | 440 | No | 2020-09-16 09:06 | 44090.3794 | 22.5 | 47 | 440 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 09:06
2020-09-16 09:07 | 44090.3796 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 0 | 18.6 | 65.3 | 394 | 19.3 | 50.9 | 479 | Portable air conditioner running | 2020-09-16 09:07 | 44090.3796 | 19.3 | 50.9 | 479 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 09:06
2020-09-16 09:07 | 44090.3796 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 590 |  | 2020-09-16 09:07 | 44090.3796 | 23 | 48 | 590 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 09:06
2020-09-16 09:07 | 44090.3797 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 22 | 46.9 | 497 |  | 2020-09-16 09:07 | 44090.3797 | 22 | 46.9 | 497 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 09:06
2020-09-16 09:07 | 44090.3798 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.2 | 50.3 | 377 |  | 2020-09-16 09:07 | 44090.3798 | 22.2 | 50.3 | 377 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:06
2020-09-16 09:07 | 44090.3801 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 21 | 48 | 387 |  | 2020-09-16 09:07 | 44090.3801 | 21 | 48 | 387 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:07
2020-09-16 09:08 | 44090.3802 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 21.7 | 55 | 460 |  | 2020-09-16 09:08 | 44090.3802 | 21.7 | 55 | 460 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:07
2020-09-16 09:08 | 44090.3804 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 23.5 | 43.3 | 420 | No | 2020-09-16 09:08 | 44090.3804 | 23.5 | 43.3 | 420 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:07
2020-09-16 09:08 | 44090.3804 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 21.6 | 46.3 | 520 |  | 2020-09-16 09:08 | 44090.3804 | 21.6 | 46.3 | 520 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 09:07
2020-09-16 09:08 | 44090.3805 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.2 | 47.7 | 379 |  | 2020-09-16 09:08 | 44090.3805 | 22.2 | 47.7 | 379 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:07
2020-09-16 09:08 | 44090.3805 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 23.2 | 40.5 | 426 |  | 2020-09-16 09:08 | 44090.3805 | 23.2 | 40.5 | 426 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:07
2020-09-16 09:08 | 44090.3807 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 4 | 14 | 77 | 430 | 19.8 | 54 | 490 |  | 2020-09-16 09:08 | 44090.3807 | 19.8 | 54 | 490 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 09:08
2020-09-16 09:08 | 44090.3809 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.1 | 48.5 | 377 |  | 2020-09-16 09:08 | 44090.3809 | 22.1 | 48.5 | 377 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:08
2020-09-16 09:09 | 44090.3811 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 21.7 | 46.1 | 460 |  | 2020-09-16 09:09 | 44090.3811 | 21.7 | 46.1 | 460 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 09:08
2020-09-16 09:09 | 44090.3812 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 4 | 19 | 64.7 | 393 | 21.9 | 53.7 | 466 |  | 2020-09-16 09:09 | 44090.3812 | 21.9 | 53.7 | 466 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:08
2020-09-16 09:09 | 44090.3813 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 2 | 18.6 | 65.3 | 304 | 20.2 | 53.7 | 556 | Portable air conditioner running | 2020-09-16 09:09 | 44090.3813 | 20.2 | 53.7 | 556 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 09:09
2020-09-16 09:09 | 44090.3813 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22 | 48.4 | 374 |  | 2020-09-16 09:09 | 44090.3813 | 22 | 48.4 | 374 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:09
2020-09-16 09:09 | 44090.3814 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 12 | 16.2 | 79.4 | 388 | 22.9 | 51.2 | 440 | No | 2020-09-16 09:09 | 44090.3814 | 22.9 | 51.2 | 440 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:09
2020-09-16 09:10 | 44090.3818 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 21.8 | 45.8 | 447 |  | 2020-09-16 09:10 | 44090.3818 | 21.8 | 45.8 | 447 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 09:09
2020-09-16 09:10 | 44090.3821 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 3 | 19 | 64.7 | 393 | 22.1 | 53.6 | 475 |  | 2020-09-16 09:10 | 44090.3821 | 22.1 | 53.6 | 475 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:10
2020-09-16 09:10 | 44090.3821 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 23 | 45 | 415 | No | 2020-09-16 09:10 | 44090.3821 | 23 | 45 | 415 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:10
2020-09-16 09:10 | 44090.3822 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 1 | 16 | 69 | 383 | 21 | 49 | 431 | No | 2020-09-16 09:10 | 44090.3822 | 21 | 49 | 431 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 09:10
2020-09-16 09:11 | 44090.3825 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 21.9 | 47.3 | 458 |  | 2020-09-16 09:11 | 44090.3825 | 21.9 | 47.3 | 458 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 09:10
2020-09-16 09:11 | 44090.3825 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.2 | 50.4 | 376 |  | 2020-09-16 09:11 | 44090.3825 | 22.2 | 50.4 | 376 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:10
2020-09-16 09:11 | 44090.3825 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 23.4 | 40 | 455 |  | 2020-09-16 09:11 | 44090.3825 | 23.4 | 40 | 455 |  | caution | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:10
2020-09-16 09:11 | 44090.3829 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 0 | 18.6 | 65.3 | 394 | 20.5 | 51.1 | 433 |  | 2020-09-16 09:11 | 44090.3829 | 20.5 | 51.1 | 433 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 09:11
2020-09-16 09:12 | 44090.383 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.3 | 50.4 | 376 |  | 2020-09-16 09:12 | 44090.383 | 22.3 | 50.4 | 376 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:11
2020-09-16 09:12 | 44090.3831 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 15 | 67 | 400 | 22.1 | 44.7 | 469 |  | 2020-09-16 09:12 | 44090.3831 | 22.1 | 44.7 | 469 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 09:11
2020-09-16 09:12 | 44090.3832 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 4 | 16.2 | 79.4 | 388 | 23.2 | 51.4 | 455 | No | 2020-09-16 09:12 | 44090.3832 | 23.2 | 51.4 | 455 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:11
2020-09-16 09:12 | 44090.3835 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.3 | 50.3 | 376 |  | 2020-09-16 09:12 | 44090.3835 | 22.3 | 50.3 | 376 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:12
2020-09-16 09:13 | 44090.3838 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 19 | 64.7 | 393 | 22 | 53.8 | 515 |  | 2020-09-16 09:13 | 44090.3838 | 22 | 53.8 | 515 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:12
2020-09-16 09:13 | 44090.3838 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 73.4 | 369 | 22 | 47 | 380 |  | 2020-09-16 09:13 | 44090.3838 | 22 | 47 | 380 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:12
2020-09-16 09:13 | 44090.3839 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 0 | 18.6 | 65.3 | 394 | 20.4 | 52.2 | 438 |  | 2020-09-16 09:13 | 44090.3839 | 20.4 | 52.2 | 438 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 09:12
2020-09-16 09:13 | 44090.384 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.3 | 50 | 378 |  | 2020-09-16 09:13 | 44090.384 | 22.3 | 50 | 378 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:12
2020-09-16 09:13 | 44090.384 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 23.5 | 40.3 | 470 |  | 2020-09-16 09:13 | 44090.384 | 23.5 | 40.3 | 470 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:13
2020-09-16 09:13 | 44090.3842 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 22.8 | 44.7 | 412 | No | 2020-09-16 09:13 | 44090.3842 | 22.8 | 44.7 | 412 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:13
2020-09-16 09:14 | 44090.3849 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.3 | 49.6 | 385 |  | 2020-09-16 09:14 | 44090.3849 | 22.3 | 49.6 | 385 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:14
2020-09-16 09:14 | 44090.3849 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 22 | 50.6 | 462 |  | 2020-09-16 09:14 | 44090.3849 | 22 | 50.6 | 462 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:14
2020-09-16 09:14 | 44090.385 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 22 | 48 | 424 | No | 2020-09-16 09:14 | 44090.385 | 22 | 48 | 424 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 09:14
2020-09-16 09:15 | 44090.3854 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 21.5 | 45.5 | 417 | No | 2020-09-16 09:15 | 44090.3854 | 21.5 | 45.5 | 417 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:15
2020-09-16 09:15 | 44090.3857 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.4 | 49.4 | 385 |  | 2020-09-16 09:15 | 44090.3857 | 22.4 | 49.4 | 385 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:15
2020-09-16 09:16 | 44090.3859 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 0 | 18.6 | 65.3 | 394 | 20.2 | 53.3 | 458 |  | 2020-09-16 09:16 | 44090.3859 | 20.2 | 53.3 | 458 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 09:15
2020-09-16 09:16 | 44090.3861 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 23.5 | 40.2 | 454 |  | 2020-09-16 09:16 | 44090.3861 | 23.5 | 40.2 | 454 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:15
2020-09-16 09:16 | 44090.3862 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 0 | 16.2 | 79.4 | 388 | 22.6 | 51.3 | 406 | No | 2020-09-16 09:16 | 44090.3862 | 22.6 | 51.3 | 406 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:16
2020-09-16 09:16 | 44090.3862 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.4 | 50 | 395 |  | 2020-09-16 09:16 | 44090.3862 | 22.4 | 50 | 395 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:16
2020-09-16 09:16 | 44090.3863 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 22.1 | 49.2 | 411 |  | 2020-09-16 09:16 | 44090.3863 | 22.1 | 49.2 | 411 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:16
2020-09-16 09:16 | 44090.3864 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 47 | 384 |  | 2020-09-16 09:16 | 44090.3864 | 22 | 47 | 384 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:16
2020-09-16 09:17 | 44090.387 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 22.3 | 50 | 405 |  | 2020-09-16 09:17 | 44090.387 | 22.3 | 50 | 405 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:17
2020-09-16 09:17 | 44090.387 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 1 | 17 | 71 | 380 | 22.1 | 49.8 | 401 |  | 2020-09-16 09:17 | 44090.387 | 22.1 | 49.8 | 401 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:17
2020-09-16 09:18 | 44090.3873 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 23.6 | 39.7 | 455 |  | 2020-09-16 09:18 | 44090.3873 | 23.6 | 39.7 | 455 |  | caution | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:17
2020-09-16 09:18 | 44090.3875 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 1 | 17 | 71 | 380 | 22.2 | 49.7 | 412 |  | 2020-09-16 09:18 | 44090.3875 | 22.2 | 49.7 | 412 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:17
2020-09-16 09:18 | 44090.3876 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 21 | 49 | 436 | No | 2020-09-16 09:18 | 44090.3876 | 21 | 49 | 436 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 09:18
2020-09-16 09:18 | 44090.3877 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 21.2 | 49.8 | 411 | No | 2020-09-16 09:18 | 44090.3877 | 21.2 | 49.8 | 411 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:18
2020-09-16 09:19 | 44090.3879 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 1 | 17 | 71 | 380 | 22.3 | 49.6 | 414 |  | 2020-09-16 09:19 | 44090.3879 | 22.3 | 49.6 | 414 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:18
2020-09-16 09:19 | 44090.388 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 22.5 | 49.6 | 400 |  | 2020-09-16 09:19 | 44090.388 | 22.5 | 49.6 | 400 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:18
2020-09-16 09:19 | 44090.3881 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 590 |  | 2020-09-16 09:19 | 44090.3881 | 23 | 48 | 590 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 09:18
2020-09-16 09:19 | 44090.3882 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 45 | 376 |  | 2020-09-16 09:19 | 44090.3882 | 22 | 45 | 376 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:19
2020-09-16 09:19 | 44090.3883 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 16.2 | 79.4 | 388 | 23 | 47.2 | 403 | No | 2020-09-16 09:19 | 44090.3883 | 23 | 47.2 | 403 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:19
2020-09-16 09:19 | 44090.3883 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 2 | 17 | 71 | 380 | 22.4 | 50 | 411 |  | 2020-09-16 09:19 | 44090.3883 | 22.4 | 50 | 411 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:19
2020-09-16 09:20 | 44090.3888 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 22.3 | 49.8 | 399 |  | 2020-09-16 09:20 | 44090.3888 | 22.3 | 49.8 | 399 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:19
2020-09-16 09:20 | 44090.3889 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 1 | 17 | 71 | 380 | 22.4 | 49.5 | 408 |  | 2020-09-16 09:20 | 44090.3889 | 22.4 | 49.5 | 408 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:20
2020-09-16 09:20 | 44090.3891 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 23.6 | 39.7 | 476 |  | 2020-09-16 09:20 | 44090.3891 | 23.6 | 39.7 | 476 |  | caution | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:20
2020-09-16 09:21 | 44090.3895 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.5 | 49.2 | 408 |  | 2020-09-16 09:21 | 44090.3895 | 22.5 | 49.2 | 408 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:20
2020-09-16 09:21 | 44090.3896 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 45 | 380 |  | 2020-09-16 09:21 | 44090.3896 | 22 | 45 | 380 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:21
2020-09-16 09:21 | 44090.3897 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 21.8 | 50.6 | 406 |  | 2020-09-16 09:21 | 44090.3897 | 21.8 | 50.6 | 406 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:21
2020-09-16 09:21 | 44090.3897 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 4 | 16 | 69 | 383 | 21 | 52 | 551 | No | 2020-09-16 09:21 | 44090.3897 | 21 | 52 | 551 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 09:21
2020-09-16 09:21 | 44090.3898 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 4 | 15 | 70 | 390 | 23.2 | 44.6 | 426 | No | 2020-09-16 09:21 | 44090.3898 | 23.2 | 44.6 | 426 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:21
2020-09-16 09:22 | 44090.3902 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.2 | 48.2 | 400 |  | 2020-09-16 09:22 | 44090.3902 | 22.2 | 48.2 | 400 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:21
2020-09-16 09:22 | 44090.3903 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 46 | 374 |  | 2020-09-16 09:22 | 44090.3903 | 22 | 46 | 374 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:22
2020-09-16 09:22 | 44090.3904 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 3 | 16.2 | 79.4 | 388 | 22.6 | 46 | 400 | No | 2020-09-16 09:22 | 44090.3904 | 22.6 | 46 | 400 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:22
2020-09-16 09:22 | 44090.3905 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 5 | 18 | 59 | 395 | 23 | 46 | 540 |  | 2020-09-16 09:22 | 44090.3905 | 23 | 46 | 540 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 09:22
2020-09-16 09:22 | 44090.3906 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 22 | 50.8 | 405 |  | 2020-09-16 09:22 | 44090.3906 | 22 | 50.8 | 405 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:22
2020-09-16 09:23 | 44090.3907 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 48 | 590 | 23 | 48 | 590 |  | 2020-09-16 09:23 | 44090.3907 | 23 | 48 | 590 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 09:22
2020-09-16 09:23 | 44090.3907 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 22.1 | 49.5 | 387 |  | 2020-09-16 09:23 | 44090.3907 | 22.1 | 49.5 | 387 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:22
2020-09-16 09:23 | 44090.3911 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 19.8 | 57.6 | 444 |  | 2020-09-16 09:23 | 44090.3911 | 19.8 | 57.6 | 444 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 09:23
2020-09-16 09:23 | 44090.3911 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 21.7 | 50.1 | 388 |  | 2020-09-16 09:23 | 44090.3911 | 21.7 | 50.1 | 388 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:23
2020-09-16 09:24 | 44090.3914 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 17.9 | 66.3 | 414 | 20.3 | 55.5 | 451 |  | 2020-09-16 09:24 | 44090.3914 | 20.3 | 55.5 | 451 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 09:23
2020-09-16 09:24 | 44090.3914 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 21.8 | 50.8 | 402 |  | 2020-09-16 09:24 | 44090.3914 | 21.8 | 50.8 | 402 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:23
2020-09-16 09:24 | 44090.3916 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 17 | 71 | 380 | 21.9 | 50.6 | 387 |  | 2020-09-16 09:24 | 44090.3916 | 21.9 | 50.6 | 387 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 09:23
2020-09-16 09:24 | 44090.3918 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 46 | 371 |  | 2020-09-16 09:24 | 44090.3918 | 22 | 46 | 371 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:24
2020-09-16 09:24 | 44090.3919 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 16.2 | 79.4 | 388 | 23.4 | 48.1 | 406 | No | 2020-09-16 09:24 | 44090.3919 | 23.4 | 48.1 | 406 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:24
2020-09-16 09:25 | 44090.3921 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.7 | 67.7 | 375 | 23.5 | 39.9 | 478 |  | 2020-09-16 09:25 | 44090.3921 | 23.5 | 39.9 | 478 |  | caution | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:24
2020-09-16 09:25 | 44090.3923 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 24.4 | 41.2 | 468 | No | 2020-09-16 09:25 | 44090.3923 | 24.4 | 41.2 | 468 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:24
2020-09-16 09:25 | 44090.3924 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 46 | 371 |  | 2020-09-16 09:25 | 44090.3924 | 22 | 46 | 371 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:25
2020-09-16 09:25 | 44090.3926 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 21 | 50 | 528 | No | 2020-09-16 09:25 | 44090.3926 | 21 | 50 | 528 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 09:25
2020-09-16 09:25 | 44090.3927 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 18 | 59 | 395 | 21 | 51 | 483 |  | 2020-09-16 09:25 | 44090.3927 | 21 | 51 | 483 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 09:25
2020-09-16 09:26 | 44090.3929 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 22.5 | 49.7 | 400 |  | 2020-09-16 09:26 | 44090.3929 | 22.5 | 49.7 | 400 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:25
2020-09-16 09:26 | 44090.3931 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 24.2 | 41.1 | 463 | No | 2020-09-16 09:26 | 44090.3931 | 24.2 | 41.1 | 463 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:26
2020-09-16 09:26 | 44090.3934 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 16.7 | 67.7 | 375 | 23.5 | 39.8 | 459 |  | 2020-09-16 09:26 | 44090.3934 | 23.5 | 39.8 | 459 |  | caution | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:26
2020-09-16 09:27 | 44090.3935 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 1 | 18 | 67.7 | 436 | 21.3 | 50.7 | 463 | No | 2020-09-16 09:27 | 44090.3935 | 21.3 | 50.7 | 463 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 09:26
2020-09-16 09:27 | 44090.3936 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 17.9 | 66.3 | 414 | 20.3 | 56.1 | 449 |  | 2020-09-16 09:27 | 44090.3936 | 20.3 | 56.1 | 449 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 09:26
2020-09-16 09:27 | 44090.3938 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 22.3 | 49.1 | 404 |  | 2020-09-16 09:27 | 44090.3938 | 22.3 | 49.1 | 404 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:27
2020-09-16 09:27 | 44090.3939 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 595 |  | 2020-09-16 09:27 | 44090.3939 | 23 | 48 | 595 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 09:27
2020-09-16 09:27 | 44090.3939 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 24.4 | 41.2 | 467 | No | 2020-09-16 09:27 | 44090.3939 | 24.4 | 41.2 | 467 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:27
2020-09-16 09:28 | 44090.3942 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 1 | 16 | 69 | 383 | 21.5 | 50 | 475 | No | 2020-09-16 09:28 | 44090.3942 | 21.5 | 50 | 475 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 09:27
2020-09-16 09:28 | 44090.3943 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 16.2 | 79.4 | 388 | 22.1 | 52 | 499 | No | 2020-09-16 09:28 | 44090.3943 | 22.1 | 52 | 499 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:27
2020-09-16 09:28 | 44090.3944 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 22 | 49.8 | 409 |  | 2020-09-16 09:28 | 44090.3944 | 22 | 49.8 | 409 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:27
2020-09-16 09:28 | 44090.3946 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 23.3 | 46 | 393 |  | 2020-09-16 09:28 | 44090.3946 | 23.3 | 46 | 393 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:28
2020-09-16 09:28 | 44090.3946 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 1 | 15 | 70 | 390 | 24.5 | 42.1 | 472 | No | 2020-09-16 09:28 | 44090.3946 | 24.5 | 42.1 | 472 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:28
2020-09-16 09:28 | 44090.3947 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 22.6 | 48 | 403 |  | 2020-09-16 09:28 | 44090.3947 | 22.6 | 48 | 403 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:28
2020-09-16 09:29 | 44090.3949 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 46 | 367 |  | 2020-09-16 09:29 | 44090.3949 | 22 | 46 | 367 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:28
2020-09-16 09:29 | 44090.3951 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 17.9 | 66.3 | 414 | 21.2 | 54 | 459 |  | 2020-09-16 09:29 | 44090.3951 | 21.2 | 54 | 459 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 09:28
2020-09-16 09:30 | 44090.3955 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 22.1 | 49.7 | 403 |  | 2020-09-16 09:30 | 44090.3955 | 22.1 | 49.7 | 403 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:29
2020-09-16 09:30 | 44090.3956 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 22 | 48.8 | 458 |  | 2020-09-16 09:30 | 44090.3956 | 22 | 48.8 | 458 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 09:29
2020-09-16 09:30 | 44090.3957 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 20 | 57 | 453 |  | 2020-09-16 09:30 | 44090.3957 | 20 | 57 | 453 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:29
2020-09-16 09:30 | 44090.3957 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 46 | 368 |  | 2020-09-16 09:30 | 44090.3957 | 22 | 46 | 368 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:29
2020-09-16 09:30 | 44090.3959 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 16.2 | 79.4 | 388 | 22.3 | 55.9 | 413 | No | 2020-09-16 09:30 | 44090.3959 | 22.3 | 55.9 | 413 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:30
2020-09-16 09:31 | 44090.3963 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 23.6 | 40.4 | 408 |  | 2020-09-16 09:31 | 44090.3963 | 23.6 | 40.4 | 408 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:30
2020-09-16 09:31 | 44090.3964 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 17.9 | 66.3 | 414 | 21.8 | 51.3 | 450 |  | 2020-09-16 09:31 | 44090.3964 | 21.8 | 51.3 | 450 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 09:30
2020-09-16 09:31 | 44090.3965 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 22 | 50.4 | 398 |  | 2020-09-16 09:31 | 44090.3965 | 22 | 50.4 | 398 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:31
2020-09-16 09:31 | 44090.3967 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 46 | 368 |  | 2020-09-16 09:31 | 44090.3967 | 22 | 46 | 368 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:31
2020-09-16 09:31 | 44090.3968 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 2 | 20 | 62 | 400 | 21 | 54 | 607 |  | 2020-09-16 09:31 | 44090.3968 | 21 | 54 | 607 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:31
2020-09-16 09:32 | 44090.3973 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 2 | 18 | 67.7 | 436 | 22.2 | 48.2 | 460 |  | 2020-09-16 09:32 | 44090.3973 | 22.2 | 48.2 | 460 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 09:32
2020-09-16 09:32 | 44090.3974 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 580 |  | 2020-09-16 09:32 | 44090.3974 | 23 | 48 | 580 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 09:32
2020-09-16 09:32 | 44090.3975 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 46 | 365 |  | 2020-09-16 09:32 | 44090.3975 | 22 | 46 | 365 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:32
2020-09-16 09:32 | 44090.3976 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 17.9 | 66.3 | 414 | 21.7 | 50.5 | 448 |  | 2020-09-16 09:32 | 44090.3976 | 21.7 | 50.5 | 448 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 09:32
2020-09-16 09:33 | 44090.3976 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 23.7 | 41.4 | 450 | No | 2020-09-16 09:33 | 44090.3976 | 23.7 | 41.4 | 450 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:32
2020-09-16 09:33 | 44090.3977 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.3 | 67.7 | 375 | 23.6 | 39.7 | 395 |  | 2020-09-16 09:33 | 44090.3977 | 23.6 | 39.7 | 395 |  | caution | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:32
2020-09-16 09:33 | 44090.3979 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 21 | 55 | 484 |  | 2020-09-16 09:33 | 44090.3979 | 21 | 55 | 484 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:33
2020-09-16 09:33 | 44090.3981 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 22.2 | 49.3 | 419 |  | 2020-09-16 09:33 | 44090.3981 | 22.2 | 49.3 | 419 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:33
2020-09-16 09:34 | 44090.3984 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 16.2 | 79.4 | 388 | 23.5 | 47.5 | 463 | No | 2020-09-16 09:34 | 44090.3984 | 23.5 | 47.5 | 463 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:33
2020-09-16 09:34 | 44090.3984 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 21 | 54 | 483 |  | 2020-09-16 09:34 | 44090.3984 | 21 | 54 | 483 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:33
2020-09-16 09:34 | 44090.3986 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 23.6 | 42.4 | 446 | No | 2020-09-16 09:34 | 44090.3986 | 23.6 | 42.4 | 446 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:34
2020-09-16 09:34 | 44090.3987 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 21.6 | 49.1 | 431 |  | 2020-09-16 09:34 | 44090.3987 | 21.6 | 49.1 | 431 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 09:34
2020-09-16 09:34 | 44090.3987 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 17.9 | 66.3 | 414 | 22.6 | 50.3 | 452 |  | 2020-09-16 09:34 | 44090.3987 | 22.6 | 50.3 | 452 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 09:34
2020-09-16 09:35 | 44090.399 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 22.3 | 49.4 | 420 |  | 2020-09-16 09:35 | 44090.399 | 22.3 | 49.4 | 420 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:34
2020-09-16 09:35 | 44090.3992 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 22 | 52 | 475 |  | 2020-09-16 09:35 | 44090.3992 | 22 | 52 | 475 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:34
2020-09-16 09:35 | 44090.3993 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.7 | 67.7 | 375 | 23.2 | 40.7 | 440 |  | 2020-09-16 09:35 | 44090.3993 | 23.2 | 40.7 | 440 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:34
2020-09-16 09:36 | 44090.3998 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 18.9 | 64 | 374 | 20.9 | 52.6 | 395 |  | 2020-09-16 09:36 | 44090.3998 | 20.9 | 52.6 | 395 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 09:35
2020-09-16 09:36 | 44090.3998 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 23.4 | 46.6 | 431 |  | 2020-09-16 09:36 | 44090.3998 | 23.4 | 46.6 | 431 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:35
2020-09-16 09:36 | 44090.3999 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 22 | 53 | 472 |  | 2020-09-16 09:36 | 44090.3999 | 22 | 53 | 472 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:35
2020-09-16 09:36 | 44090.3999 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 17.9 | 66.3 | 414 | 21.7 | 51.7 | 459 |  | 2020-09-16 09:36 | 44090.3999 | 21.7 | 51.7 | 459 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 09:35
2020-09-16 09:36 | 44090.4 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 19 | 64.7 | 393 | 22 | 49.1 | 406 |  | 2020-09-16 09:36 | 44090.4 | 22 | 49.1 | 406 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 09:35
2020-09-16 09:36 | 44090.4 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 16.2 | 79.4 | 388 | 23.3 | 49 | 481 | No | 2020-09-16 09:36 | 44090.4 | 23.3 | 49 | 481 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:35
2020-09-16 09:36 | 44090.4 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 605 |  | 2020-09-16 09:36 | 44090.4 | 23 | 48 | 605 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 09:35
2020-09-16 09:36 | 44090.4001 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 21.3 | 48.1 | 431 |  | 2020-09-16 09:36 | 44090.4001 | 21.3 | 48.1 | 431 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 09:36
2020-09-16 09:36 | 44090.4001 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 0 | 18 | 63.9 | 400 | 21.2 | 56.3 | 438 |  | 2020-09-16 09:36 | 44090.4001 | 21.2 | 56.3 | 438 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 09:36
2020-09-16 09:37 | 44090.4008 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.7 | 67.7 | 375 | 23.8 | 39.7 | 416 |  | 2020-09-16 09:37 | 44090.4008 | 23.8 | 39.7 | 416 |  | caution | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:37
2020-09-16 09:37 | 44090.4009 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 0 | 22.2 | 33.6 | 417 | 23 | 34.5 | 493 |  | 2020-09-16 09:37 | 44090.4009 | 23 | 34.5 | 493 |  | low | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:37
2020-09-16 09:38 | 44090.4012 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 0 | 18.9 | 64 | 374 | 21.4 | 54.7 | 422 |  | 2020-09-16 09:38 | 44090.4012 | 21.4 | 54.7 | 422 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 09:37
2020-09-16 09:38 | 44090.4012 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 3 | 16.2 | 79.4 | 388 | 23.3 | 46.6 | 418 | No | 2020-09-16 09:38 | 44090.4012 | 23.3 | 46.6 | 418 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:37
2020-09-16 09:38 | 44090.4014 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 17.9 | 66.3 | 414 | 21.7 | 51.8 | 439 |  | 2020-09-16 09:38 | 44090.4014 | 21.7 | 51.8 | 439 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 09:38
2020-09-16 09:38 | 44090.4016 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 23.4 | 47.9 | 434 |  | 2020-09-16 09:38 | 44090.4016 | 23.4 | 47.9 | 434 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:38
2020-09-16 09:39 | 44090.4018 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 2 | 18 | 63.9 | 400 | 22.5 | 51.7 | 496 |  | 2020-09-16 09:39 | 44090.4018 | 22.5 | 51.7 | 496 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 09:38
2020-09-16 09:39 | 44090.4019 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 2 | 18.5 | 62.8 | 403 | 21.3 | 52.5 | 627 |  | 2020-09-16 09:39 | 44090.4019 | 21.3 | 52.5 | 627 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 09:38
2020-09-16 09:39 | 44090.402 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 22.8 | 48.7 | 452 |  | 2020-09-16 09:39 | 44090.402 | 22.8 | 48.7 | 452 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:38
2020-09-16 09:39 | 44090.4021 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 21.3 | 48.1 | 435 |  | 2020-09-16 09:39 | 44090.4021 | 21.3 | 48.1 | 435 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 09:39
2020-09-16 09:40 | 44090.4025 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 17.9 | 66.3 | 414 | 21.1 | 54.7 | 495 |  | 2020-09-16 09:40 | 44090.4025 | 21.1 | 54.7 | 495 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 09:39
2020-09-16 09:40 | 44090.4025 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 0 | 18.9 | 64 | 374 | 22 | 54.4 | 453 |  | 2020-09-16 09:40 | 44090.4025 | 22 | 54.4 | 453 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 09:39
2020-09-16 09:40 | 44090.4026 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 46 | 372 |  | 2020-09-16 09:40 | 44090.4026 | 22 | 46 | 372 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:39
2020-09-16 09:40 | 44090.4028 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 1 | 16.3 | 61.6 | 414 | 22 | 44.5 | 424 | 101 in session | 2020-09-16 09:40 | 44090.4028 | 22 | 44.5 | 424 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 09:40
2020-09-16 09:40 | 44090.4031 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 22.8 | 49 | 457 |  | 2020-09-16 09:40 | 44090.4031 | 22.8 | 49 | 457 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:40
2020-09-16 09:41 | 44090.4037 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 21.7 | 48 | 441 |  | 2020-09-16 09:41 | 44090.4037 | 21.7 | 48 | 441 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 09:41
2020-09-16 09:42 | 44090.4038 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 1 | 15 | 70 | 390 | 23.6 | 43.3 | 550 | No | 2020-09-16 09:42 | 44090.4038 | 23.6 | 43.3 | 550 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:41
2020-09-16 09:42 | 44090.4039 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 7 | 16.2 | 79.4 | 388 | 23 | 44.6 | 451 | No | 2020-09-16 09:42 | 44090.4039 | 23 | 44.6 | 451 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:41
2020-09-16 09:42 | 44090.4039 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 17.9 | 66.3 | 414 | 21.3 | 54.7 | 545 |  | 2020-09-16 09:42 | 44090.4039 | 21.3 | 54.7 | 545 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 09:41
2020-09-16 09:42 | 44090.4039 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 0 | 18.9 | 64 | 374 | 21.8 | 52.5 | 435 |  | 2020-09-16 09:42 | 44090.4039 | 21.8 | 52.5 | 435 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 09:41
2020-09-16 09:42 | 44090.4042 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 23.1 | 48.5 | 420 |  | 2020-09-16 09:42 | 44090.4042 | 23.1 | 48.5 | 420 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:42
2020-09-16 09:43 | 44090.4045 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 16.7 | 67.7 | 375 | 24.5 | 39 | 480 |  | 2020-09-16 09:43 | 44090.4045 | 24.5 | 39 | 480 |  | caution | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:42
2020-09-16 09:43 | 44090.4046 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 1 | 18 | 63.9 | 400 | 23.2 | 49 | 455 |  | 2020-09-16 09:43 | 44090.4046 | 23.2 | 49 | 455 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 09:42
2020-09-16 09:43 | 44090.4047 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 45 | 364 |  | 2020-09-16 09:43 | 44090.4047 | 22 | 45 | 364 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:42
2020-09-16 09:43 | 44090.405 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 18.9 | 64 | 374 | 20.8 | 52.8 | 420 |  | 2020-09-16 09:43 | 44090.405 | 20.8 | 52.8 | 420 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 09:43
2020-09-16 09:43 | 44090.4051 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 23.1 | 43 | 444 | No | 2020-09-16 09:43 | 44090.4051 | 23.1 | 43 | 444 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:43
2020-09-16 09:43 | 44090.4051 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 1 | 16 | 69 | 383 | 20 | 57.6 | 498 | No | 2020-09-16 09:43 | 44090.4051 | 20 | 57.6 | 498 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 09:43
2020-09-16 09:44 | 44090.4052 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 21.8 | 48.5 | 474 |  | 2020-09-16 09:43 | 44090.4052 | 21.8 | 48.5 | 474 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 09:43
2020-09-16 09:44 | 44090.4053 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 22.8 | 49.6 | 472 |  | 2020-09-16 09:44 | 44090.4053 | 22.8 | 49.6 | 472 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:43
2020-09-16 09:44 | 44090.4054 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 4 | 16.2 | 47.5 | 388 | 21.8 | 42.4 | 417 | No | 2020-09-16 09:44 | 44090.4054 | 21.8 | 42.4 | 417 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:43
2020-09-16 09:45 | 44090.406 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 23.2 | 48.9 | 470 |  | 2020-09-16 09:45 | 44090.406 | 23.2 | 48.9 | 470 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:44
2020-09-16 09:45 | 44090.4061 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 3 | 18.5 | 62.8 | 403 | 21.2 | 51.1 | 537 |  | 2020-09-16 09:45 | 44090.4061 | 21.2 | 51.1 | 537 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 09:44
2020-09-16 09:45 | 44090.4062 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 45 | 369 |  | 2020-09-16 09:45 | 44090.4062 | 22 | 45 | 369 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:44
2020-09-16 09:45 | 44090.4062 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 3 | 18.9 | 64 | 374 | 20.8 | 56.2 | 459 |  | 2020-09-16 09:45 | 44090.4062 | 20.8 | 56.2 | 459 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 09:45
2020-09-16 09:45 | 44090.4063 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 16.7 | 67.7 | 375 | 23.8 | 39.8 | 496 |  | 2020-09-16 09:45 | 44090.4063 | 23.8 | 39.8 | 496 |  | caution | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:45
2020-09-16 09:45 | 44090.4064 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 3 | 16.2 | 79.4 | 388 | 23.1 | 50.5 | 379 | No | 2020-09-16 09:45 | 44090.4064 | 23.1 | 50.5 | 379 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:45
2020-09-16 09:45 | 44090.4064 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 17.9 | 66.3 | 414 | 20.9 | 57.3 | 493 |  | 2020-09-16 09:45 | 44090.4064 | 20.9 | 57.3 | 493 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 09:45
2020-09-16 09:45 | 44090.4065 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 23 | 49.1 | 482 |  | 2020-09-16 09:45 | 44090.4065 | 23 | 49.1 | 482 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:45
2020-09-16 09:45 | 44090.4066 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 1 | 16.3 | 61.6 | 414 | 21 | 46.7 | 411 | 101 in session | 2020-09-16 09:45 | 44090.4066 | 21 | 46.7 | 411 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 09:45
2020-09-16 09:45 | 44090.4066 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 1 | 15 | 70 | 390 | 23.2 | 43.6 | 498 | No | 2020-09-16 09:45 | 44090.4066 | 23.2 | 43.6 | 498 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:45
2020-09-16 09:46 | 44090.4067 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 1 | 18 | 63.9 | 400 | 23.4 | 48 | 442 |  | 2020-09-16 09:46 | 44090.4067 | 23.4 | 48 | 442 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 09:45
2020-09-16 09:46 | 44090.4067 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 21.9 | 47.5 | 449 |  | 2020-09-16 09:46 | 44090.4067 | 21.9 | 47.5 | 449 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 09:45
2020-09-16 09:46 | 44090.407 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 0 | 16 | 69 | 383 | 20.5 | 52 | 450 | No | 2020-09-16 09:46 | 44090.407 | 20.5 | 52 | 450 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 09:46
2020-09-16 09:47 | 44090.4075 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 45 | 378 |  | 2020-09-16 09:47 | 44090.4075 | 22 | 45 | 378 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:46
2020-09-16 09:47 | 44090.4076 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 2 | 18.9 | 64 | 374 | 20.9 | 56.1 | 473 |  | 2020-09-16 09:47 | 44090.4076 | 20.9 | 56.1 | 473 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 09:46
2020-09-16 09:47 | 44090.4076 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 16.7 | 67.7 | 375 | 23.1 | 40.3 | 502 |  | 2020-09-16 09:47 | 44090.4076 | 23.1 | 40.3 | 502 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 09:46
2020-09-16 09:47 | 44090.4076 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 3 | 18 | 59 | 395 | 22 | 48 | 452 |  | 2020-09-16 09:47 | 44090.4076 | 22 | 48 | 452 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 09:46
2020-09-16 09:47 | 44090.4078 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 2 | 18 | 67.7 | 436 | 22.1 | 48.5 | 464 |  | 2020-09-16 09:47 | 44090.4078 | 22.1 | 48.5 | 464 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 09:47
2020-09-16 09:48 | 44090.4082 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 4 | 21 | 63 | 402 | 21 | 60 | 444 |  | 2020-09-16 09:48 | 44090.4082 | 21 | 60 | 444 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 09:47
2020-09-16 09:48 | 44090.4082 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 600 |  | 2020-09-16 09:48 | 44090.4082 | 23 | 48 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 09:47
2020-09-16 09:48 | 44090.4082 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 23 | 50 | 436 | Courtroom 1 was unavailable | 2020-09-16 09:48 | 44090.4082 | 23 | 50 | 436 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:47
2020-09-16 09:48 | 44090.4084 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 17.9 | 66.3 | 414 | 21.2 | 54.4 | 507 |  | 2020-09-16 09:48 | 44090.4084 | 21.2 | 54.4 | 507 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 09:48
2020-09-16 09:48 | 44090.4084 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 3 | 18 | 61 | 400 | 19.9 | 51 | 613 |  | 2020-09-16 09:48 | 44090.4084 | 19.9 | 51 | 613 |  |  | 2020-09-14 | B21554¦¦¦Sep-16-2020 09:48
2020-09-16 09:48 | 44090.4084 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 3 | 18.5 | 62.8 | 403 | 21.9 | 50.1 | 590 |  | 2020-09-16 09:48 | 44090.4084 | 21.9 | 50.1 | 590 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 09:48
2020-09-16 09:48 | 44090.4084 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 16.2 | 79.4 | 388 | 24.2 | 47.9 | 410 | No | 2020-09-16 09:48 | 44090.4084 | 24.2 | 47.9 | 410 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:48
2020-09-16 09:48 | 44090.4084 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 22.7 | 41.7 | 467 | No | 2020-09-16 09:48 | 44090.4084 | 22.7 | 41.7 | 467 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:48
2020-09-16 09:48 | 44090.4085 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 45 | 371 |  | 2020-09-16 09:48 | 44090.4085 | 22 | 45 | 371 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:48
2020-09-16 09:48 | 44090.4086 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 2 | 18.9 | 64 | 374 | 21.6 | 56 | 467 |  | 2020-09-16 09:48 | 44090.4086 | 21.6 | 56 | 467 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 09:48
2020-09-16 09:49 | 44090.4087 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 3 | 16.3 | 61.6 | 414 | 21.5 | 45.2 | 442 | 101 in session | 2020-09-16 09:49 | 44090.4087 | 21.5 | 45.2 | 442 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 09:48
2020-09-16 09:49 | 44090.409 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 1 | 16 | 69 | 383 |  |  |  | Yes, no access to office. | 2020-09-16 09:49 | 44090.409 | [5 empty] | 2020-09-14 | B20151¦¦¦Sep-16-2020 09:48
2020-09-16 09:49 | 44090.409 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 3 | 18 | 59 | 395 | 22 | 48 | 449 |  | 2020-09-16 09:49 | 44090.409 | 22 | 48 | 449 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 09:49
2020-09-16 09:49 | 44090.409 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 4 | 21 | 63 | 402 | 22 | 53 | 440 |  | 2020-09-16 09:49 | 44090.409 | 22 | 53 | 440 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 09:49
2020-09-16 09:49 | 44090.4092 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 17.9 | 66.3 | 414 | 21.6 | 52.6 | 508 |  | 2020-09-16 09:49 | 44090.4092 | 21.6 | 52.6 | 508 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 09:49
2020-09-16 09:50 | 44090.4096 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 5 | 18 | 67.7 | 436 | 22.4 | 67.3 | 451 |  | 2020-09-16 09:50 | 44090.4096 | 22.4 | 67.3 | 451 |  | high | 2020-09-14 | B25039¦¦¦Sep-16-2020 09:49
2020-09-16 09:50 | 44090.4097 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 6 | 21 | 63 | 402 | 22 | 53 | 513 |  | 2020-09-16 09:50 | 44090.4097 | 22 | 53 | 513 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 09:49
2020-09-16 09:50 | 44090.4097 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 45 | 373 |  | 2020-09-16 09:50 | 44090.4097 | 22 | 45 | 373 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:49
2020-09-16 09:50 | 44090.4097 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 4 | 15 | 70 | 390 | 24.2 | 40.2 | 489 | No | 2020-09-16 09:50 | 44090.4097 | 24.2 | 40.2 | 489 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:50
2020-09-16 09:50 | 44090.4099 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 16.2 | 79.4 | 388 | 23.7 | 48.6 | 471 | No | 2020-09-16 09:50 | 44090.4099 | 23.7 | 48.6 | 471 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:50
2020-09-16 09:50 | 44090.4099 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 14 | 18 | 61 | 400 | 20.3 | 45 | 583 |  | 2020-09-16 09:50 | 44090.4099 | 20.3 | 45 | 583 |  |  | 2020-09-14 | B21554¦¦¦Sep-16-2020 09:50
2020-09-16 09:50 | 44090.41 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 3 | 18 | 59 | 395 | 22 | 48 | 444 |  | 2020-09-16 09:50 | 44090.41 | 22 | 48 | 444 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 09:50
2020-09-16 09:50 | 44090.41 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 18.9 | 64 | 374 | 21.6 | 53.6 | 444 |  | 2020-09-16 09:50 | 44090.41 | 21.6 | 53.6 | 444 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 09:50
2020-09-16 09:50 | 44090.41 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 2 | 20 | 62 | 400 | 23 | 51 | 427 |  | 2020-09-16 09:50 | 44090.41 | 23 | 51 | 427 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:50
2020-09-16 09:51 | 44090.4102 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 17.9 | 66.3 | 414 | 21.4 | 52.3 | 501 |  | 2020-09-16 09:51 | 44090.4102 | 21.4 | 52.3 | 501 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 09:50
2020-09-16 09:51 | 44090.4102 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 0 | 18 | 63.9 | 400 | 23.6 | 47 | 436 |  | 2020-09-16 09:51 | 44090.4102 | 23.6 | 47 | 436 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 09:50
2020-09-16 09:51 | 44090.4102 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 3 | 18.5 | 62.8 | 403 | 21.5 | 51 | 484 |  | 2020-09-16 09:51 | 44090.4102 | 21.5 | 51 | 484 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 09:50
2020-09-16 09:51 | 44090.4105 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 1 | 16.3 | 61.6 | 414 | 20.7 | 45.5 | 431 | 101 in session | 2020-09-16 09:51 | 44090.4105 | 20.7 | 45.5 | 431 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 09:51
2020-09-16 09:51 | 44090.4106 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 17.5 | 63.4 | 369 | 22 | 45 | 375 |  | 2020-09-16 09:51 | 44090.4106 | 22 | 45 | 375 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 09:51
2020-09-16 09:52 | 44090.4108 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 23 | 48 | 430 |  | 2020-09-16 09:52 | 44090.4108 | 23 | 48 | 430 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:51
2020-09-16 09:52 | 44090.4109 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 16.2 | 79.4 | 388 | 23 | 43.5 | 399 | No | 2020-09-16 09:52 | 44090.4109 | 23 | 43.5 | 399 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 09:51
2020-09-16 09:52 | 44090.4111 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 2 | 16 | 69 | 383 | 21 | 51.4 | 473 | No | 2020-09-16 09:52 | 44090.4111 | 21 | 51.4 | 473 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 09:51
2020-09-16 09:52 | 44090.4111 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 18 | 59 | 395 | 22 | 45 | 401 |  | 2020-09-16 09:52 | 44090.4111 | 22 | 45 | 401 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 09:52
2020-09-16 09:52 | 44090.4112 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 2 | 21 | 63 | 402 | 21 | 53 | 448 |  | 2020-09-16 09:52 | 44090.4112 | 21 | 53 | 448 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 09:52
2020-09-16 09:52 | 44090.4113 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 21.1 | 52.4 | 453 |  | 2020-09-16 09:52 | 44090.4113 | 21.1 | 52.4 | 453 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 09:52
2020-09-16 09:52 | 44090.4114 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 18.9 | 64 | 374 | 21.8 | 51.4 | 405 |  | 2020-09-16 09:52 | 44090.4114 | 21.8 | 51.4 | 405 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 09:52
2020-09-16 09:53 | 44090.4115 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 4 | 18 | 61 | 400 | 21.6 | 48 | 645 |  | 2020-09-16 09:53 | 44090.4115 | 21.6 | 48 | 645 |  |  | 2020-09-14 | B21554¦¦¦Sep-16-2020 09:52
2020-09-16 09:53 | 44090.4115 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 3 | 20 | 62 | 400 | 23 | 46 | 480 |  | 2020-09-16 09:53 | 44090.4115 | 23 | 46 | 480 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:52
2020-09-16 09:53 | 44090.4118 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 47 | 580 |  | 2020-09-16 09:53 | 44090.4118 | 23 | 47 | 580 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 09:52
2020-09-16 09:53 | 44090.4121 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 18 | 59 | 395 |  |  |  | Occupied no access | 2020-09-16 09:53 | 44090.4121 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 09:53
2020-09-16 09:53 | 44090.4121 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 3 | 21 | 63 | 402 | 21 | 53 | 419 |  | 2020-09-16 09:53 | 44090.4121 | 21 | 53 | 419 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 09:53
2020-09-16 09:54 | 44090.4122 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 3 | 20 | 62 | 400 | 23 | 46 | 494 |  | 2020-09-16 09:54 | 44090.4122 | 23 | 46 | 494 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:53
2020-09-16 09:54 | 44090.4123 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 2 | 18 | 63.9 | 400 | 23.6 | 47.1 | 474 |  | 2020-09-16 09:54 | 44090.4123 | 23.6 | 47.1 | 474 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 09:53
2020-09-16 09:54 | 44090.4125 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 3 | 18.5 | 62.8 | 403 | 21.7 | 51.8 | 626 |  | 2020-09-16 09:54 | 44090.4125 | 21.7 | 51.8 | 626 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 09:54
2020-09-16 09:54 | 44090.4127 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 4 | 21 | 63 | 402 | 20 | 54 | 418 |  | 2020-09-16 09:54 | 44090.4127 | 20 | 54 | 418 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 09:54
2020-09-16 09:55 | 44090.4129 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 7 | 18 | 67.7 | 436 | 22 | 47.5 | 448 |  | 2020-09-16 09:55 | 44090.4129 | 22 | 47.5 | 448 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 09:54
2020-09-16 09:55 | 44090.4131 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 22 | 53 | 448 |  | 2020-09-16 09:55 | 44090.4131 | 22 | 53 | 448 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:54
2020-09-16 09:55 | 44090.4134 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 4 | 20 | 62.4 | 387 | 21.9 | 48.1 | 484 |  | 2020-09-16 09:55 | 44090.4134 | 21.9 | 48.1 | 484 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 09:55
2020-09-16 09:55 | 44090.4134 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 1 | 16 | 69 | 383 | 21.6 | 51 | 463 | No | 2020-09-16 09:55 | 44090.4134 | 21.6 | 51 | 463 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 09:55
2020-09-16 09:55 | 44090.4135 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 1 | 16.3 | 61.6 | 414 | 21 | 45.9 | 425 | 101 in session | 2020-09-16 09:55 | 44090.4135 | 21 | 45.9 | 425 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 09:55
2020-09-16 09:55 | 44090.4135 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 22 | 53 | 444 |  | 2020-09-16 09:56 | 44090.4135 | 22 | 53 | 444 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:55
2020-09-16 09:56 | 44090.4136 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 1 | 18 | 63.9 | 400 | 23.7 | 46.7 | 457 |  | 2020-09-16 09:56 | 44090.4136 | 23.7 | 46.7 | 457 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 09:55
2020-09-16 09:56 | 44090.4137 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 2 | 21 | 63 | 402 | 20 | 59 | 446 |  | 2020-09-16 09:56 | 44090.4137 | 20 | 59 | 446 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 09:55
2020-09-16 09:56 | 44090.4138 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 24 | 38.5 | 413 | No | 2020-09-16 09:56 | 44090.4138 | 24 | 38.5 | 413 |  | caution | 2020-09-14 | B14660¦¦¦Sep-16-2020 09:55
2020-09-16 09:56 | 44090.4138 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 4 | 17 | 71.7 | 391 | 22.5 | 49.3 | 515 |  | 2020-09-16 09:56 | 44090.4138 | 22.5 | 49.3 | 515 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:55
2020-09-16 09:56 | 44090.4139 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 23 | 48.4 | 507 |  | 2020-09-16 09:56 | 44090.4139 | 23 | 48.4 | 507 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:55
2020-09-16 09:56 | 44090.4139 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 2 | 18.5 | 62.8 | 403 | 21.7 | 50.4 | 539 |  | 2020-09-16 09:56 | 44090.4139 | 21.7 | 50.4 | 539 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 09:56
2020-09-16 09:56 | 44090.4142 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 22 | 54 | 437 |  | 2020-09-16 09:56 | 44090.4142 | 22 | 54 | 437 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:56
2020-09-16 09:56 | 44090.4142 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 3 | 21 | 63 | 402 | 21 | 61 | 434 |  | 2020-09-16 09:56 | 44090.4142 | 21 | 61 | 434 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 09:56
2020-09-16 09:57 | 44090.4147 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 22.5 | 49.1 | 516 |  | 2020-09-16 09:57 | 44090.4147 | 22.5 | 49.1 | 516 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:57
2020-09-16 09:57 | 44090.4148 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 22 | 58 | 429 |  | 2020-09-16 09:57 | 44090.4148 | 22 | 58 | 429 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 09:57
2020-09-16 09:57 | 44090.4149 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 1 | 18.5 | 62.8 | 403 | 21.8 | 48.7 | 518 |  | 2020-09-16 09:57 | 44090.4149 | 21.8 | 48.7 | 518 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 09:57
2020-09-16 09:57 | 44090.4149 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 484 | 22.7 | 48.2 | 501 |  | 2020-09-16 09:57 | 44090.4149 | 22.7 | 48.2 | 501 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:57
2020-09-16 09:57 | 44090.4149 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 0 | 16 | 69 | 383 | 22 | 49 | 454 | No | 2020-09-16 09:57 | 44090.4149 | 22 | 49 | 454 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 09:57
2020-09-16 09:58 | 44090.415 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 23 | 54 | 431 |  | 2020-09-16 09:58 | 44090.415 | 23 | 54 | 431 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:57
2020-09-16 09:58 | 44090.4152 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 22 | 58 | 422 |  | 2020-09-16 09:58 | 44090.4152 | 22 | 58 | 422 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 09:57
2020-09-16 09:58 | 44090.4156 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 22 | 58 | 418 |  | 2020-09-16 09:58 | 44090.4156 | 22 | 58 | 418 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 09:58
2020-09-16 09:59 | 44090.4158 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 18 | 59 | 395 | 22 | 46 | 410 |  | 2020-09-16 09:59 | 44090.4158 | 22 | 46 | 410 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 09:58
2020-09-16 09:59 | 44090.4159 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 23 | 54 | 420 |  | 2020-09-16 09:59 | 44090.4159 | 23 | 54 | 420 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 09:58
2020-09-16 09:59 | 44090.416 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 22 | 58 | 413 |  | 2020-09-16 09:59 | 44090.416 | 22 | 58 | 413 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 09:58
2020-09-16 09:59 | 44090.4162 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 22.5 | 50.1 | 497 |  | 2020-09-16 09:59 | 44090.4162 | 22.5 | 50.1 | 497 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:59
2020-09-16 09:59 | 44090.4162 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 22.5 | 51.3 | 476 |  | 2020-09-16 09:59 | 44090.4162 | 22.5 | 51.3 | 476 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 09:59
2020-09-16 10:00 | 44090.4164 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 22 | 58 | 410 |  | 2020-09-16 10:00 | 44090.4164 | 22 | 58 | 410 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 09:59
2020-09-16 10:00 | 44090.4164 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 1 | 18.5 | 62.8 | 403 | 21.3 | 50.7 | 575 |  | 2020-09-16 10:00 | 44090.4164 | 21.3 | 50.7 | 575 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 09:59
2020-09-16 10:00 | 44090.4167 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 23 | 55 | 414 |  | 2020-09-16 10:00 | 44090.4167 | 23 | 55 | 414 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:00
2020-09-16 10:00 | 44090.4168 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 22 | 58 | 412 |  | 2020-09-16 10:00 | 44090.4168 | 22 | 58 | 412 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:00
2020-09-16 10:01 | 44090.4173 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 22.6 | 50.4 | 480 |  | 2020-09-16 10:01 | 44090.4173 | 22.6 | 50.4 | 480 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:00
2020-09-16 10:01 | 44090.4173 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 22 | 57 | 405 |  | 2020-09-16 10:01 | 44090.4173 | 22 | 57 | 405 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:00
2020-09-16 10:01 | 44090.4173 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 22.6 | 49.5 | 464 |  | 2020-09-16 10:01 | 44090.4173 | 22.6 | 49.5 | 464 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:00
2020-09-16 10:01 | 44090.4173 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 18 | 59 | 395 | 22 | 46 | 412 |  | 2020-09-16 10:01 | 44090.4173 | 22 | 46 | 412 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:00
2020-09-16 10:01 | 44090.4175 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23.5 | 48 | 610 |  | 2020-09-16 10:01 | 44090.4175 | 23.5 | 48 | 610 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:01
2020-09-16 10:01 | 44090.4176 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 0 | 16 | 69 | 383 | 21.8 | 48.2 | 418 | No | 2020-09-16 10:01 | 44090.4176 | 21.8 | 48.2 | 418 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 10:01
2020-09-16 10:01 | 44090.4176 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 416 | 23 | 55 | 416 |  | 2020-09-16 10:01 | 44090.4176 | 23 | 55 | 416 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:01
2020-09-16 10:01 | 44090.4177 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 19.8 | 59 | 533 | 21.6 | 47 | 588 | Yes | 2020-09-16 10:01 | 44090.4177 | 21.6 | 47 | 588 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:01
2020-09-16 10:02 | 44090.4179 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 22 | 58 | 409 |  | 2020-09-16 10:02 | 44090.4179 | 22 | 58 | 409 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:01
2020-09-16 10:02 | 44090.4181 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 2 | 20 | 62 | 400 | 23 | 52 | 440 |  | 2020-09-16 10:02 | 44090.4181 | 23 | 52 | 440 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:02
2020-09-16 10:03 | 44090.4184 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 24.6 | 40 | 518 | No | 2020-09-16 10:03 | 44090.4184 | 24.6 | 40 | 518 |  | caution | 2020-09-14 | B14660¦¦¦Sep-16-2020 10:02
2020-09-16 10:03 | 44090.4185 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 22.6 | 50.5 | 476 |  | 2020-09-16 10:03 | 44090.4185 | 22.6 | 50.5 | 476 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:02
2020-09-16 10:03 | 44090.4185 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 22.6 | 50.8 | 455 |  | 2020-09-16 10:03 | 44090.4185 | 22.6 | 50.8 | 455 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:02
2020-09-16 10:03 | 44090.4187 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 22 | 48.2 | 454 |  | 2020-09-16 10:03 | 44090.4187 | 22 | 48.2 | 454 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 10:02
2020-09-16 10:03 | 44090.4189 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 5 | 18.5 | 62.8 | 403 | 21.7 | 51.2 | 832 |  | 2020-09-16 10:03 | 44090.4189 | 21.7 | 51.2 | 832 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:03
2020-09-16 10:03 | 44090.419 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 22 | 55 | 415 |  | 2020-09-16 10:03 | 44090.419 | 22 | 55 | 415 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:03
2020-09-16 10:03 | 44090.419 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 18 | 59 | 395 | 22 | 48 | 413 |  | 2020-09-16 10:03 | 44090.419 | 22 | 48 | 413 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:03
2020-09-16 10:04 | 44090.4196 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 19.8 | 59 | 533 | 21.8 | 47.4 | 529 | Yes | 2020-09-16 10:04 | 44090.4196 | 21.8 | 47.4 | 529 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:04
2020-09-16 10:04 | 44090.4197 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 2 | 15 | 70 | 390 | 23.7 | 40.9 | 461 | No | 2020-09-16 10:04 | 44090.4197 | 23.7 | 40.9 | 461 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 10:04
2020-09-16 10:05 | 44090.4198 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 1 | 16 | 69 | 383 | 22.3 | 45.4 | 425 | No | 2020-09-16 10:05 | 44090.4198 | 22.3 | 45.4 | 425 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 10:04
2020-09-16 10:05 | 44090.4198 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 413 | 23 | 55 | 413 |  | 2020-09-16 10:05 | 44090.4198 | 23 | 55 | 413 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:04
2020-09-16 10:05 | 44090.4199 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 1 | 18 | 67.7 | 436 | 21.9 | 48.7 | 438 |  | 2020-09-16 10:05 | 44090.4199 | 21.9 | 48.7 | 438 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 10:04
2020-09-16 10:05 | 44090.4201 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 5 | 17.5 | 69 | 384 | 22.8 | 49.3 | 514 |  | 2020-09-16 10:05 | 44090.4201 | 22.8 | 49.3 | 514 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:04
2020-09-16 10:05 | 44090.4202 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 585 |  | 2020-09-16 10:05 | 44090.4202 | 23 | 48 | 585 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:05
2020-09-16 10:05 | 44090.4203 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 5 | 17 | 71.7 | 391 | 22.9 | 48.4 | 557 |  | 2020-09-16 10:05 | 44090.4203 | 22.9 | 48.4 | 557 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:05
2020-09-16 10:05 | 44090.4204 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 21.5 | 51.5 | 489 |  | 2020-09-16 10:05 | 44090.4204 | 21.5 | 51.5 | 489 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:05
2020-09-16 10:05 | 44090.4204 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 18 | 59 | 395 | 22 | 48 | 415 |  | 2020-09-16 10:05 | 44090.4204 | 22 | 48 | 415 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:05
2020-09-16 10:06 | 44090.4209 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 22 | 47.9 | 482 |  | 2020-09-16 10:06 | 44090.4209 | 22 | 47.9 | 482 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 10:06
2020-09-16 10:06 | 44090.4211 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 1 | 16 | 69 | 383 | 22.3 | 45.2 | 425 | No | 2020-09-16 10:06 | 44090.4211 | 22.3 | 45.2 | 425 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 10:06
2020-09-16 10:06 | 44090.4211 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 19.8 | 59 | 533 | 21.8 | 49 | 508 | Yes | 2020-09-16 10:06 | 44090.4211 | 21.8 | 49 | 508 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:06
2020-09-16 10:07 | 44090.4213 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 18 | 59 | 395 | 22 | 48 | 435 |  | 2020-09-16 10:07 | 44090.4213 | 22 | 48 | 435 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:06
2020-09-16 10:07 | 44090.4215 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 8 | 17 | 71.7 | 391 | 23.1 | 46 | 549 |  | 2020-09-16 10:07 | 44090.4215 | 23.1 | 46 | 549 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:06
2020-09-16 10:07 | 44090.4216 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 8 | 17.5 | 69 | 384 | 23.2 | 47 | 530 |  | 2020-09-16 10:07 | 44090.4216 | 23.2 | 47 | 530 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:07
2020-09-16 10:07 | 44090.4217 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 21.4 | 50.8 | 466 |  | 2020-09-16 10:07 | 44090.4217 | 21.4 | 50.8 | 466 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:07
2020-09-16 10:08 | 44090.4219 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 21.9 | 48.1 | 444 |  | 2020-09-16 10:08 | 44090.4219 | 21.9 | 48.1 | 444 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 10:07
2020-09-16 10:08 | 44090.422 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 23 | 55 | 421 |  | 2020-09-16 10:08 | 44090.422 | 23 | 55 | 421 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:07
2020-09-16 10:08 | 44090.4221 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 18 | 59 | 395 | 22 | 47 | 436 |  | 2020-09-16 10:08 | 44090.4221 | 22 | 47 | 436 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:07
2020-09-16 10:08 | 44090.4223 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 19.8 | 59 | 533 | 21.7 | 47.4 | 511 | Yes | 2020-09-16 10:08 | 44090.4223 | 21.7 | 47.4 | 511 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:08
2020-09-16 10:09 | 44090.4226 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 22 | 56 | 417 |  | 2020-09-16 10:09 | 44090.4226 | 22 | 56 | 417 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:08
2020-09-16 10:09 | 44090.4227 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 21.5 | 49.8 | 456 |  | 2020-09-16 10:09 | 44090.4227 | 21.5 | 49.8 | 456 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:08
2020-09-16 10:09 | 44090.4229 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 22 | 47.3 | 487 |  | 2020-09-16 10:09 | 44090.4229 | 22 | 47.3 | 487 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 10:08
2020-09-16 10:09 | 44090.4229 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 18 | 59 | 395 | 22 | 49 | 437 |  | 2020-09-16 10:09 | 44090.4229 | 22 | 49 | 437 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:09
2020-09-16 10:09 | 44090.423 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 4 | 17.5 | 69 | 384 | 22.6 | 47.1 | 448 |  | 2020-09-16 10:09 | 44090.423 | 22.6 | 47.1 | 448 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:09
2020-09-16 10:09 | 44090.423 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 4 | 17 | 71.7 | 391 | 22.6 | 47.1 | 432 |  | 2020-09-16 10:09 | 44090.423 | 22.6 | 47.1 | 432 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:09
2020-09-16 10:09 | 44090.4231 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 0 | 16 | 69 | 383 | 22 | 47.2 | 439 | No | 2020-09-16 10:09 | 44090.4231 | 22 | 47.2 | 439 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 10:09
2020-09-16 10:09 | 44090.4232 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 15 | 70 | 390 | 23.8 | 38.8 | 414 | No | 2020-09-16 10:09 | 44090.4232 | 23.8 | 38.8 | 414 |  | caution | 2020-09-14 | B14660¦¦¦Sep-16-2020 10:09
2020-09-16 10:10 | 44090.4233 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 21 | 60 | 404 |  | 2020-09-16 10:10 | 44090.4233 | 21 | 60 | 404 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:09
2020-09-16 10:10 | 44090.4234 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 22 | 51 | 438 |  | 2020-09-16 10:10 | 44090.4234 | 22 | 51 | 438 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:09
2020-09-16 10:10 | 44090.4234 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 18 | 61 | 400 | 20 | 54 | 515 |  | 2020-09-16 10:10 | 44090.4234 | 20 | 54 | 515 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 10:09
2020-09-16 10:10 | 44090.4235 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 21.6 | 49.7 | 456 |  | 2020-09-16 10:10 | 44090.4235 | 21.6 | 49.7 | 456 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:09
2020-09-16 10:10 | 44090.4237 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 22 | 59 | 398 |  | 2020-09-16 10:10 | 44090.4237 | 22 | 59 | 398 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:10
2020-09-16 10:10 | 44090.4237 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 2 | 18 | 59 | 395 | 22 | 48 | 571 |  | 2020-09-16 10:10 | 44090.4237 | 22 | 48 | 571 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:10
2020-09-16 10:10 | 44090.4237 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 580 |  | 2020-09-16 10:10 | 44090.4237 | 23 | 48 | 580 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:10
2020-09-16 10:10 | 44090.4238 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 19.8 | 59 | 533 | 21.7 | 43.9 | 530 | Yes | 2020-09-16 10:10 | 44090.4238 | 21.7 | 43.9 | 530 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:10
2020-09-16 10:11 | 44090.424 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 22 | 47.1 | 475 |  | 2020-09-16 10:11 | 44090.424 | 22 | 47.1 | 475 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 10:10
2020-09-16 10:11 | 44090.4241 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 22 | 59 | 385 |  | 2020-09-16 10:11 | 44090.4241 | 22 | 59 | 385 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:10
2020-09-16 10:11 | 44090.4242 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 21.4 | 50.7 | 464 |  | 2020-09-16 10:11 | 44090.4242 | 21.4 | 50.7 | 464 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:10
2020-09-16 10:11 | 44090.4243 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 1 | 18 | 61 | 400 | 19 | 50 | 500 |  | 2020-09-16 10:11 | 44090.4243 | 19 | 50 | 500 |  |  | 2020-09-14 | B21554¦¦¦Sep-16-2020 10:11
2020-09-16 10:11 | 44090.4245 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 4 | 17 | 71.7 | 391 | 22.8 | 50.4 | 508 |  | 2020-09-16 10:11 | 44090.4245 | 22.8 | 50.4 | 508 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:11
2020-09-16 10:11 | 44090.4246 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 21 | 59 | 394 |  | 2020-09-16 10:11 | 44090.4246 | 21 | 59 | 394 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:11
2020-09-16 10:11 | 44090.4246 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 18 | 59 | 395 |  |  |  | Court in session, no access | 2020-09-16 10:11 | 44090.4246 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:11
2020-09-16 10:12 | 44090.4247 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 4 | 17.5 | 69 | 384 | 23 | 50.3 | 496 |  | 2020-09-16 10:12 | 44090.4247 | 23 | 50.3 | 496 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:11
2020-09-16 10:12 | 44090.4249 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 23 | 52 | 440 |  | 2020-09-16 10:12 | 44090.4249 | 23 | 52 | 440 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:11
2020-09-16 10:12 | 44090.4249 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 21 | 58 | 400 |  | 2020-09-16 10:12 | 44090.4249 | 21 | 58 | 400 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:11
2020-09-16 10:12 | 44090.425 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 2 | 18 | 61 | 400 | 19.7 | 49.8 | 508 |  | 2020-09-16 10:12 | 44090.425 | 19.7 | 49.8 | 508 |  |  | 2020-09-14 | B21554¦¦¦Sep-16-2020 10:12
2020-09-16 10:12 | 44090.4252 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 21.1 | 51.9 | 461 |  | 2020-09-16 10:12 | 44090.4252 | 21.1 | 51.9 | 461 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:12
2020-09-16 10:12 | 44090.4252 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 22.6 | 46.8 | 471 |  | 2020-09-16 10:12 | 44090.4252 | 22.6 | 46.8 | 471 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 10:12
2020-09-16 10:12 | 44090.4253 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 22 | 59 | 401 |  | 2020-09-16 10:12 | 44090.4253 | 22 | 59 | 401 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:12
2020-09-16 10:13 | 44090.4254 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 19.8 | 59 | 533 | 21.2 | 43.8 | 458 | Yes | 2020-09-16 10:13 | 44090.4254 | 21.2 | 43.8 | 458 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:12
2020-09-16 10:13 | 44090.4255 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 4 | 17 | 71.7 | 391 | 22.9 | 49.7 | 452 |  | 2020-09-16 10:13 | 44090.4255 | 22.9 | 49.7 | 452 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:12
2020-09-16 10:13 | 44090.4256 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 18 | 59 | 395 |  |  |  | Court in session, no access | 2020-09-16 10:13 | 44090.4256 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:12
2020-09-16 10:13 | 44090.4257 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 4 | 17.5 | 69 | 384 | 23 | 49.5 | 439 |  | 2020-09-16 10:13 | 44090.4257 | 23 | 49.5 | 439 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:12
2020-09-16 10:13 | 44090.4258 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 21 | 56 | 399 |  | 2020-09-16 10:13 | 44090.4258 | 21 | 56 | 399 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:13
2020-09-16 10:13 | 44090.4258 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 49 | 590 |  | 2020-09-16 10:13 | 44090.4258 | 23 | 49 | 590 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:13
2020-09-16 10:13 | 44090.426 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 2 | 18 | 61 | 400 | 20.5 | 50 | 588 |  | 2020-09-16 10:13 | 44090.426 | 20.5 | 50 | 588 |  |  | 2020-09-14 | B21554¦¦¦Sep-16-2020 10:13
2020-09-16 10:14 | 44090.4262 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 23 | 51 | 439 | Courtroom 500 and 501 are unavailable | 2020-09-16 10:14 | 44090.4262 | 23 | 51 | 439 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:13
2020-09-16 10:14 | 44090.4262 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 21 | 52 | 388 |  | 2020-09-16 10:14 | 44090.4262 | 21 | 52 | 388 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:13
2020-09-16 10:14 | 44090.4262 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 22.5 | 46.6 | 471 |  | 2020-09-16 10:14 | 44090.4262 | 22.5 | 46.6 | 471 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 10:13
2020-09-16 10:14 | 44090.4263 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 19.8 | 59 | 533 | 20.6 | 55.6 | 436 | Yes | 2020-09-16 10:14 | 44090.4263 | 20.6 | 55.6 | 436 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:13
2020-09-16 10:14 | 44090.4264 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 18 | 59 | 395 | 22 | 47 | 471 |  | 2020-09-16 10:14 | 44090.4264 | 22 | 47 | 471 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:14
2020-09-16 10:14 | 44090.4266 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 23.1 | 49.5 | 429 |  | 2020-09-16 10:14 | 44090.4266 | 23.1 | 49.5 | 429 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:14
2020-09-16 10:14 | 44090.4266 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 2 | 17 | 71.7 | 391 | 22.8 | 49.8 | 440 |  | 2020-09-16 10:14 | 44090.4266 | 22.8 | 49.8 | 440 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:14
2020-09-16 10:14 | 44090.4266 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 21 | 53 | 408 |  | 2020-09-16 10:14 | 44090.4266 | 21 | 53 | 408 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:14
2020-09-16 10:14 | 44090.4267 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 2 | 20 | 62 | 400 | 23 | 51 | 440 |  | 2020-09-16 10:14 | 44090.4267 | 23 | 51 | 440 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:14
2020-09-16 10:15 | 44090.4271 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 18 | 59 | 395 | 22 | 46 | 468 |  | 2020-09-16 10:15 | 44090.4271 | 22 | 46 | 468 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:15
2020-09-16 10:15 | 44090.4272 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 5 | 19.8 | 59 | 533 | 20.7 | 51.2 | 434 | Yes | 2020-09-16 10:15 | 44090.4272 | 20.7 | 51.2 | 434 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:15
2020-09-16 10:15 | 44090.4273 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 21.8 | 48.9 | 473 |  | 2020-09-16 10:15 | 44090.4273 | 21.8 | 48.9 | 473 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 10:15
2020-09-16 10:15 | 44090.4273 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 23 | 54 | 433 |  | 2020-09-16 10:15 | 44090.4273 | 23 | 54 | 433 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:15
2020-09-16 10:15 | 44090.4274 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 21.1 | 52.5 | 489 |  | 2020-09-16 10:15 | 44090.4274 | 21.1 | 52.5 | 489 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:15
2020-09-16 10:15 | 44090.4274 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 2 | 17 | 71.7 | 391 | 22.7 | 49.8 | 443 |  | 2020-09-16 10:15 | 44090.4274 | 22.7 | 49.8 | 443 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:15
2020-09-16 10:16 | 44090.4275 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 2 | 17.5 | 69 | 384 | 22.9 | 49.7 | 427 |  | 2020-09-16 10:16 | 44090.4275 | 22.9 | 49.7 | 427 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:15
2020-09-16 10:16 | 44090.4276 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 49 | 600 |  | 2020-09-16 10:16 | 44090.4276 | 23 | 49 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:15
2020-09-16 10:16 | 44090.4277 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 23 | 54 | 430 |  | 2020-09-16 10:16 | 44090.4277 | 23 | 54 | 430 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:15
2020-09-16 10:16 | 44090.4278 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 2 | 21 | 63 | 402 | 21 | 54 | 431 |  | 2020-09-16 10:16 | 44090.4278 | 21 | 54 | 431 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:15
2020-09-16 10:16 | 44090.428 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 4 | 19.8 | 59 | 533 | 21.5 | 50.1 | 588 | Yes | 2020-09-16 10:16 | 44090.428 | 21.5 | 50.1 | 588 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:16
2020-09-16 10:16 | 44090.4281 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 18 | 59 | 395 |  |  |  | Court in session, no access | 2020-09-16 10:16 | 44090.4281 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:16
2020-09-16 10:17 | 44090.4282 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 21.8 | 48.2 | 477 |  | 2020-09-16 10:17 | 44090.4282 | 21.8 | 48.2 | 477 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 10:16
2020-09-16 10:17 | 44090.4282 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 21 | 56 | 434 |  | 2020-09-16 10:17 | 44090.4282 | 21 | 56 | 434 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:16
2020-09-16 10:17 | 44090.4282 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 21.1 | 52.3 | 485 |  | 2020-09-16 10:17 | 44090.4282 | 21.1 | 52.3 | 485 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:16
2020-09-16 10:17 | 44090.4286 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 21 | 56 | 451 |  | 2020-09-16 10:17 | 44090.4286 | 21 | 56 | 451 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:17
2020-09-16 10:17 | 44090.4287 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 19.8 | 59 | 533 | 21.8 | 49.9 | 630 | Yes | 2020-09-16 10:17 | 44090.4287 | 21.8 | 49.9 | 630 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:17
2020-09-16 10:18 | 44090.4289 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 18 | 59 | 395 |  |  |  | Occupied, no access | 2020-09-16 10:18 | 44090.4289 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:17
2020-09-16 10:18 | 44090.4289 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 49 | 600 |  | 2020-09-16 10:18 | 44090.4289 | 23 | 49 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:17
2020-09-16 10:18 | 44090.429 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 23.1 | 50 | 459 |  | 2020-09-16 10:18 | 44090.429 | 23.1 | 50 | 459 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:17
2020-09-16 10:18 | 44090.4293 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 21.8 | 48.6 | 442 |  | 2020-09-16 10:18 | 44090.4293 | 21.8 | 48.6 | 442 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 10:18
2020-09-16 10:18 | 44090.4295 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 21 | 55 | 431 |  | 2020-09-16 10:18 | 44090.4295 | 21 | 55 | 431 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:18
2020-09-16 10:19 | 44090.4296 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 19.8 | 59 | 533 | 22.2 | 48 | 429 | Yes | 2020-09-16 10:19 | 44090.4296 | 22.2 | 48 | 429 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:18
2020-09-16 10:19 | 44090.4299 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 21 | 58 | 427 |  | 2020-09-16 10:19 | 44090.4299 | 21 | 58 | 427 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:19
2020-09-16 10:19 | 44090.43 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 21.5 | 52.1 | 634 |  | 2020-09-16 10:19 | 44090.43 | 21.5 | 52.1 | 634 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:19
2020-09-16 10:19 | 44090.4301 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 27.5 | 69 | 384 | 23.3 | 49.9 | 439 |  | 2020-09-16 10:19 | 44090.4301 | 23.3 | 49.9 | 439 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:19
2020-09-16 10:19 | 44090.4302 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 18 | 59 | 395 | 22 | 46 | 429 |  | 2020-09-16 10:19 | 44090.4302 | 22 | 46 | 429 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:19
2020-09-16 10:20 | 44090.4303 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 7 | 18 | 61 | 400 | 21.5 | 48 | 725 |  | 2020-09-16 10:20 | 44090.4303 | 21.5 | 48 | 725 |  |  | 2020-09-14 | B21554¦¦¦Sep-16-2020 10:19
2020-09-16 10:20 | 44090.4303 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 21 | 63 | 402 | 21 | 59 | 420 |  | 2020-09-16 10:20 | 44090.4303 | 21 | 59 | 420 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 10:19
2020-09-16 10:20 | 44090.4304 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 18 | 67.7 | 436 | 22 | 47.3 | 446 |  | 2020-09-16 10:20 | 44090.4304 | 22 | 47.3 | 446 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 10:19
2020-09-16 10:20 | 44090.4304 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 19.8 | 59 | 533 | 22.2 | 48.9 | 711 | Yes | 2020-09-16 10:20 | 44090.4304 | 22.2 | 48.9 | 711 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:19
2020-09-16 10:20 | 44090.4307 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 49 | 600 |  | 2020-09-16 10:20 | 44090.4307 | 23 | 49 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:20
2020-09-16 10:20 | 44090.4308 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 20 | 62 | 400 | 22 | 62 | 400 |  | 2020-09-16 10:20 | 44090.4308 | 22 | 62 | 400 |  | caution | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:20
2020-09-16 10:21 | 44090.431 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 22 | 50.4 | 595 |  | 2020-09-16 10:21 | 44090.431 | 22 | 50.4 | 595 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:20
2020-09-16 10:21 | 44090.4311 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 4 | 17 | 71.7 | 391 | 23.2 | 54.3 | 480 |  | 2020-09-16 10:21 | 44090.4311 | 23.2 | 54.3 | 480 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:20
2020-09-16 10:21 | 44090.4313 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 18 | 59 | 395 | 22 | 46 | 441 |  | 2020-09-16 10:21 | 44090.4313 | 22 | 46 | 441 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:21
2020-09-16 10:21 | 44090.4314 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 6 | 19.8 | 59 | 533 | 21.6 | 50 | 590 | Yes | 2020-09-16 10:21 | 44090.4314 | 21.6 | 50 | 590 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:21
2020-09-16 10:21 | 44090.4316 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 27.5 | 69 | 384 | 23.3 | 49.9 | 439 |  | 2020-09-16 10:21 | 44090.4316 | 23.3 | 49.9 | 439 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:21
2020-09-16 10:22 | 44090.432 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 23.2 | 50.8 | 461 |  | 2020-09-16 10:22 | 44090.432 | 23.2 | 50.8 | 461 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:22
2020-09-16 10:22 | 44090.432 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 18 | 59 | 395 |  |  |  | Court in session, no access | 2020-09-16 10:22 | 44090.432 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:22
2020-09-16 10:22 | 44090.4322 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 23.3 | 50.8 | 449 |  | 2020-09-16 10:22 | 44090.4322 | 23.3 | 50.8 | 449 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:22
2020-09-16 10:23 | 44090.4323 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 597 |  | 2020-09-16 10:23 | 44090.4323 | 23 | 48 | 597 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:22
2020-09-16 10:23 | 44090.4324 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 19.8 | 59 | 533 | 21.8 | 51.6 | 474 | Yes | 2020-09-16 10:23 | 44090.4324 | 21.8 | 51.6 | 474 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:22
2020-09-16 10:23 | 44090.4326 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 21.8 | 49.1 | 539 |  | 2020-09-16 10:23 | 44090.4326 | 21.8 | 49.1 | 539 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:22
2020-09-16 10:23 | 44090.4327 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 18 | 59 | 395 |  |  |  | Occupied, no access | 2020-09-16 10:23 | 44090.4327 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:23
2020-09-16 10:24 | 44090.4331 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 19.8 | 59 | 533 | 21.6 | 53.6 | 471 | Yes | 2020-09-16 10:24 | 44090.4331 | 21.6 | 53.6 | 471 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:23
2020-09-16 10:24 | 44090.4331 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 3 | 18 | 61 | 400 | 21.4 | 46 | 718 |  | 2020-09-16 10:24 | 44090.4331 | 21.4 | 46 | 718 |  |  | 2020-09-14 | B21554¦¦¦Sep-16-2020 10:23
2020-09-16 10:24 | 44090.4332 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 432 | 22.5 | 55.4 | 692 |  | 2020-09-16 10:24 | 44090.4332 | 22.5 | 55.4 | 692 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:23
2020-09-16 10:24 | 44090.4334 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 23.3 | 51.2 | 461 |  | 2020-09-16 10:24 | 44090.4334 | 23.3 | 51.2 | 461 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:24
2020-09-16 10:24 | 44090.4335 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 18 | 59 | 395 | 22 | 47 | 452 |  | 2020-09-16 10:24 | 44090.4335 | 22 | 47 | 452 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:24
2020-09-16 10:25 | 44090.4338 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 19.8 | 59 | 533 | 22 | 50.7 | 482 | Yes | 2020-09-16 10:25 | 44090.4338 | 22 | 50.7 | 482 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:24
2020-09-16 10:25 | 44090.4341 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 600 |  | 2020-09-16 10:25 | 44090.4341 | 23 | 48 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:25
2020-09-16 10:25 | 44090.4341 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 18 | 59 | 395 | 22 | 46 | 448 |  | 2020-09-16 10:25 | 44090.4341 | 22 | 46 | 448 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:25
2020-09-16 10:25 | 44090.4342 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 2 | 18.5 | 62.8 | 405 | 21.3 | 51.1 | 631 |  | 2020-09-16 10:25 | 44090.4342 | 21.3 | 51.1 | 631 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:25
2020-09-16 10:25 | 44090.4343 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 654 | 22.9 | 49.8 | 651 |  | 2020-09-16 10:25 | 44090.4343 | 22.9 | 49.8 | 651 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:25
2020-09-16 10:26 | 44090.4345 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 19.8 | 59 | 533 | 22.3 | 47.5 | 498 | Yes | 2020-09-16 10:26 | 44090.4345 | 22.3 | 47.5 | 498 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:25
2020-09-16 10:26 | 44090.435 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 18 | 59 | 395 | 23 | 46 | 465 |  | 2020-09-16 10:26 | 44090.435 | 23 | 46 | 465 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:26
2020-09-16 10:27 | 44090.4352 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 |  |  |  | No access | 2020-09-16 10:27 | 44090.4352 | [5 empty] | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:26
2020-09-16 10:27 | 44090.4352 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 1 | 19.8 | 59 | 533 | 21.4 | 46.8 | 607 | Yes | 2020-09-16 10:27 | 44090.4352 | 21.4 | 46.8 | 607 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:26
2020-09-16 10:27 | 44090.4352 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 23.5 | 51.3 | 470 |  | 2020-09-16 10:27 | 44090.4352 | 23.5 | 51.3 | 470 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:26
2020-09-16 10:27 | 44090.4353 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 1 | 24.2 | 57.7 | 432 | 23.1 | 52.3 | 554 |  | 2020-09-16 10:27 | 44090.4353 | 23.1 | 52.3 | 554 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:26
2020-09-16 10:27 | 44090.4355 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 1 | 18 | 61 | 400 | 21.7 | 41.2 | 540 |  | 2020-09-16 10:27 | 44090.4355 | 21.7 | 41.2 | 540 |  |  | 2020-09-14 | B21554¦¦¦Sep-16-2020 10:27
2020-09-16 10:27 | 44090.4357 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 23.8 | 55.5 | 459 |  | 2020-09-16 10:27 | 44090.4357 | 23.8 | 55.5 | 459 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:27
2020-09-16 10:28 | 44090.4358 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 18 | 59 | 395 |  |  |  | Court in session, no access | 2020-09-16 10:28 | 44090.4358 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:27
2020-09-16 10:28 | 44090.4359 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 432 | 23 | 50 | 525 |  | 2020-09-16 10:28 | 44090.4359 | 23 | 50 | 525 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:27
2020-09-16 10:28 | 44090.4359 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 19.8 | 59 | 533 | 21.9 | 48.2 | 641 | Yes | 2020-09-16 10:28 | 44090.4359 | 21.9 | 48.2 | 641 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:27
2020-09-16 10:28 | 44090.436 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 23.8 | 49.3 | 466 |  | 2020-09-16 10:28 | 44090.436 | 23.8 | 49.3 | 466 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:27
2020-09-16 10:28 | 44090.4362 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 5 | 18.5 | 62.8 | 403 | 21.8 | 51.1 | 815 |  | 2020-09-16 10:28 | 44090.4362 | 21.8 | 51.1 | 815 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:28
2020-09-16 10:28 | 44090.4364 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 18 | 59 | 395 |  |  |  | Occupied, no access | 2020-09-16 10:28 | 44090.4364 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:28
2020-09-16 10:29 | 44090.4366 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 2 | 22.1 | 44 | 434 | 21.3 | 50.1 | 535 |  | 2020-09-16 10:29 | 44090.4366 | 21.3 | 50.1 | 535 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 10:28
2020-09-16 10:29 | 44090.4366 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 432 | 22.8 | 50.6 | 480 |  | 2020-09-16 10:29 | 44090.4366 | 22.8 | 50.6 | 480 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:28
2020-09-16 10:29 | 44090.4366 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 6 | 19.8 | 59 | 533 | 22.2 | 48.4 | 614 | Yes | 2020-09-16 10:29 | 44090.4366 | 22.2 | 48.4 | 614 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:28
2020-09-16 10:29 | 44090.4371 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 18 | 59 | 395 | 23 | 46 | 652 |  | 2020-09-16 10:29 | 44090.4371 | 23 | 46 | 652 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:29
2020-09-16 10:29 | 44090.4371 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.1 | 44 | 434 | 21.9 | 47.7 | 554 |  | 2020-09-16 10:29 | 44090.4371 | 21.9 | 47.7 | 554 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 10:29
2020-09-16 10:30 | 44090.4375 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 480 | 22.7 | 50.7 | 491 |  | 2020-09-16 10:30 | 44090.4375 | 22.7 | 50.7 | 491 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:29
2020-09-16 10:30 | 44090.4377 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 23.2 | 46.6 | 485 |  | 2020-09-16 10:30 | 44090.4377 | 23.2 | 46.6 | 485 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:30
2020-09-16 10:30 | 44090.4377 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 586 |  | 2020-09-16 10:30 | 44090.4377 | 23 | 48 | 586 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:30
2020-09-16 10:30 | 44090.4377 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 4 | 19.8 | 59 | 533 | 21.9 | 48.4 | 560 | Court 1 could not access | 2020-09-16 10:30 | 44090.4377 | 21.9 | 48.4 | 560 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 10:30
2020-09-16 10:30 | 44090.4377 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 23.3 | 46.9 | 493 |  | 2020-09-16 10:30 | 44090.4377 | 23.3 | 46.9 | 493 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:30
2020-09-16 10:30 | 44090.4377 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23.5 | 45 | 457 |  | 2020-09-16 10:30 | 44090.4377 | 23.5 | 45 | 457 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:30
2020-09-16 10:30 | 44090.4378 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 18 | 59 | 395 |  |  |  | Occupied, no access | 2020-09-16 10:30 | 44090.4378 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 10:30
2020-09-16 10:31 | 44090.4382 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 432 | 22.6 | 51.6 | 507 |  | 2020-09-16 10:31 | 44090.4382 | 22.6 | 51.6 | 507 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:30
2020-09-16 10:31 | 44090.4382 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.1 | 44 | 434 | 22.3 | 50.1 | 535 |  | 2020-09-16 10:31 | 44090.4382 | 22.3 | 50.1 | 535 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 10:30
2020-09-16 10:32 | 44090.4386 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23.2 | 45.6 | 441 |  | 2020-09-16 10:32 | 44090.4386 | 23.2 | 45.6 | 441 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:31
2020-09-16 10:32 | 44090.4388 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 2 | 24.4 | 53 | 505 | 22.8 | 52.7 | 505 |  | 2020-09-16 10:32 | 44090.4388 | 22.8 | 52.7 | 505 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:31
2020-09-16 10:32 | 44090.4389 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 590 |  | 2020-09-16 10:32 | 44090.4389 | 23 | 48 | 590 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:31
2020-09-16 10:33 | 44090.4395 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23.1 | 45.8 | 437 |  | 2020-09-16 10:33 | 44090.4395 | 23.1 | 45.8 | 437 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:32
2020-09-16 10:33 | 44090.4395 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 4 | 22.1 | 50.1 | 434 | 22.6 | 47.1 | 560 |  | 2020-09-16 10:33 | 44090.4395 | 22.6 | 47.1 | 560 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 10:32
2020-09-16 10:33 | 44090.4395 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 |  |  |  | Courtroom 6 locked | 2020-09-16 10:33 | 44090.4395 | [5 empty] | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:32
2020-09-16 10:33 | 44090.4396 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 |  |  |  | Unable to access | 2020-09-16 10:33 | 44090.4396 | [5 empty] | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:33
2020-09-16 10:33 | 44090.4397 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 53.4 | 505 | 22.8 | 51.4 | 503 |  | 2020-09-16 10:33 | 44090.4397 | 22.8 | 51.4 | 503 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:33
2020-09-16 10:34 | 44090.4402 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 1 | 18.5 | 62.8 | 403 | 21.6 | 50.8 | 648 |  | 2020-09-16 10:34 | 44090.4402 | 21.6 | 50.8 | 648 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:33
2020-09-16 10:34 | 44090.4402 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 9 | 18 | 67 | 440 | 23 | 48 | 600 |  | 2020-09-16 10:34 | 44090.4402 | 23 | 48 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:33
2020-09-16 10:34 | 44090.4405 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 2 | 24.2 | 57.7 | 432 | 22.5 | 53.2 | 596 |  | 2020-09-16 10:34 | 44090.4405 | 22.5 | 53.2 | 596 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:34
2020-09-16 10:35 | 44090.4406 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23 | 39.9 | 443 |  | 2020-09-16 10:35 | 44090.4406 | 23 | 39.9 | 443 |  | caution | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:34
2020-09-16 10:35 | 44090.4407 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.1 | 44 | 434 | 22.6 | 46.9 | 526 |  | 2020-09-16 10:35 | 44090.4407 | 22.6 | 46.9 | 526 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 10:34
2020-09-16 10:35 | 44090.4411 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 432 | 23 | 52.4 | 647 |  | 2020-09-16 10:35 | 44090.4411 | 23 | 52.4 | 647 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:35
2020-09-16 10:36 | 44090.4414 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 21.5 | 59.9 | 499 |  | 2020-09-16 10:36 | 44090.4414 | 21.5 | 59.9 | 499 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:35
2020-09-16 10:36 | 44090.4416 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23.7 | 44.2 | 426 |  | 2020-09-16 10:36 | 44090.4416 | 23.7 | 44.2 | 426 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:35
2020-09-16 10:36 | 44090.4417 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 21.5 | 52.3 | 651 |  | 2020-09-16 10:36 | 44090.4417 | 21.5 | 52.3 | 651 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:35
2020-09-16 10:36 | 44090.4419 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 432 | 22.9 | 53.1 | 616 |  | 2020-09-16 10:36 | 44090.4419 | 22.9 | 53.1 | 616 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:36
2020-09-16 10:37 | 44090.4421 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.1 | 44 | 434 | 22.2 | 47.8 | 483 |  | 2020-09-16 10:37 | 44090.4421 | 22.2 | 47.8 | 483 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 10:36
2020-09-16 10:37 | 44090.4424 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23.6 | 40.8 | 441 |  | 2020-09-16 10:37 | 44090.4424 | 23.6 | 40.8 | 441 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:37
2020-09-16 10:37 | 44090.4427 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 432 | 22.9 | 52.2 | 617 |  | 2020-09-16 10:37 | 44090.4427 | 22.9 | 52.2 | 617 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:37
2020-09-16 10:38 | 44090.4431 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 590 |  | 2020-09-16 10:38 | 44090.4431 | 23 | 48 | 590 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:38
2020-09-16 10:38 | 44090.4432 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23.4 | 43.5 | 444 |  | 2020-09-16 10:38 | 44090.4432 | 23.4 | 43.5 | 444 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:38
2020-09-16 10:38 | 44090.4433 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.1 | 44 | 434 | 22.1 | 48.6 | 448 |  | 2020-09-16 10:38 | 44090.4433 | 22.1 | 48.6 | 448 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 10:38
2020-09-16 10:39 | 44090.4434 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 51.5 | 606 | 23 | 52.8 | 595 |  | 2020-09-16 10:39 | 44090.4434 | 23 | 52.8 | 595 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:38
2020-09-16 10:39 | 44090.4441 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 51.4 | 592 | 23 | 50.1 | 589 |  | 2020-09-16 10:39 | 44090.4441 | 23 | 50.1 | 589 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:39
2020-09-16 10:40 | 44090.4444 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.1 | 44 | 434 | 22.2 | 46.8 | 467 |  | 2020-09-16 10:40 | 44090.4444 | 22.2 | 46.8 | 467 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 10:39
2020-09-16 10:40 | 44090.4444 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23.3 | 42.6 | 489 |  | 2020-09-16 10:40 | 44090.4444 | 23.3 | 42.6 | 489 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:39
2020-09-16 10:41 | 44090.4448 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 50.4 | 580 | 23 | 50.1 | 569 |  | 2020-09-16 10:41 | 44090.4448 | 23 | 50.1 | 569 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:40
2020-09-16 10:42 | 44090.4455 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 432 | 23 | 49.8 | 531 |  | 2020-09-16 10:42 | 44090.4455 | 23 | 49.8 | 531 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:41
2020-09-16 10:42 | 44090.4456 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.1 | 44 | 434 | 21.9 | 48.6 | 504 |  | 2020-09-16 10:42 | 44090.4456 | 21.9 | 48.6 | 504 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 10:41
2020-09-16 10:42 | 44090.4457 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 44.1 | 486 | 22.8 | 43.8 | 464 |  | 2020-09-16 10:42 | 44090.4457 | 22.8 | 43.8 | 464 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:41
2020-09-16 10:43 | 44090.4462 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 432 | 23.2 | 54.9 | 544 |  | 2020-09-16 10:42 | 44090.4462 | 23.2 | 54.9 | 544 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:42
2020-09-16 10:43 | 44090.4463 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 3 | 18.5 | 62.8 | 403 | 21.8 | 51 | 1022 |  | 2020-09-16 10:43 | 44090.4463 | 21.8 | 51 | 1022 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:42
2020-09-16 10:43 | 44090.4464 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 21.2 | 48.3 | 376 | 23.7 | 39.7 | 456 |  | 2020-09-16 10:43 | 44090.4464 | 23.7 | 39.7 | 456 |  | caution | 2020-09-14 | B70277¦¦¦Sep-16-2020 10:42
2020-09-16 10:43 | 44090.4465 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.1 | 48.3 | 559 | 22.1 | 49.6 | 566 |  | 2020-09-16 10:43 | 44090.4465 | 22.1 | 49.6 | 566 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 10:42
2020-09-16 10:43 | 44090.4467 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 22.3 | 47 | 533 |  | 2020-09-16 10:43 | 44090.4467 | 22.3 | 47 | 533 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:43
2020-09-16 10:44 | 44090.4473 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 21 | 49 | 531 |  | 2020-09-16 10:44 | 44090.4473 | 21 | 49 | 531 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:44
2020-09-16 10:44 | 44090.4472 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 432 | 22.7 | 52.2 | 575 |  | 2020-09-16 10:44 | 44090.4472 | 22.7 | 52.2 | 575 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:43
2020-09-16 10:45 | 44090.4476 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 22.1 | 46.9 | 529 |  | 2020-09-16 10:45 | 44090.4476 | 22.1 | 46.9 | 529 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:44
2020-09-16 10:45 | 44090.4478 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.4 | 57.7 | 432 | 22.8 | 54.1 | 470 |  | 2020-09-16 10:45 | 44090.4478 | 22.8 | 54.1 | 470 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:44
2020-09-16 10:45 | 44090.4479 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 20.4 | 51.3 | 515 |  | 2020-09-16 10:45 | 44090.4479 | 20.4 | 51.3 | 515 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:44
2020-09-16 10:45 | 44090.4483 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 21.2 | 48.3 | 376 | 23.7 | 39.5 | 433 |  | 2020-09-16 10:45 | 44090.4483 | 23.7 | 39.5 | 433 |  | caution | 2020-09-14 | B70277¦¦¦Sep-16-2020 10:45
2020-09-16 10:46 | 44090.4483 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 600 |  | 2020-09-16 10:46 | 44090.4483 | 23 | 48 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:45
2020-09-16 10:46 | 44090.4485 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 6 | 20 | 62.4 | 387 | 22 | 49.1 | 514 |  | 2020-09-16 10:46 | 44090.4485 | 22 | 49.1 | 514 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:45
2020-09-16 10:46 | 44090.4486 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 432 | 22.5 | 52.2 | 416 |  | 2020-09-16 10:46 | 44090.4486 | 22.5 | 52.2 | 416 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:45
2020-09-16 10:46 | 44090.4486 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 19.9 | 48.1 | 431 |  | 2020-09-16 10:46 | 44090.4486 | 19.9 | 48.1 | 431 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:46
2020-09-16 10:47 | 44090.4491 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 432 | 22.3 | 52.8 | 417 |  | 2020-09-16 10:47 | 44090.4491 | 22.3 | 52.8 | 417 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:46
2020-09-16 10:47 | 44090.4493 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 2 | 18.5 | 62 | 410 | 20.2 | 57.5 | 497 |  | 2020-09-16 10:47 | 44090.4493 | 20.2 | 57.5 | 497 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 10:47
2020-09-16 10:47 | 44090.4496 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 1 | 20 | 62.4 | 387 | 22 | 49.9 | 517 |  | 2020-09-16 10:47 | 44090.4496 | 22 | 49.9 | 517 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:47
2020-09-16 10:48 | 44090.45 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 20.2 | 50.8 | 502 |  | 2020-09-16 10:48 | 44090.45 | 20.2 | 50.8 | 502 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:47
2020-09-16 10:48 | 44090.4501 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 417 | 22.1 | 56.3 | 414 |  | 2020-09-16 10:48 | 44090.4501 | 22.1 | 56.3 | 414 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:48
2020-09-16 10:48 | 44090.4502 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 49 | 620 |  | 2020-09-16 10:48 | 44090.4502 | 23 | 49 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:48
2020-09-16 10:49 | 44090.4506 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 4 | 20 | 62.4 | 387 | 23.1 | 47.5 | 493 |  | 2020-09-16 10:49 | 44090.4506 | 23.1 | 47.5 | 493 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:48
2020-09-16 10:50 | 44090.4511 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 214.2 | 57.7 | 432 | 22.2 | 55.6 | 408 |  | 2020-09-16 10:50 | 44090.4511 | 22.2 | 55.6 | 408 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:49
2020-09-16 10:50 | 44090.4513 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23.4 | 46.5 | 491 |  | 2020-09-16 10:50 | 44090.4513 | 23.4 | 46.5 | 491 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:49
2020-09-16 10:50 | 44090.4515 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 2 | 18.5 | 62 | 410 | 20.2 | 53.9 | 501 |  | 2020-09-16 10:50 | 44090.4515 | 20.2 | 53.9 | 501 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 10:50
2020-09-16 10:50 | 44090.4515 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 20.1 | 53.2 | 689 |  | 2020-09-16 10:50 | 44090.4515 | 20.1 | 53.2 | 689 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:50
2020-09-16 10:50 | 44090.4517 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.2 | 57.7 | 432 | 21.8 | 55.7 | 403 |  | 2020-09-16 10:50 | 44090.4517 | 21.8 | 55.7 | 403 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 10:50
2020-09-16 10:51 | 44090.4518 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23.4 | 46.5 | 491 |  | 2020-09-16 10:51 | 44090.4518 | 23.4 | 46.5 | 491 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:50
2020-09-16 10:51 | 44090.4523 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 23 | 48.2 | 510 |  | 2020-09-16 10:51 | 44090.4523 | 23 | 48.2 | 510 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:51
2020-09-16 10:51 | 44090.4524 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 22.9 | 49.1 | 545 |  | 2020-09-16 10:51 | 44090.4524 | 22.9 | 49.1 | 545 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:51
2020-09-16 10:52 | 44090.4527 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 45.7 | 473 | 23.4 | 46 | 479 |  | 2020-09-16 10:52 | 44090.4527 | 23.4 | 46 | 479 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:51
2020-09-16 10:52 | 44090.4527 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 20.1 | 50.6 | 490 |  | 2020-09-16 10:52 | 44090.4527 | 20.1 | 50.6 | 490 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:51
2020-09-16 10:52 | 44090.4527 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 21.2 | 48.3 | 376 | 23.1 | 40.2 | 402 |  | 2020-09-16 10:52 | 44090.4527 | 23.1 | 40.2 | 402 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 10:51
2020-09-16 10:53 | 44090.4534 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 22.8 | 50.5 | 492 |  | 2020-09-16 10:53 | 44090.4534 | 22.8 | 50.5 | 492 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:52
2020-09-16 10:53 | 44090.4536 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 49 | 391 | 22.6 | 49.5 | 540 |  | 2020-09-16 10:53 | 44090.4536 | 22.6 | 49.5 | 540 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:53
2020-09-16 10:53 | 44090.4536 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 18.5 | 62.8 | 403 | 20.2 | 52.8 | 474 |  | 2020-09-16 10:53 | 44090.4536 | 20.2 | 52.8 | 474 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 10:53
2020-09-16 10:54 | 44090.4542 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 1 | 18.5 | 62 | 410 | 20.6 | 53.5 | 599 |  | 2020-09-16 10:54 | 44090.4542 | 20.6 | 53.5 | 599 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 10:54
2020-09-16 10:54 | 44090.4543 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 23 | 49.1 | 479 |  | 2020-09-16 10:54 | 44090.4543 | 23 | 49.1 | 479 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:54
2020-09-16 10:54 | 44090.4544 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 58.2 | 434 | 22.4 | 58 | 434 |  | 2020-09-16 10:54 | 44090.4544 | 22.4 | 58 | 434 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:54
2020-09-16 10:55 | 44090.4547 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 2 | 17 | 71.7 | 391 | 22.8 | 47.6 | 469 |  | 2020-09-16 10:55 | 44090.4547 | 22.8 | 47.6 | 469 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:54
2020-09-16 10:55 | 44090.4548 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 17.5 | 63.4 | 369 | 23 | 43 | 369 |  | 2020-09-16 10:55 | 44090.4548 | 23 | 43 | 369 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 10:54
2020-09-16 10:55 | 44090.4549 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23.4 | 45.7 | 479 |  | 2020-09-16 10:55 | 44090.4549 | 23.4 | 45.7 | 479 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:55
2020-09-16 10:55 | 44090.4551 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 21.2 | 48.3 | 376 | 22.7 | 41.3 | 399 |  | 2020-09-16 10:55 | 44090.4551 | 22.7 | 41.3 | 399 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 10:55
2020-09-16 10:56 | 44090.4553 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 4 | 17.5 | 69 | 384 | 23.3 | 53.3 | 460 |  | 2020-09-16 10:56 | 44090.4553 | 23.3 | 53.3 | 460 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:55
2020-09-16 10:56 | 44090.4557 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 49 | 630 |  | 2020-09-16 10:56 | 44090.4557 | 23 | 49 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:56
2020-09-16 10:56 | 44090.4558 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 0 | 18.5 | 62 | 410 | 21 | 50.3 | 431 | Dehumidifier is running | 2020-09-16 10:56 | 44090.4558 | 21 | 50.3 | 431 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 10:56
2020-09-16 10:56 | 44090.4558 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 17.5 | 63.4 | 369 | 23 | 43 | 385 |  | 2020-09-16 10:56 | 44090.4558 | 23 | 43 | 385 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 10:56
2020-09-16 10:57 | 44090.456 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23.5 | 45.6 | 477 |  | 2020-09-16 10:57 | 44090.456 | 23.5 | 45.6 | 477 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 10:56
2020-09-16 10:57 | 44090.4563 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 20.5 | 57.3 | 428 |  | 2020-09-16 10:57 | 44090.4563 | 20.5 | 57.3 | 428 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 10:57
2020-09-16 10:57 | 44090.4564 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 3 | 20.4 | 62.5 | 384 | 21 | 56.3 | 528 |  | 2020-09-16 10:57 | 44090.4564 | 21 | 56.3 | 528 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 10:57
2020-09-16 10:57 | 44090.4564 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 5 | 17 | 71.7 | 391 | 22.6 | 50 | 563 |  | 2020-09-16 10:57 | 44090.4564 | 22.6 | 50 | 563 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:57
2020-09-16 10:58 | 44090.4568 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 49 | 660 |  | 2020-09-16 10:58 | 44090.4568 | 23 | 49 | 660 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:57
2020-09-16 10:58 | 44090.4569 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 4 | 20 | 62 | 385 | 21.2 | 52.5 | 522 |  | 2020-09-16 10:58 | 44090.4569 | 21.2 | 52.5 | 522 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 10:57
2020-09-16 10:58 | 44090.4569 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 6 | 20 | 55 | 400 | 20 | 54 | 587 |  | 2020-09-16 10:58 | 44090.4569 | 20 | 54 | 587 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 10:57
2020-09-16 10:58 | 44090.457 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 21.2 | 48.3 | 376 | 22.6 | 41.9 | 405 |  | 2020-09-16 10:58 | 44090.457 | 22.6 | 41.9 | 405 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 10:58
2020-09-16 10:58 | 44090.4572 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 22.8 | 50.7 | 466 |  | 2020-09-16 10:58 | 44090.4572 | 22.8 | 50.7 | 466 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:58
2020-09-16 10:58 | 44090.4572 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 22.8 | 50.2 | 547 |  | 2020-09-16 10:58 | 44090.4572 | 22.8 | 50.2 | 547 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 10:58
2020-09-16 10:58 | 44090.4573 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.4 | 58.2 | 438 |  | 2020-09-16 10:58 | 44090.4573 | 22.4 | 58.2 | 438 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 10:58
2020-09-16 10:59 | 44090.4574 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 21 | 50.4 | 437 | No | 2020-09-16 10:59 | 44090.4574 | 21 | 50.4 | 437 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 10:58
2020-09-16 10:59 | 44090.4576 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 6 | 20.4 | 62.5 | 384 | 21.2 | 54.6 | 469 |  | 2020-09-16 10:59 | 44090.4576 | 21.2 | 54.6 | 469 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 10:58
2020-09-16 10:59 | 44090.4577 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 0 | 18.5 | 62 | 410 | 19.7 | 48.8 | 492 | Air conditioner running,set to 17c | 2020-09-16 10:59 | 44090.4577 | 19.7 | 48.8 | 492 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 10:59
2020-09-16 10:59 | 44090.4579 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 20 | 55 | 400 | 20.2 | 53.4 | 576 |  | 2020-09-16 10:59 | 44090.4579 | 20.2 | 53.4 | 576 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 10:59
2020-09-16 11:00 | 44090.458 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 3 | 20 | 67 | 385 | 21.7 | 51 | 567 |  | 2020-09-16 11:00 | 44090.458 | 21.7 | 51 | 567 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 10:59
2020-09-16 11:00 | 44090.4583 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23.5 | 48 | 630 |  | 2020-09-16 11:00 | 44090.4583 | 23.5 | 48 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 10:59
2020-09-16 11:00 | 44090.4583 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 21.2 | 48.3 | 376 | 22.7 | 41.7 | 404 |  | 2020-09-16 11:00 | 44090.4583 | 22.7 | 41.7 | 404 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 10:59
2020-09-16 11:00 | 44090.4584 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 23 | 49.8 | 465 |  | 2020-09-16 11:00 | 44090.4584 | 23 | 49.8 | 465 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:00
2020-09-16 11:00 | 44090.4585 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 3 | 20.4 | 62.5 | 384 | 21.5 | 53.6 | 482 |  | 2020-09-16 11:00 | 44090.4585 | 21.5 | 53.6 | 482 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:00
2020-09-16 11:01 | 44090.4587 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 3 | 20 | 62 | 385 | 21.8 | 50.5 | 590 |  | 2020-09-16 11:01 | 44090.4587 | 21.8 | 50.5 | 590 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:00
2020-09-16 11:01 | 44090.4589 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 22.8 | 49.2 | 540 |  | 2020-09-16 11:01 | 44090.4589 | 22.8 | 49.2 | 540 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:00
2020-09-16 11:01 | 44090.4589 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 20 | 55 | 400 | 20 | 54 | 532 |  | 2020-09-16 11:01 | 44090.4589 | 20 | 54 | 532 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 11:00
2020-09-16 11:01 | 44090.4592 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 1 | 18.5 | 62 | 410 | 20.2 | 53.2 | 510 |  | 2020-09-16 11:01 | 44090.4592 | 20.2 | 53.2 | 510 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 11:01
2020-09-16 11:01 | 44090.4593 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 23 | 49.7 | 456 |  | 2020-09-16 11:01 | 44090.4593 | 23 | 49.7 | 456 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:01
2020-09-16 11:02 | 44090.4595 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 49 | 630 |  | 2020-09-16 11:02 | 44090.4595 | 23 | 49 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 11:01
2020-09-16 11:02 | 44090.4596 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 20.4 | 62.5 | 384 | 21.5 | 53.2 | 455 |  | 2020-09-16 11:02 | 44090.4596 | 21.5 | 53.2 | 455 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:01
2020-09-16 11:02 | 44090.4596 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 22 | 49.3 | 500 |  | 2020-09-16 11:02 | 44090.4596 | 22 | 49.3 | 500 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:01
2020-09-16 11:02 | 44090.4597 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 21.2 | 48.3 | 376 | 22.9 | 42.1 | 405 |  | 2020-09-16 11:02 | 44090.4597 | 22.9 | 42.1 | 405 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:01
2020-09-16 11:02 | 44090.4598 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 1 | 16 | 69 | 383 | 21.4 | 49.2 | 436 | No | 2020-09-16 11:02 | 44090.4598 | 21.4 | 49.2 | 436 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 11:02
2020-09-16 11:03 | 44090.4601 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 22.8 | 50.7 | 499 |  | 2020-09-16 11:03 | 44090.4601 | 22.8 | 50.7 | 499 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:02
2020-09-16 11:03 | 44090.4601 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 17.5 | 63.4 | 369 | 23 | 44 | 372 |  | 2020-09-16 11:03 | 44090.4601 | 23 | 44 | 372 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 11:02
2020-09-16 11:03 | 44090.4601 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 20 | 55 | 400 | 19.6 | 54 | 492 |  | 2020-09-16 11:03 | 44090.4601 | 19.6 | 54 | 492 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 11:02
2020-09-16 11:03 | 44090.4603 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 1 | 22.2 | 45.4 | 430 | 23.2 | 45.7 | 487 |  | 2020-09-16 11:03 | 44090.4603 | 23.2 | 45.7 | 487 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 11:02
2020-09-16 11:03 | 44090.4603 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 2 | 17 | 71.7 | 391 | 23 | 50.2 | 462 |  | 2020-09-16 11:03 | 44090.4603 | 23 | 50.2 | 462 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:02
2020-09-16 11:03 | 44090.4605 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 21.5 | 53.1 | 448 |  | 2020-09-16 11:03 | 44090.4605 | 21.5 | 53.1 | 448 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:03
2020-09-16 11:03 | 44090.4607 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 2 | 20 | 62 | 385 | 22.3 | 47.9 | 455 |  | 2020-09-16 11:03 | 44090.4607 | 22.3 | 47.9 | 455 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:03
2020-09-16 11:04 | 44090.4608 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 20 | 55 | 400 | 19.6 | 60 | 575 |  | 2020-09-16 11:04 | 44090.4608 | 19.6 | 60 | 575 |  | caution | 2020-09-14 | B20474¦¦¦Sep-16-2020 11:03
2020-09-16 11:04 | 44090.4611 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 21.2 | 48.3 | 376 | 22.7 | 40.9 | 402 |  | 2020-09-16 11:04 | 44090.4611 | 22.7 | 40.9 | 402 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:03
2020-09-16 11:04 | 44090.4611 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 23.1 | 50.1 | 506 |  | 2020-09-16 11:04 | 44090.4611 | 23.1 | 50.1 | 506 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:04
2020-09-16 11:04 | 44090.4613 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 3 | 22.2 | 45.4 | 519 | 22.6 | 45.8 | 521 |  | 2020-09-16 11:04 | 44090.4613 | 22.6 | 45.8 | 521 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 11:04
2020-09-16 11:04 | 44090.4613 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 0 | 18.5 | 62 | 410 | 20.6 | 51.3 | 447 |  | 2020-09-16 11:04 | 44090.4613 | 20.6 | 51.3 | 447 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 11:04
2020-09-16 11:04 | 44090.4614 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 22.7 | 51.5 | 437 |  | 2020-09-16 11:04 | 44090.4614 | 22.7 | 51.5 | 437 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:04
2020-09-16 11:05 | 44090.4615 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 52.5 | 384 | 22 | 52.7 | 440 |  | 2020-09-16 11:05 | 44090.4615 | 22 | 52.7 | 440 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:04
2020-09-16 11:05 | 44090.4616 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23.5 | 48 | 610 |  | 2020-09-16 11:05 | 44090.4616 | 23.5 | 48 | 610 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 11:04
2020-09-16 11:05 | 44090.4617 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 20 | 55 | 400 | 20 | 57 | 506 |  | 2020-09-16 11:05 | 44090.4617 | 20 | 57 | 506 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 11:04
2020-09-16 11:05 | 44090.462 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 21.2 | 48.3 | 376 | 22.4 | 41.7 | 402 |  | 2020-09-16 11:05 | 44090.462 | 22.4 | 41.7 | 402 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:05
2020-09-16 11:05 | 44090.462 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 23.2 | 52 | 467 |  | 2020-09-16 11:05 | 44090.462 | 23.2 | 52 | 467 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:05
2020-09-16 11:06 | 44090.4622 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 23.2 | 49.2 | 471 |  | 2020-09-16 11:06 | 44090.4622 | 23.2 | 49.2 | 471 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:05
2020-09-16 11:06 | 44090.4623 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 0 | 18.5 | 62 | 410 | 20.4 | 51.9 | 449 |  | 2020-09-16 11:06 | 44090.4623 | 20.4 | 51.9 | 449 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 11:05
2020-09-16 11:06 | 44090.4623 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 20 | 55 | 400 | 20 | 55 | 479 |  | 2020-09-16 11:06 | 44090.4623 | 20 | 55 | 479 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 11:05
2020-09-16 11:06 | 44090.4623 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 7 | 25.4 | 53.5 | 423 | 22.9 | 49.6 | 480 | No | 2020-09-16 11:06 | 44090.4623 | 22.9 | 49.6 | 480 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:05
2020-09-16 11:06 | 44090.4623 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 4 | 22.2 | 45.4 | 430 | 22.6 | 49 | 506 |  | 2020-09-16 11:06 | 44090.4623 | 22.6 | 49 | 506 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 11:05
2020-09-16 11:06 | 44090.4624 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 17.5 | 63.4 | 372 | 23 | 44 | 367 |  | 2020-09-16 11:06 | 44090.4624 | 23 | 44 | 367 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 11:05
2020-09-16 11:06 | 44090.4624 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 20.4 | 62.5 | 384 | 22.4 | 50.9 | 422 |  | 2020-09-16 11:06 | 44090.4624 | 22.4 | 50.9 | 422 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:05
2020-09-16 11:07 | 44090.4629 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 2 | 17 | 71.7 | 391 | 23.1 | 51.5 | 470 |  | 2020-09-16 11:07 | 44090.4629 | 23.1 | 51.5 | 470 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:06
2020-09-16 11:07 | 44090.4629 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 4 | 16 | 69 | 383 | 21.8 | 42.7 | 526 | No | 2020-09-16 11:07 | 44090.4629 | 21.8 | 42.7 | 526 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 11:06
2020-09-16 11:07 | 44090.463 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 48 | 615 |  | 2020-09-16 11:07 | 44090.463 | 23 | 48 | 615 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 11:06
2020-09-16 11:07 | 44090.463 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 22.8 | 45.8 | 431 |  | 2020-09-16 11:07 | 44090.463 | 22.8 | 45.8 | 431 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:06
2020-09-16 11:07 | 44090.463 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 23.3 | 48.9 | 458 |  | 2020-09-16 11:07 | 44090.463 | 23.3 | 48.9 | 458 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:06
2020-09-16 11:07 | 44090.4634 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 22.6 | 49.8 | 423 |  | 2020-09-16 11:07 | 44090.4634 | 22.6 | 49.8 | 423 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:07
2020-09-16 11:08 | 44090.4637 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 2 | 22.2 | 45.4 | 430 | 22.6 | 49.4 | 524 |  | 2020-09-16 11:08 | 44090.4637 | 22.6 | 49.4 | 524 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 11:07
2020-09-16 11:08 | 44090.4637 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 22.9 | 47.6 | 428 |  | 2020-09-16 11:08 | 44090.4637 | 22.9 | 47.6 | 428 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:07
2020-09-16 11:08 | 44090.4638 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 3 | 423 | 25.4 | 53.5 | 23.2 | 48.9 | 466 | No | 2020-09-16 11:08 | 44090.4638 | 23.2 | 48.9 | 466 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:07
2020-09-16 11:08 | 44090.464 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23.5 | 48 | 610 |  | 2020-09-16 11:08 | 44090.464 | 23.5 | 48 | 610 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 11:08
2020-09-16 11:09 | 44090.4643 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 23.2 | 44.4 | 49.1 |  | 2020-09-16 11:09 | 44090.4643 | 23.2 | 44.4 | 49.1 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:08
2020-09-16 11:09 | 44090.4645 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 1 | 18.5 | 62 | 410 | 20.5 | 52.7 | 469 |  | 2020-09-16 11:09 | 44090.4645 | 20.5 | 52.7 | 469 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 11:08
2020-09-16 11:09 | 44090.4645 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 22.6 | 49.3 | 411 |  | 2020-09-16 11:09 | 44090.4645 | 22.6 | 49.3 | 411 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:08
2020-09-16 11:09 | 44090.4646 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 22.8 | 48.5 | 418 |  | 2020-09-16 11:09 | 44090.4646 | 22.8 | 48.5 | 418 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:09
2020-09-16 11:09 | 44090.4646 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 3 | 22.2 | 45.4 | 430 | 22.7 | 49.3 | 538 |  | 2020-09-16 11:09 | 44090.4646 | 22.7 | 49.3 | 538 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 11:09
2020-09-16 11:09 | 44090.4647 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 25.4 | 53.5 | 423 | 23.1 | 51.9 | 430 | No | 2020-09-16 11:09 | 44090.4647 | 23.1 | 51.9 | 430 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:09
2020-09-16 11:09 | 44090.4647 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 21.2 | 48.3 | 376 | 22.4 | 41.7 | 402 |  | 2020-09-16 11:09 | 44090.4647 | 22.4 | 41.7 | 402 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:09
2020-09-16 11:09 | 44090.4649 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 4 | 16 | 69 | 383 | 22.3 | 44.5 | 593 | No | 2020-09-16 11:09 | 44090.4649 | 22.3 | 44.5 | 593 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 11:09
2020-09-16 11:10 | 44090.4651 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23.5 | 48 | 610 |  | 2020-09-16 11:10 | 44090.4651 | 23.5 | 48 | 610 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 11:09
2020-09-16 11:10 | 44090.4652 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 22.8 | 45.2 | 382 |  | 2020-09-16 11:10 | 44090.4652 | 22.8 | 45.2 | 382 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:09
2020-09-16 11:10 | 44090.4652 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 23.3 | 49.8 | 476 |  | 2020-09-16 11:10 | 44090.4652 | 23.3 | 49.8 | 476 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:09
2020-09-16 11:10 | 44090.4653 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 22.4 | 51.1 | 422 |  | 2020-09-16 11:10 | 44090.4653 | 22.4 | 51.1 | 422 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:10
2020-09-16 11:10 | 44090.4654 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 22.8 | 48.4 | 399 |  | 2020-09-16 11:10 | 44090.4654 | 22.8 | 48.4 | 399 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:10
2020-09-16 11:10 | 44090.4655 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 3 | 18.5 | 62 | 410 | 22.9 | 45.9 | 532 |  | 2020-09-16 11:10 | 44090.4655 | 22.9 | 45.9 | 532 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 11:10
2020-09-16 11:11 | 44090.466 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 5 | 20 | 62 | 385 | 22 | 54.5 | 436 |  | 2020-09-16 11:11 | 44090.466 | 22 | 54.5 | 436 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:11
2020-09-16 11:11 | 44090.4662 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 0 | 22.2 | 45.4 | 430 | 22.5 | 49.2 | 441 |  | 2020-09-16 11:11 | 44090.4662 | 22.5 | 49.2 | 441 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 11:11
2020-09-16 11:11 | 44090.4662 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 3 | 25.4 | 53.5 | 423 | 22.3 | 41.5 | 454 | No | 2020-09-16 11:11 | 44090.4662 | 22.3 | 41.5 | 454 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:11
2020-09-16 11:12 | 44090.4664 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 21.2 | 48.3 | 376 | 22.4 | 41.7 | 402 |  | 2020-09-16 11:12 | 44090.4664 | 22.4 | 41.7 | 402 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:11
2020-09-16 11:12 | 44090.4665 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 23.6 | 50.5 | 473 |  | 2020-09-16 11:12 | 44090.4665 | 23.6 | 50.5 | 473 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:11
2020-09-16 11:12 | 44090.4665 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 22.8 | 48.3 | 393 |  | 2020-09-16 11:12 | 44090.4665 | 22.8 | 48.3 | 393 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:11
2020-09-16 11:12 | 44090.4668 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 22.9 | 23.4 | 62.3 | 447 |  | 2020-09-16 11:12 | 44090.4668 | 23.4 | 62.3 | 447 |  | caution | 2020-09-14 | B17477¦¦¦Sep-16-2020 11:12
2020-09-16 11:12 | 44090.4668 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 56 | 380 | 20.4 | 53.5 | 386 | No | 2020-09-16 11:12 | 44090.4668 | 20.4 | 53.5 | 386 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:12
2020-09-16 11:12 | 44090.467 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 22.5 | 48.5 | 482 |  | 2020-09-16 11:12 | 44090.467 | 22.5 | 48.5 | 482 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:12
2020-09-16 11:13 | 44090.4671 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 21.6 | 53.1 | 436 |  | 2020-09-16 11:13 | 44090.4671 | 21.6 | 53.1 | 436 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:12
2020-09-16 11:13 | 44090.4672 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 56 | 380 | 20.4 | 53.5 | 386 | No | 2020-09-16 11:13 | 44090.4672 | 20.4 | 53.5 | 386 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:12
2020-09-16 11:13 | 44090.4672 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 22.7 | 49 | 397 |  | 2020-09-16 11:13 | 44090.4672 | 22.7 | 49 | 397 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:12
2020-09-16 11:13 | 44090.4672 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 0 | 22.2 | 45.4 | 430 | 22.6 | 52.3 | 485 |  | 2020-09-16 11:13 | 44090.4672 | 22.6 | 52.3 | 485 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 11:12
2020-09-16 11:13 | 44090.4673 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.4 | 47.8 | 429 | No | 2020-09-16 11:13 | 44090.4673 | 22.4 | 47.8 | 429 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 11:12
2020-09-16 11:13 | 44090.4675 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 7 | 25.4 | 53.5 | 423 | 21.8 | 45.6 | 517 | No | 2020-09-16 11:13 | 44090.4675 | 21.8 | 45.6 | 517 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:13
2020-09-16 11:14 | 44090.4679 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 24 | 48 | 630 |  | 2020-09-16 11:14 | 44090.4679 | 24 | 48 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 11:13
2020-09-16 11:14 | 44090.4679 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 2 | 17 | 71.7 | 391 | 23.3 | 51.4 | 489 |  | 2020-09-16 11:14 | 44090.4679 | 23.3 | 51.4 | 489 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:13
2020-09-16 11:14 | 44090.4682 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 0 | 22.2 | 45.4 | 430 | 22.6 | 49.9 | 446 |  | 2020-09-16 11:14 | 44090.4682 | 22.6 | 49.9 | 446 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 11:14
2020-09-16 11:14 | 44090.4683 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 22 | 50 | 419 |  | 2020-09-16 11:14 | 44090.4683 | 22 | 50 | 419 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:14
2020-09-16 11:14 | 44090.4683 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 21.3 | 59.7 | 402 |  | 2020-09-16 11:14 | 44090.4683 | 21.3 | 59.7 | 402 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:14
2020-09-16 11:15 | 44090.4685 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 20.4 | 53.7 | 388 | No | 2020-09-16 11:15 | 44090.4685 | 20.4 | 53.7 | 388 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:14
2020-09-16 11:15 | 44090.4685 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 23.6 | 62.3 | 446 |  | 2020-09-16 11:15 | 44090.4685 | 23.6 | 62.3 | 446 |  | caution | 2020-09-14 | B17477¦¦¦Sep-16-2020 11:14
2020-09-16 11:15 | 44090.469 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 23.1 | 50.2 | 494 |  | 2020-09-16 11:15 | 44090.469 | 23.1 | 50.2 | 494 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:15
2020-09-16 11:16 | 44090.4692 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 21.2 | 48.3 | 376 | 22.4 | 41.7 | 402 |  | 2020-09-16 11:16 | 44090.4692 | 22.4 | 41.7 | 402 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:15
2020-09-16 11:16 | 44090.4693 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 22.1 | 50.1 | 412 |  | 2020-09-16 11:16 | 44090.4693 | 22.1 | 50.1 | 412 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:15
2020-09-16 11:16 | 44090.4693 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 17.5 | 63.4 | 369 | 23 | 44 | 369 |  | 2020-09-16 11:16 | 44090.4693 | 23 | 44 | 369 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 11:15
2020-09-16 11:16 | 44090.4694 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 3 | 20 | 62 | 385 | 21.6 | 53.1 | 458 |  | 2020-09-16 11:16 | 44090.4694 | 21.6 | 53.1 | 458 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:15
2020-09-16 11:16 | 44090.4695 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 25.4 | 53.5 | 423 | 23.1 | 50.6 | 338 | No | 2020-09-16 11:16 | 44090.4695 | 23.1 | 50.6 | 338 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:16
2020-09-16 11:16 | 44090.4696 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 0 | 22.2 | 45.4 | 430 | 22.6 | 49.9 | 457 |  | 2020-09-16 11:16 | 44090.4696 | 22.6 | 49.9 | 457 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 11:16
2020-09-16 11:16 | 44090.4696 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 24 | 49 | 620 |  | 2020-09-16 11:16 | 44090.4696 | 24 | 49 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 11:16
2020-09-16 11:17 | 44090.4698 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 22.8 | 52.4 | 484 |  | 2020-09-16 11:17 | 44090.4698 | 22.8 | 52.4 | 484 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:16
2020-09-16 11:17 | 44090.47 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 2 | 20 | 62 | 385 | 21.8 | 52.1 | 473 |  | 2020-09-16 11:17 | 44090.47 | 21.8 | 52.1 | 473 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:16
2020-09-16 11:17 | 44090.4701 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 22.1 | 50.5 | 404 |  | 2020-09-16 11:17 | 44090.4701 | 22.1 | 50.5 | 404 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:16
2020-09-16 11:17 | 44090.4701 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 23.3 | 50.2 | 421 |  | 2020-09-16 11:17 | 44090.4701 | 23.3 | 50.2 | 421 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 11:16
2020-09-16 11:17 | 44090.4701 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 21.2 | 48.3 | 376 | 22.4 | 41.7 | 402 |  | 2020-09-16 11:17 | 44090.4701 | 22.4 | 41.7 | 402 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:17
2020-09-16 11:17 | 44090.4702 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.1 | 48.3 | 453 | No | 2020-09-16 11:17 | 44090.4702 | 22.1 | 48.3 | 453 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 11:17
2020-09-16 11:18 | 44090.4706 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 20.7 | 53.3 | 417 | No | 2020-09-16 11:18 | 44090.4706 | 20.7 | 53.3 | 417 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:17
2020-09-16 11:18 | 44090.4706 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 25.5 | 53.5 | 423 | 23.4 | 49.8 | 439 | No | 2020-09-16 11:18 | 44090.4706 | 23.4 | 49.8 | 439 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:17
2020-09-16 11:18 | 44090.4707 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 2 | 20 | 62 | 385 | 22 | 51.3 | 485 |  | 2020-09-16 11:18 | 44090.4707 | 22 | 51.3 | 485 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:17
2020-09-16 11:18 | 44090.4709 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 17.5 | 63.4 | 369 | 23 | 45 | 391 |  | 2020-09-16 11:18 | 44090.4709 | 23 | 45 | 391 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 11:18
2020-09-16 11:19 | 44090.4712 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 23 | 51.3 | 414 |  | 2020-09-16 11:19 | 44090.4712 | 23 | 51.3 | 414 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 11:18
2020-09-16 11:19 | 44090.4713 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 18 | 24 | 49 | 640 |  | 2020-09-16 11:19 | 44090.4713 | 24 | 49 | 640 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 11:18
2020-09-16 11:19 | 44090.4713 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 22.6 | 49 | 408 |  | 2020-09-16 11:19 | 44090.4713 | 22.6 | 49 | 408 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:18
2020-09-16 11:19 | 44090.4713 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 23.1 | 50.4 | 476 |  | 2020-09-16 11:19 | 44090.4713 | 23.1 | 50.4 | 476 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:18
2020-09-16 11:19 | 44090.4718 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 21.2 | 48.3 | 376 | 23.2 | 41.7 | 435 |  | 2020-09-16 11:19 | 44090.4718 | 23.2 | 41.7 | 435 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:19
2020-09-16 11:19 | 44090.4719 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 22.5 | 48.5 | 482 |  | 2020-09-16 11:19 | 44090.4719 | 22.5 | 48.5 | 482 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:19
2020-09-16 11:19 | 44090.4719 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 22 | 49 | 455 |  | 2020-09-16 11:20 | 44090.4719 | 22 | 49 | 455 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:19
2020-09-16 11:20 | 44090.4721 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 22.6 | 49 | 414 |  | 2020-09-16 11:20 | 44090.4721 | 22.6 | 49 | 414 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:19
2020-09-16 11:20 | 44090.4721 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 17.5 | 63.4 | 369 | 23 | 45 | 379 |  | 2020-09-16 11:20 | 44090.4721 | 23 | 45 | 379 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 11:19
2020-09-16 11:20 | 44090.4721 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 24 | 48 | 630 |  | 2020-09-16 11:20 | 44090.4721 | 24 | 48 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 11:19
2020-09-16 11:20 | 44090.4722 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 4 | 25.4 | 53.5 | 423 | 24.8 | 47.5 | 428 | No | 2020-09-16 11:20 | 44090.4722 | 24.8 | 47.5 | 428 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:20
2020-09-16 11:20 | 44090.4723 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 21.7 | 51.2 | 418 | No | 2020-09-16 11:20 | 44090.4723 | 21.7 | 51.2 | 418 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:20
2020-09-16 11:20 | 44090.4724 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 21.9 | 49.9 | 446 | No | 2020-09-16 11:20 | 44090.4724 | 21.9 | 49.9 | 446 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 11:20
2020-09-16 11:21 | 44090.4727 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 22 | 48.4 | 457 |  | 2020-09-16 11:21 | 44090.4727 | 22 | 48.4 | 457 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:20
2020-09-16 11:21 | 44090.4732 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 22.4 | 50 | 408 |  | 2020-09-16 11:21 | 44090.4732 | 22.4 | 50 | 408 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:21
2020-09-16 11:21 | 44090.4732 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 24 | 48 | 620 |  | 2020-09-16 11:21 | 44090.4732 | 24 | 48 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 11:21
2020-09-16 11:22 | 44090.4733 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 22.1 | 49 | 460 |  | 2020-09-16 11:22 | 44090.4733 | 22.1 | 49 | 460 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:21
2020-09-16 11:22 | 44090.4733 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 23 | 54.3 | 431 |  | 2020-09-16 11:22 | 44090.4733 | 23 | 54.3 | 431 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 11:21
2020-09-16 11:23 | 44090.474 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 24 | 48 | 620 |  | 2020-09-16 11:23 | 44090.474 | 24 | 48 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 11:22
2020-09-16 11:23 | 44090.4741 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 22.5 | 48.3 | 425 | No | 2020-09-16 11:23 | 44090.4741 | 22.5 | 48.3 | 425 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:22
2020-09-16 11:23 | 44090.4743 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 22 | 47.6 | 478 |  | 2020-09-16 11:23 | 44090.4743 | 22 | 47.6 | 478 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:23
2020-09-16 11:23 | 44090.4745 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 21.2 | 48.3 | 376 | 23.4 | 41.5 | 430 |  | 2020-09-16 11:23 | 44090.4745 | 23.4 | 41.5 | 430 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:23
2020-09-16 11:23 | 44090.4746 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 3 | 16 | 69 | 383 | 21.8 | 49.8 | 576 | No | 2020-09-16 11:23 | 44090.4746 | 21.8 | 49.8 | 576 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 11:23
2020-09-16 11:24 | 44090.4748 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 22 | 49.7 | 426 |  | 2020-09-16 11:24 | 44090.4748 | 22 | 49.7 | 426 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:23
2020-09-16 11:24 | 44090.4749 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 25.4 | 53.5 | 423 | 23.8 | 48.3 | 412 | No | 2020-09-16 11:24 | 44090.4749 | 23.8 | 48.3 | 412 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:23
2020-09-16 11:24 | 44090.4749 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 20 | 55 | 400 | 20.2 | 53 | 500 |  | 2020-09-16 11:24 | 44090.4749 | 20.2 | 53 | 500 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 11:23
2020-09-16 11:24 | 44090.475 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 21.9 | 47.9 | 478 |  | 2020-09-16 11:24 | 44090.475 | 21.9 | 47.9 | 478 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:23
2020-09-16 11:24 | 44090.475 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 24 | 48 | 620 |  | 2020-09-16 11:24 | 44090.475 | 24 | 48 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 11:24
2020-09-16 11:25 | 44090.4754 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.7 | 56.3 | 433 |  | 2020-09-16 11:25 | 44090.4754 | 22.7 | 56.3 | 433 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 11:24
2020-09-16 11:25 | 44090.4755 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 21.2 | 48.3 | 376 | 23.5 | 41 | 422 |  | 2020-09-16 11:25 | 44090.4755 | 23.5 | 41 | 422 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:24
2020-09-16 11:25 | 44090.4756 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 22.2 | 48.1 | 405 |  | 2020-09-16 11:25 | 44090.4756 | 22.2 | 48.1 | 405 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:24
2020-09-16 11:25 | 44090.4756 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 22.1 | 47.8 | 478 |  | 2020-09-16 11:25 | 44090.4756 | 22.1 | 47.8 | 478 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:24
2020-09-16 11:25 | 44090.4759 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 24 | 48 | 690 |  | 2020-09-16 11:25 | 44090.4759 | 24 | 48 | 690 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 11:25
2020-09-16 11:26 | 44090.4765 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 8 | 25.4 | 53.5 | 423 | 23.6 | 49.4 | 475 | No | 2020-09-16 11:26 | 44090.4765 | 23.6 | 49.4 | 475 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:26
2020-09-16 11:26 | 44090.4765 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 22 | 50 | 628 | No | 2020-09-16 11:26 | 44090.4765 | 22 | 50 | 628 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 11:26
2020-09-16 11:26 | 44090.4766 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 20.4 | 62.5 | 384 | 22.2 | 49.5 | 402 |  | 2020-09-16 11:26 | 44090.4766 | 22.2 | 49.5 | 402 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:26
2020-09-16 11:26 | 44090.4766 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 22.8 | 46.9 | 417 | No | 2020-09-16 11:26 | 44090.4766 | 22.8 | 46.9 | 417 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:26
2020-09-16 11:26 | 44090.4766 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 17.5 | 63.4 | 369 | 22 | 46 | 373 |  | 2020-09-16 11:26 | 44090.4766 | 22 | 46 | 373 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 11:26
2020-09-16 11:27 | 44090.477 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 21.2 | 48.3 | 376 | 23.6 | 40.9 | 443 |  | 2020-09-16 11:27 | 44090.477 | 23.6 | 40.9 | 443 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:26
2020-09-16 11:27 | 44090.4773 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.7 | 56.2 | 436 |  | 2020-09-16 11:27 | 44090.4773 | 22.7 | 56.2 | 436 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 11:27
2020-09-16 11:27 | 44090.4774 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 17.5 | 63.4 | 369 | 22 | 46 | 373 |  | 2020-09-16 11:27 | 44090.4774 | 22 | 46 | 373 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 11:27
2020-09-16 11:28 | 44090.4775 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 18 | 67 | 440 | 23 | 49 | 600 |  | 2020-09-16 11:28 | 44090.4775 | 23 | 49 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 11:27
2020-09-16 11:28 | 44090.4776 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 22 | 47.3 | 501 |  | 2020-09-16 11:28 | 44090.4776 | 22 | 47.3 | 501 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:27
2020-09-16 11:28 | 44090.4778 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 23.1 | 48.9 | 421 |  | 2020-09-16 11:28 | 44090.4778 | 23.1 | 48.9 | 421 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:28
2020-09-16 11:29 | 44090.4782 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 1 | 16 | 69 | 383 | 22.6 | 47 | 490 | No | 2020-09-16 11:29 | 44090.4782 | 22.6 | 47 | 490 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 11:28
2020-09-16 11:29 | 44090.4782 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 4 | 25.4 | 53.5 | 423 | 22.9 | 52.8 | 465 | No | 2020-09-16 11:29 | 44090.4782 | 22.9 | 52.8 | 465 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:28
2020-09-16 11:29 | 44090.4783 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 22 | 47.1 | 494 |  | 2020-09-16 11:29 | 44090.4783 | 22 | 47.1 | 494 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 11:28
2020-09-16 11:29 | 44090.4784 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 20 | 55 | 400 | 20.3 | 53 | 487 |  | 2020-09-16 11:29 | 44090.4784 | 20.3 | 53 | 487 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 11:28
2020-09-16 11:29 | 44090.4786 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 17.5 | 63.4 | 369 | 22 | 46 | 373 |  | 2020-09-16 11:29 | 44090.4786 | 22 | 46 | 373 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 11:29
2020-09-16 11:29 | 44090.4787 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 23 | 47.1 | 422 |  | 2020-09-16 11:29 | 44090.4787 | 23 | 47.1 | 422 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:29
2020-09-16 11:30 | 44090.479 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 22.7 | 48.1 | 443 | No | 2020-09-16 11:30 | 44090.479 | 22.7 | 48.1 | 443 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:29
2020-09-16 11:30 | 44090.4793 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 2 | 20.3 | 55.3 | 426 | 22.8 | 49.4 | 472 |  | 2020-09-16 11:30 | 44090.4793 | 22.8 | 49.4 | 472 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 11:30
2020-09-16 11:30 | 44090.4793 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.5 | 54.5 | 433 |  | 2020-09-16 11:30 | 44090.4793 | 22.5 | 54.5 | 433 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 11:30
2020-09-16 11:30 | 44090.4794 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 22.4 | 47.6 | 416 |  | 2020-09-16 11:30 | 44090.4794 | 22.4 | 47.6 | 416 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:30
2020-09-16 11:31 | 44090.4797 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 6 | 25.4 | 53.5 | 423 | 22.2 | 51.7 | 487 | No | 2020-09-16 11:31 | 44090.4797 | 22.2 | 51.7 | 487 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:30
2020-09-16 11:31 | 44090.4797 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 17.5 | 63.4 | 369 | 22 | 46 | 373 |  | 2020-09-16 11:31 | 44090.4797 | 22 | 46 | 373 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 11:30
2020-09-16 11:32 | 44090.4804 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 17.5 | 63.4 | 369 | 22 | 46 | 373 |  | 2020-09-16 11:32 | 44090.4804 | 22 | 46 | 373 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 11:31
2020-09-16 11:32 | 44090.4806 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 1 | 20.3 | 55.3 | 426 | 23.5 | 47.3 | 451 |  | 2020-09-16 11:32 | 44090.4806 | 23.5 | 47.3 | 451 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 11:32
2020-09-16 11:33 | 44090.481 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 14 | 25.4 | 53.5 | 423 | 22.6 | 56.8 | 533 | No | 2020-09-16 11:33 | 44090.481 | 22.6 | 56.8 | 533 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:32
2020-09-16 11:33 | 44090.4811 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 21.2 | 48.3 | 376 | 23.8 | 40.3 | 428 |  | 2020-09-16 11:33 | 44090.4811 | 23.8 | 40.3 | 428 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:32
2020-09-16 11:33 | 44090.4812 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 17.5 | 63.4 | 369 | 22 | 47 | 372 |  | 2020-09-16 11:33 | 44090.4812 | 22 | 47 | 372 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 11:33
2020-09-16 11:34 | 44090.4818 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 23.3 | 44.8 | 420 | No | 2020-09-16 11:34 | 44090.4818 | 23.3 | 44.8 | 420 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:33
2020-09-16 11:34 | 44090.4819 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 21.2 | 48.3 | 376 | 23.8 | 39.8 | 457 |  | 2020-09-16 11:34 | 44090.4819 | 23.8 | 39.8 | 457 |  | caution | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:33
2020-09-16 11:34 | 44090.482 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 23 | 54.2 | 431 |  | 2020-09-16 11:34 | 44090.482 | 23 | 54.2 | 431 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 11:34
2020-09-16 11:34 | 44090.4822 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 3 | 25.4 | 53.5 | 423 | 23.1 | 48.4 | 511 | No | 2020-09-16 11:34 | 44090.4822 | 23.1 | 48.4 | 511 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:34
2020-09-16 11:36 | 44090.483 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 1 | 20.4 | 62.5 | 384 | 23.1 | 48.7 | 445 |  | 2020-09-16 11:36 | 44090.483 | 23.1 | 48.7 | 445 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 11:35
2020-09-16 11:36 | 44090.4835 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 7 | 25.4 | 53.5 | 423 | 23 | 45.5 | 459 | No | 2020-09-16 11:36 | 44090.4835 | 23 | 45.5 | 459 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:36
2020-09-16 11:36 | 44090.4836 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 0 | 20.3 | 55.3 | 426 | 25.5 | 42 | 452 |  | 2020-09-16 11:36 | 44090.4836 | 25.5 | 42 | 452 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 11:36
2020-09-16 11:37 | 44090.4839 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 21.2 | 48.3 | 376 | 22.9 | 41.8 | 431 |  | 2020-09-16 11:37 | 44090.4839 | 22.9 | 41.8 | 431 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:36
2020-09-16 11:37 | 44090.4841 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 23 | 54.6 | 445 |  | 2020-09-16 11:37 | 44090.4841 | 23 | 54.6 | 445 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 11:37
2020-09-16 11:38 | 44090.4848 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 3 | 25.4 | 53.5 | 423 | 23.1 | 49 | 448 | No | 2020-09-16 11:38 | 44090.4848 | 23.1 | 49 | 448 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:38
2020-09-16 11:39 | 44090.4853 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 3 | 20.5 | 55.3 | 426 | 25.5 | 42.7 | 496 |  | 2020-09-16 11:39 | 44090.4853 | 25.5 | 42.7 | 496 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 11:38
2020-09-16 11:39 | 44090.4854 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 2 | 20 | 58 | 388 | 22.8 | 47.6 | 450 | No | 2020-09-16 11:39 | 44090.4854 | 22.8 | 47.6 | 450 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:38
2020-09-16 11:40 | 44090.4859 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 6 | 25.4 | 53.5 | 423 | 22.6 | 52.2 | 445 | No | 2020-09-16 11:40 | 44090.4859 | 22.6 | 52.2 | 445 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 11:39
2020-09-16 11:40 | 44090.486 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 19.5 | 55 | 402 | 21 | 51.3 | 527 |  | 2020-09-16 11:40 | 44090.486 | 21 | 51.3 | 527 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 11:39
2020-09-16 11:40 | 44090.4861 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 21.2 | 48.3 | 376 | 23 | 42.4 | 402 |  | 2020-09-16 11:40 | 44090.4861 | 23 | 42.4 | 402 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:40
2020-09-16 11:40 | 44090.4863 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 20 | 50 | 390 | 23 | 41 | 537 |  | 2020-09-16 11:40 | 44090.4863 | 23 | 41 | 537 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 11:40
2020-09-16 11:41 | 44090.4867 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 1 | 20.3 | 55.3 | 426 | 24.6 | 43.5 | 463 |  | 2020-09-16 11:41 | 44090.4867 | 24.6 | 43.5 | 463 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 11:40
2020-09-16 11:41 | 44090.4867 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 2 | 20 | 50 | 390 | 23 | 44 | 549 |  | 2020-09-16 11:41 | 44090.4867 | 23 | 44 | 549 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 11:40
2020-09-16 11:41 | 44090.4871 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 20 | 50 | 390 | 23 | 43 | 546 |  | 2020-09-16 11:41 | 44090.4871 | 23 | 43 | 546 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 11:41
2020-09-16 11:42 | 44090.4872 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 1 | 20 | 58 | 388 | 23 | 46 | 445 | No | 2020-09-16 11:42 | 44090.4872 | 23 | 46 | 445 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:41
2020-09-16 11:42 | 44090.4877 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 1 | 20 | 50 | 490 | 23 | 45 | 529 |  | 2020-09-16 11:42 | 44090.4877 | 23 | 45 | 529 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 11:42
2020-09-16 11:42 | 44090.4878 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 20 | 61.5 | 370 | 21.1 | 54 | 434 |  | 2020-09-16 11:42 | 44090.4878 | 21.1 | 54 | 434 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 11:42
2020-09-16 11:43 | 44090.4885 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 1 | 20 | 58 | 388 | 22.9 | 46.9 | 436 | No | 2020-09-16 11:43 | 44090.4885 | 22.9 | 46.9 | 436 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:43
2020-09-16 11:43 | 44090.4885 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 4 | 19.5 | 554.6 | 402 | 20.8 | 51.3 | 492 |  | 2020-09-16 11:43 | 44090.4885 | 20.8 | 51.3 | 492 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 11:43
2020-09-16 11:44 | 44090.4886 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 1 | 20 | 50 | 390 | 22 | 46 | 523 |  | 2020-09-16 11:44 | 44090.4886 | 22 | 46 | 523 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 11:43
2020-09-16 11:44 | 44090.4887 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 20 | 61.5 | 370 | 21.8 | 53.6 | 412 |  | 2020-09-16 11:44 | 44090.4887 | 21.8 | 53.6 | 412 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 11:43
2020-09-16 11:44 | 44090.4889 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 21.2 | 48.3 | 376 | 23.1 | 42.2 | 403 |  | 2020-09-16 11:44 | 44090.4889 | 23.1 | 42.2 | 403 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:44
2020-09-16 11:44 | 44090.4891 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 20 | 50 | 390 | 22 | 41 | 522 |  | 2020-09-16 11:44 | 44090.4891 | 22 | 41 | 522 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 11:44
2020-09-16 11:45 | 44090.4895 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 20 | 61.5 | 370 | 23.6 | 56.1 | 457 |  | 2020-09-16 11:45 | 44090.4895 | 23.6 | 56.1 | 457 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 11:44
2020-09-16 11:45 | 44090.4896 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 20 | 58 | 388 | Yes court was in session | 2020-09-16 11:45 | 44090.4896 | 20 | 58 | 388 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:45
2020-09-16 11:45 | 44090.4896 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 20 | 50 | 430 | 22 | 42 | 544 |  | 2020-09-16 11:45 | 44090.4896 | 22 | 42 | 544 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 11:45
2020-09-16 11:46 | 44090.49 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 20 | 50 | 390 | 22 |  | 40 |  | 2020-09-16 11:46 | 44090.49 | 22 |  | 40 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 11:45
2020-09-16 11:46 | 44090.4901 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 0 | 16 | 69 | 383 | 21.3 | 48.8 | 445 | No | 2020-09-16 11:46 | 44090.4901 | 21.3 | 48.8 | 445 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 11:45
2020-09-16 11:46 | 44090.4901 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 0 | 20.3 | 55.3 | 426 | 24 | 44.9 | 455 |  | 2020-09-16 11:46 | 44090.4901 | 24 | 44.9 | 455 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 11:45
2020-09-16 11:46 | 44090.4902 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 20 | 61.5 | 370 | 20.7 | 54 | 441 |  | 2020-09-16 11:46 | 44090.4902 | 20.7 | 54 | 441 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 11:45
2020-09-16 11:46 | 44090.4905 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 20 | 50 | 390 | 22 | 44 | 561 |  | 2020-09-16 11:46 | 44090.4905 | 22 | 44 | 561 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 11:46
2020-09-16 11:47 | 44090.4909 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 4 | 20 | 50 | 390 | 22 | 43 | 568 |  | 2020-09-16 11:47 | 44090.4909 | 22 | 43 | 568 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 11:46
2020-09-16 11:47 | 44090.4909 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 3 | 20 | 61.5 | 370 | 22.1 | 54.5 | 460 |  | 2020-09-16 11:47 | 44090.4909 | 22.1 | 54.5 | 460 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 11:46
2020-09-16 11:47 | 44090.4912 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 5 | 19.5 | 54.6 | 402 | 21.5 | 50.2 | 519 |  | 2020-09-16 11:47 | 44090.4912 | 21.5 | 50.2 | 519 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 11:47
2020-09-16 11:47 | 44090.4912 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 0 | 20.3 | 55.3 | 426 | 24 | 45 | 467 |  | 2020-09-16 11:47 | 44090.4912 | 24 | 45 | 467 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 11:47
2020-09-16 11:47 | 44090.4913 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 21.2 | 48.3 | 376 | 23.7 | 42.7 | 450 |  | 2020-09-16 11:47 | 44090.4913 | 23.7 | 42.7 | 450 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:47
2020-09-16 11:47 | 44090.4913 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.9 | 55.3 | 433 |  | 2020-09-16 11:47 | 44090.4913 | 22.9 | 55.3 | 433 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 11:47
2020-09-16 11:47 | 44090.4913 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 2 | 20 | 50 | 390 | 22 | 43 | 562 |  | 2020-09-16 11:48 | 44090.4913 | 22 | 43 | 562 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 11:47
2020-09-16 11:48 | 44090.4914 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 0 | 16 | 69 | 383 | 21.3 | 49 | 452 | No | 2020-09-16 11:48 | 44090.4914 | 21.3 | 49 | 452 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 11:47
2020-09-16 11:48 | 44090.4916 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 20 | 61.5 | 370 | 22.3 | 53.7 | 453 |  | 2020-09-16 11:48 | 44090.4916 | 22.3 | 53.7 | 453 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 11:47
2020-09-16 11:48 | 44090.4916 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 22.5 | 48.7 | 458 | No | 2020-09-16 11:48 | 44090.4916 | 22.5 | 48.7 | 458 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:47
2020-09-16 11:48 | 44090.4918 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 20 | 50 | 390 | 22 | 44 | 567 | Couldn't get into courtroom 1,3 and 4 | 2020-09-16 11:48 | 44090.4918 | 22 | 44 | 567 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 11:48
2020-09-16 11:49 | 44090.4923 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 2 | 20 | 61.5 | 370 | 21.8 | 53.2 | 448 |  | 2020-09-16 11:49 | 44090.4923 | 21.8 | 53.2 | 448 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 11:48
2020-09-16 11:50 | 44090.4929 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 23 | 54.8 | 431 |  | 2020-09-16 11:50 | 44090.4929 | 23 | 54.8 | 431 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 11:49
2020-09-16 11:50 | 44090.493 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 20 | 61.5 | 370 | 23.9 | 56.2 | 438 |  | 2020-09-16 11:50 | 44090.493 | 23.9 | 56.2 | 438 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 11:49
2020-09-16 11:51 | 44090.4935 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 3 | 16 | 69 | 383 | 21.7 | 50.8 | 473 | No | 2020-09-16 11:51 | 44090.4935 | 21.7 | 50.8 | 473 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 11:50
2020-09-16 11:51 | 44090.4935 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 20.7 | 48.6 | 411 | No | 2020-09-16 11:51 | 44090.4935 | 20.7 | 48.6 | 411 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:50
2020-09-16 11:51 | 44090.4937 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 20 | 61.5 | 370 | 21.1 | 53.6 | 421 |  | 2020-09-16 11:51 | 44090.4937 | 21.1 | 53.6 | 421 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 11:50
2020-09-16 11:52 | 44090.4945 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 3 | 19.5 | 54.6 | 402 | 20.3 | 53.4 | 467 |  | 2020-09-16 11:52 | 44090.4945 | 20.3 | 53.4 | 467 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 11:52
2020-09-16 11:52 | 44090.4947 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 20.3 | 54 | 411 | No | 2020-09-16 11:52 | 44090.4947 | 20.3 | 54 | 411 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:52
2020-09-16 11:53 | 44090.4949 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 2 | 16 | 69 | 383 | 21.9 | 49.8 | 611 | No | 2020-09-16 11:53 | 44090.4949 | 21.9 | 49.8 | 611 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 11:52
2020-09-16 11:54 | 44090.4955 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.1 | 55.1 | 428 | 23 | 54.7 | 441 |  | 2020-09-16 11:54 | 44090.4955 | 23 | 54.7 | 441 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 11:53
2020-09-16 11:55 | 44090.4963 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 21.2 | 48.3 | 376 | 23.6 | 42.5 | 461 |  | 2020-09-16 11:55 | 44090.4963 | 23.6 | 42.5 | 461 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:54
2020-09-16 11:55 | 44090.4964 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.1 | 49.3 | 463 | No | 2020-09-16 11:55 | 44090.4964 | 22.1 | 49.3 | 463 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 11:54
2020-09-16 11:55 | 44090.4966 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 4 | 20 | 58 | 388 | 21.7 | 50.5 | 430 | No | 2020-09-16 11:55 | 44090.4966 | 21.7 | 50.5 | 430 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:55
2020-09-16 11:56 | 44090.4969 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 4 | 19.8 | 59 | 533 | 21.9 | 48.4 | 560 | Court 1 could not access | 2020-09-16 11:56 | 44090.4969 | 21.9 | 48.4 | 560 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 11:55
2020-09-16 11:56 | 44090.4971 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 23.1 | 47 | 551 |  | 2020-09-16 11:56 | 44090.4971 | 23.1 | 47 | 551 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:55
2020-09-16 11:57 | 44090.4976 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 3 | 19.5 | 54.6 | 402 | 19.9 | 54.5 | 496 |  | 2020-09-16 11:57 | 44090.4976 | 19.9 | 54.5 | 496 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 11:56
2020-09-16 11:57 | 44090.4978 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 21.2 | 48.3 | 376 | 23.5 | 43.5 | 539 |  | 2020-09-16 11:57 | 44090.4978 | 23.5 | 43.5 | 539 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:56
2020-09-16 11:57 | 44090.4979 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 22.1 | 49.2 | 423 | No | 2020-09-16 11:57 | 44090.4979 | 22.1 | 49.2 | 423 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:57
2020-09-16 11:57 | 44090.498 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.8 | 55.7 | 436 |  | 2020-09-16 11:57 | 44090.498 | 22.8 | 55.7 | 436 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 11:57
2020-09-16 11:57 | 44090.4981 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.5 | 47.8 | 478 | No | 2020-09-16 11:57 | 44090.4981 | 22.5 | 47.8 | 478 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 11:57
2020-09-16 11:57 | 44090.4981 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 1 | 20 | 53.6 | 442 | 22.4 | 46.2 | 714 | Yes | 2020-09-16 11:57 | 44090.4981 | 22.4 | 46.2 | 714 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 11:57
2020-09-16 11:58 | 44090.4984 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 5 | 17 | 71.7 | 391 | 22.9 | 47.6 | 554 |  | 2020-09-16 11:58 | 44090.4984 | 22.9 | 47.6 | 554 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:57
2020-09-16 11:58 | 44090.4985 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 22.5 | 47.4 | 507 |  | 2020-09-16 11:58 | 44090.4985 | 22.5 | 47.4 | 507 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:57
2020-09-16 11:58 | 44090.4987 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 21.2 | 48.3 | 376 | 23.2 | 45.5 | 557 |  | 2020-09-16 11:58 | 44090.4987 | 23.2 | 45.5 | 557 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 11:58
2020-09-16 11:59 | 44090.499 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 1 | 20 | 53.6 | 442 | 23.4 | 46.3 | 566 | Yes | 2020-09-16 11:58 | 44090.499 | 23.4 | 46.3 | 566 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 11:58
2020-09-16 11:59 | 44090.4994 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 2 | 17 | 71.7 | 391 | 23 | 47.7 | 461 |  | 2020-09-16 11:59 | 44090.4994 | 23 | 47.7 | 461 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:59
2020-09-16 11:59 | 44090.4996 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 1 | 20 | 53.6 | 442 | 22.3 | 48.9 | 492 | Yes | 2020-09-16 11:59 | 44090.4996 | 22.3 | 48.9 | 492 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 11:59
2020-09-16 11:59 | 44090.4996 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 22.5 | 48.7 | 426 | No | 2020-09-16 11:59 | 44090.4996 | 22.5 | 48.7 | 426 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 11:59
2020-09-16 12:00 | 44090.4998 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.3 | 47.4 | 478 | No | 2020-09-16 12:00 | 44090.4998 | 22.3 | 47.4 | 478 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 11:59
2020-09-16 12:00 | 44090.4998 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 22.7 | 50.9 | 478 |  | 2020-09-16 12:00 | 44090.4998 | 22.7 | 50.9 | 478 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 11:59
2020-09-16 12:00 | 44090.5001 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 1 | 20 | 53.6 | 442 | 22 | 47 | 625 | Yes | 2020-09-16 12:00 | 44090.5001 | 22 | 47 | 625 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 12:00
2020-09-16 12:00 | 44090.5002 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.9 | 55.4 | 436 |  | 2020-09-16 12:00 | 44090.5002 | 22.9 | 55.4 | 436 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 12:00
2020-09-16 12:00 | 44090.5002 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 3 | 19.5 | 54.6 | 402 | 20.2 | 53.7 | 487 |  | 2020-09-16 12:00 | 44090.5002 | 20.2 | 53.7 | 487 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 12:00
2020-09-16 12:01 | 44090.5006 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 18.9 | 60.8 | 421 | 22.2 | 52.5 | 497 | Courtrooms B,C and D had trial going on therefore access was denied. | 2020-09-16 12:01 | 44090.5006 | 22.2 | 52.5 | 497 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 12:00
2020-09-16 12:01 | 44090.5006 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 22.8 | 49.9 | 577 |  | 2020-09-16 12:01 | 44090.5006 | 22.8 | 49.9 | 577 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:00
2020-09-16 12:01 | 44090.5009 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 23 | 47.1 | 424 | No | 2020-09-16 12:01 | 44090.5009 | 23 | 47.1 | 424 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 12:01
2020-09-16 12:01 | 44090.5009 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 20 | 53.6 | 442 | 22 | 43 | 572 | Yes | 2020-09-16 12:01 | 44090.5009 | 22 | 43 | 572 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 12:01
2020-09-16 12:02 | 44090.5013 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 1 | 16 | 69 | 383 | 22.7 | 45.6 | 437 | No | 2020-09-16 12:02 | 44090.5013 | 22.7 | 45.6 | 437 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 12:01
2020-09-16 12:03 | 44090.5018 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.5 | 56.2 | 435 |  | 2020-09-16 12:03 | 44090.5018 | 22.5 | 56.2 | 435 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 12:02
2020-09-16 12:03 | 44090.5018 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 20 | 53.6 | 442 | 21 | 44 | 467 | Yes | 2020-09-16 12:03 | 44090.5018 | 21 | 44 | 467 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 12:02
2020-09-16 12:03 | 44090.5019 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 18.9 | 60.8 | 421 | 21.8 | 51.3 | 485 | Courtrooms B,C and D had trial going on therefore access was denied | 2020-09-16 12:03 | 44090.5019 | 21.8 | 51.3 | 485 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 12:02
2020-09-16 12:03 | 44090.5019 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 23 | 48 | 452 | No | 2020-09-16 12:03 | 44090.5019 | 23 | 48 | 452 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 12:02
2020-09-16 12:03 | 44090.502 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 23 | 50.3 | 523 |  | 2020-09-16 12:03 | 44090.502 | 23 | 50.3 | 523 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:02
2020-09-16 12:03 | 44090.5024 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 22.5 | 51.7 | 483 |  | 2020-09-16 12:03 | 44090.5024 | 22.5 | 51.7 | 483 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:03
2020-09-16 12:04 | 44090.5025 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 20 | 53.6 | 442 | 21 | 52 | 428 | Yes | 2020-09-16 12:04 | 44090.5025 | 21 | 52 | 428 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 12:03
2020-09-16 12:04 | 44090.5028 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 1 | 16 | 69 | 383 | 23 | 44.8 | 424 | No | 2020-09-16 12:04 | 44090.5028 | 23 | 44.8 | 424 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 12:04
2020-09-16 12:04 | 44090.5029 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 25.8 | 42.5 | 593 |  | 2020-09-16 12:04 | 44090.5029 | 25.8 | 42.5 | 593 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:04
2020-09-16 12:04 | 44090.5031 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 19.5 | 54.6 | 402 | 20.2 | 53.9 | 502 |  | 2020-09-16 12:04 | 44090.5031 | 20.2 | 53.9 | 502 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 12:04
2020-09-16 12:05 | 44090.5034 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 23.1 | 49.8 | 470 |  | 2020-09-16 12:05 | 44090.5034 | 23.1 | 49.8 | 470 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:04
2020-09-16 12:05 | 44090.5035 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 2 | 21.5 | 47.7 | 402 | 23 | 42.7 | 419 | No | 2020-09-16 12:05 | 44090.5035 | 23 | 42.7 | 419 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 12:05
2020-09-16 12:05 | 44090.5037 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 25.1 | 42.9 | 702 |  | 2020-09-16 12:05 | 44090.5037 | 25.1 | 42.9 | 702 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:05
2020-09-16 12:05 | 44090.5038 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 22.9 | 49.8 | 483 |  | 2020-09-16 12:05 | 44090.5038 | 22.9 | 49.8 | 483 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:05
2020-09-16 12:06 | 44090.5039 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 20 | 53.6 | 442 | 22 | 50.7 | 833 | Yes | 2020-09-16 12:06 | 44090.5039 | 22 | 50.7 | 833 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 12:05
2020-09-16 12:06 | 44090.5041 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 22.7 | 47.3 | 445 | No | 2020-09-16 12:06 | 44090.5041 | 22.7 | 47.3 | 445 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 12:05
2020-09-16 12:06 | 44090.5041 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.6 | 55.8 | 441 |  | 2020-09-16 12:06 | 44090.5041 | 22.6 | 55.8 | 441 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 12:05
2020-09-16 12:06 | 44090.5043 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 23 | 50 | 470 |  | 2020-09-16 12:06 | 44090.5043 | 23 | 50 | 470 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:06
2020-09-16 12:07 | 44090.5047 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 4 | 20 | 53.6 | 442 | 21 | 51 | 826 | Yes | 2020-09-16 12:07 | 44090.5047 | 21 | 51 | 826 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 12:06
2020-09-16 12:07 | 44090.5047 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 2 | 24.9 | 56.7 | 398 | 24.6 | 44.6 | 706 |  | 2020-09-16 12:07 | 44090.5047 | 24.6 | 44.6 | 706 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:06
2020-09-16 12:07 | 44090.505 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.7 | 46.8 | 437 | No | 2020-09-16 12:07 | 44090.505 | 22.7 | 46.8 | 437 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 12:07
2020-09-16 12:08 | 44090.5052 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 25 | 39 | 368 | 23 | 43 | 385 |  | 2020-09-16 12:08 | 44090.5052 | 23 | 43 | 385 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:07
2020-09-16 12:08 | 44090.5054 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 20 | 53.6 | 442 | 22 | 49.7 | 841 | Yes | 2020-09-16 12:08 | 44090.5054 | 22 | 49.7 | 841 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 12:07
2020-09-16 12:08 | 44090.5054 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 22.9 | 50.1 | 465 |  | 2020-09-16 12:08 | 44090.5054 | 22.9 | 50.1 | 465 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:07
2020-09-16 12:08 | 44090.5055 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 25.2 | 42.3 | 454 | Door locked, reading at doorway | 2020-09-16 12:08 | 44090.5055 | 25.2 | 42.3 | 454 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:07
2020-09-16 12:08 | 44090.5057 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 24.2 | 45.7 | 681 |  | 2020-09-16 12:08 | 44090.5057 | 24.2 | 45.7 | 681 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:08
2020-09-16 12:08 | 44090.5057 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 23 | 49.4 | 428 | No | 2020-09-16 12:08 | 44090.5057 | 23 | 49.4 | 428 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 12:08
2020-09-16 12:09 | 44090.5061 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 4 | 20 | 53.6 | 442 | 21.8 | 51.3 | 802 | Yes | 2020-09-16 12:09 | 44090.5061 | 21.8 | 51.3 | 802 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 12:08
2020-09-16 12:09 | 44090.5062 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 5 | 21.5 | 47.7 | 402 | 23.2 | 44.7 | 540 | No | 2020-09-16 12:09 | 44090.5062 | 23.2 | 44.7 | 540 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 12:08
2020-09-16 12:09 | 44090.5063 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.6 | 57 | 436 |  | 2020-09-16 12:09 | 44090.5063 | 22.6 | 57 | 436 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 12:09
2020-09-16 12:09 | 44090.5066 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 23.7 | 48.3 | 579 |  | 2020-09-16 12:09 | 44090.5066 | 23.7 | 48.3 | 579 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:09
2020-09-16 12:10 | 44090.5068 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 20 | 53.6 | 442 | 23.3 | 41 | 740 | Yes | 2020-09-16 12:10 | 44090.5068 | 23.3 | 41 | 740 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 12:09
2020-09-16 12:10 | 44090.5069 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 19.5 | 54.6 | 402 | 20.5 | 53.2 | 555 |  | 2020-09-16 12:10 | 44090.5069 | 20.5 | 53.2 | 555 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 12:09
2020-09-16 12:10 | 44090.507 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 25 | 39 | 368 | 23 | 44 | 392 |  | 2020-09-16 12:10 | 44090.507 | 23 | 44 | 392 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:10
2020-09-16 12:10 | 44090.507 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 462 | 24.3 | 42.8 | 468 |  | 2020-09-16 12:10 | 44090.507 | 24.3 | 42.8 | 468 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:10
2020-09-16 12:10 | 44090.5073 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 23.6 | 49.2 | 480 |  | 2020-09-16 12:10 | 44090.5073 | 23.6 | 49.2 | 480 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:10
2020-09-16 12:11 | 44090.5073 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 22.8 | 50.4 | 471 |  | 2020-09-16 12:11 | 44090.5073 | 22.8 | 50.4 | 471 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:10
2020-09-16 12:11 | 44090.5074 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 20 | 53.6 | 442 | 21.8 | 50 | 476 | Yes | 2020-09-16 12:11 | 44090.5074 | 21.8 | 50 | 476 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 12:10
2020-09-16 12:11 | 44090.5077 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 25 | 39 | 368 | 23 | 44 | 394 |  | 2020-09-16 12:11 | 44090.5077 | 23 | 44 | 394 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:11
2020-09-16 12:12 | 44090.5081 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 23.7 | 50.1 | 489 |  | 2020-09-16 12:12 | 44090.5081 | 23.7 | 50.1 | 489 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:11
2020-09-16 12:12 | 44090.5083 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 3 | 22 | 65 | 386 | 23 | 57 | 430 |  | 2020-09-16 12:12 | 44090.5083 | 23 | 57 | 430 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:11
2020-09-16 12:12 | 44090.5085 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 23.6 | 46.4 | 539 |  | 2020-09-16 12:12 | 44090.5085 | 23.6 | 46.4 | 539 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:12
2020-09-16 12:12 | 44090.5085 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 23.1 | 51.5 | 469 |  | 2020-09-16 12:12 | 44090.5085 | 23.1 | 51.5 | 469 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:12
2020-09-16 12:12 | 44090.5085 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 20 | 53.6 | 442 | 21 | 50.3 | 475 | Yes | 2020-09-16 12:12 | 44090.5085 | 21 | 50.3 | 475 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 12:12
2020-09-16 12:12 | 44090.5086 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.6 | 56.3 | 442 |  | 2020-09-16 12:12 | 44090.5086 | 22.6 | 56.3 | 442 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 12:12
2020-09-16 12:13 | 44090.5088 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 23.6 | 49.7 | 469 |  | 2020-09-16 12:13 | 44090.5088 | 23.6 | 49.7 | 469 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:12
2020-09-16 12:13 | 44090.5093 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 20 | 53.6 | 442 | 21 | 50.3 | 475 | Yes | 2020-09-16 12:13 | 44090.5093 | 21 | 50.3 | 475 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 12:13
2020-09-16 12:13 | 44090.5093 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 2 | 21.5 | 47.7 | 402 | 22.5 | 44 | 476 | No | 2020-09-16 12:13 | 44090.5093 | 22.5 | 44 | 476 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 12:13
2020-09-16 12:13 | 44090.5094 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 4 | 22 | 65 | 388 | 22 | 50 | 440 |  | 2020-09-16 12:13 | 44090.5094 | 22 | 50 | 440 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:13
2020-09-16 12:14 | 44090.5095 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 23.4 | 51.3 | 460 |  | 2020-09-16 12:14 | 44090.5095 | 23.4 | 51.3 | 460 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:13
2020-09-16 12:14 | 44090.5095 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 25 | 39 | 368 | 23 | 44 | 403 |  | 2020-09-16 12:14 | 44090.5095 | 23 | 44 | 403 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:13
2020-09-16 12:14 | 44090.51 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 20 | 53.6 | 442 | 21.8 | 50.4 | 470 | Yes | 2020-09-16 12:14 | 44090.51 | 21.8 | 50.4 | 470 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 12:14
2020-09-16 12:15 | 44090.5101 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 23.2 | 49.8 | 474 |  | 2020-09-16 12:15 | 44090.5101 | 23.2 | 49.8 | 474 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:14
2020-09-16 12:15 | 44090.5102 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.8 | 56.6 | 443 |  | 2020-09-16 12:15 | 44090.5102 | 22.8 | 56.6 | 443 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 12:14
2020-09-16 12:15 | 44090.5104 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 9 | 22 | 65 | 388 | 23 | 48 | 527 |  | 2020-09-16 12:15 | 44090.5104 | 23 | 48 | 527 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:14
2020-09-16 12:15 | 44090.5104 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 23.5 | 44.8 | 529 |  | 2020-09-16 12:15 | 44090.5104 | 23.5 | 44.8 | 529 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:14
2020-09-16 12:15 | 44090.5104 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 2 | 24.9 | 56.7 | 398 | 23.4 | 49.6 | 660 |  | 2020-09-16 12:15 | 44090.5104 | 23.4 | 49.6 | 660 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:14
2020-09-16 12:15 | 44090.5105 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 52 | 590 |  | 2020-09-16 12:15 | 44090.5105 | 23 | 52 | 590 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:15
2020-09-16 12:15 | 44090.5105 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 18 | 59 | 395 |  |  |  | Occupied, no access | 2020-09-16 12:15 | 44090.5105 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:15
2020-09-16 12:16 | 44090.5109 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 2 | 22 | 65 | 388 | 22 | 52 | 448 |  | 2020-09-16 12:16 | 44090.5109 | 22 | 52 | 448 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:15
2020-09-16 12:16 | 44090.5111 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 23.4 | 49.7 | 637 |  | 2020-09-16 12:16 | 44090.5111 | 23.4 | 49.7 | 637 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:15
2020-09-16 12:16 | 44090.5114 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 23.4 | 51.2 | 478 |  | 2020-09-16 12:16 | 44090.5114 | 23.4 | 51.2 | 478 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:16
2020-09-16 12:16 | 44090.5115 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 3 | 27 | 40 | 388 | 23 | 47 | 555 |  | 2020-09-16 12:16 | 44090.5115 | 23 | 47 | 555 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:16
2020-09-16 12:17 | 44090.5115 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 4 | 20 | 53.6 | 442 | 23.2 | 44 | 742 | Yes | 2020-09-16 12:17 | 44090.5115 | 23.2 | 44 | 742 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 12:16
2020-09-16 12:17 | 44090.5116 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 50 | 590 |  | 2020-09-16 12:17 | 44090.5116 | 23 | 50 | 590 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:16
2020-09-16 12:17 | 44090.5117 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 4 | 17.5 | 69 | 384 | 23.4 | 47.2 | 573 |  | 2020-09-16 12:17 | 44090.5117 | 23.4 | 47.2 | 573 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:16
2020-09-16 12:17 | 44090.5119 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 23.2 | 50.9 | 592 |  | 2020-09-16 12:17 | 44090.5119 | 23.2 | 50.9 | 592 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:17
2020-09-16 12:18 | 44090.5123 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 2 | 21.4 | 59.2 | 400 | 21.9 | 54.5 | 517 |  | 2020-09-16 12:18 | 44090.5123 | 21.9 | 54.5 | 517 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:17
2020-09-16 12:18 | 44090.5124 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 2 | 22 | 65 | 388 | 21 | 52 | 435 |  | 2020-09-16 12:18 | 44090.5124 | 21 | 52 | 435 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:17
2020-09-16 12:18 | 44090.5124 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 2 | 17 | 71.7 | 391 | 23.2 | 51.3 | 488 |  | 2020-09-16 12:18 | 44090.5124 | 23.2 | 51.3 | 488 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:17
2020-09-16 12:18 | 44090.5124 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 1 | 22 | 55 | 377 | 21 | 53 | 401 |  | 2020-09-16 12:18 | 44090.5124 | 21 | 53 | 401 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 12:17
2020-09-16 12:18 | 44090.5125 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 23 | 58.7 | 433 |  | 2020-09-16 12:18 | 44090.5125 | 23 | 58.7 | 433 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 12:17
2020-09-16 12:18 | 44090.5125 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 27 | 40 | 388 | 24 | 43 | 547 |  | 2020-09-16 12:18 | 44090.5125 | 24 | 43 | 547 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:18
2020-09-16 12:18 | 44090.5127 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 4 | 20 | 53.6 | 442 | 22.5 | 47.8 | 686 | Court 3 judge, court 3 lawyer, court 3 waiting area, court 1 judge | 2020-09-16 12:18 | 44090.5127 | 22.5 | 47.8 | 686 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 12:18
2020-09-16 12:18 | 44090.5127 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 50 | 590 |  | 2020-09-16 12:18 | 44090.5127 | 24 | 50 | 590 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:18
2020-09-16 12:18 | 44090.5128 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 2 | 21.5 | 47.7 | 402 | 21.2 | 46.2 | 514 | No | 2020-09-16 12:18 | 44090.5128 | 21.2 | 46.2 | 514 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 12:18
2020-09-16 12:18 | 44090.5128 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 4 | 22 | 65 | 388 | 21 | 54 | 424 |  | 2020-09-16 12:18 | 44090.5128 | 21 | 54 | 424 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:18
2020-09-16 12:18 | 44090.5128 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 23.1 | 51 | 585 |  | 2020-09-16 12:18 | 44090.5128 | 23.1 | 51 | 585 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:18
2020-09-16 12:19 | 44090.5129 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 2 | 21.4 | 59.2 | 400 | 22 | 53.7 | 497 |  | 2020-09-16 12:19 | 44090.5129 | 22 | 53.7 | 497 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:18
2020-09-16 12:19 | 44090.513 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 23 | 51.6 | 486 |  | 2020-09-16 12:19 | 44090.513 | 23 | 51.6 | 486 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:18
2020-09-16 12:19 | 44090.5131 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 44 | 373 |  | 2020-09-16 12:19 | 44090.5131 | 23 | 44 | 373 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:18
2020-09-16 12:19 | 44090.5131 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 23.2 | 48.4 | 570 |  | 2020-09-16 12:19 | 44090.5131 | 23.2 | 48.4 | 570 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:18
2020-09-16 12:19 | 44090.5133 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 4 | 27 | 40 | 388 | 24 | 43 | 557 |  | 2020-09-16 12:19 | 44090.5133 | 24 | 43 | 557 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:19
2020-09-16 12:20 | 44090.5136 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 538 | 23.1 | 50.4 | 531 |  | 2020-09-16 12:20 | 44090.5136 | 23.1 | 50.4 | 531 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:19
2020-09-16 12:20 | 44090.5138 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17 | 71.7 | 391 | 22.8 | 52.3 | 480 |  | 2020-09-16 12:20 | 44090.5138 | 22.8 | 52.3 | 480 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:19
2020-09-16 12:20 | 44090.5139 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 22.6 | 49.8 | 522 |  | 2020-09-16 12:20 | 44090.5139 | 22.6 | 49.8 | 522 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:19
2020-09-16 12:20 | 44090.514 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 2 | 22 | 65 | 388 | 21 | 60 | 421 |  | 2020-09-16 12:20 | 44090.514 | 21 | 60 | 421 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:20
2020-09-16 12:20 | 44090.514 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 4 | 27 | 40 | 388 | 24 | 43 | 538 |  | 2020-09-16 12:20 | 44090.514 | 24 | 43 | 538 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:20
2020-09-16 12:20 | 44090.5142 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 48 | 600 |  | 2020-09-16 12:20 | 44090.5142 | 24 | 48 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:20
2020-09-16 12:21 | 44090.5144 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 6 | 21.5 | 47.7 | 402 | 22.2 | 46.6 | 461 | No | 2020-09-16 12:21 | 44090.5144 | 22.2 | 46.6 | 461 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 12:20
2020-09-16 12:21 | 44090.5146 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 23.1 | 49.8 | 521 |  | 2020-09-16 12:21 | 44090.5146 | 23.1 | 49.8 | 521 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:21
2020-09-16 12:21 | 44090.5147 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 23.3 | 50.1 | 527 |  | 2020-09-16 12:21 | 44090.5147 | 23.3 | 50.1 | 527 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:21
2020-09-16 12:21 | 44090.5147 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 4 | 27 | 40 | 388 | 23 | 43 | 520 |  | 2020-09-16 12:21 | 44090.5147 | 23 | 43 | 520 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:21
2020-09-16 12:22 | 44090.515 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 22.8 | 50.6 | 609 |  | 2020-09-16 12:22 | 44090.515 | 22.8 | 50.6 | 609 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:21
2020-09-16 12:22 | 44090.5151 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 2 | 22 | 63 | 388 | 21 | 60 | 416 |  | 2020-09-16 12:22 | 44090.5151 | 21 | 60 | 416 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:21
2020-09-16 12:22 | 44090.5153 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 43 | 373 |  | 2020-09-16 12:22 | 44090.5153 | 23 | 43 | 373 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:22
2020-09-16 12:22 | 44090.5154 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 48 | 600 |  | 2020-09-16 12:22 | 44090.5154 | 24 | 48 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:22
2020-09-16 12:22 | 44090.5155 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 23.3 | 49.4 | 526 |  | 2020-09-16 12:22 | 44090.5155 | 23.3 | 49.4 | 526 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:22
2020-09-16 12:22 | 44090.5155 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 27 | 40 | 388 | 23 | 44 | 471 |  | 2020-09-16 12:22 | 44090.5155 | 23 | 44 | 471 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:22
2020-09-16 12:22 | 44090.5155 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 22 | 59 | 410 |  | 2020-09-16 12:22 | 44090.5155 | 22 | 59 | 410 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:22
2020-09-16 12:23 | 44090.5159 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 22 | 60 | 411 |  | 2020-09-16 12:23 | 44090.5159 | 22 | 60 | 411 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:22
2020-09-16 12:23 | 44090.5161 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 23.3 | 52.2 | 554 |  | 2020-09-16 12:23 | 44090.5161 | 23.3 | 52.2 | 554 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:23
2020-09-16 12:23 | 44090.5162 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 2 | 21.5 | 47.7 | 402 | 22.2 | 46.8 | 448 | No | 2020-09-16 12:23 | 44090.5162 | 22.2 | 46.8 | 448 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 12:23
2020-09-16 12:23 | 44090.5163 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 9 | 21.4 | 59.2 | 400 | 22.6 | 47 | 623 |  | 2020-09-16 12:23 | 44090.5163 | 22.6 | 47 | 623 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:23
2020-09-16 12:24 | 44090.5163 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 22 | 59 | 412 |  | 2020-09-16 12:24 | 44090.5163 | 22 | 59 | 412 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:23
2020-09-16 12:24 | 44090.5163 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 27 | 40 | 388 |  |  |  | Occupied, no access | 2020-09-16 12:24 | 44090.5163 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:23
2020-09-16 12:24 | 44090.5164 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 49 | 610 |  | 2020-09-16 12:24 | 44090.5164 | 24 | 49 | 610 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:23
2020-09-16 12:24 | 44090.5165 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 23.6 | 45 | 419 | No | 2020-09-16 12:24 | 44090.5165 | 23.6 | 45 | 419 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 12:23
2020-09-16 12:24 | 44090.5165 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 23.3 | 51.3 | 554 |  | 2020-09-16 12:24 | 44090.5165 | 23.3 | 51.3 | 554 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:23
2020-09-16 12:24 | 44090.5167 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 22 | 60 | 405 |  | 2020-09-16 12:24 | 44090.5167 | 22 | 60 | 405 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:24
2020-09-16 12:24 | 44090.517 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 22.7 | 48.9 | 428 |  | 2020-09-16 12:24 | 44090.517 | 22.7 | 48.9 | 428 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:24
2020-09-16 12:25 | 44090.5171 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 23 | 59 | 396 |  | 2020-09-16 12:25 | 44090.5171 | 23 | 59 | 396 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:24
2020-09-16 12:25 | 44090.5173 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17 | 71.7 | 391 | 23.2 | 50.1 | 461 |  | 2020-09-16 12:25 | 44090.5173 | 23.2 | 50.1 | 461 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:24
2020-09-16 12:25 | 44090.5173 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 27 | 40 | 388 |  |  |  | Occupied, no access | 2020-09-16 12:25 | 44090.5173 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:24
2020-09-16 12:25 | 44090.5174 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 18.9 | 60.8 | 421 | 23.3 | 48.2 | 488 | Courtrooms B,C and D had trial going on therefore access was denied | 2020-09-16 12:25 | 44090.5174 | 23.3 | 48.2 | 488 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 12:25
2020-09-16 12:25 | 44090.5175 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 18.9 | 60.8 | 421 | 21.8 | 52.2 | 562 | Courtrooms B,C and D had trial going on therefore access was denied | 2020-09-16 12:25 | 44090.5175 | 21.8 | 52.2 | 562 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 12:25
2020-09-16 12:25 | 44090.5175 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 23 | 59 | 397 |  | 2020-09-16 12:25 | 44090.5175 | 23 | 59 | 397 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:25
2020-09-16 12:25 | 44090.5176 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 9 | 21.4 | 59.2 | 400 | 21.8 | 48.8 | 805 |  | 2020-09-16 12:25 | 44090.5176 | 21.8 | 48.8 | 805 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:25
2020-09-16 12:25 | 44090.5176 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 18.9 | 60.8 | 421 | 22.1 | 51.8 | 562 | Courtrooms B,C and D had trial going on therefore access was denied | 2020-09-16 12:25 | 44090.5176 | 22.1 | 51.8 | 562 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 12:25
2020-09-16 12:26 | 44090.5177 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 2 | 18.9 | 60.8 | 421 | 22.3 | 50.3 | 561 | Courtrooms B,C and D had trial going on therefore access was denied | 2020-09-16 12:26 | 44090.5177 | 22.3 | 50.3 | 561 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 12:25
2020-09-16 12:26 | 44090.5177 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 48 | 640 |  | 2020-09-16 12:26 | 44090.5177 | 24 | 48 | 640 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:25
2020-09-16 12:26 | 44090.5178 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 18.9 | 60.8 | 421 | 20.4 | 61.5 | 484 | Courtrooms B,C and D had trial going on therefore access was denied | 2020-09-16 12:26 | 44090.5178 | 20.4 | 61.5 | 484 |  | caution | 2020-09-14 | B20478¦¦¦Sep-16-2020 12:25
2020-09-16 12:26 | 44090.5179 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 22.7 | 52.1 | 564 |  | 2020-09-16 12:26 | 44090.5179 | 22.7 | 52.1 | 564 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:25
2020-09-16 12:26 | 44090.5179 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 18.9 | 60.8 | 421 | 20.6 | 58.3 | 480 | Courtrooms B,C and D had trial going on therefore access was denied | 2020-09-16 12:26 | 44090.5179 | 20.6 | 58.3 | 480 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 12:25
2020-09-16 12:26 | 44090.518 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 18.9 | 60.8 | 421 | 20.6 | 58.6 | 484 | Courtrooms B,C and D had trial going on therefore access was denied | 2020-09-16 12:26 | 44090.518 | 20.6 | 58.6 | 484 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 12:25
2020-09-16 12:26 | 44090.518 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 23 | 58 | 396 |  | 2020-09-16 12:26 | 44090.518 | 23 | 58 | 396 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:25
2020-09-16 12:26 | 44090.518 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 43 | 389 |  | 2020-09-16 12:26 | 44090.518 | 23 | 43 | 389 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:25
2020-09-16 12:26 | 44090.518 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 18.9 | 60.8 | 421 | 21.7 | 52.6 | 442 | Courtrooms B,C and D had trial going on therefore access was denied | 2020-09-16 12:26 | 44090.518 | 21.7 | 52.6 | 442 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 12:25
2020-09-16 12:26 | 44090.5181 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 18.9 | 60.8 | 421 | 21.6 | 52.2 | 443 | Courtrooms B,C and D had trial going on therefore access was denied | 2020-09-16 12:26 | 44090.5181 | 21.6 | 52.2 | 443 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 12:26
2020-09-16 12:27 | 44090.5185 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 23 | 57 | 397 |  | 2020-09-16 12:27 | 44090.5185 | 23 | 57 | 397 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:26
2020-09-16 12:27 | 44090.5185 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 18.9 | 60.8 | 421 | 22.4 | 48.3 | 485 | Courtrooms B,C and D had trial going on therefore access was denied | 2020-09-16 12:27 | 44090.5185 | 22.4 | 48.3 | 485 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 12:26
2020-09-16 12:27 | 44090.5186 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 1 | 20 | 58 | 388 | 23.7 | 46 | 420 | No | 2020-09-16 12:27 | 44090.5186 | 23.7 | 46 | 420 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 12:26
2020-09-16 12:27 | 44090.5187 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 22.9 | 54.3 | 469 |  | 2020-09-16 12:27 | 44090.5187 | 22.9 | 54.3 | 469 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:26
2020-09-16 12:27 | 44090.5188 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 22.2 | 51.7 | 615 |  | 2020-09-16 12:27 | 44090.5188 | 22.2 | 51.7 | 615 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:27
2020-09-16 12:27 | 44090.5189 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 48 | 600 |  | 2020-09-16 12:27 | 44090.5189 | 24 | 48 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:27
2020-09-16 12:27 | 44090.519 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 23 | 57 | 398 |  | 2020-09-16 12:27 | 44090.519 | 23 | 57 | 398 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:27
2020-09-16 12:28 | 44090.5192 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 27 | 40 | 388 | 22 | 46 | 451 |  | 2020-09-16 12:28 | 44090.5192 | 22 | 46 | 451 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:27
2020-09-16 12:28 | 44090.5194 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 22.6 | 53.5 | 426 |  | 2020-09-16 12:28 | 44090.5194 | 22.6 | 53.5 | 426 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:27
2020-09-16 12:28 | 44090.5195 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 22.3 | 51.7 | 599 |  | 2020-09-16 12:28 | 44090.5195 | 22.3 | 51.7 | 599 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:28
2020-09-16 12:28 | 44090.5195 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 22 | 57 | 410 |  | 2020-09-16 12:28 | 44090.5195 | 22 | 57 | 410 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:28
2020-09-16 12:28 | 44090.5196 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 44 | 391 |  | 2020-09-16 12:28 | 44090.5196 | 23 | 44 | 391 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:28
2020-09-16 12:28 | 44090.5198 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 48 | 600 |  | 2020-09-16 12:28 | 44090.5198 | 24 | 48 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:28
2020-09-16 12:29 | 44090.5201 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 27 | 40 | 388 | 22 | 48 | 459 |  | 2020-09-16 12:29 | 44090.5201 | 22 | 48 | 459 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:28
2020-09-16 12:29 | 44090.5201 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 22 | 51 | 420 |  | 2020-09-16 12:29 | 44090.5201 | 22 | 51 | 420 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:28
2020-09-16 12:29 | 44090.5202 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.4 | 56.7 | 398 | 22.5 | 56.1 | 407 |  | 2020-09-16 12:29 | 44090.5202 | 22.5 | 56.1 | 407 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:29
2020-09-16 12:29 | 44090.5202 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 23.5 | 45.5 | 411 | No | 2020-09-16 12:29 | 44090.5202 | 23.5 | 45.5 | 411 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 12:29
2020-09-16 12:30 | 44090.5205 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 22 | 53 | 445 |  | 2020-09-16 12:30 | 44090.5205 | 22 | 53 | 445 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:29
2020-09-16 12:30 | 44090.5205 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 44 | 383 |  | 2020-09-16 12:30 | 44090.5205 | 23 | 44 | 383 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:29
2020-09-16 12:30 | 44090.5206 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 2 | 17.5 | 69 | 384 | 23.2 | 48.2 | 498 |  | 2020-09-16 12:30 | 44090.5206 | 23.2 | 48.2 | 498 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:29
2020-09-16 12:30 | 44090.5208 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 22.3 | 55.1 | 409 |  | 2020-09-16 12:30 | 44090.5208 | 22.3 | 55.1 | 409 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:29
2020-09-16 12:30 | 44090.5208 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 22.1 | 52.5 | 489 |  | 2020-09-16 12:30 | 44090.5208 | 22.1 | 52.5 | 489 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:29
2020-09-16 12:30 | 44090.5208 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 48 | 615 |  | 2020-09-16 12:30 | 44090.5208 | 24 | 48 | 615 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:29
2020-09-16 12:30 | 44090.5209 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 22 | 53 | 481 |  | 2020-09-16 12:30 | 44090.5209 | 22 | 53 | 481 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:30
2020-09-16 12:30 | 44090.521 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 27 | 40 | 388 | 22 | 48 | 463 |  | 2020-09-16 12:30 | 44090.521 | 22 | 48 | 463 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:30
2020-09-16 12:31 | 44090.5212 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 44 | 383 |  | 2020-09-16 12:31 | 44090.5212 | 23 | 44 | 383 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:30
2020-09-16 12:31 | 44090.5213 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 22.2 | 56.5 | 407 |  | 2020-09-16 12:31 | 44090.5213 | 22.2 | 56.5 | 407 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:30
2020-09-16 12:31 | 44090.5214 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 3 | 17.5 | 69 | 384 | 23.3 | 49.3 | 499 |  | 2020-09-16 12:31 | 44090.5214 | 23.3 | 49.3 | 499 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:30
2020-09-16 12:31 | 44090.5216 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 23 | 60.2 | 428 |  | 2020-09-16 12:31 | 44090.5216 | 23 | 60.2 | 428 |  | caution | 2020-09-14 | B17477¦¦¦Sep-16-2020 12:31
2020-09-16 12:31 | 44090.5216 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 27 | 40 | 388 | 22 | 48 | 476 |  | 2020-09-16 12:31 | 44090.5216 | 22 | 48 | 476 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:31
2020-09-16 12:31 | 44090.5216 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 22.4 | 59.2 | 400 | 22 | 53 | 483 |  | 2020-09-16 12:31 | 44090.5216 | 22 | 53 | 483 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:31
2020-09-16 12:31 | 44090.5219 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 48 | 680 |  | 2020-09-16 12:32 | 44090.5219 | 24 | 48 | 680 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:31
2020-09-16 12:32 | 44090.5219 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 24.9 | 56.7 | 398 | 22.1 | 57.8 | 406 |  | 2020-09-16 12:32 | 44090.5219 | 22.1 | 57.8 | 406 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 12:31
2020-09-16 12:32 | 44090.522 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 22 | 53 | 435 |  | 2020-09-16 12:32 | 44090.522 | 22 | 53 | 435 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:31
2020-09-16 12:32 | 44090.5223 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 44 | 379 |  | 2020-09-16 12:32 | 44090.5223 | 23 | 44 | 379 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:32
2020-09-16 12:32 | 44090.5224 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 23.5 | 47.5 | 579 |  | 2020-09-16 12:32 | 44090.5224 | 23.5 | 47.5 | 579 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:32
2020-09-16 12:32 | 44090.5225 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 27 | 40 | 388 | 22 | 47 | 475 |  | 2020-09-16 12:32 | 44090.5225 | 22 | 47 | 475 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:32
2020-09-16 12:32 | 44090.5225 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 21.8 | 53.7 | 487 |  | 2020-09-16 12:32 | 44090.5225 | 21.8 | 53.7 | 487 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:32
2020-09-16 12:32 | 44090.5225 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 23.1 | 48.6 | 458 |  | 2020-09-16 12:32 | 44090.5225 | 23.1 | 48.6 | 458 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:32
2020-09-16 12:32 | 44090.5226 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.3 | 61.9 | 430 |  | 2020-09-16 12:32 | 44090.5226 | 22.3 | 61.9 | 430 |  | caution | 2020-09-14 | B17477¦¦¦Sep-16-2020 12:32
2020-09-16 12:33 | 44090.5226 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 22.8 | 46.9 | 418 | No | 2020-09-16 12:32 | 44090.5226 | 22.8 | 46.9 | 418 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 12:32
2020-09-16 12:33 | 44090.5229 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 48 | 595 |  | 2020-09-16 12:33 | 44090.5229 | 24 | 48 | 595 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:33
2020-09-16 12:33 | 44090.523 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 22 | 53 | 425 |  | 2020-09-16 12:33 | 44090.523 | 22 | 53 | 425 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:33
2020-09-16 12:34 | 44090.5233 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 27 | 40 | 388 | 22 | 50 | 532 |  | 2020-09-16 12:34 | 44090.5233 | 22 | 50 | 532 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:33
2020-09-16 12:34 | 44090.5234 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 21 | 56 | 429 |  | 2020-09-16 12:34 | 44090.5234 | 21 | 56 | 429 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:33
2020-09-16 12:34 | 44090.5235 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 24.5 | 47.4 | 455 |  | 2020-09-16 12:34 | 44090.5235 | 24.5 | 47.4 | 455 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:33
2020-09-16 12:34 | 44090.5238 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.3 | 61.4 | 431 |  | 2020-09-16 12:34 | 44090.5238 | 22.3 | 61.4 | 431 |  | caution | 2020-09-14 | B17477¦¦¦Sep-16-2020 12:34
2020-09-16 12:34 | 44090.5238 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 23.5 | 42.2 | 549 |  | 2020-09-16 12:34 | 44090.5238 | 23.5 | 42.2 | 549 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:34
2020-09-16 12:34 | 44090.5239 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 21 | 57 | 426 |  | 2020-09-16 12:34 | 44090.5239 | 21 | 57 | 426 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:34
2020-09-16 12:35 | 44090.5242 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 22.2 | 53 | 528 |  | 2020-09-16 12:35 | 44090.5242 | 22.2 | 53 | 528 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:34
2020-09-16 12:35 | 44090.5243 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 3 | 27 | 40 | 388 | 22 | 50 | 549 |  | 2020-09-16 12:35 | 44090.5243 | 22 | 50 | 549 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:35
2020-09-16 12:35 | 44090.5243 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 24.6 | 43 | 402 |  | 2020-09-16 12:35 | 44090.5243 | 24.6 | 43 | 402 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:35
2020-09-16 12:35 | 44090.5243 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 21 | 62 | 422 |  | 2020-09-16 12:35 | 44090.5243 | 21 | 62 | 422 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:35
2020-09-16 12:35 | 44090.5245 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 23 | 47.7 | 422 | No | 2020-09-16 12:35 | 44090.5245 | 23 | 47.7 | 422 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 12:35
2020-09-16 12:36 | 44090.5247 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.3 | 61.9 | 437 |  | 2020-09-16 12:36 | 44090.5247 | 22.3 | 61.9 | 437 |  | caution | 2020-09-14 | B17477¦¦¦Sep-16-2020 12:35
2020-09-16 12:36 | 44090.5248 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 22 | 62 | 415 |  | 2020-09-16 12:36 | 44090.5248 | 22 | 62 | 415 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:35
2020-09-16 12:36 | 44090.5249 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 22.8 | 43.6 | 547 |  | 2020-09-16 12:36 | 44090.5249 | 22.8 | 43.6 | 547 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:35
2020-09-16 12:36 | 44090.5251 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 27 | 40 | 388 |  |  |  | Occupied, no access | 2020-09-16 12:36 | 44090.5251 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:36
2020-09-16 12:36 | 44090.5252 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 48 | 615 |  | 2020-09-16 12:36 | 44090.5252 | 24 | 48 | 615 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:36
2020-09-16 12:36 | 44090.5252 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 1 | 17.5 | 69 | 384 | 23.6 | 45.5 | 371 |  | 2020-09-16 12:36 | 44090.5252 | 23.6 | 45.5 | 371 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 12:36
2020-09-16 12:36 | 44090.5252 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 22 | 61 | 412 |  | 2020-09-16 12:36 | 44090.5252 | 22 | 61 | 412 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:36
2020-09-16 12:36 | 44090.5252 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 22.3 | 49.4 | 555 |  | 2020-09-16 12:36 | 44090.5252 | 22.3 | 49.4 | 555 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:36
2020-09-16 12:37 | 44090.5255 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 22 | 60 | 406 |  | 2020-09-16 12:37 | 44090.5255 | 22 | 60 | 406 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:36
2020-09-16 12:37 | 44090.5256 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 21.6 | 63.7 | 406 | 22.2 | 61.7 | 430 |  | 2020-09-16 12:37 | 44090.5256 | 22.2 | 61.7 | 430 |  | caution | 2020-09-14 | B17477¦¦¦Sep-16-2020 12:36
2020-09-16 12:37 | 44090.5259 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 27 | 40 | 388 |  |  |  | Occupied, no access | 2020-09-16 12:37 | 44090.5259 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:37
2020-09-16 12:37 | 44090.5259 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 22.4 | 44.6 | 546 |  | 2020-09-16 12:37 | 44090.5259 | 22.4 | 44.6 | 546 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:37
2020-09-16 12:37 | 44090.5259 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 22.4 | 59.2 | 400 | 22.2 | 49.5 | 570 |  | 2020-09-16 12:37 | 44090.5259 | 22.2 | 49.5 | 570 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:37
2020-09-16 12:37 | 44090.5259 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 22 | 60 | 402 |  | 2020-09-16 12:37 | 44090.5259 | 22 | 60 | 402 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:37
2020-09-16 12:38 | 44090.5263 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 4 | 20 | 58 | 388 | 23 | 47.1 | 430 | No | 2020-09-16 12:38 | 44090.5263 | 23 | 47.1 | 430 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 12:37
2020-09-16 12:38 | 44090.5263 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 22 | 65 | 388 | 23 | 59 | 400 |  | 2020-09-16 12:38 | 44090.5263 | 23 | 59 | 400 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 12:37
2020-09-16 12:38 | 44090.5263 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 48 | 600 |  | 2020-09-16 12:38 | 44090.5263 | 24 | 48 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:37
2020-09-16 12:38 | 44090.5266 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 27 | 40 | 388 | 23 | 49 | 523 |  | 2020-09-16 12:38 | 44090.5266 | 23 | 49 | 523 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:38
2020-09-16 12:38 | 44090.5267 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 2 | 21.6 | 63.7 | 406 | 22.7 | 63 | 436 |  | 2020-09-16 12:38 | 44090.5267 | 22.7 | 63 | 436 |  | caution | 2020-09-14 | B17477¦¦¦Sep-16-2020 12:38
2020-09-16 12:39 | 44090.5271 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 22.2 | 45.9 | 547 |  | 2020-09-16 12:39 | 44090.5271 | 22.2 | 45.9 | 547 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:39
2020-09-16 12:39 | 44090.5271 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 1 | 21.4 | 59.2 | 400 | 22 | 54 | 559 |  | 2020-09-16 12:39 | 44090.5271 | 22 | 54 | 559 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:39
2020-09-16 12:39 | 44090.5274 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 27 | 40 | 388 | 22 | 48 | 513 |  | 2020-09-16 12:40 | 44090.5274 | 22 | 48 | 513 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:39
2020-09-16 12:40 | 44090.5277 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 48 | 600 |  | 2020-09-16 12:40 | 44090.5277 | 24 | 48 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:39
2020-09-16 12:40 | 44090.5278 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 1 | 22 | 55 | 377 | 22 | 54 | 400 |  | 2020-09-16 12:40 | 44090.5278 | 22 | 54 | 400 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 12:40
2020-09-16 12:40 | 44090.5281 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 3 | 21.4 | 59.2 | 400 | 21.7 | 53.3 | 620 |  | 2020-09-16 12:40 | 44090.5281 | 21.7 | 53.3 | 620 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:40
2020-09-16 12:41 | 44090.5282 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 27 | 40 | 388 |  |  |  | Occupied, no access | 2020-09-16 12:41 | 44090.5282 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:40
2020-09-16 12:41 | 44090.5284 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 25 | 39 | 368 | 23 | 44 | 373 |  | 2020-09-16 12:41 | 44090.5284 | 23 | 44 | 373 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:40
2020-09-16 12:41 | 44090.5286 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.8 | 47.1 | 542 |  | 2020-09-16 12:41 | 44090.5286 | 21.8 | 47.1 | 542 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:41
2020-09-16 12:41 | 44090.5287 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 23.2 | 46.2 | 407 | No | 2020-09-16 12:41 | 44090.5287 | 23.2 | 46.2 | 407 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 12:41
2020-09-16 12:41 | 44090.5287 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 3 | 21.4 | 59.2 | 400 | 21.6 | 53.7 | 634 |  | 2020-09-16 12:41 | 44090.5287 | 21.6 | 53.7 | 634 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:41
2020-09-16 12:42 | 44090.5289 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 27 | 40 | 388 |  |  |  | Occupied, no access | 2020-09-16 12:42 | 44090.5289 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:41
2020-09-16 12:43 | 44090.5297 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 27 | 40 | 388 | 23 | 48 | 445 |  | 2020-09-16 12:43 | 44090.5297 | 23 | 48 | 445 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:42
2020-09-16 12:43 | 44090.5297 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.9 | 46.9 | 526 |  | 2020-09-16 12:43 | 44090.5297 | 21.9 | 46.9 | 526 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:42
2020-09-16 12:43 | 44090.5298 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 25 | 39 | 368 | 23 | 44 | 370 |  | 2020-09-16 12:43 | 44090.5298 | 23 | 44 | 370 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:42
2020-09-16 12:43 | 44090.53 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 1 | 20 | 58 | 388 | 23 | 47.3 | 435 | No | 2020-09-16 12:43 | 44090.53 | 23 | 47.3 | 435 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 12:43
2020-09-16 12:43 | 44090.5302 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 21.6 | 54 | 400 |  | 2020-09-16 12:43 | 44090.5302 | 21.6 | 54 | 400 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 12:43
2020-09-16 12:44 | 44090.5303 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 3 | 21.4 | 59.2 | 400 | 22.4 | 50.7 | 773 |  | 2020-09-16 12:44 | 44090.5303 | 22.4 | 50.7 | 773 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:43
2020-09-16 12:44 | 44090.5305 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 27 | 40 | 388 | 23 | 47 | 491 |  | 2020-09-16 12:44 | 44090.5305 | 23 | 47 | 491 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:43
2020-09-16 12:44 | 44090.5307 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 49 | 590 |  | 2020-09-16 12:44 | 44090.5307 | 24 | 49 | 590 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:44
2020-09-16 12:44 | 44090.5309 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 25 | 39 | 368 | 23 | 44 | 371 |  | 2020-09-16 12:44 | 44090.5309 | 23 | 44 | 371 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:44
2020-09-16 12:45 | 44090.5311 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.9 | 46.8 | 515 |  | 2020-09-16 12:45 | 44090.5311 | 21.9 | 46.8 | 515 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:44
2020-09-16 12:45 | 44090.5311 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 23 | 50.6 | 408 |  | 2020-09-16 12:45 | 44090.5311 | 23 | 50.6 | 408 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 12:44
2020-09-16 12:45 | 44090.5311 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 27 | 40 | 388 |  |  |  | Occupied, no access | 2020-09-16 12:45 | 44090.5311 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:44
2020-09-16 12:45 | 44090.5311 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 4 | 21.4 | 59.2 | 400 | 22.7 | 50.1 | 769 |  | 2020-09-16 12:45 | 44090.5311 | 22.7 | 50.1 | 769 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:44
2020-09-16 12:45 | 44090.5315 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 1 | 20 | 62.4 | 387 | 22.8 | 49.7 | 475 |  | 2020-09-16 12:45 | 44090.5315 | 22.8 | 49.7 | 475 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 12:45
2020-09-16 12:46 | 44090.5316 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 25 | 39 | 368 | 23 | 44 | 372 |  | 2020-09-16 12:46 | 44090.5316 | 23 | 44 | 372 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:45
2020-09-16 12:46 | 44090.5316 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 3 | 23 | 50 | 380 | 23.1 | 47.3 | 465 |  | 2020-09-16 12:46 | 44090.5316 | 23.1 | 47.3 | 465 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 12:45
2020-09-16 12:46 | 44090.5317 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 27 | 40 | 388 |  |  |  |  | 2020-09-16 12:46 | 44090.5317 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:45
2020-09-16 12:46 | 44090.5319 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 49 | 630 |  | 2020-09-16 12:46 | 44090.5319 | 23 | 49 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:45
2020-09-16 12:46 | 44090.5321 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 22 | 52 | 398 |  | 2020-09-16 12:46 | 44090.5321 | 22 | 52 | 398 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 12:46
2020-09-16 12:46 | 44090.5322 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 20 | 58 | 388 | 23 | 46.9 | 407 | No | 2020-09-16 12:46 | 44090.5322 | 23 | 46.9 | 407 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 12:46
2020-09-16 12:46 | 44090.5322 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 22.5 | 49.7 | 463 |  | 2020-09-16 12:46 | 44090.5322 | 22.5 | 49.7 | 463 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 12:46
2020-09-16 12:46 | 44090.5323 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 2 | 21.4 | 59.2 | 400 | 22.8 | 56 | 576 | Open window fresh air | 2020-09-16 12:46 | 44090.5323 | 22.8 | 56 | 576 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 12:46
2020-09-16 12:47 | 44090.5323 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.9 | 47.2 | 517 |  | 2020-09-16 12:47 | 44090.5323 | 21.9 | 47.2 | 517 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:46
2020-09-16 12:47 | 44090.5323 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 27 | 40 | 388 | 23 | 47 | 505 |  | 2020-09-16 12:47 | 44090.5323 | 23 | 47 | 505 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:46
2020-09-16 12:47 | 44090.5324 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 25 | 39 | 368 | 23 | 44 | 373 |  | 2020-09-16 12:47 | 44090.5324 | 23 | 44 | 373 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:46
2020-09-16 12:47 | 44090.5324 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 2 | 23 | 50 | 380 | 22.7 | 49.1 | 546 |  | 2020-09-16 12:47 | 44090.5324 | 22.7 | 49.1 | 546 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 12:46
2020-09-16 12:47 | 44090.5329 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 50 | 620 |  | 2020-09-16 12:47 | 44090.5329 | 23 | 50 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:47
2020-09-16 12:48 | 44090.5331 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 27 | 40 | 388 | 23 | 47 | 508 |  | 2020-09-16 12:48 | 44090.5331 | 23 | 47 | 508 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:47
2020-09-16 12:48 | 44090.5335 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 22.4 | 48.3 | 447 |  | 2020-09-16 12:48 | 44090.5335 | 22.4 | 48.3 | 447 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 12:48
2020-09-16 12:48 | 44090.5335 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 2 | 23 | 50 | 380 | 22.3 | 49.6 | 555 |  | 2020-09-16 12:48 | 44090.5335 | 22.3 | 49.6 | 555 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 12:48
2020-09-16 12:48 | 44090.5335 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.8 | 47.9 | 522 |  | 2020-09-16 12:48 | 44090.5335 | 21.8 | 47.9 | 522 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:48
2020-09-16 12:48 | 44090.5337 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 21.5 | 50.5 | 551 |  | 2020-09-16 12:48 | 44090.5337 | 21.5 | 50.5 | 551 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 12:48
2020-09-16 12:49 | 44090.534 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 27 | 40 | 388 | 23 | 46 | 520 |  | 2020-09-16 12:49 | 44090.534 | 23 | 46 | 520 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:48
2020-09-16 12:49 | 44090.5341 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 50 | 600 |  | 2020-09-16 12:49 | 44090.5341 | 23 | 50 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:49
2020-09-16 12:49 | 44090.5342 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 22.6 | 43.9 | 446 |  | 2020-09-16 12:49 | 44090.5342 | 22.6 | 43.9 | 446 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 12:49
2020-09-16 12:49 | 44090.5342 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 22 | 52 | 397 |  | 2020-09-16 12:49 | 44090.5342 | 22 | 52 | 397 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 12:49
2020-09-16 12:49 | 44090.5343 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 22.3 | 49.9 | 504 |  | 2020-09-16 12:49 | 44090.5343 | 22.3 | 49.9 | 504 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 12:49
2020-09-16 12:50 | 44090.5344 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 21.2 | 51.6 | 571 |  | 2020-09-16 12:50 | 44090.5344 | 21.2 | 51.6 | 571 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 12:49
2020-09-16 12:50 | 44090.5346 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 27 | 40 | 388 |  |  |  | Occupied, no access | 2020-09-16 12:50 | 44090.5346 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:49
2020-09-16 12:50 | 44090.5349 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23 | 47 | 424 |  | 2020-09-16 12:50 | 44090.5349 | 23 | 47 | 424 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 12:50
2020-09-16 12:50 | 44090.535 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 2 | 23 | 50 | 380 | 22.4 | 48.9 | 449 | Could not access Court rooms 1-4 | 2020-09-16 12:50 | 44090.535 | 22.4 | 48.9 | 449 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 12:50
2020-09-16 12:50 | 44090.535 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.8 | 49 | 555 |  | 2020-09-16 12:50 | 44090.535 | 21.8 | 49 | 555 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:50
2020-09-16 12:51 | 44090.5351 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 50 | 600 |  | 2020-09-16 12:51 | 44090.5351 | 23 | 50 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:50
2020-09-16 12:51 | 44090.5353 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 27 | 40 | 388 |  |  |  | Occupied, no access | 2020-09-16 12:51 | 44090.5353 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:50
2020-09-16 12:51 | 44090.5354 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 21 | 53 | 787 |  | 2020-09-16 12:51 | 44090.5354 | 21 | 53 | 787 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 12:51
2020-09-16 12:51 | 44090.5356 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.7 | 45.2 | 444 | No | 2020-09-16 12:51 | 44090.5356 | 22.7 | 45.2 | 444 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 12:51
2020-09-16 12:51 | 44090.5357 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 22.9 | 52.2 | 438 |  | 2020-09-16 12:51 | 44090.5357 | 22.9 | 52.2 | 438 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 12:51
2020-09-16 12:51 | 44090.5357 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23.1 | 45.5 | 442 |  | 2020-09-16 12:51 | 44090.5357 | 23.1 | 45.5 | 442 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 12:51
2020-09-16 12:52 | 44090.536 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 27 | 40 | 388 | 24 | 46 | 608 |  | 2020-09-16 12:52 | 44090.536 | 24 | 46 | 608 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:51
2020-09-16 12:52 | 44090.5361 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.7 | 49.5 | 550 |  | 2020-09-16 12:52 | 44090.5361 | 21.7 | 49.5 | 550 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:52
2020-09-16 12:52 | 44090.5363 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 52 | 620 |  | 2020-09-16 12:52 | 44090.5363 | 23 | 52 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:52
2020-09-16 12:52 | 44090.5363 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 23 | 46.7 | 427 |  | 2020-09-16 12:52 | 44090.5363 | 23 | 46.7 | 427 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 12:52
2020-09-16 12:53 | 44090.5369 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 23.1 | 49.2 | 430 |  | 2020-09-16 12:53 | 44090.5369 | 23.1 | 49.2 | 430 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 12:53
2020-09-16 12:53 | 44090.537 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.6 | 45.7 | 448 | No | 2020-09-16 12:53 | 44090.537 | 22.6 | 45.7 | 448 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 12:53
2020-09-16 12:53 | 44090.537 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 5 | 21.4 | 59.2 | 400 | 22.1 | 52.3 | 827 |  | 2020-09-16 12:53 | 44090.537 | 22.1 | 52.3 | 827 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 12:53
2020-09-16 12:54 | 44090.5372 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 50 | 630 |  | 2020-09-16 12:54 | 44090.5372 | 23 | 50 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:53
2020-09-16 12:54 | 44090.5372 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.9 | 49.3 | 558 |  | 2020-09-16 12:54 | 44090.5372 | 21.9 | 49.3 | 558 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:53
2020-09-16 12:54 | 44090.5372 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 27 | 40 | 388 | 23 | 47 | 665 |  | 2020-09-16 12:54 | 44090.5372 | 23 | 47 | 665 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 12:53
2020-09-16 12:54 | 44090.5374 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23.3 | 48.9 | 453 |  | 2020-09-16 12:54 | 44090.5374 | 23.3 | 48.9 | 453 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 12:53
2020-09-16 12:54 | 44090.5375 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 22.9 | 51.5 | 436 |  | 2020-09-16 12:54 | 44090.5375 | 22.9 | 51.5 | 436 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 12:54
2020-09-16 12:54 | 44090.5377 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 23 | 51 | 429 |  | 2020-09-16 12:54 | 44090.5377 | 23 | 51 | 429 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 12:54
2020-09-16 12:54 | 44090.5378 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 7 | 21.5 | 47.7 | 402 | 22.3 | 44.9 | 493 | No | 2020-09-16 12:54 | 44090.5378 | 22.3 | 44.9 | 493 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 12:54
2020-09-16 12:55 | 44090.538 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 44 | 377 |  | 2020-09-16 12:55 | 44090.538 | 23 | 44 | 377 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:54
2020-09-16 12:55 | 44090.5381 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 1 | 22 | 44 | 402 | 22 | 43 | 569 |  | 2020-09-16 12:55 | 44090.5381 | 22 | 43 | 569 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 12:54
2020-09-16 12:55 | 44090.5382 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 50 | 600 |  | 2020-09-16 12:55 | 44090.5382 | 23 | 50 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:55
2020-09-16 12:55 | 44090.5384 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 3 | 28.5 | 39 | 395 | 22.8 | 39.4 | 683 |  | 2020-09-16 12:55 | 44090.5384 | 22.8 | 39.4 | 683 |  | caution | 2020-09-14 | B21554¦¦¦Sep-16-2020 12:55
2020-09-16 12:55 | 44090.5385 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 1 | 22 | 44 | 402 | 22 | 45 | 566 |  | 2020-09-16 12:55 | 44090.5385 | 22 | 45 | 566 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 12:55
2020-09-16 12:56 | 44090.5386 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 22.2 | 48 | 544 |  | 2020-09-16 12:56 | 44090.5386 | 22.2 | 48 | 544 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:55
2020-09-16 12:56 | 44090.5386 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 44 | 371 |  | 2020-09-16 12:56 | 44090.5386 | 23 | 44 | 371 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:55
2020-09-16 12:56 | 44090.5387 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 22.1 | 51.9 | 737 |  | 2020-09-16 12:56 | 44090.5387 | 22.1 | 51.9 | 737 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 12:55
2020-09-16 12:56 | 44090.5387 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 1 | 20 | 62.4 | 387 | 23.2 | 36.9 | 439 |  | 2020-09-16 12:56 | 44090.5387 | 23.2 | 36.9 | 439 |  | caution | 2020-09-14 | B70740¦¦¦Sep-16-2020 12:55
2020-09-16 12:56 | 44090.5389 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 22 | 44 | 402 | 23 | 43 | 573 |  | 2020-09-16 12:56 | 44090.5389 | 23 | 43 | 573 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 12:56
2020-09-16 12:56 | 44090.539 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.2 | 51.2 | 428 | No | 2020-09-16 12:56 | 44090.539 | 22.2 | 51.2 | 428 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 12:56
2020-09-16 12:56 | 44090.5392 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 50 | 620 |  | 2020-09-16 12:56 | 44090.5392 | 23 | 50 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:56
2020-09-16 12:56 | 44090.5392 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 22.3 | 55.5 | 455 |  | 2020-09-16 12:56 | 44090.5392 | 22.3 | 55.5 | 455 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 12:56
2020-09-16 12:57 | 44090.5393 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 1 | 22 | 44 | 403 | 22 | 45 | 577 |  | 2020-09-16 12:57 | 44090.5393 | 22 | 45 | 577 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 12:56
2020-09-16 12:57 | 44090.5395 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 2 | 21.5 | 47.7 | 402 | 22.7 | 44.5 | 451 | No | 2020-09-16 12:57 | 44090.5395 | 22.7 | 44.5 | 451 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 12:56
2020-09-16 12:57 | 44090.5396 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 45 | 371 |  | 2020-09-16 12:57 | 44090.5396 | 23 | 45 | 371 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:56
2020-09-16 12:57 | 44090.5397 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 22 | 44 | 402 | 22 | 45 | 570 |  | 2020-09-16 12:57 | 44090.5397 | 22 | 45 | 570 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 12:57
2020-09-16 12:57 | 44090.5399 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 1 | 21.4 | 59.2 | 400 | 22 | 52 | 785 |  | 2020-09-16 12:57 | 44090.5399 | 22 | 52 | 785 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 12:57
2020-09-16 12:57 | 44090.5399 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 22.2 | 47.7 | 545 |  | 2020-09-16 12:57 | 44090.5399 | 22.2 | 47.7 | 545 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:57
2020-09-16 12:58 | 44090.54 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 5 | 23 | 50 | 380 | 22.2 | 55.9 | 433 |  | 2020-09-16 12:58 | 44090.54 | 22.2 | 55.9 | 433 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 12:57
2020-09-16 12:58 | 44090.5401 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 22.2 | 40.2 | 432 |  | 2020-09-16 12:58 | 44090.5401 | 22.2 | 40.2 | 432 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 12:57
2020-09-16 12:58 | 44090.5403 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.6 | 50.2 | 440 | No | 2020-09-16 12:58 | 44090.5403 | 22.6 | 50.2 | 440 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 12:58
2020-09-16 12:58 | 44090.5404 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 50 | 610 |  | 2020-09-16 12:58 | 44090.5404 | 23 | 50 | 610 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:58
2020-09-16 12:58 | 44090.5405 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 44 | 371 |  | 2020-09-16 12:58 | 44090.5405 | 23 | 44 | 371 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 12:58
2020-09-16 12:58 | 44090.5406 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 1 | 22 | 44 | 402 | 22 | 47 | 543 |  | 2020-09-16 12:58 | 44090.5406 | 22 | 47 | 543 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 12:58
2020-09-16 12:58 | 44090.5406 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 2 | 21.5 | 47.7 | 402 | 23 | 42.6 | 532 | No | 2020-09-16 12:58 | 44090.5406 | 23 | 42.6 | 532 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 12:58
2020-09-16 12:59 | 44090.5409 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 21.8 | 55.2 | 436 |  | 2020-09-16 12:59 | 44090.5409 | 21.8 | 55.2 | 436 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 12:58
2020-09-16 13:00 | 44090.5413 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 1 | 22 | 44 | 402 | 22 | 45 | 518 |  | 2020-09-16 12:59 | 44090.5413 | 22 | 45 | 518 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 12:59
2020-09-16 13:00 | 44090.5413 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 50 | 630 |  | 2020-09-16 13:00 | 44090.5413 | 23 | 50 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 12:59
2020-09-16 13:00 | 44090.5414 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 2 | 23.4 | 49.5 | 425 | 22 | 53.2 | 509 |  | 2020-09-16 13:00 | 44090.5414 | 22 | 53.2 | 509 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 12:59
2020-09-16 13:00 | 44090.5415 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 22.1 | 48.5 | 544 |  | 2020-09-16 13:00 | 44090.5415 | 22.1 | 48.5 | 544 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 12:59
2020-09-16 13:00 | 44090.5415 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 21.8 | 55.3 | 404 |  | 2020-09-16 13:00 | 44090.5415 | 21.8 | 55.3 | 404 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 12:59
2020-09-16 13:00 | 44090.5416 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 22.6 | 48.3 | 584 |  | 2020-09-16 13:00 | 44090.5416 | 22.6 | 48.3 | 584 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 12:59
2020-09-16 13:00 | 44090.5417 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 20.1 | 47.6 | 428 |  | 2020-09-16 13:00 | 44090.5417 | 20.1 | 47.6 | 428 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 13:00
2020-09-16 13:00 | 44090.5417 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 45 | 366 |  | 2020-09-16 13:00 | 44090.5417 | 23 | 45 | 366 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:00
2020-09-16 13:00 | 44090.5418 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 22 | 44 | 402 | 23 | 45 | 540 |  | 2020-09-16 13:00 | 44090.5418 | 23 | 45 | 540 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 13:00
2020-09-16 13:00 | 44090.5418 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 2 | 21.5 | 47.7 | 402 | 23 | 43 | 509 | No | 2020-09-16 13:00 | 44090.5418 | 23 | 43 | 509 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 13:00
2020-09-16 13:01 | 44090.542 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 3 | 23.4 | 49.5 | 425 | 22.2 | 54.3 | 496 |  | 2020-09-16 13:01 | 44090.542 | 22.2 | 54.3 | 496 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 13:00
2020-09-16 13:01 | 44090.5422 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 22 | 44 | 402 | 23 | 43 | 549 |  | 2020-09-16 13:01 | 44090.5422 | 23 | 43 | 549 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 13:00
2020-09-16 13:01 | 44090.5423 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 22 | 52 | 409 |  | 2020-09-16 13:01 | 44090.5423 | 22 | 52 | 409 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:00
2020-09-16 13:01 | 44090.5423 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 23.6 | 28.5 | 39 | 395 | 23.3 | 36.7 | 489 |  | 2020-09-16 13:01 | 44090.5423 | 23.3 | 36.7 | 489 |  | caution | 2020-09-14 | B21554¦¦¦Sep-16-2020 13:00
2020-09-16 13:01 | 44090.5424 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 23.1 | 45.3 | 390 | No | 2020-09-16 13:01 | 44090.5424 | 23.1 | 45.3 | 390 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 13:01
2020-09-16 13:01 | 44090.5427 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 22 | 44 | 402 | 22 | 43 | 542 |  | 2020-09-16 13:01 | 44090.5427 | 22 | 43 | 542 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 13:01
2020-09-16 13:01 | 44090.5427 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 22.8 | 45.2 | 499 |  | 2020-09-16 13:02 | 44090.5427 | 22.8 | 45.2 | 499 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 13:01
2020-09-16 13:02 | 44090.5427 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 50 | 630 |  | 2020-09-16 13:02 | 44090.5427 | 23 | 50 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:01
2020-09-16 13:02 | 44090.5429 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.7 | 48.5 | 539 |  | 2020-09-16 13:02 | 44090.5429 | 21.7 | 48.5 | 539 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 13:01
2020-09-16 13:02 | 44090.543 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 20.7 | 54.4 | 499 |  | 2020-09-16 13:02 | 44090.543 | 20.7 | 54.4 | 499 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 13:01
2020-09-16 13:02 | 44090.543 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 8 | 21.5 | 47.7 | 402 | 23.3 | 44.1 | 477 | No | 2020-09-16 13:02 | 44090.543 | 23.3 | 44.1 | 477 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 13:01
2020-09-16 13:02 | 44090.5432 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 2 | 23 | 50 | 380 | 21.4 | 56 | 442 |  | 2020-09-16 13:02 | 44090.5432 | 21.4 | 56 | 442 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 13:02
2020-09-16 13:02 | 44090.5432 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 5 | 23.4 | 49.5 | 425 | 22.4 | 52.1 | 524 |  | 2020-09-16 13:02 | 44090.5432 | 22.4 | 52.1 | 524 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 13:02
2020-09-16 13:03 | 44090.5435 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 50 | 630 |  | 2020-09-16 13:03 | 44090.5435 | 23 | 50 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:02
2020-09-16 13:03 | 44090.5436 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 22.2 | 45 | 512 |  | 2020-09-16 13:03 | 44090.5436 | 22.2 | 45 | 512 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 13:02
2020-09-16 13:03 | 44090.5436 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 22 | 52 | 406 |  | 2020-09-16 13:03 | 44090.5436 | 22 | 52 | 406 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:02
2020-09-16 13:03 | 44090.5438 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 4 | 22 | 44 | 402 | 23 | 47 | 551 |  | 2020-09-16 13:03 | 44090.5438 | 23 | 47 | 551 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 13:03
2020-09-16 13:03 | 44090.5439 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 21.8 | 54.6 | 496 |  | 2020-09-16 13:03 | 44090.5439 | 21.8 | 54.6 | 496 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 13:03
2020-09-16 13:04 | 44090.5441 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.6 | 49.1 | 530 |  | 2020-09-16 13:04 | 44090.5441 | 21.6 | 49.1 | 530 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 13:03
2020-09-16 13:04 | 44090.5442 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford |  |  | 0 | 22 | 44 | 402 | 23 | 42 | 571 | Couldn't get into courtroom 1,3 and 4 | 2020-09-16 13:04 | 44090.5442 | 23 | 42 | 571 |  |  | 2020-09-14 | B25479¦¦¦Sep-16-2020 13:03
2020-09-16 13:04 | 44090.5443 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 1 | 21.2 | 50.8 | 405 | 22.5 | 47.1 | 487 |  | 2020-09-16 13:04 | 44090.5443 | 22.5 | 47.1 | 487 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 13:03
2020-09-16 13:04 | 44090.5445 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 23 | 22 | 60 | 430 | 23 | 49 | 620 |  | 2020-09-16 13:04 | 44090.5445 | 23 | 49 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:04
2020-09-16 13:04 | 44090.5446 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 23.2 | 44.4 | 445 | No | 2020-09-16 13:04 | 44090.5446 | 23.2 | 44.4 | 445 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 13:04
2020-09-16 13:04 | 44090.5446 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 21.7 | 47.8 | 501 |  | 2020-09-16 13:04 | 44090.5446 | 21.7 | 47.8 | 501 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 13:04
2020-09-16 13:04 | 44090.5448 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 2 | 28.5 | 39 | 395 | 21.3 | 35.2 | 550 | Court in session | 2020-09-16 13:04 | 44090.5448 | 21.3 | 35.2 | 550 |  | caution | 2020-09-14 | B21554¦¦¦Sep-16-2020 13:04
2020-09-16 13:05 | 44090.5448 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 2 | 23 | 50 | 380 | 22 | 52.6 | 501 |  | 2020-09-16 13:05 | 44090.5448 | 22 | 52.6 | 501 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 13:04
2020-09-16 13:05 | 44090.5452 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.4 | 49.6 | 531 |  | 2020-09-16 13:05 | 44090.5452 | 21.4 | 49.6 | 531 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 13:05
2020-09-16 13:05 | 44090.5453 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 46 | 363 |  | 2020-09-16 13:05 | 44090.5453 | 23 | 46 | 363 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:05
2020-09-16 13:05 | 44090.5453 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 21.7 | 48.5 | 499 |  | 2020-09-16 13:05 | 44090.5453 | 21.7 | 48.5 | 499 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 13:05
2020-09-16 13:05 | 44090.5454 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 21.8 | 53 | 490 |  | 2020-09-16 13:05 | 44090.5454 | 21.8 | 53 | 490 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 13:05
2020-09-16 13:06 | 44090.5455 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 49 | 640 |  | 2020-09-16 13:06 | 44090.5455 | 23 | 49 | 640 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:05
2020-09-16 13:06 | 44090.5456 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 3 | 21.5 | 47.7 | 402 | 22.8 | 41.3 | 669 | No | 2020-09-16 13:06 | 44090.5456 | 22.8 | 41.3 | 669 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 13:05
2020-09-16 13:06 | 44090.5456 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 0 | 23.4 | 49.5 | 425 | 22.6 | 51.6 | 489 |  | 2020-09-16 13:06 | 44090.5456 | 22.6 | 51.6 | 489 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 13:05
2020-09-16 13:06 | 44090.546 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 22 | 46 | 363 |  | 2020-09-16 13:06 | 44090.546 | 22 | 46 | 363 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:06
2020-09-16 13:06 | 44090.5462 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 21.9 | 51.4 | 499 |  | 2020-09-16 13:06 | 44090.5462 | 21.9 | 51.4 | 499 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 13:06
2020-09-16 13:07 | 44090.5464 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.3 | 51.6 | 536 |  | 2020-09-16 13:07 | 44090.5464 | 21.3 | 51.6 | 536 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 13:06
2020-09-16 13:07 | 44090.5465 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 3 | 23.4 | 49.5 | 425 | 22.6 | 51.8 | 494 |  | 2020-09-16 13:07 | 44090.5465 | 22.6 | 51.8 | 494 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 13:06
2020-09-16 13:07 | 44090.5466 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 23 | 51 | 411 |  | 2020-09-16 13:07 | 44090.5466 | 23 | 51 | 411 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:07
2020-09-16 13:07 | 44090.5466 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 49 | 650 |  | 2020-09-16 13:07 | 44090.5466 | 24 | 49 | 650 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:07
2020-09-16 13:07 | 44090.5467 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 21.9 | 51.5 | 761 |  | 2020-09-16 13:07 | 44090.5467 | 21.9 | 51.5 | 761 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 13:07
2020-09-16 13:07 | 44090.5468 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 22.1 | 51.5 | 477 |  | 2020-09-16 13:07 | 44090.5468 | 22.1 | 51.5 | 477 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 13:07
2020-09-16 13:07 | 44090.5468 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 20.5 | 51.6 | 551 |  | 2020-09-16 13:07 | 44090.5468 | 20.5 | 51.6 | 551 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 13:07
2020-09-16 13:08 | 44090.5469 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock |  |  | 0 | 16 | 69 | 383 | 22.3 | 45.3 | 435 | No | 2020-09-16 13:08 | 44090.5469 | 22.3 | 45.3 | 435 |  |  | 2020-09-14 | B20494¦¦¦Sep-16-2020 13:07
2020-09-16 13:08 | 44090.547 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 3 | 21.5 | 47.7 | 402 | 23.2 | 43 | 442 | No | 2020-09-16 13:08 | 44090.547 | 23.2 | 43 | 442 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 13:07
2020-09-16 13:08 | 44090.5472 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 0 | 21.2 | 50.8 | 405 | 21.7 | 47.2 | 433 | Dehumidifier running | 2020-09-16 13:08 | 44090.5472 | 21.7 | 47.2 | 433 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 13:07
2020-09-16 13:08 | 44090.5473 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 22 | 47 | 368 |  | 2020-09-16 13:08 | 44090.5473 | 22 | 47 | 368 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:08
2020-09-16 13:08 | 44090.5474 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.6 | 51 | 559 |  | 2020-09-16 13:08 | 44090.5474 | 21.6 | 51 | 559 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 13:08
2020-09-16 13:08 | 44090.5474 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 2 | 28.5 | 39 | 395 | 23.6 | 39.7 | 525 |  | 2020-09-16 13:08 | 44090.5474 | 23.6 | 39.7 | 525 |  | caution | 2020-09-14 | B21554¦¦¦Sep-16-2020 13:08
2020-09-16 13:08 | 44090.5475 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 20 | 62 | 385 | 22.1 | 49.7 | 465 |  | 2020-09-16 13:08 | 44090.5475 | 22.1 | 49.7 | 465 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 13:08
2020-09-16 13:08 | 44090.5476 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 51 | 670 |  | 2020-09-16 13:08 | 44090.5476 | 24 | 51 | 670 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:08
2020-09-16 13:09 | 44090.5478 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 0 | 23.4 | 49.5 | 425 | 22.6 | 51.7 | 443 |  | 2020-09-16 13:09 | 44090.5478 | 22.6 | 51.7 | 443 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 13:08
2020-09-16 13:09 | 44090.5479 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 21.7 | 49.5 | 457 |  | 2020-09-16 13:09 | 44090.5479 | 21.7 | 49.5 | 457 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 13:09
2020-09-16 13:09 | 44090.5479 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 20.8 | 49.7 | 510 |  | 2020-09-16 13:09 | 44090.5479 | 20.8 | 49.7 | 510 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 13:09
2020-09-16 13:09 | 44090.5482 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 4 | 20 | 62.4 | 387 | 21.6 | 53.6 | 499 |  | 2020-09-16 13:09 | 44090.5482 | 21.6 | 53.6 | 499 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 13:09
2020-09-16 13:10 | 44090.5485 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 49 | 620 |  | 2020-09-16 13:10 | 44090.5485 | 24 | 49 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:09
2020-09-16 13:10 | 44090.5485 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 369 | 22 | 47 | 369 |  | 2020-09-16 13:10 | 44090.5485 | 22 | 47 | 369 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:09
2020-09-16 13:10 | 44090.5485 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 21.8 | 49.6 | 450 |  | 2020-09-16 13:10 | 44090.5485 | 21.8 | 49.6 | 450 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 13:09
2020-09-16 13:10 | 44090.5487 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 0 | 23.4 | 49.5 | 425 | 22.6 | 52.2 | 425 |  | 2020-09-16 13:10 | 44090.5487 | 22.6 | 52.2 | 425 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 13:10
2020-09-16 13:10 | 44090.5489 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 1 | 22 | 55 | 379 | 23 | 50 | 414 |  | 2020-09-16 13:10 | 44090.5489 | 23 | 50 | 414 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:10
2020-09-16 13:10 | 44090.5489 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.5 | 50.2 | 541 |  | 2020-09-16 13:10 | 44090.5489 | 21.5 | 50.2 | 541 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 13:10
2020-09-16 13:11 | 44090.5491 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 2 | 20 | 62.4 | 387 | 22.1 | 52.6 | 497 |  | 2020-09-16 13:11 | 44090.5491 | 22.1 | 52.6 | 497 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 13:10
2020-09-16 13:11 | 44090.5494 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 22 | 47 | 368 |  | 2020-09-16 13:11 | 44090.5494 | 22 | 47 | 368 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:11
2020-09-16 13:11 | 44090.5495 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 50 | 620 |  | 2020-09-16 13:11 | 44090.5495 | 24 | 50 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:11
2020-09-16 13:12 | 44090.5498 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 3 | 16 | 69 | 383 | 22.2 | 48.8 | 549 | No | 2020-09-16 13:12 | 44090.5498 | 22.2 | 48.8 | 549 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 13:11
2020-09-16 13:12 | 44090.5498 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.7 | 50 | 549 |  | 2020-09-16 13:12 | 44090.5498 | 21.7 | 50 | 549 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 13:11
2020-09-16 13:12 | 44090.5499 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 0 | 23.4 | 49.5 | 425 | 22.8 | 51.9 | 451 |  | 2020-09-16 13:12 | 44090.5499 | 22.8 | 51.9 | 451 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 13:11
2020-09-16 13:12 | 44090.55 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 21.4 | 59.2 | 400 | 20.7 | 53.4 | 803 |  | 2020-09-16 13:12 | 44090.55 | 20.7 | 53.4 | 803 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 13:12
2020-09-16 13:12 | 44090.5501 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 21.9 | 50.7 | 491 |  | 2020-09-16 13:12 | 44090.5501 | 21.9 | 50.7 | 491 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 13:12
2020-09-16 13:12 | 44090.5502 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 2 | 21.5 | 47.7 | 402 | 22.6 | 45.6 | 418 | No | 2020-09-16 13:12 | 44090.5502 | 22.6 | 45.6 | 418 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 13:12
2020-09-16 13:13 | 44090.5504 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 2 | 28.5 | 39 | 395 | 22 | 34.9 | 565 | unable to access | 2020-09-16 13:13 | 44090.5504 | 22 | 34.9 | 565 |  | low | 2020-09-14 | B21554¦¦¦Sep-16-2020 13:12
2020-09-16 13:13 | 44090.5504 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 2 | 28.5 | 39 | 395 | 22 | 34.9 | 565 | unable to access | 2020-09-16 13:13 | 44090.5504 | 22 | 34.9 | 565 |  | low | 2020-09-14 | B21554¦¦¦Sep-16-2020 13:12
2020-09-16 13:13 | 44090.5505 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 5 | 23.4 | 49.5 | 425 | 23.4 | 56.3 | 516 |  | 2020-09-16 13:13 | 44090.5505 | 23.4 | 56.3 | 516 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 13:12
2020-09-16 13:13 | 44090.5506 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 49 | 600 |  | 2020-09-16 13:13 | 44090.5506 | 24 | 49 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:12
2020-09-16 13:13 | 44090.5508 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 22.1 | 49.5 | 451 |  | 2020-09-16 13:13 | 44090.5508 | 22.1 | 49.5 | 451 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 13:13
2020-09-16 13:13 | 44090.5509 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.3 | 45.8 | 432 | 21.8 | 50 | 551 |  | 2020-09-16 13:13 | 44090.5509 | 21.8 | 50 | 551 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 13:13
2020-09-16 13:14 | 44090.5511 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 22.1 | 51.1 | 493 |  | 2020-09-16 13:14 | 44090.5511 | 22.1 | 51.1 | 493 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 13:13
2020-09-16 13:14 | 44090.5515 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 49 | 640 |  | 2020-09-16 13:14 | 44090.5515 | 24 | 49 | 640 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:14
2020-09-16 13:14 | 44090.5515 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 1 | 22 | 55 | 379 | 23 | 50 | 413 |  | 2020-09-16 13:14 | 44090.5515 | 23 | 50 | 413 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:14
2020-09-16 13:14 | 44090.5516 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge |  |  | 1 | 23 | 50 | 380 | 21.9 | 49.7 | 465 |  | 2020-09-16 13:14 | 44090.5516 | 21.9 | 49.7 | 465 |  |  | 2020-09-14 | B16187¦¦¦Sep-16-2020 13:14
2020-09-16 13:14 | 44090.5517 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.1 | 48.2 | 557 | No | 2020-09-16 13:14 | 44090.5517 | 22.1 | 48.2 | 557 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 13:14
2020-09-16 13:15 | 44090.5518 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 22.2 | 50.7 | 492 |  | 2020-09-16 13:15 | 44090.5518 | 22.2 | 50.7 | 492 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 13:14
2020-09-16 13:15 | 44090.5519 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 3 | 24.3 | 45.8 | 432 | 22.2 | 49.2 | 553 |  | 2020-09-16 13:15 | 44090.5519 | 22.2 | 49.2 | 553 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 13:14
2020-09-16 13:15 | 44090.5521 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 2 | 21.5 | 47.7 | 402 | 24 | 44.6 | 469 | No | 2020-09-16 13:15 | 44090.5521 | 24 | 44.6 | 469 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 13:15
2020-09-16 13:15 | 44090.5524 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 48 | 630 |  | 2020-09-16 13:15 | 44090.5524 | 24 | 48 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:15
2020-09-16 13:16 | 44090.5524 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 2 | 28.5 | 39 | 395 | 21.9 | 35.3 | 555 |  | 2020-09-16 13:16 | 44090.5524 | 21.9 | 35.3 | 555 |  | caution | 2020-09-14 | B21554¦¦¦Sep-16-2020 13:15
2020-09-16 13:16 | 44090.5528 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 23 | 49 | 406 |  | 2020-09-16 13:16 | 44090.5528 | 23 | 49 | 406 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:15
2020-09-16 13:17 | 44090.5536 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 49 | 620 |  | 2020-09-16 13:17 | 44090.5536 | 24 | 49 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:17
2020-09-16 13:17 | 44090.5537 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.3 | 48.2 | 522 | No | 2020-09-16 13:17 | 44090.5537 | 22.3 | 48.2 | 522 |  |  | 2020-09-14 | B20151¦¦¦Sep-16-2020 13:17
2020-09-16 13:18 | 44090.554 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 23 | 50 | 398 |  | 2020-09-16 13:18 | 44090.554 | 23 | 50 | 398 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:17
2020-09-16 13:19 | 44090.5547 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 2 | 28.5 | 39 | 395 | 23.7 | 36.5 | 597 |  | 2020-09-16 13:19 | 44090.5547 | 23.7 | 36.5 | 597 |  | caution | 2020-09-14 | B21554¦¦¦Sep-16-2020 13:18
2020-09-16 13:19 | 44090.5549 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 48 | 630 |  | 2020-09-16 13:19 | 44090.5549 | 24 | 48 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:19
2020-09-16 13:19 | 44090.5549 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 9 | 21.2 | 50.8 | 405 | 20.3 | 53 | 455 |  | 2020-09-16 13:19 | 44090.5549 | 20.3 | 53 | 455 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 13:19
2020-09-16 13:20 | 44090.5557 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 49 | 640 |  | 2020-09-16 13:20 | 44090.5557 | 24 | 49 | 640 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:20
2020-09-16 13:22 | 44090.5569 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 2 | 28.5 | 39 | 395 | 23.7 | 36.5 | 610 |  | 2020-09-16 13:22 | 44090.5569 | 23.7 | 36.5 | 610 |  | caution | 2020-09-14 | B21554¦¦¦Sep-16-2020 13:21
2020-09-16 13:22 | 44090.5571 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 49 | 600 |  | 2020-09-16 13:22 | 44090.5571 | 24 | 49 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:22
2020-09-16 13:23 | 44090.5574 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 2 | 22.5 | 50.7 | 421 | 22.9 | 50 | 598 |  | 2020-09-16 13:23 | 44090.5574 | 22.9 | 50 | 598 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 13:22
2020-09-16 13:23 | 44090.5577 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 2 | 21.5 | 47.7 | 402 | 22.6 | 47 | 523 | No | 2020-09-16 13:23 | 44090.5577 | 22.6 | 47 | 523 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 13:23
2020-09-16 13:24 | 44090.5581 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 22 | 52 | 402 |  | 2020-09-16 13:24 | 44090.5581 | 22 | 52 | 402 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:23
2020-09-16 13:25 | 44090.5588 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.5 | 50.7 | 421 | 22.8 | 49.3 | 580 |  | 2020-09-16 13:25 | 44090.5588 | 22.8 | 49.3 | 580 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 13:24
2020-09-16 13:25 | 44090.5592 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 6 | 28.5 | 39 | 395 | 23.6 | 39.4 | 642 |  | 2020-09-16 13:25 | 44090.5592 | 23.6 | 39.4 | 642 |  | caution | 2020-09-14 | B21554¦¦¦Sep-16-2020 13:25
2020-09-16 13:26 | 44090.5596 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 44 | 384 |  | 2020-09-16 13:26 | 44090.5596 | 23 | 44 | 384 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:25
2020-09-16 13:27 | 44090.5601 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.5 | 50.7 | 421 | 23.8 | 50.5 | 564 |  | 2020-09-16 13:27 | 44090.5601 | 23.8 | 50.5 | 564 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 13:26
2020-09-16 13:27 | 44090.5603 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 22 | 51 | 393 |  | 2020-09-16 13:27 | 44090.5603 | 22 | 51 | 393 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:26
2020-09-16 13:27 | 44090.5605 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 44 | 388 |  | 2020-09-16 13:27 | 44090.5605 | 23 | 44 | 388 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:27
2020-09-16 13:27 | 44090.5605 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 49 | 620 |  | 2020-09-16 13:27 | 44090.5605 | 23 | 49 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:27
2020-09-16 13:28 | 44090.5614 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 4 | 22.6 | 56.2 | 383 | 22.8 | 52.2 | 519 |  | 2020-09-16 13:28 | 44090.5614 | 22.8 | 52.2 | 519 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:28
2020-09-16 13:28 | 44090.5614 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 4 | 22.5 | 50.7 | 421 | 23.8 | 47 | 532 |  | 2020-09-16 13:28 | 44090.5614 | 23.8 | 47 | 532 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 13:28
2020-09-16 13:28 | 44090.5615 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 2 | 28.5 | 39 | 395 | 23.2 | 39 | 706 |  | 2020-09-16 13:28 | 44090.5615 | 23.2 | 39 | 706 |  | caution | 2020-09-14 | B21554¦¦¦Sep-16-2020 13:28
2020-09-16 13:29 | 44090.5618 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 44 | 385 |  | 2020-09-16 13:29 | 44090.5618 | 23 | 44 | 385 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:28
2020-09-16 13:29 | 44090.5619 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 50 | 610 |  | 2020-09-16 13:29 | 44090.5619 | 23 | 50 | 610 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:29
2020-09-16 13:30 | 44090.5625 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 1 | 22.5 | 50.7 | 421 | 23.6 | 48.5 | 529 |  | 2020-09-16 13:30 | 44090.5625 | 23.6 | 48.5 | 529 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 13:30
2020-09-16 13:30 | 44090.5627 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 22 | 51 | 398 |  | 2020-09-16 13:30 | 44090.5627 | 22 | 51 | 398 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:30
2020-09-16 13:30 | 44090.5627 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 6 | 22.6 | 56.2 | 383 | 22.5 | 50.3 | 440 |  | 2020-09-16 13:30 | 44090.5627 | 22.5 | 50.3 | 440 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:30
2020-09-16 13:31 | 44090.5629 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 24 | 49 | 720 |  | 2020-09-16 13:31 | 44090.5629 | 24 | 49 | 720 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:30
2020-09-16 13:31 | 44090.5631 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 3 | 25 | 39 | 368 | 23 | 45 | 380 |  | 2020-09-16 13:31 | 44090.5631 | 23 | 45 | 380 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:30
2020-09-16 13:32 | 44090.5638 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 1 | 22 | 55 | 379 | 22 | 52 | 407 |  | 2020-09-16 13:32 | 44090.5638 | 22 | 52 | 407 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:31
2020-09-16 13:32 | 44090.5638 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 0 | 21.2 | 50.8 | 405 | 21 | 50.4 | 447 |  | 2020-09-16 13:32 | 44090.5638 | 21 | 50.4 | 447 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 13:31
2020-09-16 13:32 | 44090.564 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 22 | 60 | 430 | 23 | 49 | 590 |  | 2020-09-16 13:32 | 44090.564 | 23 | 49 | 590 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 13:32
2020-09-16 13:32 | 44090.564 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 22.2 | 50.3 | 397 |  | 2020-09-16 13:32 | 44090.564 | 22.2 | 50.3 | 397 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:32
2020-09-16 13:32 | 44090.564 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.5 | 50.7 | 421 | 22.9 | 47 | 506 |  | 2020-09-16 13:32 | 44090.564 | 22.9 | 47 | 506 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 13:32
2020-09-16 13:33 | 44090.5644 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 3 | 25 | 39 | 368 | 23 | 45 | 382 |  | 2020-09-16 13:33 | 44090.5644 | 23 | 45 | 382 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:32
2020-09-16 13:34 | 44090.5651 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.5 | 50.7 | 421 | 22.8 | 47.9 | 467 |  | 2020-09-16 13:34 | 44090.5651 | 22.8 | 47.9 | 467 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 13:33
2020-09-16 13:34 | 44090.5654 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 3 | 25 | 39 | 368 | 23 | 45 | 383 |  | 2020-09-16 13:34 | 44090.5654 | 23 | 45 | 383 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:34
2020-09-16 13:34 | 44090.5655 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 3 | 22.6 | 56.2 | 383 | 21.8 | 52 | 418 |  | 2020-09-16 13:34 | 44090.5655 | 21.8 | 52 | 418 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:34
2020-09-16 13:34 | 44090.5655 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 1 | 21.2 | 50.8 | 405 | 21 | 50.8 | 508 |  | 2020-09-16 13:34 | 44090.5655 | 21 | 50.8 | 508 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 13:34
2020-09-16 13:34 | 44090.5655 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 23 | 51 | 411 |  | 2020-09-16 13:34 | 44090.5655 | 23 | 51 | 411 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:34
2020-09-16 13:36 | 44090.5667 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 22.1 | 53.6 | 425 |  | 2020-09-16 13:36 | 44090.5667 | 22.1 | 53.6 | 425 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:36
2020-09-16 13:36 | 44090.5668 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.5 | 50.7 | 421 | 22.9 | 47.5 | 476 |  | 2020-09-16 13:36 | 44090.5668 | 22.9 | 47.5 | 476 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 13:36
2020-09-16 13:36 | 44090.5668 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 44 | 450 |  | 2020-09-16 13:36 | 44090.5668 | 23 | 44 | 450 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:36
2020-09-16 13:37 | 44090.5671 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 2 | 16 | 69 | 383 | 22 | 46.6 | 413 | No | 2020-09-16 13:37 | 44090.5671 | 22 | 46.6 | 413 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 13:36
2020-09-16 13:37 | 44090.5672 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 23 | 50 | 398 |  | 2020-09-16 13:37 | 44090.5672 | 23 | 50 | 398 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:36
2020-09-16 13:38 | 44090.5678 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.5 | 50.7 | 421 | 22.5 | 48.9 | 552 |  | 2020-09-16 13:38 | 44090.5678 | 22.5 | 48.9 | 552 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 13:37
2020-09-16 13:38 | 44090.5679 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 0 | 21.2 | 50.8 | 405 | 19.4 | 48.4 | 484 | Dehumidifier running,set at 17 | 2020-09-16 13:38 | 44090.5679 | 19.4 | 48.4 | 484 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 13:37
2020-09-16 13:38 | 44090.5682 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 22.5 | 50.6 | 415 |  | 2020-09-16 13:38 | 44090.5682 | 22.5 | 50.6 | 415 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:38
2020-09-16 13:38 | 44090.5684 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.5 | 50.7 | 421 | 22.5 | 49.9 | 586 |  | 2020-09-16 13:38 | 44090.5684 | 22.5 | 49.9 | 586 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 13:38
2020-09-16 13:39 | 44090.5684 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 22 | 51 | 403 |  | 2020-09-16 13:38 | 44090.5684 | 22 | 51 | 403 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:38
2020-09-16 13:39 | 44090.5684 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 6 | 25.4 | 53.5 | 423 | 22.6 | 52.2 | 445 | No | 2020-09-16 13:39 | 44090.5684 | 22.6 | 52.2 | 445 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 13:38
2020-09-16 13:39 | 44090.5686 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 25 | 39 | 368 | 23 | 45 | 380 |  | 2020-09-16 13:39 | 44090.5686 | 23 | 45 | 380 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:38
2020-09-16 13:39 | 44090.5686 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 0 | 16 | 69 | 383 | 21.9 | 47 | 422 | No | 2020-09-16 13:39 | 44090.5686 | 21.9 | 47 | 422 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 13:38
2020-09-16 13:39 | 44090.5691 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 1 | 39 | 45 | 380 | 23 | 45 | 380 |  | 2020-09-16 13:39 | 44090.5691 | 23 | 45 | 380 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:39
2020-09-16 13:40 | 44090.5694 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 4 | 394 | 24.5 | 48.4 | 24.5 | 40.9 | 433 | No | 2020-09-16 13:40 | 44090.5694 | 24.5 | 40.9 | 433 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 13:39
2020-09-16 13:40 | 44090.5695 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 0 | 21.2 | 50.8 | 405 | 19.6 | 54.2 | 450 |  | 2020-09-16 13:40 | 44090.5695 | 19.6 | 54.2 | 450 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 13:40
2020-09-16 13:41 | 44090.5704 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 23.1 | 51.4 | 480 |  | 2020-09-16 13:41 | 44090.5704 | 23.1 | 51.4 | 480 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:41
2020-09-16 13:42 | 44090.5705 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 3 | 24.5 | 48.4 | 394 | 22.4 | 45.3 | 449 | No | 2020-09-16 13:42 | 44090.5705 | 22.4 | 45.3 | 449 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 13:41
2020-09-16 13:42 | 44090.5707 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 23 | 48 | 390 |  | 2020-09-16 13:42 | 44090.5707 | 23 | 48 | 390 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:41
2020-09-16 13:42 | 44090.5711 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 2 | 16 | 69 | 383 | 22.1 | 49.3 | 482 | No | 2020-09-16 13:42 | 44090.5711 | 22.1 | 49.3 | 482 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 13:42
2020-09-16 13:43 | 44090.5714 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 1 | 21.2 | 50.8 | 405 | 21.2 | 52 | 465 |  | 2020-09-16 13:43 | 44090.5714 | 21.2 | 52 | 465 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 13:42
2020-09-16 13:43 | 44090.5716 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 3 | 24.5 | 48.4 | 394 | 22.3 | 48.3 | 433 | No | 2020-09-16 13:43 | 44090.5716 | 22.3 | 48.3 | 433 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 13:43
2020-09-16 13:43 | 44090.5717 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 23 | 49.6 | 423 |  | 2020-09-16 13:43 | 44090.5717 | 23 | 49.6 | 423 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:43
2020-09-16 13:44 | 44090.5723 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 23 | 48 | 394 |  | 2020-09-16 13:44 | 44090.5723 | 23 | 48 | 394 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:44
2020-09-16 13:44 | 44090.5726 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 7 | 24.5 | 48.4 | 394 | 23 | 53.3 | 422 | No | 2020-09-16 13:44 | 44090.5726 | 23 | 53.3 | 422 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 13:44
2020-09-16 13:45 | 44090.5726 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.1 | 49 | 496 | No | 2020-09-16 13:45 | 44090.5726 | 22.1 | 49 | 496 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 13:44
2020-09-16 13:45 | 44090.5728 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 23.2 | 47.6 | 405 |  | 2020-09-16 13:45 | 44090.5728 | 23.2 | 47.6 | 405 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:44
2020-09-16 13:46 | 44090.5735 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 24.5 | 48.4 | 394 | 23.7 | 46.2 | 420 | No | 2020-09-16 13:46 | 44090.5735 | 23.7 | 46.2 | 420 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 13:45
2020-09-16 13:47 | 44090.5746 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 23.2 | 49.2 | 401 |  | 2020-09-16 13:47 | 44090.5746 | 23.2 | 49.2 | 401 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:47
2020-09-16 13:48 | 44090.5747 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 22 | 55 | 379 | 22 | 50 | 396 |  | 2020-09-16 13:48 | 44090.5747 | 22 | 50 | 396 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 13:47
2020-09-16 13:48 | 44090.5748 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 1 | 21.2 | 50.8 | 405 | 20.9 | 52 | 455 |  | 2020-09-16 13:48 | 44090.5748 | 20.9 | 52 | 455 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 13:47
2020-09-16 13:48 | 44090.5751 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.5 | 47.8 | 468 | No | 2020-09-16 13:48 | 44090.5751 | 22.5 | 47.8 | 468 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 13:48
2020-09-16 13:48 | 44090.5752 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 24.4 | 48.4 | 394 | 24.3 | 48.3 | 411 | No | 2020-09-16 13:48 | 44090.5752 | 24.3 | 48.3 | 411 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 13:48
2020-09-16 13:50 | 44090.5761 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 23.1 | 48.7 | 404 |  | 2020-09-16 13:50 | 44090.5761 | 23.1 | 48.7 | 404 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:49
2020-09-16 13:50 | 44090.5766 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.7 | 47.6 | 524 | No | 2020-09-16 13:50 | 44090.5766 | 22.7 | 47.6 | 524 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 13:50
2020-09-16 13:50 | 44090.5766 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 24.5 | 48.4 | 394 | 23.7 | 48.4 | 411 | No | 2020-09-16 13:50 | 44090.5766 | 23.7 | 48.4 | 411 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 13:50
2020-09-16 13:51 | 44090.5771 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 22.5 | 49.8 | 405 |  | 2020-09-16 13:51 | 44090.5771 | 22.5 | 49.8 | 405 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:51
2020-09-16 13:51 | 44090.5772 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston |  |  | 2 | 21.2 | 50.8 | 405 | 20.6 | 53.1 | 439 | Second reading, not sure if first went through | 2020-09-16 13:51 | 44090.5772 | 20.6 | 53.1 | 439 |  |  | 2020-09-14 | B90558¦¦¦Sep-16-2020 13:51
2020-09-16 13:51 | 44090.5773 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 24.5 | 48.4 | 394 | 23.8 | 48.9 | 409 | No | 2020-09-16 13:51 | 44090.5773 | 23.8 | 48.9 | 409 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 13:51
2020-09-16 13:52 | 44090.578 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 2 | 24.5 | 48.4 | 394 | 23.1 | 42.5 | 413 | No | 2020-09-16 13:52 | 44090.578 | 23.1 | 42.5 | 413 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 13:52
2020-09-16 13:53 | 44090.5783 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 22.5 | 50.6 | 402 |  | 2020-09-16 13:53 | 44090.5783 | 22.5 | 50.6 | 402 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:52
2020-09-16 13:53 | 44090.5787 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 0 | 16 | 69 | 383 | 22.6 | 46.8 | 451 | No | 2020-09-16 13:53 | 44090.5787 | 22.6 | 46.8 | 451 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 13:53
2020-09-16 13:53 | 44090.5787 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 7 | 22.3 | 44.5 | 452 | 21.9 | 47.7 | 591 |  | 2020-09-16 13:53 | 44090.5787 | 21.9 | 47.7 | 591 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 13:53
2020-09-16 13:54 | 44090.5789 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 5 | 24.5 | 48.4 | 394 | 22.2 | 43.3 | 433 | No | 2020-09-16 13:54 | 44090.5789 | 22.2 | 43.3 | 433 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 13:53
2020-09-16 13:55 | 44090.5795 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 22.3 | 51.3 | 394 |  | 2020-09-16 13:54 | 44090.5795 | 22.3 | 51.3 | 394 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:54
2020-09-16 13:55 | 44090.5799 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 3 | 24.5 | 48.4 | 394 | 22.1 | 54.4 | 431 | No | 2020-09-16 13:55 | 44090.5799 | 22.1 | 54.4 | 431 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 13:55
2020-09-16 13:55 | 44090.5801 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 1 | 16 | 69 | 383 | 23 | 46.1 | 414 | No | 2020-09-16 13:55 | 44090.5801 | 23 | 46.1 | 414 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 13:55
2020-09-16 13:56 | 44090.5806 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 3 | 24.5 | 48.4 | 394 | 22.3 | 58.2 | 404 | No | 2020-09-16 13:56 | 44090.5806 | 22.3 | 58.2 | 404 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 13:56
2020-09-16 13:56 | 44090.5806 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 22.5 | 51.1 | 403 |  | 2020-09-16 13:56 | 44090.5806 | 22.5 | 51.1 | 403 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:56
2020-09-16 13:57 | 44090.5812 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23.3 | 41.2 | 373 |  | 2020-09-16 13:57 | 44090.5812 | 23.3 | 41.2 | 373 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:56
2020-09-16 13:57 | 44090.5815 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 4 | 24.5 | 48.4 | 394 | 22.3 | 51.6 | 404 | No | 2020-09-16 13:57 | 44090.5815 | 22.3 | 51.6 | 404 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 13:57
2020-09-16 13:57 | 44090.5816 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 4 | 22.3 | 44.5 | 452 | 20.8 | 51 | 480 |  | 2020-09-16 13:57 | 44090.5816 | 20.8 | 51 | 480 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 13:57
2020-09-16 13:58 | 44090.5816 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 1 | 16 | 69 | 383 | 23.2 | 45.4 | 411 | No | 2020-09-16 13:57 | 44090.5816 | 23.2 | 45.4 | 411 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 13:57
2020-09-16 13:58 | 44090.5818 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 22.9 | 48.9 | 402 |  | 2020-09-16 13:58 | 44090.5818 | 22.9 | 48.9 | 402 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 13:57
2020-09-16 14:00 | 44090.5831 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 7 | 24.5 | 48.4 | 394 | 22.7 | 48.1 | 443 | No | 2020-09-16 14:00 | 44090.5831 | 22.7 | 48.1 | 443 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 13:59
2020-09-16 14:00 | 44090.5833 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23.3 | 41.5 | 375 |  | 2020-09-16 14:00 | 44090.5833 | 23.3 | 41.5 | 375 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 13:59
2020-09-16 14:00 | 44090.5836 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford |  |  | 1 | 16 | 69 | 383 | 23 | 47.1 | 455 | No | 2020-09-16 14:00 | 44090.5836 | 23 | 47.1 | 455 |  |  | 2020-09-14 | B20489¦¦¦Sep-16-2020 14:00
2020-09-16 14:01 | 44090.5838 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 22 | 53 | 394 |  | 2020-09-16 14:01 | 44090.5838 | 22 | 53 | 394 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:00
2020-09-16 14:01 | 44090.5839 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 396 |  | 2020-09-16 14:01 | 44090.5839 | 23 | 42 | 396 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:00
2020-09-16 14:01 | 44090.5842 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 3 | 24.5 | 48.4 | 394 | 22.7 |  | 437 | No | 2020-09-16 14:01 | 44090.5842 | 22.7 |  | 437 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 14:01
2020-09-16 14:02 | 44090.5846 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 22.3 | 44.5 | 452 | 21 | 56.4 | 520 |  | 2020-09-16 14:02 | 44090.5846 | 21 | 56.4 | 520 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:01
2020-09-16 14:02 | 44090.5847 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 22.8 | 49.8 | 427 |  | 2020-09-16 14:02 | 44090.5847 | 22.8 | 49.8 | 427 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 14:01
2020-09-16 14:02 | 44090.5848 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 394 |  | 2020-09-16 14:02 | 44090.5848 | 23 | 42 | 394 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:02
2020-09-16 14:02 | 44090.585 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough |  |  | 4 | 24.5 | 48.4 | 394 | 22 | 50.1 | 425 | No | 2020-09-16 14:02 | 44090.585 | 22 | 50.1 | 425 |  |  | 2020-09-14 | B21128¦¦¦Sep-16-2020 14:02
2020-09-16 14:02 | 44090.585 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 22 | 53 | 406 |  | 2020-09-16 14:02 | 44090.585 | 22 | 53 | 406 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:02
2020-09-16 14:03 | 44090.5856 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 5 | 30 | 35 | 386 | 24 | 47 | 512 |  | 2020-09-16 14:03 | 44090.5856 | 24 | 47 | 512 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:03
2020-09-16 14:03 | 44090.5857 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 22.5 | 50 | 406 |  | 2020-09-16 14:03 | 44090.5857 | 22.5 | 50 | 406 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 14:03
2020-09-16 14:04 | 44090.5862 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 22 | 52 | 403 |  | 2020-09-16 14:04 | 44090.5862 | 22 | 52 | 403 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:04
2020-09-16 14:05 | 44090.5865 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 2 | 22.5 | 50.1 | 385 | 23.7 | 44.3 | 437 |  | 2020-09-16 14:05 | 44090.5865 | 23.7 | 44.3 | 437 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 14:04
2020-09-16 14:05 | 44090.5866 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 30 | 35 | 386 | 26 | 35 | 534 |  | 2020-09-16 14:05 | 44090.5866 | 26 | 35 | 534 | caution | caution | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:04
2020-09-16 14:05 | 44090.5871 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 22.2 | 59 | 360 | 23.2 | 47.7 | 383 |  | 2020-09-16 14:05 | 44090.5871 | 23.2 | 47.7 | 383 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 14:05
2020-09-16 14:06 | 44090.5874 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 22 | 51 | 402 |  | 2020-09-16 14:06 | 44090.5874 | 22 | 51 | 402 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:05
2020-09-16 14:06 | 44090.5875 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 22.5 | 44.5 | 452 | 20 | 53 | 459 |  | 2020-09-16 14:06 | 44090.5875 | 20 | 53 | 459 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:05
2020-09-16 14:06 | 44090.5875 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 22.6 | 48.5 | 406 |  | 2020-09-16 14:06 | 44090.5875 | 22.6 | 48.5 | 406 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 14:05
2020-09-16 14:06 | 44090.5875 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23.2 | 42 | 366 |  | 2020-09-16 14:06 | 44090.5875 | 23.2 | 42 | 366 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:06
2020-09-16 14:06 | 44090.5875 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 23.6 | 42.3 | 398 | No | 2020-09-16 14:06 | 44090.5875 | 23.6 | 42.3 | 398 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:06
2020-09-16 14:06 | 44090.5876 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 30 | 35 | 386 | 24 | 46 | 511 |  | 2020-09-16 14:06 | 44090.5876 | 24 | 46 | 511 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:06
2020-09-16 14:07 | 44090.5879 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 1 | 22.5 | 50.1 | 385 | 23.8 | 46 | 430 |  | 2020-09-16 14:07 | 44090.5879 | 23.8 | 46 | 430 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 14:06
2020-09-16 14:07 | 44090.588 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 2 | 22.2 | 59 | 260 | 22.9 | 48 | 295 |  | 2020-09-16 14:07 | 44090.588 | 22.9 | 48 | 295 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 14:06
2020-09-16 14:07 | 44090.5883 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 380 |  | 2020-09-16 14:07 | 44090.5883 | 23 | 42 | 380 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:07
2020-09-16 14:07 | 44090.5884 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 23 | 50 | 408 |  | 2020-09-16 14:07 | 44090.5884 | 23 | 50 | 408 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:07
2020-09-16 14:07 | 44090.5884 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 30 | 35 | 386 | 24 | 46 | 513 |  | 2020-09-16 14:07 | 44090.5884 | 24 | 46 | 513 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:07
2020-09-16 14:08 | 44090.5887 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 22.6 | 49.6 | 395 |  | 2020-09-16 14:08 | 44090.5887 | 22.6 | 49.6 | 395 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 14:07
2020-09-16 14:08 | 44090.589 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 22.2 | 59 | 360 | 22.7 | 48.3 | 396 |  | 2020-09-16 14:08 | 44090.589 | 22.7 | 48.3 | 396 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 14:08
2020-09-16 14:09 | 44090.5896 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 22.4 | 49.8 | 400 |  | 2020-09-16 14:09 | 44090.5896 | 22.4 | 49.8 | 400 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 14:09
2020-09-16 14:10 | 44090.5902 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 22 | 51 | 421 | No | 2020-09-16 14:10 | 44090.5902 | 22 | 51 | 421 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:09
2020-09-16 14:10 | 44090.5902 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 30 | 35 | 386 | 24 | 47 | 503 |  | 2020-09-16 14:10 | 44090.5902 | 24 | 47 | 503 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:09
2020-09-16 14:10 | 44090.5902 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 0 | 22.5 | 50.1 | 385 | 23.6 | 45.3 | 430 |  | 2020-09-16 14:10 | 44090.5902 | 23.6 | 45.3 | 430 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 14:09
2020-09-16 14:10 | 44090.5903 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 22.2 | 59 | 360 | 22.1 | 52 | 417 |  | 2020-09-16 14:10 | 44090.5903 | 22.1 | 52 | 417 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 14:09
2020-09-16 14:10 | 44090.5903 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 22.5 | 44.5 | 452 | 20.2 | 53.4 | 462 |  | 2020-09-16 14:10 | 44090.5903 | 20.2 | 53.4 | 462 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:09
2020-09-16 14:11 | 44090.5906 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 22 | 50 | 405 |  | 2020-09-16 14:11 | 44090.5906 | 22 | 50 | 405 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:10
2020-09-16 14:11 | 44090.5908 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 22.2 | 59 | 360 | 22.9 | 52.9 | 466 |  | 2020-09-16 14:11 | 44090.5908 | 22.9 | 52.9 | 466 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 14:10
2020-09-16 14:11 | 44090.5909 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 30 | 35 | 386 | 23 | 46 | 464 |  | 2020-09-16 14:11 | 44090.5909 | 23 | 46 | 464 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:10
2020-09-16 14:12 | 44090.5915 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 23.6 |  | 413 |  | 2020-09-16 14:12 | 44090.5915 | 23.6 |  | 413 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 14:11
2020-09-16 14:12 | 44090.5918 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 23 | 50 | 421 |  | 2020-09-16 14:12 | 44090.5918 | 23 | 50 | 421 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:12
2020-09-16 14:12 | 44090.5918 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 30 | 35 | 386 |  |  |  | Occupied, no access | 2020-09-16 14:12 | 44090.5918 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:12
2020-09-16 14:12 | 44090.5919 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 22.4 | 50.2 | 415 | No | 2020-09-16 14:12 | 44090.5919 | 22.4 | 50.2 | 415 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:12
2020-09-16 14:12 | 44090.592 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 22.2 | 59 | 360 | 22 | 52 | 440 |  | 2020-09-16 14:12 | 44090.592 | 22 | 52 | 440 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 14:12
2020-09-16 14:13 | 44090.5923 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 366 |  | 2020-09-16 14:13 | 44090.5923 | 23 | 42 | 366 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:12
2020-09-16 14:13 | 44090.5923 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 22.3 | 44.5 | 452 | 20.3 | 53 | 544 |  | 2020-09-16 14:13 | 44090.5923 | 20.3 | 53 | 544 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:12
2020-09-16 14:13 | 44090.5924 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 0 | 22.5 | 50.1 | 385 | 23.7 | 46.1 | 425 |  | 2020-09-16 14:13 | 44090.5924 | 23.7 | 46.1 | 425 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 14:13
2020-09-16 14:13 | 44090.5924 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 23.6 | 47.1 | 403 |  | 2020-09-16 14:13 | 44090.5924 | 23.6 | 47.1 | 403 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 14:13
2020-09-16 14:13 | 44090.5926 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 30 | 35 | 386 |  |  |  | Occupied, no access | 2020-09-16 14:13 | 44090.5926 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:13
2020-09-16 14:14 | 44090.5928 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 1 | 22.2 | 59 | 360 | 21.7 | 52.3 | 424 |  | 2020-09-16 14:14 | 44090.5928 | 21.7 | 52.3 | 424 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 14:13
2020-09-16 14:14 | 44090.5931 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 367 |  | 2020-09-16 14:14 | 44090.5931 | 23 | 42 | 367 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:14
2020-09-16 14:14 | 44090.5933 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 2 | 23 | 48 | 362 | 23 | 49 | 430 |  | 2020-09-16 14:14 | 44090.5933 | 23 | 49 | 430 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:14
2020-09-16 14:14 | 44090.5933 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 22.7 | 47.8 | 395 |  | 2020-09-16 14:14 | 44090.5933 | 22.7 | 47.8 | 395 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 14:14
2020-09-16 14:14 | 44090.5934 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 30 | 35 | 386 | 23 | 45 | 457 |  | 2020-09-16 14:14 | 44090.5934 | 23 | 45 | 457 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:14
2020-09-16 14:15 | 44090.5935 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 3 | 22.2 | 59 | 360 | 21.4 | 54.8 | 436 |  | 2020-09-16 14:15 | 44090.5935 | 21.4 | 54.8 | 436 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 14:14
2020-09-16 14:15 | 44090.5938 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 23 | 48.5 | 411 | No | 2020-09-16 14:15 | 44090.5938 | 23 | 48.5 | 411 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:15
2020-09-16 14:16 | 44090.5942 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 30 | 35 | 386 | 22 | 45 | 459 |  | 2020-09-16 14:16 | 44090.5942 | 22 | 45 | 459 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:15
2020-09-16 14:16 | 44090.5943 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland |  |  | 2 | 22.6 | 56.2 | 383 | 22.6 | 50.2 | 412 |  | 2020-09-16 14:16 | 44090.5943 | 22.6 | 50.2 | 412 |  |  | 2020-09-14 | B20390¦¦¦Sep-16-2020 14:15
2020-09-16 14:16 | 44090.5943 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 20 | 59.9 | 389 | 23.1 | 49.7 | 449 | Courtroom B,C and D had trial going on hence the access was denied | 2020-09-16 14:16 | 44090.5943 | 23.1 | 49.7 | 449 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 14:15
2020-09-16 14:16 | 44090.5943 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 20 | 59.9 | 389 | 21.6 | 52.3 | 521 | Courtroom B,C and D had trial going on hence the access was denied | 2020-09-16 14:16 | 44090.5943 | 21.6 | 52.3 | 521 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 14:15
2020-09-16 14:16 | 44090.5943 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 364 |  | 2020-09-16 14:16 | 44090.5943 | 23 | 42 | 364 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:15
2020-09-16 14:16 | 44090.5944 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 3 | 22.2 | 59 | 360 | 21.6 | 54.7 | 445 |  | 2020-09-16 14:16 | 44090.5944 | 21.6 | 54.7 | 445 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 14:15
2020-09-16 14:16 | 44090.5944 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 20 | 59.9 | 389 | 21.7 | 52.4 | 522 | Courtroom B,C and D had trial going on hence the access was denied | 2020-09-16 14:16 | 44090.5944 | 21.7 | 52.4 | 522 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 14:15
2020-09-16 14:16 | 44090.5944 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 20 | 59.9 | 389 | 22.3 | 50.6 | 513 | Courtroom B,C and D had trial going on hence the access was denied | 2020-09-16 14:16 | 44090.5944 | 22.3 | 50.6 | 513 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 14:16
2020-09-16 14:16 | 44090.5945 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 20 | 59.9 | 389 | 20.4 | 48.2 | 489 | Courtroom B,C and D had trial going on hence the access was denied | 2020-09-16 14:16 | 44090.5945 | 20.4 | 48.2 | 489 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 14:16
2020-09-16 14:16 | 44090.5946 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 20 | 59.9 | 389 | 21 | 56 | 504 | Courtroom B,C and D had trial going on hence the access was denied | 2020-09-16 14:16 | 44090.5946 | 21 | 56 | 504 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 14:16
2020-09-16 14:16 | 44090.5947 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 20 | 59.9 | 389 | 20.5 | 59 | 493 | Courtroom B,C and D had trial going on hence the access was denied | 2020-09-16 14:16 | 44090.5947 | 20.5 | 59 | 493 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 14:16
2020-09-16 14:16 | 44090.5947 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 20 | 59.9 | 389 | 21.6 | 52.8 | 465 | Courtroom B,C and D had trial going on hence the access was denied | 2020-09-16 14:16 | 44090.5947 | 21.6 | 52.8 | 465 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 14:16
2020-09-16 14:16 | 44090.5947 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 20 | 59.9 | 59.9 | 21.4 | 52.8 | 479 | Courtroom B,C and D had trial going on hence the access was denied | 2020-09-16 14:16 | 44090.5947 | 21.4 | 52.8 | 479 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 14:16
2020-09-16 14:16 | 44090.5948 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 3 | 23 | 48 | 362 | 23 | 49 | 445 |  | 2020-09-16 14:16 | 44090.5948 | 23 | 49 | 445 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:16
2020-09-16 14:16 | 44090.5948 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 20 | 59.9 | 389 | 23 | 50.5 | 450 | Courtroom B,C and D had trial going on hence the access was denied | 2020-09-16 14:16 | 44090.5948 | 23 | 50.5 | 450 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 14:16
2020-09-16 14:17 | 44090.5948 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 20 | 59.9 | 389 | 22.6 | 49.6 | 500 | Courtroom B,C and D had trial going on hence the access was denied | 2020-09-16 14:17 | 44090.5948 | 22.6 | 49.6 | 500 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 14:16
2020-09-16 14:17 | 44090.5949 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 362 |  | 2020-09-16 14:17 | 44090.5949 | 23 | 42 | 362 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:16
2020-09-16 14:17 | 44090.5949 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston |  |  | 0 | 20 | 59.9 | 389 | 23.1 | 49.9 | 477 | Courtroom B,C and D had trial going on hence the access was denied | 2020-09-16 14:17 | 44090.5949 | 23.1 | 49.9 | 477 |  |  | 2020-09-14 | B20478¦¦¦Sep-16-2020 14:16
2020-09-16 14:17 | 44090.595 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 3 | 22.5 | 50.1 | 385 | 23.7 | 46.8 | 455 |  | 2020-09-16 14:17 | 44090.595 | 23.7 | 46.8 | 455 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 14:16
2020-09-16 14:17 | 44090.5954 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 362 |  | 2020-09-16 14:17 | 44090.5954 | 23 | 42 | 362 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:17
2020-09-16 14:18 | 44090.5957 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 23.3 | 44.5 | 452 | 20.2 | 54.7 | 562 |  | 2020-09-16 14:18 | 44090.5957 | 20.2 | 54.7 | 562 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:17
2020-09-16 14:18 | 44090.5958 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 30 | 35 | 386 | 22 | 47 | 457 |  | 2020-09-16 14:18 | 44090.5958 | 22 | 47 | 457 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:17
2020-09-16 14:18 | 44090.5962 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton |  |  | 3 | 22.2 | 59 | 360 | 22.9 | 50.6 | 447 |  | 2020-09-16 14:18 | 44090.5962 | 22.9 | 50.6 | 447 |  |  | 2020-09-14 | B11228¦¦¦Sep-16-2020 14:18
2020-09-16 14:19 | 44090.5962 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 23 | 49 | 435 |  | 2020-09-16 14:19 | 44090.5962 | 23 | 49 | 435 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:18
2020-09-16 14:20 | 44090.5971 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 30 | 35 | 386 | 22 | 49 | 474 |  | 2020-09-16 14:20 | 44090.5971 | 22 | 49 | 474 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:19
2020-09-16 14:20 | 44090.5974 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 23 | 49 | 407 |  | 2020-09-16 14:20 | 44090.5974 | 23 | 49 | 407 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:20
2020-09-16 14:20 | 44090.5974 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 0 | 22.5 | 50.1 | 385 | 23.6 | 44.9 | 429 |  | 2020-09-16 14:20 | 44090.5974 | 23.6 | 44.9 | 429 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 14:20
2020-09-16 14:21 | 44090.5978 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 30 | 35 | 386 | 22 | 49 | 505 |  | 2020-09-16 14:21 | 44090.5978 | 22 | 49 | 505 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:20
2020-09-16 14:22 | 44090.5984 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 23 | 49 | 414 |  | 2020-09-16 14:22 | 44090.5984 | 23 | 49 | 414 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:21
2020-09-16 14:22 | 44090.5984 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 30 | 35 | 386 | 22 | 50 | 507 |  | 2020-09-16 14:22 | 44090.5984 | 22 | 50 | 507 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:21
2020-09-16 14:22 | 44090.5987 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston |  |  | 1 | 22.5 | 50.1 | 385 | 23.6 | 46 | 432 |  | 2020-09-16 14:22 | 44090.5987 | 23.6 | 46 | 432 |  |  | 2020-09-14 | B20550¦¦¦Sep-16-2020 14:22
2020-09-16 14:22 | 44090.5987 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 22.3 | 44.5 | 452 | 21.3 | 53.9 | 531 |  | 2020-09-16 14:22 | 44090.5987 | 21.3 | 53.9 | 531 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:22
2020-09-16 14:22 | 44090.5988 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 22.5 | 49.8 | 439 | No | 2020-09-16 14:22 | 44090.5988 | 22.5 | 49.8 | 439 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:22
2020-09-16 14:22 | 44090.5989 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 27 | 36.2 | 370 | 25.8 | 36.2 | 391 |  | 2020-09-16 14:22 | 44090.5989 | 25.8 | 36.2 | 391 |  | caution | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:22
2020-09-16 14:23 | 44090.599 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 24.6 | 45.6 | 561 |  | 2020-09-16 14:23 | 44090.599 | 24.6 | 45.6 | 561 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:22
2020-09-16 14:23 | 44090.5991 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 3 | 30 | 35 | 386 | 22 | 53 | 533 |  | 2020-09-16 14:23 | 44090.5991 | 22 | 53 | 533 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:22
2020-09-16 14:24 | 44090.5998 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 24.3 | 44.3 | 697 |  | 2020-09-16 14:24 | 44090.5998 | 24.3 | 44.3 | 697 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:23
2020-09-16 14:24 | 44090.5999 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 30 | 35 | 386 | 22 | 45 | 432 |  | 2020-09-16 14:24 | 44090.5999 | 22 | 45 | 432 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:23
2020-09-16 14:24 | 44090.6001 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 27 | 36.2 | 370 | 25.1 | 37.8 | 389 |  | 2020-09-16 14:24 | 44090.6001 | 25.1 | 37.8 | 389 |  | caution | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:24
2020-09-16 14:24 | 44090.6002 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 23 | 50 | 398 |  | 2020-09-16 14:24 | 44090.6002 | 23 | 50 | 398 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:24
2020-09-16 14:25 | 44090.6005 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 2 | 23.1 | 56.7 | 393 | 23.8 | 45.5 | 656 |  | 2020-09-16 14:25 | 44090.6005 | 23.8 | 45.5 | 656 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:24
2020-09-16 14:25 | 44090.6009 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 30 | 35 | 386 | 22 | 46 | 433 |  | 2020-09-16 14:25 | 44090.6009 | 22 | 46 | 433 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:25
2020-09-16 14:25 | 44090.601 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 22.3 | 44.5 | 452 | 20.9 | 52.5 | 586 |  | 2020-09-16 14:25 | 44090.601 | 20.9 | 52.5 | 586 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:25
2020-09-16 14:26 | 44090.6012 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 23.8 | 47.9 | 651 |  | 2020-09-16 14:26 | 44090.6012 | 23.8 | 47.9 | 651 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:25
2020-09-16 14:26 | 44090.6012 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 23 | 49.2 | 411 | No | 2020-09-16 14:26 | 44090.6012 | 23 | 49.2 | 411 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:25
2020-09-16 14:26 | 44090.6012 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42.5 | 376 |  | 2020-09-16 14:26 | 44090.6012 | 23 | 42.5 | 376 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:25
2020-09-16 14:26 | 44090.6013 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 27 | 36.2 | 370 | 24.1 | 39 | 385 |  | 2020-09-16 14:26 | 44090.6013 | 24.1 | 39 | 385 |  | caution | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:25
2020-09-16 14:26 | 44090.6016 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 23 | 50 | 420 |  | 2020-09-16 14:26 | 44090.6016 | 23 | 50 | 420 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:26
2020-09-16 14:27 | 44090.6018 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42.5 | 376 |  | 2020-09-16 14:27 | 44090.6018 | 23 | 42.5 | 376 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:26
2020-09-16 14:27 | 44090.602 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 24 | 49.6 | 526 |  | 2020-09-16 14:27 | 44090.602 | 24 | 49.6 | 526 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:26
2020-09-16 14:27 | 44090.6021 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 30 | 35 | 386 | 22 | 47 | 452 |  | 2020-09-16 14:27 | 44090.6021 | 22 | 47 | 452 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:26
2020-09-16 14:27 | 44090.6022 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 2 | 24.4 | 51.6 | 401 | 23.5 | 49.9 | 511 |  | 2020-09-16 14:27 | 44090.6022 | 23.5 | 49.9 | 511 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:27
2020-09-16 14:27 | 44090.6023 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 23.1 | 47.2 | 410 | Np | 2020-09-16 14:27 | 44090.6023 | 23.1 | 47.2 | 410 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:27
2020-09-16 14:28 | 44090.6026 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 23 | 50 | 395 |  | 2020-09-16 14:28 | 44090.6026 | 23 | 50 | 395 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:27
2020-09-16 14:28 | 44090.6026 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 24.1 | 49.4 | 430 |  | 2020-09-16 14:28 | 44090.6026 | 24.1 | 49.4 | 430 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:27
2020-09-16 14:28 | 44090.6027 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 22.5 | 44.5 | 452 | 20.3 | 53.9 | 613 |  | 2020-09-16 14:28 | 44090.6027 | 20.3 | 53.9 | 613 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:27
2020-09-16 14:28 | 44090.6028 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 27 | 36.2 | 370 | 23.5 | 40.5 | 380 |  | 2020-09-16 14:28 | 44090.6028 | 23.5 | 40.5 | 380 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:27
2020-09-16 14:28 | 44090.6028 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42.8 | 372 |  | 2020-09-16 14:28 | 44090.6028 | 23 | 42.8 | 372 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:28
2020-09-16 14:28 | 44090.6029 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 30 | 35 | 386 | 22 | 50 | 488 |  | 2020-09-16 14:28 | 44090.6029 | 22 | 50 | 488 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:28
2020-09-16 14:29 | 44090.6033 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23.1 | 42.8 | 383 |  | 2020-09-16 14:29 | 44090.6033 | 23.1 | 42.8 | 383 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:28
2020-09-16 14:29 | 44090.6033 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 24 | 52.2 | 435 |  | 2020-09-16 14:29 | 44090.6033 | 24 | 52.2 | 435 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:28
2020-09-16 14:29 | 44090.6037 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 30 | 35 | 386 |  |  |  | Occupied, no access | 2020-09-16 14:29 | 44090.6037 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:29
2020-09-16 14:30 | 44090.604 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 43 | 388 |  | 2020-09-16 14:30 | 44090.604 | 23 | 43 | 388 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:29
2020-09-16 14:30 | 44090.604 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 23.9 | 50.4 | 432 |  | 2020-09-16 14:30 | 44090.604 | 23.9 | 50.4 | 432 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:29
2020-09-16 14:30 | 44090.6041 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 27 | 36.2 | 370 | 23.1 | 42.2 | 380 |  | 2020-09-16 14:30 | 44090.6041 | 23.1 | 42.2 | 380 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:29
2020-09-16 14:30 | 44090.6042 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 23 | 49 | 404 |  | 2020-09-16 14:30 | 44090.6042 | 23 | 49 | 404 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:30
2020-09-16 14:31 | 44090.6046 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 30 | 35 | 386 | 22 | 44 | 436 |  | 2020-09-16 14:31 | 44090.6046 | 22 | 44 | 436 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:30
2020-09-16 14:31 | 44090.6047 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.6 | 53 | 449 | 24 | 50.9 | 458 |  | 2020-09-16 14:31 | 44090.6047 | 24 | 50.9 | 458 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:30
2020-09-16 14:31 | 44090.605 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 2 | 28 | 38 | 372 | 23.3 | 48.4 | 433 | No | 2020-09-16 14:31 | 44090.605 | 23.3 | 48.4 | 433 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:31
2020-09-16 14:32 | 44090.6053 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 27 | 36.2 | 370 | 23.1 | 42.7 | 382 |  | 2020-09-16 14:32 | 44090.6053 | 23.1 | 42.7 | 382 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:31
2020-09-16 14:32 | 44090.6053 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 23 | 49 | 399 |  | 2020-09-16 14:32 | 44090.6053 | 23 | 49 | 399 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:31
2020-09-16 14:32 | 44090.6054 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 2 | 23.1 | 56.7 | 393 | 23.5 | 49.1 | 622 |  | 2020-09-16 14:32 | 44090.6054 | 23.5 | 49.1 | 622 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:31
2020-09-16 14:32 | 44090.6054 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 30 | 35 | 386 | 22 | 49 | 487 |  | 2020-09-16 14:32 | 44090.6054 | 22 | 49 | 487 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:31
2020-09-16 14:32 | 44090.6055 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.6 | 52.6 | 493 |  | 2020-09-16 14:32 | 44090.6055 | 23.6 | 52.6 | 493 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 14:31
2020-09-16 14:32 | 44090.6057 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 7 | 24.4 | 51.6 | 401 | 23.5 | 50.1 | 919 |  | 2020-09-16 14:32 | 44090.6057 | 23.5 | 50.1 | 919 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:32
2020-09-16 14:32 | 44090.6059 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 22.3 | 44.5 | 452 | 19.9 | 55.1 | 610 |  | 2020-09-16 14:32 | 44090.6059 | 19.9 | 55.1 | 610 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:32
2020-09-16 14:33 | 44090.606 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 23.6 | 46.6 | 435 | No | 2020-09-16 14:33 | 44090.606 | 23.6 | 46.6 | 435 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:32
2020-09-16 14:33 | 44090.606 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 30 | 35 | 386 |  |  |  | Occupied, no access | 2020-09-16 14:33 | 44090.606 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:32
2020-09-16 14:33 | 44090.606 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 23.6 | 48.9 | 567 |  | 2020-09-16 14:33 | 44090.606 | 23.6 | 48.9 | 567 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:32
2020-09-16 14:33 | 44090.6063 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 27 | 36.2 | 370 | 23.1 | 43.4 | 394 |  | 2020-09-16 14:33 | 44090.6063 | 23.1 | 43.4 | 394 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:33
2020-09-16 14:33 | 44090.6066 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton |  |  | 0 | 23 | 48 | 362 | 23 | 49 | 396 |  | 2020-09-16 14:33 | 44090.6066 | 23 | 49 | 396 |  |  | 2020-09-14 | B20603¦¦¦Sep-16-2020 14:33
2020-09-16 14:34 | 44090.6067 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 23.1 | 50.2 | 525 |  | 2020-09-16 14:34 | 44090.6067 | 23.1 | 50.2 | 525 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:33
2020-09-16 14:34 | 44090.607 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 30 | 35 | 386 |  |  |  | Occupied, no access | 2020-09-16 14:34 | 44090.607 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:34
2020-09-16 14:34 | 44090.607 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 3 | 24.4 | 51.6 | 401 | 22.2 | 51.2 | 514 |  | 2020-09-16 14:34 | 44090.607 | 22.2 | 51.2 | 514 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:34
2020-09-16 14:34 | 44090.6073 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 1 | 28 | 38 | 372 | 23 | 49.6 | 422 | No | 2020-09-16 14:34 | 44090.6073 | 23 | 49.6 | 422 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:34
2020-09-16 14:35 | 44090.6077 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 23.2 | 50.8 | 493 |  | 2020-09-16 14:35 | 44090.6077 | 23.2 | 50.8 | 493 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:35
2020-09-16 14:35 | 44090.6077 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 30 | 35 | 386 | 23 | 43 | 470 |  | 2020-09-16 14:35 | 44090.6077 | 23 | 43 | 470 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:35
2020-09-16 14:35 | 44090.608 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 27 | 36.2 | 370 | 22.7 | 42.7 | 392 |  | 2020-09-16 14:35 | 44090.608 | 22.7 | 42.7 | 392 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:35
2020-09-16 14:36 | 44090.608 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 22.3 | 44.5 | 452 | 19.8 | 56.1 | 622 |  | 2020-09-16 14:36 | 44090.608 | 19.8 | 56.1 | 622 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:35
2020-09-16 14:36 | 44090.6081 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 2 | 24.4 | 51.6 | 401 | 22.3 | 54.2 | 512 |  | 2020-09-16 14:36 | 44090.6081 | 22.3 | 54.2 | 512 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:35
2020-09-16 14:36 | 44090.6084 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 23.5 | 50.4 | 487 |  | 2020-09-16 14:36 | 44090.6084 | 23.5 | 50.4 | 487 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:36
2020-09-16 14:36 | 44090.6085 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 30 | 35 | 386 | 23 | 50 | 493 |  | 2020-09-16 14:36 | 44090.6085 | 23 | 50 | 493 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:36
2020-09-16 14:37 | 44090.609 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 24.4 | 50.5 | 527 | 22.3 | 50.4 | 546 |  | 2020-09-16 14:37 | 44090.609 | 22.3 | 50.4 | 546 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:36
2020-09-16 14:37 | 44090.6092 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 30 | 35 | 386 | 23 | 49 | 480 |  | 2020-09-16 14:37 | 44090.6092 | 23 | 49 | 480 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:37
2020-09-16 14:37 | 44090.6092 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 2 | 23.3 | 51.9 | 401 | 21.5 | 60.8 | 529 |  | 2020-09-16 14:37 | 44090.6092 | 21.5 | 60.8 | 529 |  | caution | 2020-09-14 | B17477¦¦¦Sep-16-2020 14:37
2020-09-16 14:37 | 44090.6093 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 22.5 | 50.9 | 393 | No | 2020-09-16 14:37 | 44090.6093 | 22.5 | 50.9 | 393 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:37
2020-09-16 14:37 | 44090.6093 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 23.3 | 50.8 | 477 |  | 2020-09-16 14:37 | 44090.6093 | 23.3 | 50.8 | 477 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:37
2020-09-16 14:38 | 44090.6096 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 27 | 36.2 | 370 | 22.6 | 43.5 | 393 |  | 2020-09-16 14:38 | 44090.6096 | 22.6 | 43.5 | 393 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:37
2020-09-16 14:38 | 44090.6096 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 22.1 | 51.2 | 563 |  | 2020-09-16 14:38 | 44090.6096 | 22.1 | 51.2 | 563 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:37
2020-09-16 14:38 | 44090.6101 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 23.7 | 52.1 | 470 |  | 2020-09-16 14:38 | 44090.6101 | 23.7 | 52.1 | 470 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:38
2020-09-16 14:39 | 44090.6101 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 30 | 35 | 386 |  |  |  | Occupied, no access | 2020-09-16 14:39 | 44090.6101 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:38
2020-09-16 14:39 | 44090.6106 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 22.3 | 57.1 | 446 |  | 2020-09-16 14:39 | 44090.6106 | 22.3 | 57.1 | 446 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 14:39
2020-09-16 14:40 | 44090.6108 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 30 | 35 | 386 |  |  |  | Occupied, no access | 2020-09-16 14:40 | 44090.6108 | [5 empty] | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:39
2020-09-16 14:40 | 44090.6111 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 22 | 50.6 | 446 | No | 2020-09-16 14:40 | 44090.6111 | 22 | 50.6 | 446 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:39
2020-09-16 14:40 | 44090.6111 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 23.5 | 50.2 | 492 |  | 2020-09-16 14:40 | 44090.6111 | 23.5 | 50.2 | 492 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:40
2020-09-16 14:40 | 44090.6112 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 22.3 | 44.5 | 452 | 19.7 | 55.5 | 477 |  | 2020-09-16 14:40 | 44090.6112 | 19.7 | 55.5 | 477 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:40
2020-09-16 14:41 | 44090.6115 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 0 | 30 | 35 | 386 | 24 | 48 | 517 |  | 2020-09-16 14:41 | 44090.6115 | 24 | 48 | 517 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:40
2020-09-16 14:41 | 44090.6117 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 22.6 | 56.3 | 443 |  | 2020-09-16 14:41 | 44090.6117 | 22.6 | 56.3 | 443 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 14:40
2020-09-16 14:41 | 44090.6119 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 23.5 | 50.1 | 481 |  | 2020-09-16 14:41 | 44090.6119 | 23.5 | 50.1 | 481 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:41
2020-09-16 14:42 | 44090.6122 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough |  |  | 1 | 30 | 35 | 386 | 24 | 49 | 561 |  | 2020-09-16 14:42 | 44090.6122 | 24 | 49 | 561 |  |  | 2020-09-14 | B70235¦¦¦Sep-16-2020 14:41
2020-09-16 14:42 | 44090.6123 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 12 | 24.4 | 51.6 | 401 | 21.8 | 46.8 | 687 |  | 2020-09-16 14:42 | 44090.6123 | 21.8 | 46.8 | 687 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:41
2020-09-16 14:42 | 44090.6125 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 27 | 36.2 | 370 | 23.2 | 43.2 | 392 |  | 2020-09-16 14:42 | 44090.6125 | 23.2 | 43.2 | 392 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:41
2020-09-16 14:42 | 44090.6126 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 4 | 25 | 60 | 390 | 24 | 53 | 436 |  | 2020-09-16 14:42 | 44090.6126 | 24 | 53 | 436 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:42
2020-09-16 14:43 | 44090.6132 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23 | 55 | 435 |  | 2020-09-16 14:43 | 44090.6132 | 23 | 55 | 435 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 14:42
2020-09-16 14:43 | 44090.6134 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 55.7 | 393 | 22.6 | 52.7 | 530 |  | 2020-09-16 14:43 | 44090.6134 | 22.6 | 52.7 | 530 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:43
2020-09-16 14:43 | 44090.6134 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 27 | 36.2 | 370 | 23.4 | 42.5 | 392 |  | 2020-09-16 14:43 | 44090.6134 | 23.4 | 42.5 | 392 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:43
2020-09-16 14:43 | 44090.6134 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 20.6 | 49.7 | 406 | No | 2020-09-16 14:43 | 44090.6134 | 20.6 | 49.7 | 406 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:43
2020-09-16 14:43 | 44090.6135 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 2 | 23 | 51.1 | 431 | 22.6 | 49.6 | 518 |  | 2020-09-16 14:43 | 44090.6135 | 22.6 | 49.6 | 518 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 14:43
2020-09-16 14:43 | 44090.6135 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 372 |  | 2020-09-16 14:43 | 44090.6135 | 23 | 42 | 372 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:43
2020-09-16 14:44 | 44090.6141 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 22.7 | 52.6 | 551 |  | 2020-09-16 14:44 | 44090.6141 | 22.7 | 52.6 | 551 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:44
2020-09-16 14:44 | 44090.6141 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 23.3 | 52.6 | 480 |  | 2020-09-16 14:44 | 44090.6141 | 23.3 | 52.6 | 480 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:44
2020-09-16 14:44 | 44090.6142 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23 | 55.1 | 440 |  | 2020-09-16 14:44 | 44090.6142 | 23 | 55.1 | 440 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 14:44
2020-09-16 14:44 | 44090.6142 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 25 | 35 | 353 | 23 | 42 | 366 |  | 2020-09-16 14:44 | 44090.6142 | 23 | 42 | 366 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:44
2020-09-16 14:45 | 44090.6146 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 4 | 23 | 51.1 | 431 | 22.6 | 51.7 | 522 |  | 2020-09-16 14:45 | 44090.6146 | 22.6 | 51.7 | 522 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 14:44
2020-09-16 14:45 | 44090.6148 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 27 | 36.2 | 370 | 23.2 | 41 | 423 |  | 2020-09-16 14:45 | 44090.6148 | 23.2 | 41 | 423 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:45
2020-09-16 14:45 | 44090.6148 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 23.1 | 53.5 | 426 |  | 2020-09-16 14:45 | 44090.6148 | 23.1 | 53.5 | 426 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:45
2020-09-16 14:45 | 44090.6149 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 19.7 | 58.2 | 408 | No | 2020-09-16 14:45 | 44090.6149 | 19.7 | 58.2 | 408 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:45
2020-09-16 14:45 | 44090.6149 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 371 |  | 2020-09-16 14:45 | 44090.6149 | 23 | 42 | 371 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:45
2020-09-16 14:45 | 44090.6149 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 26.3 | 38.1 | 537 |  | 2020-09-16 14:45 | 44090.6149 | 26.3 | 38.1 | 537 | caution | caution | 2020-09-14 | B25039¦¦¦Sep-16-2020 14:45
2020-09-16 14:46 | 44090.6151 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 22.5 | 44.5 | 477 | 19.6 | 55.8 | 486 |  | 2020-09-16 14:46 | 44090.6151 | 19.6 | 55.8 | 486 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:45
2020-09-16 14:46 | 44090.6154 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 382 |  | 2020-09-16 14:46 | 44090.6154 | 23 | 42 | 382 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:46
2020-09-16 14:46 | 44090.6154 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 2 | 24.4 | 51.6 | 401 | 22.6 | 55.6 | 493 |  | 2020-09-16 14:46 | 44090.6154 | 22.6 | 55.6 | 493 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:46
2020-09-16 14:46 | 44090.6154 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 4 | 25 | 60 | 390 | 23 | 54 | 465 |  | 2020-09-16 14:46 | 44090.6154 | 23 | 54 | 465 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:46
2020-09-16 14:47 | 44090.6158 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 23 | 56.2 | 408 |  | 2020-09-16 14:47 | 44090.6158 | 23 | 56.2 | 408 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:46
2020-09-16 14:47 | 44090.6158 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 4 | 23 | 51.1 | 431 | 22.7 | 51.4 | 557 |  | 2020-09-16 14:47 | 44090.6158 | 22.7 | 51.4 | 557 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 14:46
2020-09-16 14:47 | 44090.6158 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 27 | 36.2 | 370 | 23.1 | 43.2 | 436 |  | 2020-09-16 14:47 | 44090.6158 | 23.1 | 43.2 | 436 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:46
2020-09-16 14:47 | 44090.6159 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.6 | 53 | 427 |  | 2020-09-16 14:47 | 44090.6159 | 23.6 | 53 | 427 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 14:46
2020-09-16 14:47 | 44090.616 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 387 |  | 2020-09-16 14:47 | 44090.616 | 23 | 42 | 387 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:47
2020-09-16 14:47 | 44090.6161 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 22.3 | 46.9 | 571 |  | 2020-09-16 14:47 | 44090.6161 | 22.3 | 46.9 | 571 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 14:47
2020-09-16 14:47 | 44090.6161 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 4 | 28 | 38 | 372 | 21 | 55.4 | 415 | No | 2020-09-16 14:47 | 44090.6161 | 21 | 55.4 | 415 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:47
2020-09-16 14:47 | 44090.6162 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 5 | 25 | 60 | 390 | 22 | 53 | 525 |  | 2020-09-16 14:47 | 44090.6162 | 22 | 53 | 525 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:47
2020-09-16 14:48 | 44090.6165 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 22.6 | 53.6 | 477 |  | 2020-09-16 14:48 | 44090.6165 | 22.6 | 53.6 | 477 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:47
2020-09-16 14:48 | 44090.6165 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 22.7 | 58 | 412 |  | 2020-09-16 14:48 | 44090.6165 | 22.7 | 58 | 412 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:47
2020-09-16 14:48 | 44090.6167 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 2 | 25 | 60 | 390 | 22 | 55 | 460 |  | 2020-09-16 14:48 | 44090.6167 | 22 | 55 | 460 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:48
2020-09-16 14:48 | 44090.6169 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 4 | 23 | 51.1 | 431 | 22.5 | 51.5 | 529 |  | 2020-09-16 14:48 | 44090.6169 | 22.5 | 51.5 | 529 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 14:48
2020-09-16 14:49 | 44090.617 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 22.6 | 45.9 | 571 |  | 2020-09-16 14:49 | 44090.617 | 22.6 | 45.9 | 571 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 14:48
2020-09-16 14:49 | 44090.6171 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 22.3 | 44.5 | 452 | 19.5 | 56.5 | 498 |  | 2020-09-16 14:49 | 44090.6171 | 19.5 | 56.5 | 498 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:48
2020-09-16 14:49 | 44090.6171 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 22.4 | 55.1 | 476 |  | 2020-09-16 14:49 | 44090.6171 | 22.4 | 55.1 | 476 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:48
2020-09-16 14:49 | 44090.6172 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 2 | 27 | 36.2 | 370 | 23.1 | 43.6 | 405 |  | 2020-09-16 14:49 | 44090.6172 | 23.1 | 43.6 | 405 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:48
2020-09-16 14:49 | 44090.6173 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 21.7 | 53.1 | 413 | No | 2020-09-16 14:49 | 44090.6173 | 21.7 | 53.1 | 413 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:48
2020-09-16 14:49 | 44090.6175 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 22.1 | 56.4 | 430 |  | 2020-09-16 14:49 | 44090.6175 | 22.1 | 56.4 | 430 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 14:49
2020-09-16 14:49 | 44090.6175 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 22.9 | 57.3 | 407 |  | 2020-09-16 14:49 | 44090.6175 | 22.9 | 57.3 | 407 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:49
2020-09-16 14:49 | 44090.6175 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 3 | 23 | 51.1 | 431 | 22.6 | 50.6 | 518 |  | 2020-09-16 14:49 | 44090.6175 | 22.6 | 50.6 | 518 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 14:49
2020-09-16 14:49 | 44090.6176 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 3 | 25 | 60 | 390 | 21 | 56 | 420 |  | 2020-09-16 14:49 | 44090.6176 | 21 | 56 | 420 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:49
2020-09-16 14:50 | 44090.6178 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 22.3 | 55.5 | 475 |  | 2020-09-16 14:50 | 44090.6178 | 22.3 | 55.5 | 475 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:49
2020-09-16 14:50 | 44090.6181 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23.5 | 41.3 | 377 |  | 2020-09-16 14:50 | 44090.6181 | 23.5 | 41.3 | 377 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:50
2020-09-16 14:50 | 44090.6182 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 4 | 25 | 60 | 390 | 21 | 56 | 422 |  | 2020-09-16 14:50 | 44090.6182 | 21 | 56 | 422 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:50
2020-09-16 14:50 | 44090.6182 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 22 | 48.3 | 572 |  | 2020-09-16 14:50 | 44090.6182 | 22 | 48.3 | 572 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 14:50
2020-09-16 14:50 | 44090.6183 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga |  |  | 0 | 23.1 | 56.7 | 393 | 22.7 | 57.8 | 402 |  | 2020-09-16 14:50 | 44090.6183 | 22.7 | 57.8 | 402 |  |  | 2020-09-14 | B10577¦¦¦Sep-16-2020 14:50
2020-09-16 14:50 | 44090.6184 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 0 | 23 | 51.1 | 431 | 22.4 | 51.4 | 452 |  | 2020-09-16 14:50 | 44090.6184 | 22.4 | 51.4 | 452 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 14:50
2020-09-16 14:51 | 44090.6186 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 22.2 | 52.6 | 430 | No | 2020-09-16 14:51 | 44090.6186 | 22.2 | 52.6 | 430 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:50
2020-09-16 14:51 | 44090.6187 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 2 | 25 | 60 | 390 | 21 | 62 | 424 |  | 2020-09-16 14:51 | 44090.6187 | 21 | 62 | 424 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:50
2020-09-16 14:51 | 44090.6188 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 22.6 | 54.1 | 487 |  | 2020-09-16 14:51 | 44090.6188 | 22.6 | 54.1 | 487 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:51
2020-09-16 14:51 | 44090.6191 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 0 | 23 | 51.1 | 431 | 22.4 | 52.3 | 489 |  | 2020-09-16 14:51 | 44090.6191 | 22.4 | 52.3 | 489 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 14:51
2020-09-16 14:52 | 44090.6192 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.6 | 50 | 572 |  | 2020-09-16 14:52 | 44090.6192 | 21.6 | 50 | 572 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 14:51
2020-09-16 14:52 | 44090.6193 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 2 | 25 | 60 | 390 | 21 | 64 | 429 |  | 2020-09-16 14:52 | 44090.6193 | 21 | 64 | 429 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:51
2020-09-16 14:52 | 44090.6196 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 22.3 | 50.4 | 425 | No | 2020-09-16 14:52 | 44090.6196 | 22.3 | 50.4 | 425 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:52
2020-09-16 14:53 | 44090.6198 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 22.6 | 55.3 | 483 |  | 2020-09-16 14:53 | 44090.6198 | 22.6 | 55.3 | 483 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:52
2020-09-16 14:53 | 44090.6199 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 51 | 605 |  | 2020-09-16 14:53 | 44090.6199 | 23 | 51 | 605 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 14:52
2020-09-16 14:53 | 44090.6199 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 21 | 62 | 423 |  | 2020-09-16 14:53 | 44090.6199 | 21 | 62 | 423 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:52
2020-09-16 14:53 | 44090.6199 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.7 | 52 | 449 |  | 2020-09-16 14:53 | 44090.6199 | 23.7 | 52 | 449 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 14:52
2020-09-16 14:53 | 44090.62 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 0 | 23 | 51.1 | 443 | 22.4 | 52 | 442 |  | 2020-09-16 14:53 | 44090.62 | 22.4 | 52 | 442 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 14:52
2020-09-16 14:53 | 44090.6202 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 22.3 | 44.5 | 452 | 19.8 | 55.9 | 537 |  | 2020-09-16 14:53 | 44090.6202 | 19.8 | 55.9 | 537 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:53
2020-09-16 14:53 | 44090.6203 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 22 | 63 | 397 |  | 2020-09-16 14:53 | 44090.6203 | 22 | 63 | 397 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:53
2020-09-16 14:54 | 44090.6205 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 600 |  | 2020-09-16 14:54 | 44090.6205 | 23 | 50 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 14:53
2020-09-16 14:54 | 44090.6207 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 22 | 64 | 421 |  | 2020-09-16 14:54 | 44090.6207 | 22 | 64 | 421 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:53
2020-09-16 14:54 | 44090.6208 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.3 | 51 | 570 |  | 2020-09-16 14:54 | 44090.6208 | 21.3 | 51 | 570 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 14:53
2020-09-16 14:54 | 44090.6209 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee |  |  | 0 | 23 | 51.1 | 431 | 22.5 | 51.4 | 466 |  | 2020-09-16 14:54 | 44090.6209 | 22.5 | 51.4 | 466 |  |  | 2020-09-14 | B25477¦¦¦Sep-16-2020 14:54
2020-09-16 14:54 | 44090.6211 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 22 | 64 | 434 |  | 2020-09-16 14:54 | 44090.6211 | 22 | 64 | 434 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:54
2020-09-16 14:55 | 44090.6215 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 24 | 51.8 | 449 |  | 2020-09-16 14:55 | 44090.6215 | 24 | 51.8 | 449 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 14:54
2020-09-16 14:55 | 44090.6216 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 27 | 36.2 | 370 | 23.4 | 43.6 | 423 |  | 2020-09-16 14:55 | 44090.6216 | 23.4 | 43.6 | 423 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:55
2020-09-16 14:55 | 44090.6216 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 23 | 61 | 407 |  | 2020-09-16 14:55 | 44090.6216 | 23 | 61 | 407 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:55
2020-09-16 14:55 | 44090.6217 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 1 | 23 | 50 | 450 | 24 | 51 | 610 |  | 2020-09-16 14:55 | 44090.6217 | 24 | 51 | 610 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 14:55
2020-09-16 14:56 | 44090.622 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 23 | 61 | 398 |  | 2020-09-16 14:56 | 44090.622 | 23 | 61 | 398 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:55
2020-09-16 14:56 | 44090.622 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 22.3 | 56.7 | 502 |  | 2020-09-16 14:56 | 44090.622 | 22.3 | 56.7 | 502 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:55
2020-09-16 14:56 | 44090.6221 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.2 | 51.2 | 558 |  | 2020-09-16 14:56 | 44090.6221 | 21.2 | 51.2 | 558 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 14:55
2020-09-16 14:56 | 44090.6224 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 22.3 | 44.5 | 452 | 19.7 | 56.4 | 592 |  | 2020-09-16 14:56 | 44090.6224 | 19.7 | 56.4 | 592 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:56
2020-09-16 14:56 | 44090.6224 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 24 | 52.2 | 449 |  | 2020-09-16 14:56 | 44090.6224 | 24 | 52.2 | 449 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 14:56
2020-09-16 14:56 | 44090.6225 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 23 | 59 | 395 |  | 2020-09-16 14:56 | 44090.6225 | 23 | 59 | 395 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:56
2020-09-16 14:56 | 44090.6225 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 1 | 23 | 50 | 450 | 24 | 48 | 615 |  | 2020-09-16 14:56 | 44090.6225 | 24 | 48 | 615 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 14:56
2020-09-16 14:57 | 44090.6227 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 22.3 | 55.9 | 489 |  | 2020-09-16 14:57 | 44090.6227 | 22.3 | 55.9 | 489 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:56
2020-09-16 14:57 | 44090.6228 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 40.7 | 370 |  | 2020-09-16 14:57 | 44090.6228 | 23 | 40.7 | 370 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:56
2020-09-16 14:57 | 44090.6229 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 22.3 | 44.5 | 452 | 19.8 | 57.7 | 601 |  | 2020-09-16 14:57 | 44090.6229 | 19.8 | 57.7 | 601 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:56
2020-09-16 14:57 | 44090.623 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 23 | 60 | 395 |  | 2020-09-16 14:57 | 44090.623 | 23 | 60 | 395 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 14:57
2020-09-16 14:57 | 44090.6232 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 22.5 | 51 | 464 | No | 2020-09-16 14:57 | 44090.6232 | 22.5 | 51 | 464 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:57
2020-09-16 14:58 | 44090.6233 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.2 | 51.4 | 569 |  | 2020-09-16 14:58 | 44090.6233 | 21.2 | 51.4 | 569 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 14:57
2020-09-16 14:58 | 44090.6234 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 27 | 36.2 | 370 | 23.5 | 43 | 420 |  | 2020-09-16 14:58 | 44090.6234 | 23.5 | 43 | 420 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:57
2020-09-16 14:58 | 44090.6234 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 1 | 23 | 50 | 450 | 25 | 49 | 620 |  | 2020-09-16 14:58 | 44090.6234 | 25 | 49 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 14:57
2020-09-16 14:58 | 44090.6235 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23.5 | 41 | 376 |  | 2020-09-16 14:58 | 44090.6235 | 23.5 | 41 | 376 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:57
2020-09-16 14:58 | 44090.6239 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.4 | 51.7 | 444 |  | 2020-09-16 14:58 | 44090.6239 | 23.4 | 51.7 | 444 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 14:58
2020-09-16 14:58 | 44090.6239 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23.4 | 41 | 37.6 |  | 2020-09-16 14:58 | 44090.6239 | 23.4 | 41 | 37.6 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 14:58
2020-09-16 14:59 | 44090.624 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 22.3 | 56.4 | 495 |  | 2020-09-16 14:59 | 44090.624 | 22.3 | 56.4 | 495 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:58
2020-09-16 14:59 | 44090.624 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 2 | 22.3 | 44.5 | 452 | 19.8 | 55.7 | 498 |  | 2020-09-16 14:59 | 44090.624 | 19.8 | 55.7 | 498 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:58
2020-09-16 14:59 | 44090.6242 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 378 | 22.8 | 50.6 | 494 | No | 2020-09-16 14:59 | 44090.6242 | 22.8 | 50.6 | 494 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 14:58
2020-09-16 14:59 | 44090.6243 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 24 | 48 | 600 |  | 2020-09-16 14:59 | 44090.6243 | 24 | 48 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 14:58
2020-09-16 14:59 | 44090.6244 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 5 | 22.3 | 44.5 | 452 | 20.2 | 54.9 | 494 |  | 2020-09-16 14:59 | 44090.6244 | 20.2 | 54.9 | 494 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 14:59
2020-09-16 14:59 | 44090.6245 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 27 | 36.2 | 370 | 23.6 | 42.6 | 432 |  | 2020-09-16 14:59 | 44090.6245 | 23.6 | 42.6 | 432 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 14:59
2020-09-16 14:59 | 44090.6246 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.1 | 51.8 | 567 |  | 2020-09-16 14:59 | 44090.6246 | 21.1 | 51.8 | 567 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 14:59
2020-09-16 15:00 | 44090.6249 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 22.5 | 53.9 | 544 |  | 2020-09-16 15:00 | 44090.6249 | 22.5 | 53.9 | 544 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 14:59
2020-09-16 15:01 | 44090.6254 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 23 | 49.6 | 410 | No | 2020-09-16 15:01 | 44090.6254 | 23 | 49.6 | 410 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 15:00
2020-09-16 15:01 | 44090.6256 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 4 | 22.3 | 44.5 | 452 | 20.5 | 53.5 | 505 |  | 2020-09-16 15:01 | 44090.6256 | 20.5 | 53.5 | 505 |  |  | 2020-09-14 | B20474¦¦¦Sep-16-2020 15:00
2020-09-16 15:01 | 44090.6256 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.1 | 51.1 | 559 |  | 2020-09-16 15:01 | 44090.6256 | 21.1 | 51.1 | 559 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:00
2020-09-16 15:01 | 44090.6257 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 1 | 23.3 | 51.9 | 401 | 23 | 54.3 | 464 |  | 2020-09-16 15:01 | 44090.6257 | 23 | 54.3 | 464 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:01
2020-09-16 15:01 | 44090.6259 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 700 |  | 2020-09-16 15:01 | 44090.6259 | 23 | 50 | 700 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:01
2020-09-16 15:02 | 44090.6262 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 22.2 | 51.9 | 548 |  | 2020-09-16 15:02 | 44090.6262 | 22.2 | 51.9 | 548 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 15:01
2020-09-16 15:02 | 44090.6266 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 27 | 36.2 | 370 | 23.8 | 42.4 | 397 |  | 2020-09-16 15:02 | 44090.6266 | 23.8 | 42.4 | 397 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 15:02
2020-09-16 15:03 | 44090.6269 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 1 | 28 | 38 | 372 | 23.2 | 51.3 | 462 | No | 2020-09-16 15:03 | 44090.6269 | 23.2 | 51.3 | 462 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 15:02
2020-09-16 15:03 | 44090.627 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.3 | 50.4 | 551 |  | 2020-09-16 15:03 | 44090.627 | 21.3 | 50.4 | 551 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:02
2020-09-16 15:03 | 44090.6271 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 22.9 | 54.9 | 491 |  | 2020-09-16 15:03 | 44090.6271 | 22.9 | 54.9 | 491 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:03
2020-09-16 15:03 | 44090.6271 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 24 | 51 | 650 |  | 2020-09-16 15:03 | 44090.6271 | 24 | 51 | 650 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:03
2020-09-16 15:03 | 44090.6273 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 5 | 23.3 | 41.3 | 392 | 24.1 | 42.5 | 490 | No | 2020-09-16 15:03 | 44090.6273 | 24.1 | 42.5 | 490 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 15:03
2020-09-16 15:04 | 44090.6277 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 27 | 36.2 | 370 | 23.8 | 42.4 | 405 |  | 2020-09-16 15:04 | 44090.6277 | 23.8 | 42.4 | 405 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 15:03
2020-09-16 15:04 | 44090.628 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 24 | 48 | 640 |  | 2020-09-16 15:04 | 44090.628 | 24 | 48 | 640 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:04
2020-09-16 15:04 | 44090.6281 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.5 | 50.9 | 552 |  | 2020-09-16 15:05 | 44090.6281 | 21.5 | 50.9 | 552 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:04
2020-09-16 15:05 | 44090.6284 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 1 | 28 | 38 | 372 | 23.8 | 48.9 | 426 | No | 2020-09-16 15:05 | 44090.6284 | 23.8 | 48.9 | 426 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 15:04
2020-09-16 15:05 | 44090.6284 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 1 | 22.4 | 44 | 414 | 22.8 | 49.9 | 594 |  | 2020-09-16 15:05 | 44090.6284 | 22.8 | 49.9 | 594 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 15:04
2020-09-16 15:05 | 44090.6287 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 24.9 | 49.8 | 456 |  | 2020-09-16 15:05 | 44090.6287 | 24.9 | 49.8 | 456 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:05
2020-09-16 15:06 | 44090.6288 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 1 | 23.3 | 41.3 | 392 | 23.4 | 43.5 | 418 | No | 2020-09-16 15:06 | 44090.6288 | 23.4 | 43.5 | 418 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 15:05
2020-09-16 15:06 | 44090.6291 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.5 | 51.6 | 551 |  | 2020-09-16 15:06 | 44090.6291 | 21.5 | 51.6 | 551 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:05
2020-09-16 15:06 | 44090.6292 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 43 | 365 |  | 2020-09-16 15:06 | 44090.6292 | 23 | 43 | 365 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 15:06
2020-09-16 15:06 | 44090.6294 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 23.5 | 48 | 420 | No | 2020-09-16 15:06 | 44090.6294 | 23.5 | 48 | 420 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 15:06
2020-09-16 15:06 | 44090.6294 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.4 | 44 | 414 | 22.9 | 49.7 | 534 |  | 2020-09-16 15:06 | 44090.6294 | 22.9 | 49.7 | 534 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 15:06
2020-09-16 15:07 | 44090.6295 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton |  |  | 5 | 24.4 | 51.6 | 401 | 23.4 | 51.7 | 801 |  | 2020-09-16 15:07 | 44090.6295 | 23.4 | 51.7 | 801 |  |  | 2020-09-14 | B20367¦¦¦Sep-16-2020 15:06
2020-09-16 15:07 | 44090.6295 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 24 | 48 | 630 |  | 2020-09-16 15:07 | 44090.6295 | 24 | 48 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:06
2020-09-16 15:07 | 44090.6298 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 27 | 36.2 | 370 | 23 | 43.1 | 430 |  | 2020-09-16 15:07 | 44090.6298 | 23 | 43.1 | 430 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 15:06
2020-09-16 15:07 | 44090.63 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.4 | 44 | 414 | 23 | 50 | 518 |  | 2020-09-16 15:07 | 44090.63 | 23 | 50 | 518 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 15:07
2020-09-16 15:07 | 44090.63 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.6 | 52.4 | 556 |  | 2020-09-16 15:07 | 44090.63 | 21.6 | 52.4 | 556 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:07
2020-09-16 15:07 | 44090.6302 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 1 | 23.3 | 51.9 | 401 | 24.3 | 51 | 451 |  | 2020-09-16 15:07 | 44090.6302 | 24.3 | 51 | 451 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:07
2020-09-16 15:08 | 44090.6303 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 43 | 367 |  | 2020-09-16 15:08 | 44090.6303 | 23 | 43 | 367 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 15:07
2020-09-16 15:08 | 44090.6304 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 1 | 23.3 | 41.3 | 392 | 23.4 | 43.5 | 418 | No | 2020-09-16 15:08 | 44090.6304 | 23.4 | 43.5 | 418 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 15:07
2020-09-16 15:08 | 44090.6307 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 24 | 48 | 680 |  | 2020-09-16 15:08 | 44090.6307 | 24 | 48 | 680 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:08
2020-09-16 15:09 | 44090.6309 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 23 | 60 | 420 |  | 2020-09-16 15:09 | 44090.6309 | 23 | 60 | 420 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 15:08
2020-09-16 15:09 | 44090.6309 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 22.9 | 49.1 | 420 | No | 2020-09-16 15:09 | 44090.6309 | 22.9 | 49.1 | 420 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 15:08
2020-09-16 15:09 | 44090.631 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 24.5 | 41.5 | 574 |  | 2020-09-16 15:09 | 44090.631 | 24.5 | 41.5 | 574 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:08
2020-09-16 15:09 | 44090.6311 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 1 | 22.4 | 44 | 414 | 23 | 50 | 510 |  | 2020-09-16 15:09 | 44090.6311 | 23 | 50 | 510 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 15:08
2020-09-16 15:09 | 44090.6313 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23.5 | 42 | 367 |  | 2020-09-16 15:09 | 44090.6313 | 23.5 | 42 | 367 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 15:09
2020-09-16 15:09 | 44090.6314 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 24.4 | 43.4 | 504 |  | 2020-09-16 15:09 | 44090.6314 | 24.4 | 43.4 | 504 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 15:09
2020-09-16 15:09 | 44090.6315 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 24 | 47 | 620 |  | 2020-09-16 15:09 | 44090.6315 | 24 | 47 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:09
2020-09-16 15:09 | 44090.6315 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 23 | 56 | 430 |  | 2020-09-16 15:09 | 44090.6315 | 23 | 56 | 430 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 15:09
2020-09-16 15:10 | 44090.6317 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 1 | 23.3 | 41.3 | 392 | 23.1 | 45 | 442 | No | 2020-09-16 15:10 | 44090.6317 | 23.1 | 45 | 442 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 15:09
2020-09-16 15:10 | 44090.6318 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 1 | 22.4 | 44 | 414 | 23 | 49.3 | 497 |  | 2020-09-16 15:10 | 44090.6318 | 23 | 49.3 | 497 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 15:09
2020-09-16 15:10 | 44090.6319 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 23 | 56 | 455 |  | 2020-09-16 15:10 | 44090.6319 | 23 | 56 | 455 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 15:09
2020-09-16 15:10 | 44090.6319 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 43.6 | 370 |  | 2020-09-16 15:10 | 44090.6319 | 23 | 43.6 | 370 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 15:09
2020-09-16 15:10 | 44090.632 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 27 | 36.2 | 370 | 22.8 | 42.3 | 412 |  | 2020-09-16 15:10 | 44090.632 | 22.8 | 42.3 | 412 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 15:10
2020-09-16 15:10 | 44090.6321 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.8 | 51.4 | 586 |  | 2020-09-16 15:10 | 44090.6321 | 21.8 | 51.4 | 586 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:10
2020-09-16 15:10 | 44090.6322 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 22.6 | 47.6 | 542 |  | 2020-09-16 15:10 | 44090.6322 | 22.6 | 47.6 | 542 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 15:10
2020-09-16 15:10 | 44090.6323 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 22 | 53 | 450 |  | 2020-09-16 15:10 | 44090.6323 | 22 | 53 | 450 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 15:10
2020-09-16 15:11 | 44090.6323 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 3 | 28 | 38 | 372 | 22.7 | 50.7 | 447 | No | 2020-09-16 15:10 | 44090.6323 | 22.7 | 50.7 | 447 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 15:10
2020-09-16 15:11 | 44090.6326 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 43 | 380 |  | 2020-09-16 15:11 | 44090.6326 | 23 | 43 | 380 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 15:10
2020-09-16 15:11 | 44090.6326 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 24 | 50 | 650 |  | 2020-09-16 15:11 | 44090.6326 | 24 | 50 | 650 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:11
2020-09-16 15:11 | 44090.6327 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 22 | 55 | 473 |  | 2020-09-16 15:11 | 44090.6327 | 22 | 55 | 473 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 15:11
2020-09-16 15:11 | 44090.6327 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.7 | 51.4 | 462 |  | 2020-09-16 15:11 | 44090.6327 | 23.7 | 51.4 | 462 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:11
2020-09-16 15:12 | 44090.6332 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 22 | 50.2 | 584 |  | 2020-09-16 15:12 | 44090.6332 | 22 | 50.2 | 584 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:11
2020-09-16 15:12 | 44090.6333 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.4 | 44 | 414 | 22.6 | 48.4 | 521 |  | 2020-09-16 15:12 | 44090.6333 | 22.6 | 48.4 | 521 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 15:11
2020-09-16 15:12 | 44090.6335 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 24 | 50 | 730 |  | 2020-09-16 15:12 | 44090.6335 | 24 | 50 | 730 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:12
2020-09-16 15:12 | 44090.6336 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 2 | 23.3 | 41.3 | 392 | 22.9 | 45.6 | 427 | No | 2020-09-16 15:12 | 44090.6336 | 22.9 | 45.6 | 427 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 15:12
2020-09-16 15:12 | 44090.6337 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 22 | 53 | 441 |  | 2020-09-16 15:12 | 44090.6337 | 22 | 53 | 441 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 15:12
2020-09-16 15:13 | 44090.6337 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 27 | 36.2 | 370 | 22.9 | 44.5 | 418 |  | 2020-09-16 15:13 | 44090.6337 | 22.9 | 44.5 | 418 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 15:12
2020-09-16 15:13 | 44090.6341 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 22.8 | 52.1 | 407 | No | 2020-09-16 15:13 | 44090.6341 | 22.8 | 52.1 | 407 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 15:13
2020-09-16 15:13 | 44090.6341 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 22 | 52 | 419 |  | 2020-09-16 15:13 | 44090.6341 | 22 | 52 | 419 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 15:13
2020-09-16 15:13 | 44090.6341 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.8 | 51.2 | 584 |  | 2020-09-16 15:13 | 44090.6341 | 21.8 | 51.2 | 584 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:13
2020-09-16 15:13 | 44090.6343 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.2 | 52.5 | 456 |  | 2020-09-16 15:13 | 44090.6343 | 23.2 | 52.5 | 456 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:13
2020-09-16 15:14 | 44090.6344 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.5 | 44 | 414 | 22.8 | 47.7 | 480 | Courtroom 1 unavailable | 2020-09-16 15:14 | 44090.6344 | 22.8 | 47.7 | 480 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 15:13
2020-09-16 15:14 | 44090.6344 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 21 | 56 | 446 |  | 2020-09-16 15:14 | 44090.6344 | 21 | 56 | 446 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 15:13
2020-09-16 15:14 | 44090.6348 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 24 | 49 | 800 |  | 2020-09-16 15:14 | 44090.6348 | 24 | 49 | 800 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:14
2020-09-16 15:14 | 44090.6348 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 2 | 23.3 | 41.3 | 392 | 23 | 45.8 | 432 | No | 2020-09-16 15:14 | 44090.6348 | 23 | 45.8 | 432 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 15:14
2020-09-16 15:14 | 44090.6349 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 21 | 58 | 446 |  | 2020-09-16 15:14 | 44090.6349 | 21 | 58 | 446 |  |  | 2020-09-14 | B19570¦¦¦Sep-16-2020 15:14
2020-09-16 15:15 | 44090.6351 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.9 | 51.3 | 583 |  | 2020-09-16 15:15 | 44090.6351 | 21.9 | 51.3 | 583 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:14
2020-09-16 15:15 | 44090.6353 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 23.1 | 49.6 | 407 | No | 2020-09-16 15:15 | 44090.6353 | 23.1 | 49.6 | 407 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 15:14
2020-09-16 15:15 | 44090.6353 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 22 | 66 | 436 |  | 2020-09-16 15:15 | 44090.6353 | 22 | 66 | 436 |  | high | 2020-09-14 | B19570¦¦¦Sep-16-2020 15:14
2020-09-16 15:15 | 44090.6355 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 27 | 36.2 | 370 | 23.6 | 44.1 | 446 |  | 2020-09-16 15:15 | 44090.6355 | 23.6 | 44.1 | 446 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 15:15
2020-09-16 15:15 | 44090.6356 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.7 | 51.2 | 438 |  | 2020-09-16 15:15 | 44090.6356 | 23.7 | 51.2 | 438 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:15
2020-09-16 15:15 | 44090.6356 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.4 | 44 | 414 | 22.1 | 49.5 | 550 |  | 2020-09-16 15:15 | 44090.6356 | 22.1 | 49.5 | 550 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 15:15
2020-09-16 15:15 | 44090.6356 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 22 | 51.6 | 801 |  | 2020-09-16 15:15 | 44090.6356 | 22 | 51.6 | 801 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 15:15
2020-09-16 15:16 | 44090.6358 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 24 | 47 | 640 |  | 2020-09-16 15:16 | 44090.6358 | 24 | 47 | 640 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:15
2020-09-16 15:16 | 44090.6358 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 22 | 66 | 486 |  | 2020-09-16 15:16 | 44090.6358 | 22 | 66 | 486 |  | high | 2020-09-14 | B19570¦¦¦Sep-16-2020 15:15
2020-09-16 15:16 | 44090.6362 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 22 | 65 | 431 |  | 2020-09-16 15:16 | 44090.6362 | 22 | 65 | 431 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 15:16
2020-09-16 15:16 | 44090.6362 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.7 | 51.7 | 595 |  | 2020-09-16 15:16 | 44090.6362 | 21.7 | 51.7 | 595 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:16
2020-09-16 15:16 | 44090.6362 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 22 | 52 | 776 |  | 2020-09-16 15:16 | 44090.6362 | 22 | 52 | 776 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 15:16
2020-09-16 15:16 | 44090.6363 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee |  |  | 0 | 22.4 | 44 | 414 | 22.3 | 52.6 | 544 |  | 2020-09-16 15:16 | 44090.6363 | 22.3 | 52.6 | 544 |  |  | 2020-09-14 | B19890¦¦¦Sep-16-2020 15:16
2020-09-16 15:16 | 44090.6363 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 4 | 28 | 38 | 372 | 23.2 | 50.3 | 435 | No | 2020-09-16 15:16 | 44090.6363 | 23.2 | 50.3 | 435 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 15:16
2020-09-16 15:16 | 44090.6363 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 1 | 23.3 | 41.3 | 392 | 23 | 45.9 | 466 | No | 2020-09-16 15:16 | 44090.6363 | 23 | 45.9 | 466 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 15:16
2020-09-16 15:17 | 44090.6365 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 23 | 65 | 410 |  | 2020-09-16 15:16 | 44090.6365 | 23 | 65 | 410 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 15:16
2020-09-16 15:17 | 44090.6365 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 24 | 47 | 640 |  | 2020-09-16 15:17 | 44090.6365 | 24 | 47 | 640 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:16
2020-09-16 15:17 | 44090.6367 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.7 | 51.3 | 487 |  | 2020-09-16 15:17 | 44090.6367 | 23.7 | 51.3 | 487 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:16
2020-09-16 15:17 | 44090.6368 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 23 | 65 | 422 |  | 2020-09-16 15:17 | 44090.6368 | 23 | 65 | 422 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 15:17
2020-09-16 15:17 | 44090.6371 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg |  |  | 1 | 25 | 60 | 390 | 23 | 64 | 413 |  | 2020-09-16 15:18 | 44090.6371 | 23 | 64 | 413 |  | caution | 2020-09-14 | B19570¦¦¦Sep-16-2020 15:17
2020-09-16 15:18 | 44090.6373 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.6 | 53 | 572 |  | 2020-09-16 15:18 | 44090.6373 | 21.6 | 53 | 572 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:17
2020-09-16 15:18 | 44090.6373 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 41 | 392 |  | 2020-09-16 15:18 | 44090.6373 | 23 | 41 | 392 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 15:17
2020-09-16 15:18 | 44090.6375 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 24 | 48 | 620 |  | 2020-09-16 15:18 | 44090.6375 | 24 | 48 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:17
2020-09-16 15:19 | 44090.6379 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia |  |  | 0 | 28 | 38 | 372 | 23.1 | 49.1 | 409 | No | 2020-09-16 15:19 | 44090.6379 | 23.1 | 49.1 | 409 |  |  | 2020-09-14 | B14660¦¦¦Sep-16-2020 15:18
2020-09-16 15:19 | 44090.6379 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 366 |  | 2020-09-16 15:19 | 44090.6379 | 23 | 42 | 366 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 15:18
2020-09-16 15:19 | 44090.6382 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 2 | 24.4 | 51.6 | 401 | 22.2 | 52.1 | 957 |  | 2020-09-16 15:19 | 44090.6382 | 22.2 | 52.1 | 957 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 15:19
2020-09-16 15:19 | 44090.6383 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.6 | 51.1 | 580 |  | 2020-09-16 15:19 | 44090.6383 | 21.6 | 51.1 | 580 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:19
2020-09-16 15:19 | 44090.6384 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 24 | 48 | 600 |  | 2020-09-16 15:19 | 44090.6384 | 24 | 48 | 600 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:19
2020-09-16 15:19 | 44090.6384 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 371 |  | 2020-09-16 15:19 | 44090.6384 | 23 | 42 | 371 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 15:19
2020-09-16 15:19 | 44090.6385 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.6 | 50.7 | 435 |  | 2020-09-16 15:19 | 44090.6385 | 23.6 | 50.7 | 435 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:19
2020-09-16 15:20 | 44090.6386 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 1 | 27 | 36.2 | 370 | 23.7 | 45.2 | 450 |  | 2020-09-16 15:20 | 44090.6386 | 23.7 | 45.2 | 450 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 15:19
2020-09-16 15:20 | 44090.6389 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 1 | 23.3 | 41.3 | 392 | 22.4 | 46 | 423 | No | 2020-09-16 15:20 | 44090.6389 | 22.4 | 46 | 423 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 15:19
2020-09-16 15:20 | 44090.639 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 382 |  | 2020-09-16 15:20 | 44090.639 | 23 | 42 | 382 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 15:20
2020-09-16 15:21 | 44090.6393 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 21.7 | 53.7 | 555 |  | 2020-09-16 15:21 | 44090.6393 | 21.7 | 53.7 | 555 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:20
2020-09-16 15:21 | 44090.6394 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 387 |  | 2020-09-16 15:21 | 44090.6394 | 23 | 42 | 387 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 15:20
2020-09-16 15:21 | 44090.6397 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 22 | 50 | 620 |  | 2020-09-16 15:21 | 44090.6397 | 22 | 50 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:21
2020-09-16 15:21 | 44090.6399 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 1 | 24.4 | 51.6 | 401 | 21.4 | 54.6 | 499 |  | 2020-09-16 15:21 | 44090.6399 | 21.4 | 54.6 | 499 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 15:21
2020-09-16 15:22 | 44090.64 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.6 | 52 | 418 |  | 2020-09-16 15:22 | 44090.64 | 23.6 | 52 | 418 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:21
2020-09-16 15:22 | 44090.6403 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 0 | 24.7 | 47.1 | 411 | 23.7 | 44.6 | 586 |  | 2020-09-16 15:22 | 44090.6403 | 23.7 | 44.6 | 586 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:22
2020-09-16 15:23 | 44090.6407 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 22 | 50 | 620 |  | 2020-09-16 15:23 | 44090.6407 | 22 | 50 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:22
2020-09-16 15:23 | 44090.6409 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 4 | 27 | 36.2 | 370 | 23.5 | 47 | 550 |  | 2020-09-16 15:23 | 44090.6409 | 23.5 | 47 | 550 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 15:22
2020-09-16 15:23 | 44090.6409 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.2 | 43.1 | 416 |  | 2020-09-16 15:23 | 44090.6409 | 23.2 | 43.1 | 416 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:22
2020-09-16 15:23 | 44090.641 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 3 | 23.3 | 41.3 | 392 | 22.6 | 46.2 | 446 | No | 2020-09-16 15:23 | 44090.641 | 22.6 | 46.2 | 446 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 15:23
2020-09-16 15:23 | 44090.6413 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 21.6 | 42 | 518 |  | 2020-09-16 15:23 | 44090.6413 | 21.6 | 42 | 518 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 15:23
2020-09-16 15:24 | 44090.6416 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby |  |  | 4 | 24.7 | 47.1 | 411 | 23.8 | 43.5 | 600 |  | 2020-09-16 15:24 | 44090.6416 | 23.8 | 43.5 | 600 |  |  | 2020-09-14 | B25039¦¦¦Sep-16-2020 15:23
2020-09-16 15:24 | 44090.6417 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 51 | 640 |  | 2020-09-16 15:24 | 44090.6417 | 23 | 51 | 640 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:23
2020-09-16 15:24 | 44090.6419 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 21.7 | 49.1 | 494 |  | 2020-09-16 15:24 | 44090.6419 | 21.7 | 49.1 | 494 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 15:24
2020-09-16 15:25 | 44090.6421 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 1 | 23.3 | 41.3 | 392 | 21.2 | 46.2 | 452 | No | 2020-09-16 15:25 | 44090.6421 | 21.2 | 46.2 | 452 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 15:24
2020-09-16 15:25 | 44090.6422 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie |  |  | 3 | 27 | 36.2 | 370 | 23.2 | 49.2 | 565 |  | 2020-09-16 15:25 | 44090.6422 | 23.2 | 49.2 | 565 |  |  | 2020-09-14 | B70277¦¦¦Sep-16-2020 15:24
2020-09-16 15:25 | 44090.6426 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 5 | 25.8 | 34.7 | 412 | 24.1 | 36.7 | 801 |  | 2020-09-16 15:25 | 44090.6426 | 24.1 | 36.7 | 801 |  | caution | 2020-09-14 | B21554¦¦¦Sep-16-2020 15:25
2020-09-16 15:25 | 44090.6426 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 22.9 | 54.1 | 427 |  | 2020-09-16 15:25 | 44090.6426 | 22.9 | 54.1 | 427 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:25
2020-09-16 15:25 | 44090.6427 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 630 |  | 2020-09-16 15:25 | 44090.6427 | 23 | 50 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:25
2020-09-16 15:25 | 44090.6427 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 21.7 | 49.5 | 481 |  | 2020-09-16 15:25 | 44090.6427 | 21.7 | 49.5 | 481 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 15:25
2020-09-16 15:26 | 44090.6434 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 1 | 23.3 | 41.3 | 392 | 22.4 | 47.6 | 444 | No | 2020-09-16 15:26 | 44090.6434 | 22.4 | 47.6 | 444 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 15:26
2020-09-16 15:27 | 44090.6437 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 49 | 630 |  | 2020-09-16 15:27 | 44090.6437 | 23 | 49 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:26
2020-09-16 15:27 | 44090.6437 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 22.9 | 54.2 | 448 |  | 2020-09-16 15:27 | 44090.6437 | 22.9 | 54.2 | 448 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:26
2020-09-16 15:27 | 44090.6438 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton |  |  | 0 | 24.4 | 51.6 | 401 | 21.2 | 52.6 | 803 |  | 2020-09-16 15:27 | 44090.6438 | 21.2 | 52.6 | 803 |  |  | 2020-09-14 | B90631¦¦¦Sep-16-2020 15:27
2020-09-16 15:28 | 44090.6447 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.1 | 53.8 | 454 |  | 2020-09-16 15:28 | 44090.6447 | 23.1 | 53.8 | 454 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:28
2020-09-16 15:28 | 44090.6447 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 49 | 790 |  | 2020-09-16 15:28 | 44090.6447 | 23 | 49 | 790 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:28
2020-09-16 15:29 | 44090.6452 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 1 | 23.3 | 41.3 | 392 | 22.6 | 46.5 | 455 | No | 2020-09-16 15:29 | 44090.6452 | 22.6 | 46.5 | 455 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 15:29
2020-09-16 15:30 | 44090.6456 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 49 | 620 |  | 2020-09-16 15:30 | 44090.6456 | 23 | 49 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:29
2020-09-16 15:30 | 44090.6462 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.1 | 53.8 | 447 |  | 2020-09-16 15:30 | 44090.6462 | 23.1 | 53.8 | 447 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:30
2020-09-16 15:31 | 44090.6463 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 4 | 23.3 | 41.3 | 392 | 22.1 | 46.1 | 478 | No | 2020-09-16 15:31 | 44090.6463 | 22.1 | 46.1 | 478 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 15:30
2020-09-16 15:32 | 44090.6469 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 1 | 25.8 | 34.8 | 412 | 22.8 | 34.4 | 553 |  | 2020-09-16 15:32 | 44090.6469 | 22.8 | 34.4 | 553 |  | low | 2020-09-14 | B21554¦¦¦Sep-16-2020 15:31
2020-09-16 15:32 | 44090.6472 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 700 |  | 2020-09-16 15:32 | 44090.6472 | 23 | 50 | 700 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:31
2020-09-16 15:32 | 44090.6473 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.3 | 54.1 | 448 |  | 2020-09-16 15:32 | 44090.6473 | 23.3 | 54.1 | 448 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:32
2020-09-16 15:32 | 44090.6473 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 1 | 23.3 | 41.3 | 392 | 22.2 | 46.2 | 462 | No | 2020-09-16 15:32 | 44090.6473 | 22.2 | 46.2 | 462 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 15:32
2020-09-16 15:33 | 44090.6479 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 630 |  | 2020-09-16 15:33 | 44090.6479 | 23 | 50 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:33
2020-09-16 15:34 | 44090.6486 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 1 | 23.3 | 51.9 | 401 | 23.4 | 53.8 | 439 |  | 2020-09-16 15:34 | 44090.6486 | 23.4 | 53.8 | 439 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:33
2020-09-16 15:34 | 44090.6489 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 615 |  | 2020-09-16 15:34 | 44090.6489 | 23 | 50 | 615 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:34
2020-09-16 15:35 | 44090.6496 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph |  |  | 1 | 25.8 | 34.8 | 412 | 21.9 | 39 | 559 |  | 2020-09-16 15:36 | 44090.6496 | 21.9 | 39 | 559 |  | caution | 2020-09-14 | B20474¦¦¦Sep-16-2020 15:35
2020-09-16 15:36 | 44090.6497 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 620 |  | 2020-09-16 15:36 | 44090.6497 | 23 | 50 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:35
2020-09-16 15:36 | 44090.65 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.3 | 54.1 | 429 |  | 2020-09-16 15:36 | 44090.65 | 23.3 | 54.1 | 429 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:35
2020-09-16 15:37 | 44090.6506 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 620 |  | 2020-09-16 15:37 | 44090.6506 | 23 | 50 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:36
2020-09-16 15:38 | 44090.6511 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 22.8 | 54.6 | 434 |  | 2020-09-16 15:38 | 44090.6511 | 22.8 | 54.6 | 434 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:37
2020-09-16 15:38 | 44090.6513 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 49 | 630 |  | 2020-09-16 15:38 | 44090.6513 | 23 | 49 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:37
2020-09-16 15:38 | 44090.6517 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 1 | 25.8 | 34.8 | 412 | 22.2 | 37 | 564 |  | 2020-09-16 15:38 | 44090.6517 | 22.2 | 37 | 564 |  | caution | 2020-09-14 | B21554¦¦¦Sep-16-2020 15:38
2020-09-16 15:39 | 44090.652 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 22.8 | 55.2 | 444 |  | 2020-09-16 15:39 | 44090.652 | 22.8 | 55.2 | 444 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:38
2020-09-16 15:39 | 44090.6523 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 23 | 23 | 50 | 450 | 50 | 50 | 630 |  | 2020-09-16 15:39 | 44090.6523 | 50 | 50 | 630 | high |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:39
2020-09-16 15:40 | 44090.6529 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 22.8 | 55.8 | 436 |  | 2020-09-16 15:40 | 44090.6529 | 22.8 | 55.8 | 436 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:40
2020-09-16 15:41 | 44090.6532 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 630 |  | 2020-09-16 15:41 | 44090.6532 | 23 | 50 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:40
2020-09-16 15:41 | 44090.6537 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 1 | 25.8 | 34.8 | 412 | 22.9 | 34.4 | 570 |  | 2020-09-16 15:41 | 44090.6537 | 22.9 | 34.4 | 570 |  | low | 2020-09-14 | B21554¦¦¦Sep-16-2020 15:41
2020-09-16 15:41 | 44090.6538 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 22.8 | 55.9 | 435 |  | 2020-09-16 15:41 | 44090.6538 | 22.8 | 55.9 | 435 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:41
2020-09-16 15:42 | 44090.6539 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 620 |  | 2020-09-16 15:42 | 44090.6539 | 23 | 50 | 620 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:41
2020-09-16 15:43 | 44090.6547 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 660 |  | 2020-09-16 15:43 | 44090.6547 | 23 | 50 | 660 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:42
2020-09-16 15:44 | 44090.6556 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 680 |  | 2020-09-16 15:44 | 44090.6556 | 23 | 50 | 680 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:44
2020-09-16 15:44 | 44090.6556 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 1 | 25 | 47 | 415 | 24 | 42 | 645 | Yes | 2020-09-16 15:44 | 44090.6556 | 24 | 42 | 645 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:44
2020-09-16 15:45 | 44090.6563 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 22.9 | 55.6 | 454 |  | 2020-09-16 15:45 | 44090.6563 | 22.9 | 55.6 | 454 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:45
2020-09-16 15:45 | 44090.6563 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 1 | 25 | 47 | 415 | 23 | 42 | 631 | Yes | 2020-09-16 15:45 | 44090.6563 | 23 | 42 | 631 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:45
2020-09-16 15:45 | 44090.6564 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 49 | 630 |  | 2020-09-16 15:45 | 44090.6564 | 23 | 49 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:45
2020-09-16 15:46 | 44090.6566 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 122.8 | 25.8 | 34.8 | 412 | 22.8 | 41.2 | 551 |  | 2020-09-16 15:46 | 44090.6566 | 22.8 | 41.2 | 551 |  |  | 2020-09-14 | B21554¦¦¦Sep-16-2020 15:45
2020-09-16 15:46 | 44090.6571 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 51 | 700 |  | 2020-09-16 15:46 | 44090.6571 | 23 | 51 | 700 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:46
2020-09-16 15:46 | 44090.6572 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 1 | 25 | 47 | 415 | 23.5 | 45 | 631 | Yes | 2020-09-16 15:46 | 44090.6572 | 23.5 | 45 | 631 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:46
2020-09-16 15:46 | 44090.6572 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 1 | 20 | 62.4 | 387 | 21 | 52.5 | 517 |  | 2020-09-16 15:46 | 44090.6572 | 21 | 52.5 | 517 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 15:46
2020-09-16 15:47 | 44090.6578 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 730 |  | 2020-09-16 15:47 | 44090.6578 | 23 | 50 | 730 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:47
2020-09-16 15:47 | 44090.6579 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 1 | 25 | 47 | 415 | 23 | 45.9 | 710 | Yes | 2020-09-16 15:47 | 44090.6579 | 23 | 45.9 | 710 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:47
2020-09-16 15:48 | 44090.658 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 21.5 | 53.8 | 494 |  | 2020-09-16 15:48 | 44090.658 | 21.5 | 53.8 | 494 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 15:47
2020-09-16 15:48 | 44090.6581 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.2 | 53.9 | 451 |  | 2020-09-16 15:48 | 44090.6581 | 23.2 | 53.9 | 451 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:47
2020-09-16 15:48 | 44090.6586 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 640 |  | 2020-09-16 15:48 | 44090.6586 | 23 | 50 | 640 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:48
2020-09-16 15:48 | 44090.6586 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 1 | 25 | 47 | 415 | 22.2 | 48.7 | 782 | Yes | 2020-09-16 15:48 | 44090.6586 | 22.2 | 48.7 | 782 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:48
2020-09-16 15:49 | 44090.6588 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 1 | 25.8 | 34.8 | 412 | 23.7 | 35.7 | 580 | unable to access courtroom #2 | 2020-09-16 15:49 | 44090.6588 | 23.7 | 35.7 | 580 |  | caution | 2020-09-14 | B21554¦¦¦Sep-16-2020 15:48
2020-09-16 15:49 | 44090.6589 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 21.7 | 52 | 483 |  | 2020-09-16 15:49 | 44090.6589 | 21.7 | 52 | 483 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 15:48
2020-09-16 15:49 | 44090.659 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.3 | 54.4 | 433 |  | 2020-09-16 15:49 | 44090.659 | 23.3 | 54.4 | 433 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:48
2020-09-16 15:49 | 44090.6592 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 645 |  | 2020-09-16 15:49 | 44090.6592 | 23 | 50 | 645 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:49
2020-09-16 15:50 | 44090.6596 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 1 | 25 | 47 | 415 | 22.6 | 42 | 586 | Yes | 2020-09-16 15:50 | 44090.6596 | 22.6 | 42 | 586 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:49
2020-09-16 15:50 | 44090.6599 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 22.1 | 49 | 473 |  | 2020-09-16 15:50 | 44090.6599 | 22.1 | 49 | 473 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 15:50
2020-09-16 15:51 | 44090.6602 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 700 |  | 2020-09-16 15:51 | 44090.6602 | 23 | 50 | 700 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:50
2020-09-16 15:51 | 44090.6603 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 25 | 47 | 415 | 21.7 | 44.2 | 500 | Yes | 2020-09-16 15:51 | 44090.6603 | 21.7 | 44.2 | 500 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:50
2020-09-16 15:51 | 44090.6607 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 25 | 47 | 415 | 21.6 | 54.4 | 467 | Yes | 2020-09-16 15:51 | 44090.6607 | 21.6 | 54.4 | 467 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:51
2020-09-16 15:52 | 44090.6609 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 1 | 25.8 | 34.8 | 412 | 23.6 | 32.8 | 588 |  | 2020-09-16 15:52 | 44090.6609 | 23.6 | 32.8 | 588 |  | low | 2020-09-14 | B21554¦¦¦Sep-16-2020 15:51
2020-09-16 15:52 | 44090.6611 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 1 | 20 | 62.4 | 387 | 23.5 | 45.2 | 428 |  | 2020-09-16 15:52 | 44090.6611 | 23.5 | 45.2 | 428 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 15:51
2020-09-16 15:52 | 44090.6611 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 630 |  | 2020-09-16 15:52 | 44090.6611 | 23 | 50 | 630 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:51
2020-09-16 15:52 | 44090.6612 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe |  |  | 0 | 23.3 | 51.9 | 401 | 23.5 | 54.8 | 532 |  | 2020-09-16 15:52 | 44090.6612 | 23.5 | 54.8 | 532 |  |  | 2020-09-14 | B17477¦¦¦Sep-16-2020 15:52
2020-09-16 15:52 | 44090.6613 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 25 | 47 | 415 | 21.9 | 52.1 | 560 | Yes | 2020-09-16 15:52 | 44090.6613 | 21.9 | 52.1 | 560 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:52
2020-09-16 15:53 | 44090.6617 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 4 | 25 | 47 | 415 | 22 | 48.7 | 710 | Yes | 2020-09-16 15:53 | 44090.6617 | 22 | 48.7 | 710 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:52
2020-09-16 15:53 | 44090.6621 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines |  |  | 0 | 23 | 50 | 450 | 23 | 50 | 610 |  | 2020-09-16 15:53 | 44090.6621 | 23 | 50 | 610 |  |  | 2020-09-14 | B25548¦¦¦Sep-16-2020 15:53
2020-09-16 15:54 | 44090.6622 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23.3 | 46.9 | 458 |  | 2020-09-16 15:54 | 44090.6622 | 23.3 | 46.9 | 458 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 15:53
2020-09-16 15:54 | 44090.6622 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 25 | 47 | 415 | 22.4 | 49.6 | 852 | Yes | 2020-09-16 15:54 | 44090.6622 | 22.4 | 49.6 | 852 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:53
2020-09-16 15:54 | 44090.6627 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 1 | 25 | 47 | 415 | 22.2 | 48.7 | 819 | Yes | 2020-09-16 15:54 | 44090.6627 | 22.2 | 48.7 | 819 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:54
2020-09-16 15:55 | 44090.6633 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 23.4 | 47.8 | 496 |  | 2020-09-16 15:55 | 44090.6633 | 23.4 | 47.8 | 496 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 15:55
2020-09-16 15:55 | 44090.6633 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 25 | 47 | 415 | 22.1 | 51.3 | 769 | Yes | 2020-09-16 15:55 | 44090.6633 | 22.1 | 51.3 | 769 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:55
2020-09-16 15:56 | 44090.6638 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 6 | 25 | 47 | 415 | 22 | 50.8 | 630 | Yes | 2020-09-16 15:56 | 44090.6638 | 22 | 50.8 | 630 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:55
2020-09-16 15:56 | 44090.6638 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 2 | 25.8 | 34.8 | 412 | 23.5 | 38.8 | 723 |  | 2020-09-16 15:56 | 44090.6638 | 23.5 | 38.8 | 723 |  | caution | 2020-09-14 | B21554¦¦¦Sep-16-2020 15:55
2020-09-16 15:57 | 44090.6643 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 1 | 20 | 62.4 | 387 | 22.3 | 42 | 437 |  | 2020-09-16 15:57 | 44090.6643 | 22.3 | 42 | 437 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 15:56
2020-09-16 15:57 | 44090.6643 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 2 | 25 | 47 | 415 | 21.8 | 52 | 503 | Yes | 2020-09-16 15:57 | 44090.6643 | 21.8 | 52 | 503 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:56
2020-09-16 15:57 | 44090.6647 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 25 | 47 | 415 | 21.8 | 51.9 | 493 | Yes | 2020-09-16 15:57 | 44090.6647 | 21.8 | 51.9 | 493 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:57
2020-09-16 15:58 | 44090.6652 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 25 | 47 | 415 | 21.5 | 53.5 | 486 | Yes | 2020-09-16 15:58 | 44090.6652 | 21.5 | 53.5 | 486 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:57
2020-09-16 15:59 | 44090.6657 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 3 | 25 | 47 | 415 | 22.7 | 50 | 471 | Yes | 2020-09-16 15:59 | 44090.6657 | 22.7 | 50 | 471 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:58
2020-09-16 15:59 | 44090.6658 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 22.3 | 42.7 | 466 |  | 2020-09-16 15:59 | 44090.6658 | 22.3 | 42.7 | 466 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 15:58
2020-09-16 15:59 | 44090.6662 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 1 | 25 | 47 | 415 | 21.3 | 44.5 | 683 | Yes | 2020-09-16 15:59 | 44090.6662 | 21.3 | 44.5 | 683 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 15:59
2020-09-16 16:00 | 44090.6664 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph |  |  | 3 | 25.8 | 34.8 | 412 | 23.8 | 36.4 | 712 |  | 2020-09-16 16:00 | 44090.6664 | 23.8 | 36.4 | 712 |  | caution | 2020-09-14 | B21554¦¦¦Sep-16-2020 15:59
2020-09-16 16:00 | 44090.6668 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 1 | 25 | 47 | 415 | 21.6 | 50.2 | 710 | Yes | 2020-09-16 16:00 | 44090.6668 | 21.6 | 50.2 | 710 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 16:00
2020-09-16 16:01 | 44090.6671 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 21.5 | 48.2 | 500 |  | 2020-09-16 16:01 | 44090.6671 | 21.5 | 48.2 | 500 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 16:00
2020-09-16 16:01 | 44090.6675 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 5 | 25 | 47 | 415 | 22.8 | 49.5 | 577 | Yes | 2020-09-16 16:01 | 44090.6675 | 22.8 | 49.5 | 577 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 16:01
2020-09-16 16:02 | 44090.6682 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 21.5 | 50.8 | 512 |  | 2020-09-16 16:02 | 44090.6682 | 21.5 | 50.8 | 512 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 16:02
2020-09-16 16:02 | 44090.6683 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough |  |  | 5 | 25 | 47 | 415 | 22.1 | 52.6 | 565 | Court 1 Judge, Court 1 Right Side, Court 1 Left Side - no access | 2020-09-16 16:02 | 44090.6683 | 22.1 | 52.6 | 565 |  |  | 2020-09-14 | B20022¦¦¦Sep-16-2020 16:02
2020-09-16 16:03 | 44090.669 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 21.3 | 51.3 | 512 |  | 2020-09-16 16:03 | 44090.669 | 21.3 | 51.3 | 512 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 16:03
2020-09-16 16:05 | 44090.6699 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 21.3 | 51.3 | 512 |  | 2020-09-16 16:05 | 44090.6699 | 21.3 | 51.3 | 512 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 16:04
2020-09-16 16:07 | 44090.6712 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 2 | 20 | 62.4 | 387 | 21.3 | 55.5 | 508 |  | 2020-09-16 16:07 | 44090.6712 | 21.3 | 55.5 | 508 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 16:06
2020-09-16 16:08 | 44090.6723 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 21.7 | 55.4 | 647 |  | 2020-09-16 16:08 | 44090.6723 | 21.7 | 55.4 | 647 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 16:08
2020-09-16 16:09 | 44090.673 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 4 | 20 | 62.4 | 387 |  |  |  | Unable to test. Special meeting with Crown Judge. | 2020-09-16 16:09 | 44090.673 | [5 empty] | 2020-09-14 | B70740¦¦¦Sep-16-2020 16:09
2020-09-16 16:11 | 44090.6745 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 21.5 | 53.3 | 512 |  | 2020-09-16 16:11 | 44090.6745 | 21.5 | 53.3 | 512 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 16:11
2020-09-16 16:12 | 44090.6753 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 21.5 | 54.1 | 513 |  | 2020-09-16 16:12 | 44090.6753 | 21.5 | 54.1 | 513 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 16:12
2020-09-16 16:14 | 44090.6762 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 0 | 20 | 62.4 | 387 | 21.1 | 53.5 | 516 |  | 2020-09-16 16:14 | 44090.6762 | 21.1 | 53.5 | 516 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 16:13
2020-09-16 16:15 | 44090.6769 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington |  |  | 3 | 20 | 62.4 | 387 | 21.7 | 54.2 | 522 |  | 2020-09-16 16:15 | 44090.6769 | 21.7 | 54.2 | 522 |  |  | 2020-09-14 | B70740¦¦¦Sep-16-2020 16:14
2020-09-16 16:15 | 44090.6771 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 1 | 23.3 | 41.3 | 392 | 22.4 | 46.3 | 430 | No | 2020-09-16 16:15 | 44090.6771 | 22.4 | 46.3 | 430 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 16:14
2020-09-16 16:20 | 44090.6806 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville |  |  | 2 | 23.3 | 41.3 | 392 | 22.7 | 45.7 | 457 | No | 2020-09-16 16:20 | 44090.6806 | 22.7 | 45.7 | 457 |  |  | 2020-09-14 | B70496¦¦¦Sep-16-2020 16:20
2020-09-16 17:47 | 44090.7408 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 387 |  | 2020-09-16 17:47 | 44090.7408 | 23 | 42 | 387 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 17:46
2020-09-16 17:48 | 44090.7415 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 387 |  | 2020-09-16 17:48 | 44090.7415 | 23 | 42 | 387 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 17:47
2020-09-16 18:33 | 44090.7729 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton |  |  | 2 | 26 | 35 | 353 | 23 | 42 | 387 |  | 2020-09-16 18:33 | 44090.7729 | 23 | 42 | 387 |  |  | 2020-09-14 | B20772¦¦¦Sep-16-2020 18:33
2020-09-16 | 9:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 8 | [5 empty] | 23 | 52 | 406 |  | 2020-09-16 09:00 | 9:00 | 23 | 52 | 406 |  |  | 2020-09-14 | B25683¦Courtroom 8¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 11 | [5 empty] | 23 | 52 | 406 |  | 2020-09-16 09:00 | 9:00 | 23 | 52 | 406 |  |  | 2020-09-14 | B25683¦Courtroom 11¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 9 | [5 empty] | 23 | 48 | 420 |  | 2020-09-16 09:00 | 9:00 | 23 | 48 | 420 |  |  | 2020-09-14 | B25683¦Courtroom 9¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | 2-1 | [5 empty] | 22.1 | 52.4 | 693 |  | 2020-09-16 09:00 | 9:00 | 22.1 | 52.4 | 693 |  |  | 2020-09-14 | B10644¦2-1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-3 | [5 empty] | 20.9 | 60.1 | 425 |  | 2020-09-16 09:00 | 9:00 | 20.9 | 60.1 | 425 |  | caution | 2020-09-14 | B10644¦Courtroom 2-3¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-5 | [5 empty] | 21.2 | 57.1 | 400 |  | 2020-09-16 09:00 | 9:00 | 21.2 | 57.1 | 400 |  |  | 2020-09-14 | B10644¦Courtroom 2-5¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-7 | [5 empty] | 21.8 | 55.2 | 510 |  | 2020-09-16 09:00 | 9:00 | 21.8 | 55.2 | 510 |  |  | 2020-09-14 | B10644¦Courtroom 2-7¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-2 | [5 empty] | 20.6 | 58.2 | 543 |  | 2020-09-16 09:00 | 9:00 | 20.6 | 58.2 | 543 |  |  | 2020-09-14 | B10644¦Courtroom 2-2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 3-2 | [5 empty] | 21.8 | 57.5 | 370 |  | 2020-09-16 09:00 | 9:00 | 21.8 | 57.5 | 370 |  |  | 2020-09-14 | B10644¦Courtroom 3-2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-1 | [5 empty] | 22.7 | 58 | 480 |  | 2020-09-16 09:00 | 9:00 | 22.7 | 58 | 480 |  |  | 2020-09-14 | B10644¦Courtroom 4-1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-2 | [5 empty] | 21.1 | 54.8 | 412 |  | 2020-09-16 09:00 | 9:00 | 21.1 | 54.8 | 412 |  |  | 2020-09-14 | B10644¦Courtroom 4-2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-9 | [5 empty] | 21.3 | 52.5 | 398 |  | 2020-09-16 09:00 | 9:00 | 21.3 | 52.5 | 398 |  |  | 2020-09-14 | B10644¦Courtroom 4-9¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-3 | [5 empty] | 23.4 | 52.8 | 405 |  | 2020-09-16 09:00 | 9:00 | 23.4 | 52.8 | 405 |  |  | 2020-09-14 | B10644¦Courtroom 4-3¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-7 | [5 empty] | 22.1 | 56.2 | 385 |  | 2020-09-16 09:00 | 9:00 | 22.1 | 56.2 | 385 |  |  | 2020-09-14 | B10644¦Courtroom 4-7¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-4 | [5 empty] | 22 | 58 | 502 |  | 2020-09-16 09:00 | 9:00 | 22 | 58 | 502 |  |  | 2020-09-14 | B10644¦Courtroom 4-4¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-5 | [5 empty] | 21.2 | 56.3 | 398 |  | 2020-09-16 09:00 | 9:00 | 21.2 | 56.3 | 398 |  |  | 2020-09-14 | B10644¦Courtroom 4-5¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-6 | [5 empty] | 22.5 | 58.4 | 380 |  | 2020-09-16 09:00 | 9:00 | 22.5 | 58.4 | 380 |  |  | 2020-09-14 | B10644¦Courtroom 4-6¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-8 | [5 empty] | 23.1 | 54.4 | 395 |  | 2020-09-16 09:00 | 9:00 | 23.1 | 54.4 | 395 |  |  | 2020-09-14 | B10644¦Courtroom 4-8¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-9 | [5 empty] | 21.3 | 56.1 | 402 |  | 2020-09-16 09:00 | 9:00 | 21.3 | 56.1 | 402 |  |  | 2020-09-14 | B10644¦Courtroom 4-9¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-10 | [5 empty] | 22.1 | 58 | 492 |  | 2020-09-16 09:00 | 9:00 | 22.1 | 58 | 492 |  |  | 2020-09-14 | B10644¦Courtroom 4-10¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22.8 | 53 | 430 |  | 2020-09-16 09:00 | 9:00 | 22.8 | 53 | 430 |  |  | 2020-09-14 | B10644¦Courtroom 5-1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-1 | [5 empty] | 21.9 | 56.7 | 378 |  | 2020-09-16 09:00 | 9:00 | 21.9 | 56.7 | 378 |  |  | 2020-09-14 | B10644¦Courtroom 6-1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 101 | [5 empty] | 21 | 49 |  |  | 2020-09-16 09:00 | 9:00 | 21 | 49 |  |  |  | 2020-09-14 | B20080¦Courtroom 101¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-3 | [5 empty] | 22.1 | 55.4 | 556 |  | 2020-09-16 09:00 | 9:00 | 22.1 | 55.4 | 556 |  |  | 2020-09-14 | B10644¦Courtroom 6-3¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 201 | [5 empty] | 20 | 45 | 428 |  | 2020-09-16 09:00 | 9:00 | 20 | 45 | 428 |  |  | 2020-09-14 | B20080¦Courtroom 201¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 202 | [5 empty] | 21 | 45 | 419 |  | 2020-09-16 09:00 | 9:00 | 21 | 45 | 419 |  |  | 2020-09-14 | B20080¦Courtroom 202¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 301 | [5 empty] | 22 | 45 | 419 |  | 2020-09-16 09:00 | 9:00 | 22 | 45 | 419 |  |  | 2020-09-14 | B20080¦Courtroom 301¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 302 | [5 empty] | 22 | 45 | 419 |  | 2020-09-16 09:00 | 9:00 | 22 | 45 | 419 |  |  | 2020-09-14 | B20080¦Courtroom 302¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 303 | [5 empty] | 22 | 45 | 486 |  | 2020-09-16 09:00 | 9:00 | 22 | 45 | 486 |  |  | 2020-09-14 | B20080¦Courtroom 303¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Outdoors |  |  | 15 | 71 | 432 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20080¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Outdoors |  |  | 15 | 84 | 425 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B12948¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 1 | [5 empty] | 20 | 59 | 418 |  | 2020-09-16 09:00 | 9:00 | 20 | 59 | 418 |  |  | 2020-09-14 | B12948¦Courtroom 1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 | [5 empty] | 21 | 57 | 431 |  | 2020-09-16 09:00 | 9:00 | 21 | 57 | 431 |  |  | 2020-09-14 | B12948¦Courtroom 2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 | [5 empty] | 21 | 56 | 428 |  | 2020-09-16 09:00 | 9:00 | 21 | 56 | 428 |  |  | 2020-09-14 | B12948¦Courtroom 3¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 | [5 empty] | 21 | 55 | 414 |  | 2020-09-16 09:00 | 9:00 | 21 | 55 | 414 |  |  | 2020-09-14 | B12948¦Courtroom 4¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 | [5 empty] | 22 | 54 | 403 |  | 2020-09-16 09:00 | 9:00 | 22 | 54 | 403 |  |  | 2020-09-14 | B14209¦Courtroom 1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 | [5 empty] | 21 | 56 | 435 |  | 2020-09-16 09:00 | 9:00 | 21 | 56 | 435 |  |  | 2020-09-14 | B12948¦Courtroom 5¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 - waiting area | [5 empty] | 22 | 54 | 431 |  | 2020-09-16 09:00 | 9:00 | 22 | 54 | 431 |  |  | 2020-09-14 | B14209¦Courtroom 1 - waiting area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 6 | [5 empty] | 21 | 55 | 423 |  | 2020-09-16 09:00 | 9:00 | 21 | 55 | 423 |  |  | 2020-09-14 | B12948¦Courtroom 6¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | lobby | [5 empty] | 21 | 63 | 498 |  | 2020-09-16 09:00 | 9:00 | 21 | 63 | 498 |  | caution | 2020-09-14 | B10002¦lobby¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 | [5 empty] | 21 | 56 | 408 |  | 2020-09-16 09:00 | 9:00 | 21 | 56 | 408 |  |  | 2020-09-14 | B14209¦Courtroom 2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Cell Basement | [5 empty] | 21 | 55 | 460 |  | 2020-09-16 09:00 | 9:00 | 21 | 55 | 460 |  |  | 2020-09-14 | B12948¦Cell Basement¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration Office Waiting Area | [5 empty] | 21 | 54 | 435 |  | 2020-09-16 09:00 | 9:00 | 21 | 54 | 435 |  |  | 2020-09-14 | B12948¦Administration Office Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration office | [5 empty] | 21 | 53 | 422 |  | 2020-09-16 09:00 | 9:00 | 21 | 53 | 422 |  |  | 2020-09-14 | B12948¦Administration office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Outdoors |  |  | 9 | 61 | 398 |  |  |  | North entrance - partly cloudy, windy | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B13049¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Crown attorney admin area | [5 empty] | 22 | 55 | 476 |  | 2020-09-16 09:00 | 9:00 | 22 | 55 | 476 |  |  | 2020-09-14 | B12948¦Crown attorney admin area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main Entrance Waiting Area | [5 empty] | 21 | 54 | 422 |  | 2020-09-16 09:00 | 9:00 | 21 | 54 | 422 |  |  | 2020-09-14 | B12948¦Main Entrance Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | office Skeggs | [5 empty] | 22 | 57 | 490 | Door Open | 2020-09-16 09:00 | 9:00 | 22 | 57 | 490 |  |  | 2020-09-14 | B10002¦office Skeggs¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main entrance | [5 empty] | 21 | 54 | 440 |  | 2020-09-16 09:00 | 9:00 | 21 | 54 | 440 |  |  | 2020-09-14 | B12948¦Main entrance¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 - waiting room | [5 empty] | 22 | 55 | 444 |  | 2020-09-16 09:00 | 9:00 | 22 | 55 | 444 |  |  | 2020-09-14 | B14209¦Courtroom 2 - waiting room¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Court Room 1 Waiting Area | [5 empty] | 21 | 55 | 443 |  | 2020-09-16 09:00 | 9:00 | 21 | 55 | 443 |  |  | 2020-09-14 | B12948¦Court Room 1 Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room | [5 empty] | 22 | 55 | 397 |  | 2020-09-16 09:00 | 9:00 | 22 | 55 | 397 |  |  | 2020-09-14 | B14209¦Hearing Room¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 Waiting Area | [5 empty] | 21 | 55 | 432 |  | 2020-09-16 09:00 | 9:00 | 21 | 55 | 432 |  |  | 2020-09-14 | B12948¦Courtroom 2 Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 Waiting Area | [5 empty] | 21 | 54 | 431 |  | 2020-09-16 09:00 | 9:00 | 21 | 54 | 431 |  |  | 2020-09-14 | B12948¦Courtroom 3 Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room - Waiting area | [5 empty] | 21.7 | 54 | 403 |  | 2020-09-16 09:00 | 9:00 | 21.7 | 54 | 403 |  |  | 2020-09-14 | B14209¦Hearing Room - Waiting area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room, Judge’s Chamber | [5 empty] | 22 | 54 | 400 |  | 2020-09-16 09:00 | 9:00 | 22 | 54 | 400 |  |  | 2020-09-14 | B14209¦Hearing Room, Judge’s Chamber¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd fl lobby | [5 empty] | 21 | 51 | 666 |  | 2020-09-16 09:00 | 9:00 | 21 | 51 | 666 |  |  | 2020-09-14 | B20226¦2nd fl lobby¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Cubicle Office | [5 empty] | 23 | 56 | 603 | Door Open | 2020-09-16 09:00 | 9:00 | 23 | 56 | 603 |  |  | 2020-09-14 | B10002¦Cubicle Office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 Waiting Area | [5 empty] | 22 | 53 | 432 |  | 2020-09-16 09:00 | 9:00 | 22 | 53 | 432 |  |  | 2020-09-14 | B12948¦Courtroom 5 Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Front Desk | [5 empty] | 22 | 55 | 414 |  | 2020-09-16 09:00 | 9:00 | 22 | 55 | 414 |  |  | 2020-09-14 | B14209¦Crown Attorney Front Desk¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 and 6 Waiting Area | [5 empty] | 22 | 54 | 442 |  | 2020-09-16 09:00 | 9:00 | 22 | 54 | 442 |  |  | 2020-09-14 | B12948¦Courtroom 4 and 6 Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown attorney admin area | [5 empty] | 22 | 55 | 402 |  | 2020-09-16 09:00 | 9:00 | 22 | 55 | 402 |  |  | 2020-09-14 | B14209¦Crown attorney admin area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Print Room | [5 empty] | 21 | 56 | 399 |  | 2020-09-16 09:00 | 9:00 | 21 | 56 | 399 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Print Room¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | File Room | [5 empty] | 23 | 53 | 565 |  | 2020-09-16 09:00 | 9:00 | 23 | 53 | 565 |  |  | 2020-09-14 | B10002¦File Room¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Assistant Crown Attorney Office | [5 empty] | 21 | 56 | 397 |  | 2020-09-16 09:00 | 9:00 | 21 | 56 | 397 |  |  | 2020-09-14 | B14209¦Assistant Crown Attorney Office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 2 | [5 empty] | 20 | 54 | 601 |  | 2020-09-16 09:00 | 9:00 | 20 | 54 | 601 |  |  | 2020-09-14 | B20226¦Courtroom 2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Meeting Room (232) | [5 empty] | 21 | 57 | 398 |  | 2020-09-16 09:00 | 9:00 | 21 | 57 | 398 |  |  | 2020-09-14 | B14209¦Crown Attorney Meeting Room (232)¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 1 | [5 empty] | 20 | 52 | 507 |  | 2020-09-16 09:00 | 9:00 | 20 | 52 | 507 |  |  | 2020-09-14 | B20226¦Courtroom 1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Entry/Waiting | [5 empty] | 22 | 57 | 471 |  | 2020-09-16 09:00 | 9:00 | 22 | 57 | 471 |  |  | 2020-09-14 | B70510¦Entry/Waiting¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Assistant Crown Attorney Office (236) | [5 empty] | 21 | 56 | 392 |  | 2020-09-16 09:00 | 9:00 | 21 | 56 | 392 |  |  | 2020-09-14 | B14209¦Assistant Crown Attorney Office (236)¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 21 | 52 | 545 |  | 2020-09-16 09:00 | 9:00 | 21 | 52 | 545 |  |  | 2020-09-14 | B20226¦2nd Floor Holding Cell¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Lobby | [5 empty] | 22 | 55 | 411 |  | 2020-09-16 09:00 | 9:00 | 22 | 55 | 411 |  |  | 2020-09-14 | B14209¦Court Admin Office Lobby¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room A | [5 empty] | 22 | 57 | 569 |  | 2020-09-16 09:00 | 9:00 | 22 | 57 | 569 |  |  | 2020-09-14 | B70510¦Mediation Room A¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Information Desk | [5 empty] | 22 | 56 | 491 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 491 |  |  | 2020-09-14 | B70510¦Information Desk¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 3 | [5 empty] | 22 | 54 | 432 |  | 2020-09-16 09:00 | 9:00 | 22 | 54 | 432 |  |  | 2020-09-14 | B20226¦Courtroom 3¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Didiodato | [5 empty] | 22 | 54 | 523 | Door Open | 2020-09-16 09:00 | 9:00 | 22 | 54 | 523 |  |  | 2020-09-14 | B10002¦Office Didiodato¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 101 | [5 empty] | 19 | 59 | 512 |  | 2020-09-16 09:00 | 9:00 | 19 | 59 | 512 |  |  | 2020-09-14 | B25671¦Courtroom 101¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Lunch Room 454 | [5 empty] | 22 | 56 | 460 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 460 |  |  | 2020-09-14 | B70510¦Lunch Room 454¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 201 | [5 empty] | 19 | 60 | 532 |  | 2020-09-16 09:00 | 9:00 | 19 | 60 | 532 |  | caution | 2020-09-14 | B25671¦Courtroom 201¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Copy Room 455 | [5 empty] | 22 | 55 | 457 |  | 2020-09-16 09:00 | 9:00 | 22 | 55 | 457 |  |  | 2020-09-14 | B70510¦Copy Room 455¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Outdoors |  |  | 15 | 76 | 375 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10002¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room B | [5 empty] | 22 | 55 | 453 |  | 2020-09-16 09:00 | 9:00 | 22 | 55 | 453 |  |  | 2020-09-14 | B70510¦Mediation Room B¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Outdoors |  |  | 17 | 72 | 305 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B25165¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 459 | [5 empty] | 22 | 55 | 478 |  | 2020-09-16 09:00 | 9:00 | 22 | 55 | 478 |  |  | 2020-09-14 | B70510¦Office 459¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 308 | [5 empty] | 22 | 49 | 427 |  | 2020-09-16 09:00 | 9:00 | 22 | 49 | 427 |  |  | 2020-09-14 | B25165¦Courtroom 308¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Cubicles | [5 empty] | 22 | 56 | 396 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 396 |  |  | 2020-09-14 | B14209¦Court Admin Office Cubicles¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 467 | [5 empty] | 22 | 55 | 445 |  | 2020-09-16 09:00 | 9:00 | 22 | 55 | 445 |  |  | 2020-09-14 | B70510¦Office 467¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 306 | [5 empty] | 22 | 49 | 426 |  | 2020-09-16 09:00 | 9:00 | 22 | 49 | 426 |  |  | 2020-09-14 | B25165¦Courtroom 306¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Intake Court | [5 empty] | 23 | 52 | 421 |  | 2020-09-16 09:00 | 9:00 | 23 | 52 | 421 |  |  | 2020-09-14 | B14209¦Intake Court¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Outdoors |  |  | 13 | 17 | 407 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20226¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 469 | [5 empty] | 22 | 55 | 455 |  | 2020-09-16 09:00 | 9:00 | 22 | 55 | 455 |  |  | 2020-09-14 | B70510¦Office 469¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 302 | [5 empty] | 21 | 49 | 421 |  | 2020-09-16 09:00 | 9:00 | 21 | 49 | 421 |  |  | 2020-09-14 | B25165¦Courtroom 302¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Holding Cell corridor | [5 empty] | 22 | 56 | 423 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 423 |  |  | 2020-09-14 | B14209¦Holding Cell corridor¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 208 | [5 empty] | 21 | 49 | 411 |  | 2020-09-16 09:00 | 9:00 | 21 | 49 | 411 |  |  | 2020-09-14 | B25165¦Courtroom 208¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Room 473 (Printer) | [5 empty] | 22 | 56 | 445 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 445 |  |  | 2020-09-14 | B70510¦Room 473 (Printer)¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Police Control Room | [5 empty] | 22 | 57 | 465 |  | 2020-09-16 09:00 | 9:00 | 22 | 57 | 465 |  |  | 2020-09-14 | B14209¦Police Control Room¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 206 | [5 empty] | 22 | 49 | 434 |  | 2020-09-16 09:00 | 9:00 | 22 | 49 | 434 |  |  | 2020-09-14 | B25165¦Courtroom 206¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hall 475 or 466 | [5 empty] | 22 | 55 | 445 |  | 2020-09-16 09:00 | 9:00 | 22 | 55 | 445 |  |  | 2020-09-14 | B70510¦Hall 475 or 466¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Outdoors |  |  | 13 | 21 | 442 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70050¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 204 | [5 empty] | 22 | 49 | 429 |  | 2020-09-16 09:00 | 9:00 | 22 | 49 | 429 |  |  | 2020-09-14 | B25165¦Courtroom 204¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Lobby Administration | [5 empty] | 17 | 64 | 440 |  | 2020-09-16 09:00 | 9:00 | 17 | 64 | 440 |  | caution | 2020-09-14 | B10003¦Lobby Administration¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 1 | [5 empty] | 22 | 56 | 449 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 449 |  |  | 2020-09-14 | B70510¦Hearing Room 1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 202 | [5 empty] | 21 | 49 | 416 |  | 2020-09-16 09:00 | 9:00 | 21 | 49 | 416 |  |  | 2020-09-14 | B25165¦Courtroom 202¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Meeting Rooms 1/2 | [5 empty] | 22 | 56 | 455 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 455 |  |  | 2020-09-14 | B70510¦Vestibule at Meeting Rooms 1/2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 200 | [5 empty] | 21 | 49 | 429 |  | 2020-09-16 09:00 | 9:00 | 21 | 49 | 429 |  |  | 2020-09-14 | B25165¦Courtroom 200¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Library | [5 empty] | 17 | 61 | 465 | Wall mount AC unit running | 2020-09-16 09:00 | 9:00 | 17 | 61 | 465 |  | caution | 2020-09-14 | B10003¦Library¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 100 | [5 empty] | 22 | 49 | 437 |  | 2020-09-16 09:00 | 9:00 | 22 | 49 | 437 |  |  | 2020-09-14 | B25165¦Courtroom 100¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Level 1 Corridor by room 103 | [5 empty] | 22 | 54 | 417 |  | 2020-09-16 09:00 | 9:00 | 22 | 54 | 417 |  |  | 2020-09-14 | B14209¦Level 1 Corridor by room 103¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Hearing Room 1 | [5 empty] | 22 | 56 | 451 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 451 |  |  | 2020-09-14 | B70510¦Vestibule at Hearing Room 1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 2 | [5 empty] | 22 | 56 | 450 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 450 |  |  | 2020-09-14 | B70510¦Hearing Room 2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Library | [5 empty] | 22 | 54 | 411 |  | 2020-09-16 09:00 | 9:00 | 22 | 54 | 411 |  |  | 2020-09-14 | B14209¦Library¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 439 | [5 empty] | 22 | 57 | 454 |  | 2020-09-16 09:00 | 9:00 | 22 | 57 | 454 |  |  | 2020-09-14 | B70510¦Office 439¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | First Aid Desk | [5 empty] | 22 | 57 | 451 |  | 2020-09-16 09:00 | 9:00 | 22 | 57 | 451 |  |  | 2020-09-14 | B70510¦First Aid Desk¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Law Library Meeting Room (028B) | [5 empty] | 22 | 55 | 493 |  | 2020-09-16 09:00 | 9:00 | 22 | 55 | 493 |  |  | 2020-09-14 | B14209¦Law Library Meeting Room (028B)¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 436 | [5 empty] | 22 | 56 | 442 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 442 |  |  | 2020-09-14 | B70510¦Office 436¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Lunch Room | [5 empty] | 22 | 54 | 423 |  | 2020-09-16 09:00 | 9:00 | 22 | 54 | 423 |  |  | 2020-09-14 | B14209¦Lunch Room¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Entrance by Stair G | [5 empty] | 22 | 57 | 426 |  | 2020-09-16 09:00 | 9:00 | 22 | 57 | 426 |  |  | 2020-09-14 | B14209¦Entrance by Stair G¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 432 | [5 empty] | 22 | 56 | 494 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 494 |  |  | 2020-09-14 | B70510¦Office 432¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Basement Library | [5 empty] | 17 | 65 | 428 |  | 2020-09-16 09:00 | 9:00 | 17 | 65 | 428 |  | caution | 2020-09-14 | B10003¦Basement Library¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Outdoors |  |  | 19 | 64 | [5 empty] | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20619¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Outdoors |  |  | 18 | 63 | 253 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20289¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 21 | 56 | 232 | judge | 2020-09-16 09:00 | 9:00 | 21 | 56 | 232 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 429 | [5 empty] | 22 | 56 | 500 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 500 |  |  | 2020-09-14 | B70510¦Office 429¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Courtroom 1-14 | [5 empty] | 22 | 57 | 452 |  | 2020-09-16 09:00 | 9:00 | 22 | 57 | 452 |  |  | 2020-09-14 | B20619¦Courtroom 1-14¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 21 | 55 | 231 | public | 2020-09-16 09:00 | 9:00 | 21 | 55 | 231 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 427 | [5 empty] | 22 | 56 | 465 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 465 |  |  | 2020-09-14 | B70510¦Office 427¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Outdoors |  |  | 15 | 76 | 380 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10003¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 21 | 55 | 230 | judge | 2020-09-16 09:00 | 9:00 | 21 | 55 | 230 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Main Floor Entrance Lobby | [5 empty] | 22 | 58 | 432 |  | 2020-09-16 09:00 | 9:00 | 22 | 58 | 432 |  |  | 2020-09-14 | B14209¦Main Floor Entrance Lobby¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mail Room | [5 empty] | 22 | 56 | 454 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 454 |  |  | 2020-09-14 | B70510¦Mail Room¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 21 | 54 | 226 | public | 2020-09-16 09:00 | 9:00 | 21 | 54 | 226 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Main Lobby | [5 empty] | 21 | 33 | 551 |  | 2020-09-16 09:00 | 9:00 | 21 | 33 | 551 |  | low | 2020-09-14 | B70050¦Main Lobby¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 420 | [5 empty] | 22 | 56 | 469 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 469 |  |  | 2020-09-14 | B70510¦Office 420¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 300 | [5 empty] | 22 | 51 | 264 |  | 2020-09-16 09:00 | 9:00 | 22 | 51 | 264 |  |  | 2020-09-14 | B20289¦Courtroom 300¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Outdoors |  |  | 19 | 63 | 385 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B14209¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 301 | [5 empty] | 22 | 52 | 261 |  | 2020-09-16 09:00 | 9:00 | 22 | 52 | 261 |  |  | 2020-09-14 | B20289¦Courtroom 301¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 418 | [5 empty] | 22 | 56 | 456 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 456 |  |  | 2020-09-14 | B70510¦Office 418¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 302 | [5 empty] | 22 | 51 | 251 |  | 2020-09-16 09:00 | 9:00 | 22 | 51 | 251 |  |  | 2020-09-14 | B20289¦Courtroom 302¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Outdoors |  |  | 19 | 55 | 387 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B19652¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 1 | [5 empty] | 20 | 32 | 478 |  | 2020-09-16 09:00 | 9:00 | 20 | 32 | 478 |  | low | 2020-09-14 | B70050¦Courtroom 1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom A | [5 empty] | 21 | 53 | 266 | in session; measurement taken outside courtroom | 2020-09-16 09:00 | 9:00 | 21 | 53 | 266 |  |  | 2020-09-14 | B20289¦Courtroom A¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | File Room | [5 empty] | 22 | 56 | 467 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 467 |  |  | 2020-09-14 | B70510¦File Room¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom B | [5 empty] | 21 | 52 | 294 |  | 2020-09-16 09:00 | 9:00 | 21 | 52 | 294 |  |  | 2020-09-14 | B20289¦Courtroom B¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom C (North) | [5 empty] | 21 | 52 | 305 |  | 2020-09-16 09:00 | 9:00 | 21 | 52 | 305 |  |  | 2020-09-14 | B20289¦Courtroom C (North)¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom D | [5 empty] | 22 | 52 | 293 |  | 2020-09-16 09:00 | 9:00 | 22 | 52 | 293 |  |  | 2020-09-14 | B20289¦Courtroom D¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Center) | [5 empty] | 19 | 53 | 494 |  | 2020-09-16 09:00 | 9:00 | 19 | 53 | 494 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Center)¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom E | [5 empty] | 21 | 51 | 302 |  | 2020-09-16 09:00 | 9:00 | 21 | 51 | 302 |  |  | 2020-09-14 | B20289¦Courtroom E¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom F | [5 empty] | 22 | 53 | 304 | in session; measurement taken outside courtroom | 2020-09-16 09:00 | 9:00 | 22 | 53 | 304 |  |  | 2020-09-14 | B20289¦Courtroom F¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Center) | [5 empty] | 19 | 53 | 494 |  | 2020-09-16 09:00 | 9:00 | 19 | 53 | 494 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Center)¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 1 | [5 empty] | 22 | 41 | 452 |  | 2020-09-16 09:00 | 9:00 | 22 | 41 | 452 |  |  | 2020-09-14 | B25602¦Courtroom 1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Judge Dias) | [5 empty] | 19 | 53 | 465 |  | 2020-09-16 09:00 | 9:00 | 19 | 53 | 465 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Judge Dias)¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 2 | [5 empty] | 22 | 43 | 461 |  | 2020-09-16 09:00 | 9:00 | 22 | 43 | 461 |  |  | 2020-09-14 | B25602¦Courtroom 2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 3 | [5 empty] | 22 | 39 | 450 |  | 2020-09-16 09:00 | 9:00 | 22 | 39 | 450 |  | caution | 2020-09-14 | B25602¦Courtroom 3¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 18 | 52 | 459 | Superior judges chamber | 2020-09-16 09:00 | 9:00 | 18 | 52 | 459 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 18 | 54 | 511 | 3rd floor stair landing | 2020-09-16 09:00 | 9:00 | 18 | 54 | 511 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 4 | [5 empty] | 23 | 40 | 437 |  | 2020-09-16 09:00 | 9:00 | 23 | 40 | 437 |  | caution | 2020-09-14 | B25602¦Courtroom 4¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 18 | 53 | 462 | 3rd floor Jury Room | 2020-09-16 09:00 | 9:00 | 18 | 53 | 462 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 5 | [5 empty] | 23 | 40 | 415 |  | 2020-09-16 09:00 | 9:00 | 23 | 40 | 415 |  | caution | 2020-09-14 | B25602¦Courtroom 5¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 6 | [5 empty] | 23 | 42 | 408 |  | 2020-09-16 09:00 | 9:00 | 23 | 42 | 408 |  |  | 2020-09-14 | B25602¦Courtroom 6¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 19 | 54 | 486 | Justice McDonalds chamber | 2020-09-16 09:00 | 9:00 | 19 | 54 | 486 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 18 | 53 | 452 | Justice McDonald secretary | 2020-09-16 09:00 | 9:00 | 18 | 53 | 452 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 7 | [5 empty] | 23 | 40 | 419 |  | 2020-09-16 09:00 | 9:00 | 23 | 40 | 419 |  | caution | 2020-09-14 | B25602¦Courtroom 7¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 18 | 53 | 443 | SCJTC office | 2020-09-16 09:00 | 9:00 | 18 | 53 | 443 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Health Room | [5 empty] | 22 | 56 | 466 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 466 |  |  | 2020-09-14 | B70510¦Health Room¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Visiting Justice's Office | [5 empty] | 18 | 53 | 442 |  | 2020-09-16 09:00 | 9:00 | 18 | 53 | 442 |  |  | 2020-09-14 | B19652¦Visiting Justice's Office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 | [5 empty] | 22 | 56 | 463 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 463 |  |  | 2020-09-14 | B70510¦Hearing Room 3¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 19 | 18 | 449 |  | 2020-09-16 09:00 | 9:00 | 19 | 18 | 449 |  | low | 2020-09-14 | B70050¦2nd Floor Holding Cell¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Center) | [5 empty] | 18 | 53 | 432 |  | 2020-09-16 09:00 | 9:00 | 18 | 53 | 432 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Center)¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 Waiting Area | [5 empty] | 22 | 56 | 446 |  | 2020-09-16 09:00 | 9:00 | 22 | 56 | 446 |  |  | 2020-09-14 | B70510¦Hearing Room 3 Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Judge Dias) | [5 empty] | 18 | 53 | 439 |  | 2020-09-16 09:00 | 9:00 | 18 | 53 | 439 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Judge Dias)¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 Waiting Area | [5 empty] | 18 | 54 | 472 |  | 2020-09-16 09:00 | 9:00 | 18 | 54 | 472 |  |  | 2020-09-14 | B19652¦Courtroom 2 Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Elevator Lobby | [5 empty] | 22 | 61 | 466 |  | 2020-09-16 09:00 | 9:00 | 22 | 61 | 466 |  | caution | 2020-09-14 | B70510¦Elevator Lobby¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Center) | [5 empty] | 22 | 53 | 462 |  | 2020-09-16 09:00 | 9:00 | 22 | 53 | 462 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Center)¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Yannick Bedard Office - 2nd Floor | [5 empty] | 21 | 28 | 544 |  | 2020-09-16 09:00 | 9:00 | 21 | 28 | 544 |  | low | 2020-09-14 | B70050¦Yannick Bedard Office - 2nd Floor¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Outdoors |  |  | 16 | 72 | 432 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70510¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Judge Dias) | [5 empty] | 22 | 53 | 437 |  | 2020-09-16 09:00 | 9:00 | 22 | 53 | 437 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Judge Dias)¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 2 | [5 empty] | 21 | 35 | 453 |  | 2020-09-16 09:00 | 9:00 | 21 | 35 | 453 |  | caution | 2020-09-14 | B70050¦Courtroom 2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 52 | 456 | Justice of peace chamber | 2020-09-16 09:00 | 9:00 | 22 | 52 | 456 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd fl lobby | [5 empty] | 21 | 34 | 448 |  | 2020-09-16 09:00 | 9:00 | 21 | 34 | 448 |  | low | 2020-09-14 | B70050¦2nd fl lobby¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 51 | 444 | Council chamber dias | 2020-09-16 09:00 | 9:00 | 22 | 51 | 444 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 50 | 434 | Council chamber center | 2020-09-16 09:00 | 9:00 | 22 | 50 | 434 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 2nd Floor Lunchroom | [5 empty] | 19 | 54 | 470 |  | 2020-09-16 09:00 | 9:00 | 19 | 54 | 470 |  |  | 2020-09-14 | B19652¦2nd Floor Lunchroom¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 54 | 478 | 2nd floor stair landing | 2020-09-16 09:00 | 9:00 | 21 | 54 | 478 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 54 | 475 | Court services kitchenette | 2020-09-16 09:00 | 9:00 | 21 | 54 | 475 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 54 | 475 | Court services kitchenette | 2020-09-16 09:00 | 9:00 | 21 | 54 | 475 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 51 | 687 | Court service north | 2020-09-16 09:00 | 9:00 | 22 | 51 | 687 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 51 | 671 | Court service south | 2020-09-16 09:00 | 9:00 | 21 | 51 | 671 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Outdoors |  |  | 17 | 51 | 674 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B25602¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 51 | 586 | Court service entrance vestibule | 2020-09-16 09:00 | 9:00 | 22 | 51 | 586 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 53 | 586 | 1st floor stair landing | 2020-09-16 09:00 | 9:00 | 22 | 53 | 586 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main entrance | [5 empty] | 23 | 43 | 509 |  | 2020-09-16 09:00 | 9:00 | 23 | 43 | 509 |  |  | 2020-09-14 | B14895¦Main entrance¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main Floor Waiting Area | [5 empty] | 23 | 40 | 483 |  | 2020-09-16 09:00 | 9:00 | 23 | 40 | 483 |  | caution | 2020-09-14 | B14895¦Main Floor Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom 1 | [5 empty] | 23 | 43 | 412 |  | 2020-09-16 09:00 | 9:00 | 23 | 43 | 412 |  |  | 2020-09-14 | B14895¦Courtroom 1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 101 | [5 empty] | 20 | 57 | 503 |  | 2020-09-16 09:00 | 9:00 | 20 | 57 | 503 |  |  | 2020-09-14 | B19512¦Courtroom 101¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Outdoors |  |  | 15 | 67 | 439 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B90838¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom 2 | [5 empty] | 23 | 43 | 452 |  | 2020-09-16 09:00 | 9:00 | 23 | 43 | 452 |  |  | 2020-09-14 | B14895¦Courtroom 2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 200 | [5 empty] | 21 | 51 | 556 |  | 2020-09-16 09:00 | 9:00 | 21 | 51 | 556 |  |  | 2020-09-14 | B19512¦Courtroom 200¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Courtroom 101 Courtroom 102 | [5 empty] | 22 | 53 | 434 |  | 2020-09-16 09:00 | 9:00 | 22 | 53 | 434 |  |  | 2020-09-14 | B90838¦Courtroom 101 Courtroom 102¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Crown Attorney Office | [5 empty] | 23 | 40 | 431 |  | 2020-09-16 09:00 | 9:00 | 23 | 40 | 431 |  | caution | 2020-09-14 | B14895¦Crown Attorney Office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 201 | [5 empty] | 22 | 51 | 556 |  | 2020-09-16 09:00 | 9:00 | 22 | 51 | 556 |  |  | 2020-09-14 | B19512¦Courtroom 201¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office South | [5 empty] | 23 | 41 | 630 |  | 2020-09-16 09:00 | 9:00 | 23 | 41 | 630 |  |  | 2020-09-14 | B14895¦Administration Office South¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office North | [5 empty] | 23 | 42 | 602 |  | 2020-09-16 09:00 | 9:00 | 23 | 42 | 602 |  |  | 2020-09-14 | B14895¦Administration Office North¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Outdoors |  |  | 16 | 82 | 556 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B19512¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Waiting Area | [5 empty] | 24 | 41 | 512 |  | 2020-09-16 09:00 | 9:00 | 24 | 41 | 512 |  |  | 2020-09-14 | B14895¦Basement Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Boardroom | [5 empty] | 24 | 41 | 460 |  | 2020-09-16 09:00 | 9:00 | 24 | 41 | 460 |  |  | 2020-09-14 | B14895¦Basement Boardroom¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 101 | [5 empty] | 20 | 55 | 503 |  | 2020-09-16 12:00 | 12:00 | 20 | 55 | 503 |  |  | 2020-09-14 | B19512¦Courtroom 101¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 200 | [5 empty] | 21 | 51 | 556 |  | 2020-09-16 12:00 | 12:00 | 21 | 51 | 556 |  |  | 2020-09-14 | B19512¦Courtroom 200¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Male Holding Cell | [5 empty] | 24 | 40 | 441 |  | 2020-09-16 09:00 | 9:00 | 24 | 40 | 441 |  | caution | 2020-09-14 | B14895¦Male Holding Cell¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Female Holding Cell | [5 empty] | 24 | 40 | 446 |  | 2020-09-16 09:00 | 9:00 | 24 | 40 | 446 |  | caution | 2020-09-14 | B14895¦Female Holding Cell¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 201 | [5 empty] | 22 | 51 | 556 |  | 2020-09-16 12:00 | 12:00 | 22 | 51 | 556 |  |  | 2020-09-14 | B19512¦Courtroom 201¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | 2nd Floor Waiting Area | [5 empty] | 23 | 41 | 565 |  | 2020-09-16 09:00 | 9:00 | 23 | 41 | 565 |  |  | 2020-09-14 | B14895¦2nd Floor Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 100 Courtroom 200 Courtroom 202 Courtroom 203 | [5 empty] | 21 | 47 | 460 |  | 2020-09-16 09:00 | 9:00 | 21 | 47 | 460 |  |  | 2020-09-14 | B20616¦Courtroom 100 Courtroom 200 Courtroom 202 Courtroom 203¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Outdoors |  |  | 16 | 82 | [5 empty] | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B19512¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Outdoors |  |  | 15 | 58 | 421 |  |  |  | Overcast, small winds | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B14895¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 1 | [5 empty] | 23 | 51 | 316 |  | 2020-09-16 09:00 | 9:00 | 23 | 51 | 316 |  |  | 2020-09-14 | B24638¦Courtroom 1¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Outdoors |  |  | 21 | 62 | 305 |  |  |  | Base Readings | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B25165¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 101 Courtroom 102 Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 201 Courtroom 401 Courtroom 402 Courtroom 403 | [5 empty] | 22 | 47 | 460 |  | 2020-09-16 09:00 | 9:00 | 22 | 47 | 460 |  |  | 2020-09-14 | B20616¦Courtroom 101 Courtroom 102 Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 201 Courtroom 401 Courtroom 402 Courtroom 403¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 3 | [5 empty] | 23 | 50 | 303 |  | 2020-09-16 09:00 | 9:00 | 23 | 50 | 303 |  |  | 2020-09-14 | B24638¦Courtroom 3¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 308 | [5 empty] | 22 | 51 | 551 |  | 2020-09-16 12:00 | 12:00 | 22 | 51 | 551 |  |  | 2020-09-14 | B25165¦Courtroom 308¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 306 | [5 empty] | 22 | 51 | 827 |  | 2020-09-16 12:00 | 12:00 | 22 | 51 | 827 |  |  | 2020-09-14 | B25165¦Courtroom 306¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Front Seating Area | [5 empty] | 21 | 57 | 440 |  | 2020-09-16 09:00 | 9:00 | 21 | 57 | 440 |  |  | 2020-09-14 | B18359¦Front Seating Area¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 302 | [5 empty] | 21 | 51 | 457 |  | 2020-09-16 12:00 | 12:00 | 21 | 51 | 457 |  |  | 2020-09-14 | B25165¦Courtroom 302¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Northwest Corridor | [5 empty] | 21 | 57 | 406 |  | 2020-09-16 09:00 | 9:00 | 21 | 57 | 406 |  |  | 2020-09-14 | B18359¦Northwest Corridor¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 20 | 57 | 412 | North Side | 2020-09-16 09:00 | 9:00 | 20 | 57 | 412 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 208 | [5 empty] | 21 | 51 | 494 |  | 2020-09-16 12:00 | 12:00 | 21 | 51 | 494 |  |  | 2020-09-14 | B25165¦Courtroom 208¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 21 | 57 | 423 | South side | 2020-09-16 09:00 | 9:00 | 21 | 57 | 423 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 206 | [5 empty] | 22 | 51 | 506 |  | 2020-09-16 12:00 | 12:00 | 22 | 51 | 506 |  |  | 2020-09-14 | B25165¦Courtroom 206¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 21 | 57 | 411 | North side | 2020-09-16 09:00 | 9:00 | 21 | 57 | 411 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 204 | [5 empty] | 22 | 51 | 523 |  | 2020-09-16 12:00 | 12:00 | 22 | 51 | 523 |  |  | 2020-09-14 | B25165¦Courtroom 204¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Outdoors |  |  | 23 | 50 | 302 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B24638¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 21 | 57 | 429 | South side | 2020-09-16 09:00 | 9:00 | 21 | 57 | 429 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 202 | [5 empty] | 21 | 51 | 481 |  | 2020-09-16 12:00 | 12:00 | 21 | 51 | 481 |  |  | 2020-09-14 | B25165¦Courtroom 202¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 21 | 58 | 408 | North side | 2020-09-16 09:00 | 9:00 | 21 | 58 | 408 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 200 | [5 empty] | 22 | 51 | 498 |  | 2020-09-16 12:00 | 12:00 | 22 | 51 | 498 |  |  | 2020-09-14 | B25165¦Courtroom 200¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 21 | 58 | 404 | South side | 2020-09-16 09:00 | 9:00 | 21 | 58 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 100 | [5 empty] | 22 | 51 | 485 |  | 2020-09-16 12:00 | 12:00 | 22 | 51 | 485 |  |  | 2020-09-14 | B25165¦Courtroom 100¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 56 | 413 | North side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 413 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 55 | 400 | North side | 2020-09-16 09:00 | 9:00 | 21 | 55 | 400 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 55 | 400 | *South Side* | 2020-09-16 09:00 | 9:00 | 21 | 55 | 400 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 56 | 402 | North side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 402 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 56 | 400 | South side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 400 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 21 | 56 | 400 | North side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 400 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 21 | 56 | 402 | South side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 402 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 21 | 57 | 409 | North side | 2020-09-16 09:00 | 9:00 | 21 | 57 | 409 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 21 | 57 | 402 | South side | 2020-09-16 09:00 | 9:00 | 21 | 57 | 402 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 21 | 57 | 404 | North side | 2020-09-16 09:00 | 9:00 | 21 | 57 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 21 | 57 | 410 | South side | 2020-09-16 09:00 | 9:00 | 21 | 57 | 410 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 21 | 57 | 403 | North side | 2020-09-16 09:00 | 9:00 | 21 | 57 | 403 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 21 | 57 | 400 | South side | 2020-09-16 09:00 | 9:00 | 21 | 57 | 400 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Northeast corridor | [5 empty] | 21 | 56 | 405 |  | 2020-09-16 09:00 | 9:00 | 21 | 56 | 405 |  |  | 2020-09-14 | B18359¦Northeast corridor¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 21 | 56 | 401 | North side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 401 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 21 | 56 | 405 | South side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 405 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 21 | 56 | 402 | North side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 402 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 21 | 56 | 392 | South side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 392 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 21 | 56 | 400 | North side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 400 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 21 | 56 | 402 | South side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 402 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 21 | 56 | 401 | North side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 401 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 21 | 56 | 400 | South side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 400 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 21 | 56 | 402 | North side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 402 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 21 | 56 | 400 | South side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 400 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 21 | 56 | 398 | North side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 398 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 21 | 56 | 400 | South side | 2020-09-16 09:00 | 9:00 | 21 | 56 | 400 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Outdoors |  |  | 18 | 67 | 407 |  |  |  | Outside of 15 Grosvenor Ave | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B18359¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 101 | [5 empty] | 21 | 49 |  |  | 2020-09-16 12:00 | 12:00 | 21 | 49 |  |  |  | 2020-09-14 | B20080¦Courtroom 101¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 201 | [5 empty] | 22 | 48 | 460 |  | 2020-09-16 12:00 | 12:00 | 22 | 48 | 460 |  |  | 2020-09-14 | B20080¦Courtroom 201¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 202 | [5 empty] | 22 | 48 | 453 |  | 2020-09-16 12:00 | 12:00 | 22 | 48 | 453 |  |  | 2020-09-14 | B20080¦Courtroom 202¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 301 | [5 empty] | 21 | 48 | 464 |  | 2020-09-16 12:00 | 12:00 | 21 | 48 | 464 |  |  | 2020-09-14 | B20080¦Courtroom 301¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-3 OTHER | [5 empty] | 21 | 53 | 603 |  | 2020-09-16 09:00 | 9:00 | 21 | 53 | 603 |  |  | 2020-09-14 | B25398¦Courtroom 16-3 OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 302 | [5 empty] | 22 | 48 | 509 |  | 2020-09-16 12:00 | 12:00 | 22 | 48 | 509 |  |  | 2020-09-14 | B20080¦Courtroom 302¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-2, West OTHER | [5 empty] | 20 | 54 | 601 |  | 2020-09-16 09:00 | 9:00 | 20 | 54 | 601 |  |  | 2020-09-14 | B25398¦Courtroom 16-2, West OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 303 | [5 empty] | 22 | 48 | 510 |  | 2020-09-16 12:00 | 12:00 | 22 | 48 | 510 |  |  | 2020-09-14 | B20080¦Courtroom 303¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Outdoors |  |  | 19 | 60 | 445 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20080¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-2, East OTHER | [5 empty] | 20 | 54 | 601 |  | 2020-09-16 09:00 | 9:00 | 20 | 54 | 601 |  |  | 2020-09-14 | B25398¦Courtroom 16-2, East OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-1B OTHER | [5 empty] | 20 | 55 | 604 |  | 2020-09-16 09:00 | 9:00 | 20 | 55 | 604 |  |  | 2020-09-14 | B25398¦Courtroom 16-1B OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-1A, North OTHER | [5 empty] | 20 | 56 | 607 |  | 2020-09-16 09:00 | 9:00 | 20 | 56 | 607 |  |  | 2020-09-14 | B25398¦Courtroom 16-1A, North OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 | [5 empty] | 23 | 58 | 512 |  | 2020-09-16 09:00 | 9:00 | 23 | 58 | 512 |  |  | 2020-09-14 | B14209¦Courtroom 1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-1A, South OTHER | [5 empty] | 20 | 56 | 610 |  | 2020-09-16 09:00 | 9:00 | 20 | 56 | 610 |  |  | 2020-09-14 | B25398¦Courtroom 16-1A, South OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-1A OTHER | [5 empty] | 21 | 54 | 623 |  | 2020-09-16 09:00 | 9:00 | 21 | 54 | 623 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-1A OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-3 OTHER | [5 empty] | 21 | 54 | 608 |  | 2020-09-16 09:00 | 9:00 | 21 | 54 | 608 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-3 OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Outdoors |  |  | 21 | 61 | [5 empty] | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20619¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Washrooms, 16th Floor OTHER | [5 empty] | 21 | 55 | 614 |  | 2020-09-16 09:00 | 9:00 | 21 | 55 | 614 |  |  | 2020-09-14 | B25398¦Corridor adj. to Washrooms, 16th Floor OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Courtroom 1-14 | [5 empty] | 22 | 57 | 513 |  | 2020-09-16 12:00 | 12:00 | 22 | 57 | 513 |  |  | 2020-09-14 | B20619¦Courtroom 1-14¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 16th Floor OTHER | [5 empty] | 21 | 55 | 620 |  | 2020-09-16 09:00 | 9:00 | 21 | 55 | 620 |  |  | 2020-09-14 | B25398¦Elevator Lobby, 16th Floor OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Women's Washroom, 16th Floor | [5 empty] | 21 | 53 | 610 |  | 2020-09-16 09:00 | 9:00 | 21 | 53 | 610 |  |  | 2020-09-14 | B25398¦OTHER Women's Washroom, 16th Floor¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Outdoors |  |  | 22 | 49 | 245 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20289¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 23 | 49 | 263 | judge | 2020-09-16 12:00 | 12:00 | 23 | 49 | 263 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 22 | 48 | 254 | public | 2020-09-16 12:00 | 12:00 | 22 | 48 | 254 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Mediation Centre, 16th Floor OTHER | [5 empty] | 20 | 56 | 628 |  | 2020-09-16 09:00 | 9:00 | 20 | 56 | 628 |  |  | 2020-09-14 | B25398¦Corridor adj. to Mediation Centre, 16th Floor OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 22 | 48 | 259 | judge | 2020-09-16 12:00 | 12:00 | 22 | 48 | 259 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 22 | 48 | 255 | public | 2020-09-16 12:00 | 12:00 | 22 | 48 | 255 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 300 | [5 empty] | 22 | 49 | 318 |  | 2020-09-16 12:00 | 12:00 | 22 | 49 | 318 |  |  | 2020-09-14 | B20289¦Courtroom 300¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Outdoors |  |  | 17 | 66 | 609 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B25398¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 301 | [5 empty] | 22 | 50 | 316 |  | 2020-09-16 12:00 | 12:00 | 22 | 50 | 316 |  |  | 2020-09-14 | B20289¦Courtroom 301¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 302 | [5 empty] | 23 | 49 | 342 |  | 2020-09-16 12:00 | 12:00 | 23 | 49 | 342 |  |  | 2020-09-14 | B20289¦Courtroom 302¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 303 | [5 empty] | 22 | 50 | 322 |  | 2020-09-16 12:00 | 12:00 | 22 | 50 | 322 |  |  | 2020-09-14 | B20289¦Courtroom 303¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Entry/Waiting | [5 empty] | 23 | 55 | 479 |  | 2020-09-16 12:00 | 12:00 | 23 | 55 | 479 |  |  | 2020-09-14 | B70510¦Entry/Waiting¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom A | [5 empty] | 22 | 50 | 331 |  | 2020-09-16 12:00 | 12:00 | 22 | 50 | 331 |  |  | 2020-09-14 | B20289¦Courtroom A¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom B | [5 empty] | 22 | 49 | 360 |  | 2020-09-16 12:00 | 12:00 | 22 | 49 | 360 |  |  | 2020-09-14 | B20289¦Courtroom B¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room A | [5 empty] | 23 | 54 | 527 |  | 2020-09-16 12:00 | 12:00 | 23 | 54 | 527 |  |  | 2020-09-14 | B70510¦Mediation Room A¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom C (North) | [5 empty] | 22 | 48 | 359 |  | 2020-09-16 12:00 | 12:00 | 22 | 48 | 359 |  |  | 2020-09-14 | B20289¦Courtroom C (North)¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom D | [5 empty] | 23 | 48 | 350 | in session; measurement taken outside courtroom | 2020-09-16 12:00 | 12:00 | 23 | 48 | 350 |  |  | 2020-09-14 | B20289¦Courtroom D¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Information Desk | [5 empty] | 23 | 54 | 463 |  | 2020-09-16 12:00 | 12:00 | 23 | 54 | 463 |  |  | 2020-09-14 | B70510¦Information Desk¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 1 | [5 empty] | 22 | 45 | 465 |  | 2020-09-16 12:00 | 12:00 | 22 | 45 | 465 |  |  | 2020-09-14 | B25602¦Courtroom 1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom E | [5 empty] | 23 | 48 | 414 | in session; measurement taken outside courtroom | 2020-09-16 12:00 | 12:00 | 23 | 48 | 414 |  |  | 2020-09-14 | B20289¦Courtroom E¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom F | [5 empty] | 23 | 49 | 399 | in session; measurement taken outside courtroom | 2020-09-16 12:00 | 12:00 | 23 | 49 | 399 |  |  | 2020-09-14 | B20289¦Courtroom F¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Lunch Room 454 | [5 empty] | 23 | 54 | 488 |  | 2020-09-16 12:00 | 12:00 | 23 | 54 | 488 |  |  | 2020-09-14 | B70510¦Lunch Room 454¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 2 | [5 empty] | 22 | 46 | 462 |  | 2020-09-16 12:00 | 12:00 | 22 | 46 | 462 |  |  | 2020-09-14 | B25602¦Courtroom 2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Copy Room 455 | [5 empty] | 23 | 54 | 455 |  | 2020-09-16 12:00 | 12:00 | 23 | 54 | 455 |  |  | 2020-09-14 | B70510¦Copy Room 455¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 3 | [5 empty] | 22 | 45 | 580 |  | 2020-09-16 12:00 | 12:00 | 22 | 45 | 580 |  |  | 2020-09-14 | B25602¦Courtroom 3¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 4 | [5 empty] | 22 | 45 | 635 |  | 2020-09-16 12:00 | 12:00 | 22 | 45 | 635 |  |  | 2020-09-14 | B25602¦Courtroom 4¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room B | [5 empty] | 23 | 55 | 768 |  | 2020-09-16 12:00 | 12:00 | 23 | 55 | 768 |  |  | 2020-09-14 | B70510¦Mediation Room B¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 5 | [5 empty] | 23 | 42 | 531 |  | 2020-09-16 12:00 | 12:00 | 23 | 42 | 531 |  |  | 2020-09-14 | B25602¦Courtroom 5¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 459 | [5 empty] | 23 | 54 | 489 |  | 2020-09-16 12:00 | 12:00 | 23 | 54 | 489 |  |  | 2020-09-14 | B70510¦Office 459¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 6 | [5 empty] | 22 | 43 | 437 |  | 2020-09-16 12:00 | 12:00 | 22 | 43 | 437 |  |  | 2020-09-14 | B25602¦Courtroom 6¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | office 467 | [5 empty] | 23 | 54 | 497 |  | 2020-09-16 12:00 | 12:00 | 23 | 54 | 497 |  |  | 2020-09-14 | B70510¦office 467¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 7 | [5 empty] | 23 | 41 | 413 |  | 2020-09-16 12:00 | 12:00 | 23 | 41 | 413 |  |  | 2020-09-14 | B25602¦Courtroom 7¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Outdoors |  |  | 19 | 68 | 393 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B12948¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 469 | [5 empty] | 23 | 55 | 689 |  | 2020-09-16 12:00 | 12:00 | 23 | 55 | 689 |  |  | 2020-09-14 | B70510¦Office 469¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 1 | [5 empty] | 21 | 60 | 414 |  | 2020-09-16 12:00 | 12:00 | 21 | 60 | 414 |  | caution | 2020-09-14 | B12948¦Courtroom 1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Outdoors |  |  | 22 | 45 | 672 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B25602¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Room 473 | [5 empty] | 22 | 55 | 484 |  | 2020-09-16 12:00 | 12:00 | 22 | 55 | 484 |  |  | 2020-09-14 | B70510¦Room 473¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 | [5 empty] | 21 | 58 | 440 |  | 2020-09-16 12:00 | 12:00 | 21 | 58 | 440 |  |  | 2020-09-14 | B12948¦Courtroom 4¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hall 475 or 466 | [5 empty] | 22 | 57 | 549 |  | 2020-09-16 12:00 | 12:00 | 22 | 57 | 549 |  |  | 2020-09-14 | B70510¦Hall 475 or 466¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Outdoors |  |  | 17 | 59 | 403 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B19652¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 | [5 empty] | 21 | 57 | 426 |  | 2020-09-16 12:00 | 12:00 | 21 | 57 | 426 |  |  | 2020-09-14 | B12948¦Courtroom 5¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 1 | [5 empty] | 22 | 55 | 461 |  | 2020-09-16 12:00 | 12:00 | 22 | 55 | 461 |  |  | 2020-09-14 | B70510¦Hearing Room 1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 6 | [5 empty] | 21 | 59 | 456 |  | 2020-09-16 12:00 | 12:00 | 21 | 59 | 456 |  |  | 2020-09-14 | B12948¦Courtroom 6¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Outdoors |  |  | 21 | 60 | 418 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B90838¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Cell Basement | [5 empty] | 21 | 60 | 577 |  | 2020-09-16 12:00 | 12:00 | 21 | 60 | 577 |  | caution | 2020-09-14 | B12948¦Cell Basement¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Courtroom 101 Courtroom 102 | [5 empty] | 21 | 54 | 422 |  | 2020-09-16 12:00 | 12:00 | 21 | 54 | 422 |  |  | 2020-09-14 | B90838¦Courtroom 101 Courtroom 102¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration Office Waiting Area | [5 empty] | 22 | 59 | 443 |  | 2020-09-16 12:00 | 12:00 | 22 | 59 | 443 |  |  | 2020-09-14 | B12948¦Administration Office Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 - waiting area | [5 empty] | 22 | 59 | 629 |  | 2020-09-16 12:00 | 12:00 | 22 | 59 | 629 |  |  | 2020-09-14 | B14209¦Courtroom 1 - waiting area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 | [5 empty] | 22 | 57 | 453 |  | 2020-09-16 12:00 | 12:00 | 22 | 57 | 453 |  |  | 2020-09-14 | B14209¦Courtroom 2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Center) | [5 empty] | 21 | 52 | 462 |  | 2020-09-16 12:00 | 12:00 | 21 | 52 | 462 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Center)¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Judge Dias) | [5 empty] | 21 | 52 | 448 |  | 2020-09-16 12:00 | 12:00 | 21 | 52 | 448 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Judge Dias)¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd fl lobby | [5 empty] | 21 | 41 | 695 |  | 2020-09-16 12:00 | 12:00 | 21 | 41 | 695 |  |  | 2020-09-14 | B20226¦2nd fl lobby¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 53 | 462 | Superior judges chamber | 2020-09-16 12:00 | 12:00 | 21 | 53 | 462 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 - waiting room | [5 empty] | 22 | 57 | 462 |  | 2020-09-16 12:00 | 12:00 | 22 | 57 | 462 |  |  | 2020-09-14 | B14209¦Courtroom 2 - waiting room¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 2 | [5 empty] | 21 | 45 | 706 |  | 2020-09-16 12:00 | 12:00 | 21 | 45 | 706 |  |  | 2020-09-14 | B20226¦Courtroom 2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 54 | 521 | 3rd floor stair landing | 2020-09-16 12:00 | 12:00 | 21 | 54 | 521 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room | [5 empty] | 22 | 56 | 415 |  | 2020-09-16 12:00 | 12:00 | 22 | 56 | 415 |  |  | 2020-09-14 | B14209¦Hearing Room¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 54 | 463 | 3rd floor Jury room | 2020-09-16 12:00 | 12:00 | 21 | 54 | 463 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room - Waiting area | [5 empty] | 22 | 57 | 545 |  | 2020-09-16 12:00 | 12:00 | 22 | 57 | 545 |  |  | 2020-09-14 | B14209¦Hearing Room - Waiting area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 54 | 442 | Justice McDonald chamber | 2020-09-16 12:00 | 12:00 | 21 | 54 | 442 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Meeting Rooms 1/2 | [5 empty] | 22 | 55 | 468 |  | 2020-09-16 12:00 | 12:00 | 22 | 55 | 468 |  |  | 2020-09-14 | B70510¦Vestibule at Meeting Rooms 1/2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 1 | [5 empty] | 21 | 43 | 690 |  | 2020-09-16 12:00 | 12:00 | 21 | 43 | 690 |  |  | 2020-09-14 | B20226¦Courtroom 1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room, Judge’s Chamber | [5 empty] | 22 | 55 | 428 |  | 2020-09-16 12:00 | 12:00 | 22 | 55 | 428 |  |  | 2020-09-14 | B14209¦Hearing Room, Judge’s Chamber¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 54 | 432 | Justice McDonald secretary | 2020-09-16 12:00 | 12:00 | 21 | 54 | 432 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Hearing Room 1 | [5 empty] | 22 | 56 | 468 |  | 2020-09-16 12:00 | 12:00 | 22 | 56 | 468 |  |  | 2020-09-14 | B70510¦Vestibule at Hearing Room 1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 21 | 45 | 713 |  | 2020-09-16 12:00 | 12:00 | 21 | 45 | 713 |  |  | 2020-09-14 | B20226¦2nd Floor Holding Cell¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration office | [5 empty] | 22 | 57 | 420 |  | 2020-09-16 12:00 | 12:00 | 22 | 57 | 420 |  |  | 2020-09-14 | B12948¦Administration office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 54 | 433 | SCJTC office | 2020-09-16 12:00 | 12:00 | 21 | 54 | 433 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Front Desk | [5 empty] | 22 | 56 | 511 |  | 2020-09-16 12:00 | 12:00 | 22 | 56 | 511 |  |  | 2020-09-14 | B14209¦Crown Attorney Front Desk¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 2 | [5 empty] | 22 | 56 | 460 |  | 2020-09-16 12:00 | 12:00 | 22 | 56 | 460 |  |  | 2020-09-14 | B70510¦Hearing Room 2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown attorney admin area | [5 empty] | 22 | 56 | 493 |  | 2020-09-16 12:00 | 12:00 | 22 | 56 | 493 |  |  | 2020-09-14 | B14209¦Crown attorney admin area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Crown attorney admin area | [5 empty] | 22 | 58 | 549 |  | 2020-09-16 12:00 | 12:00 | 22 | 58 | 549 |  |  | 2020-09-14 | B12948¦Crown attorney admin area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 439 | [5 empty] | 22 | 56 | 462 |  | 2020-09-16 12:00 | 12:00 | 22 | 56 | 462 |  |  | 2020-09-14 | B70510¦Office 439¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main entrance | [5 empty] | 21 | 58 | 434 |  | 2020-09-16 12:00 | 12:00 | 21 | 58 | 434 |  |  | 2020-09-14 | B12948¦Main entrance¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 53 | 439 | Visiting justice chamber | 2020-09-16 12:00 | 12:00 | 21 | 53 | 439 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | First Aid Desk | [5 empty] | 22 | 56 | 462 |  | 2020-09-16 12:00 | 12:00 | 22 | 56 | 462 |  |  | 2020-09-14 | B70510¦First Aid Desk¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main Entrance Waiting Area | [5 empty] | 22 | 59 | 440 |  | 2020-09-16 12:00 | 12:00 | 22 | 59 | 440 |  |  | 2020-09-14 | B12948¦Main Entrance Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 22 | 49 | 452 | North | 2020-09-16 09:00 | 9:00 | 22 | 49 | 452 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Court Room 1 Waiting Area | [5 empty] | 21 | 58 | 433 |  | 2020-09-16 12:00 | 12:00 | 21 | 58 | 433 |  |  | 2020-09-14 | B12948¦Court Room 1 Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 436 | [5 empty] | 23 | 55 | 517 |  | 2020-09-16 12:00 | 12:00 | 23 | 55 | 517 |  |  | 2020-09-14 | B70510¦Office 436¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Print Room | [5 empty] | 22 | 56 | 483 |  | 2020-09-16 12:00 | 12:00 | 22 | 56 | 483 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Print Room¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 Waiting Area | [5 empty] | 22 | 56 | 453 |  | 2020-09-16 12:00 | 12:00 | 22 | 56 | 453 |  |  | 2020-09-14 | B12948¦Courtroom 2 Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 3 | [5 empty] | 21 | 42 | 535 |  | 2020-09-16 12:00 | 12:00 | 21 | 42 | 535 |  |  | 2020-09-14 | B20226¦Courtroom 3¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 432 | [5 empty] | 23 | 54 | 480 |  | 2020-09-16 12:00 | 12:00 | 23 | 54 | 480 |  |  | 2020-09-14 | B70510¦Office 432¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 22 | 48 | 440 | South | 2020-09-16 09:00 | 9:00 | 22 | 48 | 440 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Center) | [5 empty] | 21 | 54 | 429 |  | 2020-09-16 12:00 | 12:00 | 21 | 54 | 429 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Center)¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Meeting Room (232) | [5 empty] | 22 | 57 | 468 |  | 2020-09-16 12:00 | 12:00 | 22 | 57 | 468 |  |  | 2020-09-14 | B14209¦Crown Attorney Meeting Room (232)¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 429 | [5 empty] | 23 | 54 | 479 |  | 2020-09-16 12:00 | 12:00 | 23 | 54 | 479 |  |  | 2020-09-14 | B70510¦Office 429¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 Waiting Area | [5 empty] | 22 | 57 | 460 |  | 2020-09-16 12:00 | 12:00 | 22 | 57 | 460 |  |  | 2020-09-14 | B12948¦Courtroom 3 Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 3 | [5 empty] | 24 | 52 | 323 |  | 2020-09-16 12:00 | 12:00 | 24 | 52 | 323 |  |  | 2020-09-14 | B24638¦Courtroom 3¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Judge Dias) | [5 empty] | 20 | 53 | 427 |  | 2020-09-16 12:00 | 12:00 | 20 | 53 | 427 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Judge Dias)¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Main entrance | [5 empty] | 22 | 47 | 477 |  | 2020-09-16 09:00 | 9:00 | 22 | 47 | 477 |  |  | 2020-09-14 | B20979¦Main entrance¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 Waiting Area | [5 empty] | 22 | 57 | 438 |  | 2020-09-16 12:00 | 12:00 | 22 | 57 | 438 |  |  | 2020-09-14 | B12948¦Courtroom 5 Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 427 | [5 empty] | 23 | 54 | 508 |  | 2020-09-16 12:00 | 12:00 | 23 | 54 | 508 |  |  | 2020-09-14 | B70510¦Office 427¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 Waiting Area | [5 empty] | 21 | 54 | 440 |  | 2020-09-16 12:00 | 12:00 | 21 | 54 | 440 |  |  | 2020-09-14 | B19652¦Courtroom 2 Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Assistant Crown Attorney Office (236) | [5 empty] | 22 | 56 | 474 |  | 2020-09-16 12:00 | 12:00 | 22 | 56 | 474 |  |  | 2020-09-14 | B14209¦Assistant Crown Attorney Office (236)¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Outdoors |  |  | 16 | 8 | 420 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20226¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 22 | 46 | 442 | north | 2020-09-16 09:00 | 9:00 | 22 | 46 | 442 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mail Room | [5 empty] | 23 | 54 | 474 |  | 2020-09-16 12:00 | 12:00 | 23 | 54 | 474 |  |  | 2020-09-14 | B70510¦Mail Room¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Assistant Crown Attorney Office | [5 empty] | 22 | 56 | 461 |  | 2020-09-16 12:00 | 12:00 | 22 | 56 | 461 |  |  | 2020-09-14 | B14209¦Assistant Crown Attorney Office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Center) | [5 empty] | 21 | 50 | 470 |  | 2020-09-16 12:00 | 12:00 | 21 | 50 | 470 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Center)¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 22 | 46 | 440 | south | 2020-09-16 09:00 | 9:00 | 22 | 46 | 440 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Judge Dias) | [5 empty] | 21 | 52 | 478 |  | 2020-09-16 12:00 | 12:00 | 21 | 52 | 478 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Judge Dias)¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 and 6 Waiting Area | [5 empty] | 22 | 57 | 422 |  | 2020-09-16 12:00 | 12:00 | 22 | 57 | 422 |  |  | 2020-09-14 | B12948¦Courtroom 4 and 6 Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 420 | [5 empty] | 23 | 54 | 500 |  | 2020-09-16 15:00 | 15:00 | 23 | 54 | 500 |  |  | 2020-09-14 | B70510¦Office 420¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 307 | [5 empty] | 22 | 46 | 470 | north | 2020-09-16 09:00 | 9:00 | 22 | 46 | 470 |  |  | 2020-09-14 | B20979¦Courtroom 307¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Lobby | [5 empty] | 22 | 56 | 490 |  | 2020-09-16 12:00 | 12:00 | 22 | 56 | 490 |  |  | 2020-09-14 | B14209¦Court Admin Office Lobby¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Outdoors |  |  | 14 | 20 | 398 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70050¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 418 | [5 empty] | 23 | 54 | 475 |  | 2020-09-16 12:00 | 12:00 | 23 | 54 | 475 |  |  | 2020-09-14 | B70510¦Office 418¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 51 | 528 |  | 2020-09-16 12:00 | 12:00 | 21 | 51 | 528 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | courtroom 307 | [5 empty] | 22 | 46 | 451 | south | 2020-09-16 09:00 | 9:00 | 22 | 46 | 451 |  |  | 2020-09-14 | B20979¦courtroom 307¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Legal Aid Ontario | [5 empty] | 23 | 47 | 447 |  | 2020-09-16 09:00 | 9:00 | 23 | 47 | 447 |  |  | 2020-09-14 | B20016¦Legal Aid Ontario¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | File Room | [5 empty] | 23 | 54 | 462 |  | 2020-09-16 12:00 | 12:00 | 23 | 54 | 462 |  |  | 2020-09-14 | B70510¦File Room¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 1 | [5 empty] | 23 | 53 | 350 |  | 2020-09-16 12:00 | 12:00 | 23 | 53 | 350 |  |  | 2020-09-14 | B24638¦Courtroom 1¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel Waiting Area | [5 empty] | 22 | 47 | 482 |  | 2020-09-16 09:00 | 9:00 | 22 | 47 | 482 |  |  | 2020-09-14 | B20016¦Duty Counsel Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 51 | 422 | south | 2020-09-16 09:00 | 9:00 | 22 | 51 | 422 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 50 | 458 | Council chamber dias | 2020-09-16 12:00 | 12:00 | 21 | 50 | 458 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel | [5 empty] | 22 | 46 | 438 |  | 2020-09-16 09:00 | 9:00 | 22 | 46 | 438 |  |  | 2020-09-14 | B20016¦Duty Counsel¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Main Lobby | [5 empty] | 20 |  | 513 |  | 2020-09-16 12:00 | 12:00 | 20 |  | 513 |  |  | 2020-09-14 | B70050¦Main Lobby¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Cubicles | [5 empty] | 22 | 57 | 505 |  | 2020-09-16 12:00 | 12:00 | 22 | 57 | 505 |  |  | 2020-09-14 | B14209¦Court Admin Office Cubicles¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 51 | 405 | north | 2020-09-16 09:00 | 9:00 | 22 | 51 | 405 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 1 | [5 empty] | 20 | 21 | 496 |  | 2020-09-16 12:00 | 12:00 | 20 | 21 | 496 |  | low | 2020-09-14 | B70050¦Courtroom 1¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lobby Courtroom 1 - 2 | [5 empty] | 22 | 48 | 457 |  | 2020-09-16 09:00 | 9:00 | 22 | 48 | 457 |  |  | 2020-09-14 | B20016¦Lobby Courtroom 1 - 2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Basement cells - hallway | [5 empty] | 23 | 51 | 530 |  | 2020-09-16 09:00 | 9:00 | 23 | 51 | 530 |  |  | 2020-09-14 | B20979¦Basement cells - hallway¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 50 | 442 | Council chamber center | 2020-09-16 12:00 | 12:00 | 21 | 50 | 442 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Outdoors |  |  | 23 | 54 | 304 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B24638¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Health Room | [5 empty] | 22 | 54 | 462 |  | 2020-09-16 12:00 | 12:00 | 22 | 54 | 462 |  |  | 2020-09-14 | B70510¦Health Room¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | hallway by 302 | [5 empty] | 22 | 46 | 451 |  | 2020-09-16 09:00 | 9:00 | 22 | 46 | 451 |  |  | 2020-09-14 | B20979¦hallway by 302¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 20 | 27 | 530 |  | 2020-09-16 12:00 | 12:00 | 20 | 27 | 530 |  | low | 2020-09-14 | B70050¦2nd Floor Holding Cell¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 | [5 empty] | 22 | 55 | 539 |  | 2020-09-16 12:00 | 12:00 | 22 | 55 | 539 |  |  | 2020-09-14 | B70510¦Hearing Room 3¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Intake Court | [5 empty] | 23 | 52 | 457 |  | 2020-09-16 12:00 | 12:00 | 23 | 52 | 457 |  |  | 2020-09-14 | B14209¦Intake Court¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Main Lobby | [5 empty] | 22 | 49 | 539 |  | 2020-09-16 09:00 | 9:00 | 22 | 49 | 539 |  |  | 2020-09-14 | B20016¦Main Lobby¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 2nd Floor Lunchroom | [5 empty] | 20 | 51 | 484 |  | 2020-09-16 12:00 | 12:00 | 20 | 51 | 484 |  |  | 2020-09-14 | B19652¦2nd Floor Lunchroom¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 Waiting Area | [5 empty] | 22 | 54 | 529 |  | 2020-09-16 12:00 | 12:00 | 22 | 54 | 529 |  |  | 2020-09-14 | B70510¦Hearing Room 3 Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | hallway by 307 | [5 empty] | 22 | 47 | 445 |  | 2020-09-16 09:00 | 9:00 | 22 | 47 | 445 |  |  | 2020-09-14 | B20979¦hallway by 307¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lower Hallway | [5 empty] | 22 | 49 | 480 |  | 2020-09-16 09:00 | 9:00 | 22 | 49 | 480 |  |  | 2020-09-14 | B20016¦Lower Hallway¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 51 | 501 | 2nd floor stairs landing | 2020-09-16 12:00 | 12:00 | 21 | 51 | 501 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Elevator Lobby | [5 empty] | 22 | 55 | 469 |  | 2020-09-16 12:00 | 12:00 | 22 | 55 | 469 |  |  | 2020-09-14 | B70510¦Elevator Lobby¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Yannick Bedard Office - 2nd Floor | [5 empty] | 22 | 21 | 674 |  | 2020-09-16 12:00 | 12:00 | 22 | 21 | 674 |  | low | 2020-09-14 | B70050¦Yannick Bedard Office - 2nd Floor¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Holding Cell corridor | [5 empty] | 23 | 55 | 496 |  | 2020-09-16 12:00 | 12:00 | 23 | 55 | 496 |  |  | 2020-09-14 | B14209¦Holding Cell corridor¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 21 | 47 | 461 | north | 2020-09-16 09:00 | 9:00 | 21 | 47 | 461 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 20 | 51 | 502 | Court services kitchenette | 2020-09-16 12:00 | 12:00 | 20 | 51 | 502 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 2 | [5 empty] | 21 | 33 | 545 |  | 2020-09-16 12:00 | 12:00 | 21 | 33 | 545 |  | low | 2020-09-14 | B70050¦Courtroom 2¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 22 | 46 | 428 |  | 2020-09-16 09:00 | 9:00 | 22 | 46 | 428 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 51 | 730 | Court service north | 2020-09-16 12:00 | 12:00 | 21 | 51 | 730 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | OTHER | [5 empty] | 22 | 49 | 472 | Courtroom 1-2-3 | 2020-09-16 09:00 | 9:00 | 22 | 49 | 472 |  |  | 2020-09-14 | B20016¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | police office | [5 empty] | 22 | 49 | 565 |  | 2020-09-16 09:00 | 9:00 | 22 | 49 | 565 |  |  | 2020-09-14 | B20979¦police office¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 51 | 510 | Court service south | 2020-09-16 12:00 | 12:00 | 21 | 51 | 510 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | outside | [5 empty] | 20 | 53 | 364 |  | 2020-09-16 09:00 | 9:00 | 20 | 53 | 364 |  |  | 2020-09-14 | B20979¦outside¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation | [5 empty] | 21 | 50 | 484 |  | 2020-09-16 12:00 | 12:00 | 21 | 50 | 484 |  |  | 2020-09-14 | B20016¦Family Mediation¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Level 1 Corridor by room 103 | [5 empty] | 23 | 53 | 501 |  | 2020-09-16 12:00 | 12:00 | 23 | 53 | 501 |  |  | 2020-09-14 | B14209¦Level 1 Corridor by room 103¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation Across Stairs | [5 empty] | 20 | 53 | 503 |  | 2020-09-16 09:00 | 9:00 | 20 | 53 | 503 |  |  | 2020-09-14 | B20016¦Family Mediation Across Stairs¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 51 | 610 | Court services entrance vestibule | 2020-09-16 12:00 | 12:00 | 21 | 51 | 610 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Main entrance | [5 empty] | 22 | 43 | 483 |  | 2020-09-16 12:00 | 12:00 | 22 | 43 | 483 |  |  | 2020-09-14 | B20979¦Main entrance¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd fl lobby | [5 empty] | 20 | 30 | 586 |  | 2020-09-16 12:00 | 12:00 | 20 | 30 | 586 |  | low | 2020-09-14 | B70050¦2nd fl lobby¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Police Court Bureau | [5 empty] | 21 | 41 | 440 |  | 2020-09-16 09:00 | 9:00 | 21 | 41 | 440 |  |  | 2020-09-14 | B19523¦Police Court Bureau¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 51 | 512 | 1st floor stair landing | 2020-09-16 12:00 | 12:00 | 21 | 51 | 512 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 23 | 45 | 461 |  | 2020-09-16 12:00 | 12:00 | 23 | 45 | 461 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 Waiting Area | [5 empty] | 21 | 41 | 439 |  | 2020-09-16 09:00 | 9:00 | 21 | 41 | 439 |  |  | 2020-09-14 | B19523¦Courtroom 4 Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Library | [5 empty] | 22 | 55 | 471 |  | 2020-09-16 12:00 | 12:00 | 22 | 55 | 471 |  |  | 2020-09-14 | B14209¦Library¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 | [5 empty] | 21 | 41 | 409 |  | 2020-09-16 09:00 | 9:00 | 21 | 41 | 409 |  |  | 2020-09-14 | B19523¦Courtroom 4¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 23 | 45 | 455 | south | 2020-09-16 12:00 | 12:00 | 23 | 45 | 455 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 41 | 448 |  | 2020-09-16 09:00 | 9:00 | 20 | 41 | 448 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Law Library Meeting Room (028B) | [5 empty] | 23 | 55 | 536 |  | 2020-09-16 12:00 | 12:00 | 23 | 55 | 536 |  |  | 2020-09-14 | B14209¦Law Library Meeting Room (028B)¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 22 | 45 | 479 | north | 2020-09-16 12:00 | 12:00 | 22 | 45 | 479 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 42 | 432 |  | 2020-09-16 09:00 | 9:00 | 20 | 42 | 432 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 22 | 45 | 487 | south | 2020-09-16 12:00 | 12:00 | 22 | 45 | 487 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 42 | 428 |  | 2020-09-16 09:00 | 9:00 | 19 | 42 | 428 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Lunch Room | [5 empty] | 22 | 54 | 465 |  | 2020-09-16 12:00 | 12:00 | 22 | 54 | 465 |  |  | 2020-09-14 | B14209¦Lunch Room¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 307 | [5 empty] | 22 | 46 | 610 | north | 2020-09-16 12:00 | 12:00 | 22 | 46 | 610 |  |  | 2020-09-14 | B20979¦Courtroom 307¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Jury Room | [5 empty] | 19 | 43 | 413 |  | 2020-09-16 09:00 | 9:00 | 19 | 43 | 413 |  |  | 2020-09-14 | B19523¦Jury Room¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | courtroom 307 | [5 empty] | 22 | 46 | 631 | south | 2020-09-16 12:00 | 12:00 | 22 | 46 | 631 |  |  | 2020-09-14 | B20979¦courtroom 307¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Entrance by Stair G | [5 empty] | 23 | 57 | 496 |  | 2020-09-16 12:00 | 12:00 | 23 | 57 | 496 |  |  | 2020-09-14 | B14209¦Entrance by Stair G¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 48 | 417 | south | 2020-09-16 12:00 | 12:00 | 22 | 48 | 417 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Ontario Court | [5 empty] | 20 | 42 | 418 |  | 2020-09-16 09:00 | 9:00 | 20 | 42 | 418 |  |  | 2020-09-14 | B19523¦Ontario Court¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 48 | 415 | north | 2020-09-16 12:00 | 12:00 | 22 | 48 | 415 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Judicial Library | [5 empty] | 21 | 41 | 426 |  | 2020-09-16 09:00 | 9:00 | 21 | 41 | 426 |  |  | 2020-09-14 | B19523¦Judicial Library¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office North | [5 empty] | 23 | 43 | 550 |  | 2020-09-16 12:00 | 12:00 | 23 | 43 | 550 |  |  | 2020-09-14 | B14895¦Administration Office North¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Basement cells - hallway | [5 empty] | 23 | 46 | 397 |  | 2020-09-16 12:00 | 12:00 | 23 | 46 | 397 |  |  | 2020-09-14 | B20979¦Basement cells - hallway¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Main Floor Entrance Lobby | [5 empty] | 23 | 59 | 613 |  | 2020-09-16 12:00 | 12:00 | 23 | 59 | 613 |  |  | 2020-09-14 | B14209¦Main Floor Entrance Lobby¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 315 | [5 empty] | 21 | 40 | 409 |  | 2020-09-16 09:00 | 9:00 | 21 | 40 | 409 |  | caution | 2020-09-14 | B19523¦Office Room 315¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | hallway by 302 | [5 empty] | 22 | 45 | 459 |  | 2020-09-16 12:00 | 12:00 | 22 | 45 | 459 |  |  | 2020-09-14 | B20979¦hallway by 302¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 316 | [5 empty] | 21 | 40 | 413 |  | 2020-09-16 09:00 | 9:00 | 21 | 40 | 413 |  | caution | 2020-09-14 | B19523¦Office Room 316¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Outdoors |  |  | 22 | 58 | 392 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B14209¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 22 | 47 | 572 | north | 2020-09-16 12:00 | 12:00 | 22 | 47 | 572 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 317 | [5 empty] | 21 | 40 | 429 |  | 2020-09-16 09:00 | 9:00 | 21 | 40 | 429 |  | caution | 2020-09-14 | B19523¦Office Room 317¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | reception area | [5 empty] | 21 | 58 | 490 |  | 2020-09-16 09:00 | 9:00 | 21 | 58 | 490 |  |  | 2020-09-14 | B70003¦reception area¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 22 | 46 | 602 | south | 2020-09-16 12:00 | 12:00 | 22 | 46 | 602 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | reception area | [5 empty] | 21 | 58 | 490 |  | 2020-09-16 09:00 | 9:00 | 21 | 58 | 490 |  |  | 2020-09-14 | B70003¦reception area¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | police office | [5 empty] | 22 | 48 | 530 |  | 2020-09-16 12:00 | 12:00 | 22 | 48 | 530 |  |  | 2020-09-14 | B20979¦police office¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Front of main hallway | [5 empty] | 21 | 58 | 485 |  | 2020-09-16 09:00 | 9:00 | 21 | 58 | 485 |  |  | 2020-09-14 | B70003¦Front of main hallway¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | outside | [5 empty] | 23 | 49 | 361 |  | 2020-09-16 12:00 | 12:00 | 23 | 49 | 361 |  |  | 2020-09-14 | B20979¦outside¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 58 | 484 | Outside of 502 | 2020-09-16 09:00 | 9:00 | 21 | 58 | 484 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 20 | 58 | 461 | Public area | 2020-09-16 09:00 | 9:00 | 20 | 58 | 461 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 58 | 460 | Judge area | 2020-09-16 09:00 | 9:00 | 21 | 58 | 460 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 59 | 485 | Outside of 503 | 2020-09-16 09:00 | 9:00 | 20 | 59 | 485 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 59 | 480 | Public area | 2020-09-16 09:00 | 9:00 | 20 | 59 | 480 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 106 Courtroom 205 Courtroom 301 Courtroom 303 Courtroom 405 | [5 empty] | 21 | 50 | 461 |  | 2020-09-16 09:00 | 9:00 | 21 | 50 | 461 |  |  | 2020-09-14 | B20616¦Courtroom 106 Courtroom 205 Courtroom 301 Courtroom 303 Courtroom 405¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 59 | 487 | Judge area | 2020-09-16 09:00 | 9:00 | 20 | 59 | 487 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office South | [5 empty] | 23 | 41 | 715 |  | 2020-09-16 12:00 | 12:00 | 23 | 41 | 715 |  |  | 2020-09-14 | B14895¦Administration Office South¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 60 | 501 | Outside of 506 | 2020-09-16 09:00 | 9:00 | 20 | 60 | 501 |  | caution | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 204 Courtroom 302 Courtroom 404 | [5 empty] | 22 | 50 | 461 |  | 2020-09-16 09:00 | 9:00 | 22 | 50 | 461 |  |  | 2020-09-14 | B20616¦Courtroom 204 Courtroom 302 Courtroom 404¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 60 | 520 | Public area | 2020-09-16 09:00 | 9:00 | 20 | 60 | 520 |  | caution | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 60 | 511 | Judge area | 2020-09-16 09:00 | 9:00 | 20 | 60 | 511 |  | caution | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 107 Courtroom 108 | [5 empty] | 21 | 52 | 473 |  | 2020-09-16 09:00 | 9:00 | 21 | 52 | 473 |  |  | 2020-09-14 | B20616¦Courtroom 107 Courtroom 108¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 61 | 497 | Outside of 509 | 2020-09-16 09:00 | 9:00 | 20 | 61 | 497 |  | caution | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 60 | 490 | Public area | 2020-09-16 09:00 | 9:00 | 20 | 60 | 490 |  | caution | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 304 Courtroom 305 | [5 empty] | 22 | 51 | 558 |  | 2020-09-16 09:00 | 9:00 | 22 | 51 | 558 |  |  | 2020-09-14 | B20616¦Courtroom 304 Courtroom 305¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 60 | 483 | Judge area | 2020-09-16 09:00 | 9:00 | 20 | 60 | 483 |  | caution | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Main entrance | [5 empty] | 21 | 54 | 421 |  | 2020-09-16 09:00 | 9:00 | 21 | 54 | 421 |  |  | 2020-09-14 | B90636¦Main entrance¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 60 | 490 | Outside of 510 | 2020-09-16 09:00 | 9:00 | 20 | 60 | 490 |  | caution | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 60 | 480 | Public area | 2020-09-16 09:00 | 9:00 | 20 | 60 | 480 |  | caution | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 22 | 50 | 405 | north | 2020-09-16 09:00 | 9:00 | 22 | 50 | 405 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 100 Courtroom 200 Courtroom 202 Courtroom 203 Courtroom 403 | [5 empty] | 21 | 48 | 444 |  | 2020-09-16 12:00 | 12:00 | 21 | 48 | 444 |  |  | 2020-09-14 | B20616¦Courtroom 100 Courtroom 200 Courtroom 202 Courtroom 203 Courtroom 403¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 60 | 483 | Judge area | 2020-09-16 09:00 | 9:00 | 20 | 60 | 483 |  | caution | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 22 | 50 | 404 | south | 2020-09-16 09:00 | 9:00 | 22 | 50 | 404 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Back of main hallway | [5 empty] | 20 | 60 | 482 |  | 2020-09-16 09:00 | 9:00 | 20 | 60 | 482 |  | caution | 2020-09-14 | B70003¦Back of main hallway¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | elevator area | [5 empty] | 20 | 60 | 509 |  | 2020-09-16 09:00 | 9:00 | 20 | 60 | 509 |  | caution | 2020-09-14 | B70003¦elevator area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 vestibule | [5 empty] | 22 | 51 | 455 |  | 2020-09-16 09:00 | 9:00 | 22 | 51 | 455 |  |  | 2020-09-14 | B90636¦Courtroom 203 vestibule¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Outdoors |  |  | 18 | 69 | 410 |  |  |  | Outside of 444 Yonge St. | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70003¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 101 Courtroom 102 Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 201 Courtroom 401 Courtroom 402 | [5 empty] | 22 | 48 | 444 |  | 2020-09-16 12:00 | 12:00 | 22 | 48 | 444 |  |  | 2020-09-14 | B20616¦Courtroom 101 Courtroom 102 Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 201 Courtroom 401 Courtroom 402¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 22 | 50 | 444 | entrance | 2020-09-16 09:00 | 9:00 | 22 | 50 | 444 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | second floor lobby | [5 empty] | 22 | 49 | 412 |  | 2020-09-16 09:00 | 9:00 | 22 | 49 | 412 |  |  | 2020-09-14 | B90636¦second floor lobby¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | third floor lobby | [5 empty] | 22 | 50 | 420 |  | 2020-09-16 09:00 | 9:00 | 22 | 50 | 420 |  |  | 2020-09-14 | B90636¦third floor lobby¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 204 Courtroom 205 Courtroom 301 Courtroom 303 Courtroom 404 Courtroom 405 | [5 empty] | 21 | 51 | 443 |  | 2020-09-16 12:00 | 12:00 | 21 | 51 | 443 |  |  | 2020-09-14 | B20616¦Courtroom 204 Courtroom 205 Courtroom 301 Courtroom 303 Courtroom 404 Courtroom 405¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 22 | 50 | 467 | west | 2020-09-16 09:00 | 9:00 | 22 | 50 | 467 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 106 | [5 empty] | 20 | 51 | 443 |  | 2020-09-16 12:00 | 12:00 | 20 | 51 | 443 |  |  | 2020-09-14 | B20616¦Courtroom 106¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 22 | 51 | 436 | east | 2020-09-16 09:00 | 9:00 | 22 | 51 | 436 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | fourth floor lobby | [5 empty] | 21 | 50 | 401 |  | 2020-09-16 09:00 | 9:00 | 21 | 50 | 401 |  |  | 2020-09-14 | B90636¦fourth floor lobby¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 302 | [5 empty] | 22 | 51 | 443 |  | 2020-09-16 12:00 | 12:00 | 22 | 51 | 443 |  |  | 2020-09-14 | B20616¦Courtroom 302¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Front Seating area | [5 empty] | 22 | 54 | 395 |  | 2020-09-16 12:00 | 12:00 | 22 | 54 | 395 |  |  | 2020-09-14 | B18359¦Front Seating area¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 211 | [5 empty] | 21 | 52 | 386 | north | 2020-09-16 09:00 | 9:00 | 21 | 52 | 386 |  |  | 2020-09-14 | B90636¦Courtroom 211¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Northwest corridor | [5 empty] | 22 | 54 | 391 |  | 2020-09-16 12:00 | 12:00 | 22 | 54 | 391 |  |  | 2020-09-14 | B18359¦Northwest corridor¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 22 | 55 | 389 | North side | 2020-09-16 12:00 | 12:00 | 22 | 55 | 389 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 211 | [5 empty] | 22 | 52 | 421 | south | 2020-09-16 09:00 | 9:00 | 22 | 52 | 421 |  |  | 2020-09-14 | B90636¦Courtroom 211¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 8 | [5 empty] | 23 | 54 | 438 |  | 2020-09-16 12:00 | 12:00 | 23 | 54 | 438 |  |  | 2020-09-14 | B25683¦Courtroom 8¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 22 | 54 | 391 | South side | 2020-09-16 12:00 | 12:00 | 22 | 54 | 391 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main entrance | [5 empty] | 22 | 47 | 550 |  | 2020-09-16 12:00 | 12:00 | 22 | 47 | 550 |  |  | 2020-09-14 | B14895¦Main entrance¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | hallway by 211 | [5 empty] | 21 | 50 | 398 |  | 2020-09-16 09:00 | 9:00 | 21 | 50 | 398 |  |  | 2020-09-14 | B90636¦hallway by 211¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 21 | 56 | 394 | North side | 2020-09-16 12:00 | 12:00 | 21 | 56 | 394 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 11 | [5 empty] | 23 | 54 | 438 |  | 2020-09-16 12:00 | 12:00 | 23 | 54 | 438 |  |  | 2020-09-14 | B25683¦Courtroom 11¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main Entrance Waiting Area | [5 empty] | 22 | 48 | 470 |  | 2020-09-16 12:00 | 12:00 | 22 | 48 | 470 |  |  | 2020-09-14 | B14895¦Main Entrance Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 21 | 56 | 397 | South side | 2020-09-16 12:00 | 12:00 | 21 | 56 | 397 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | hallway by 203 | [5 empty] | 21 | 53 | 443 |  | 2020-09-16 09:00 | 9:00 | 21 | 53 | 443 |  |  | 2020-09-14 | B90636¦hallway by 203¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 107 Courtroom 108 | [5 empty] | 21 | 51 | 464 |  | 2020-09-16 12:00 | 12:00 | 21 | 51 | 464 |  |  | 2020-09-14 | B20616¦Courtroom 107 Courtroom 108¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 9 | [5 empty] | 23 | 51 | 441 |  | 2020-09-16 12:00 | 12:00 | 23 | 51 | 441 |  |  | 2020-09-14 | B25683¦Courtroom 9¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | outside | [5 empty] | 20 | 53 | 364 |  | 2020-09-16 09:00 | 9:00 | 20 | 53 | 364 |  |  | 2020-09-14 | B90636¦outside¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom A | [5 empty] | 22 | 45 | 450 |  | 2020-09-16 12:00 | 12:00 | 22 | 45 | 450 |  |  | 2020-09-14 | B14895¦Courtroom A¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 21 | 57 | 394 | North side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 394 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Main entrance | [5 empty] | 23 | 44 | 428 |  | 2020-09-16 12:00 | 12:00 | 23 | 44 | 428 |  |  | 2020-09-14 | B90636¦Main entrance¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 21 | 57 | 400 | South side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 400 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 56 | 402 | North side | 2020-09-16 12:00 | 12:00 | 21 | 56 | 402 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom B | [5 empty] | 19 | 56 | 438 |  | 2020-09-16 12:00 | 12:00 | 19 | 56 | 438 |  |  | 2020-09-14 | B14895¦Courtroom B¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 23 | 44 | 404 | north | 2020-09-16 12:00 | 12:00 | 23 | 44 | 404 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 304 Courtroom 305 | [5 empty] | 22 | 51 | 567 |  | 2020-09-16 12:00 | 12:00 | 22 | 51 | 567 |  |  | 2020-09-14 | B20616¦Courtroom 304 Courtroom 305¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 55 | 400 | South side | 2020-09-16 12:00 | 12:00 | 21 | 55 | 400 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | 2nd Floor Waiting Area | [5 empty] | 23 | 44 | 541 |  | 2020-09-16 12:00 | 12:00 | 23 | 44 | 541 |  |  | 2020-09-14 | B14895¦2nd Floor Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 23 | 45 | 396 | south | 2020-09-16 12:00 | 12:00 | 23 | 45 | 396 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 56 | 397 | North side | 2020-09-16 12:00 | 12:00 | 21 | 56 | 397 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 22 | 38 | 453 | vestibule | 2020-09-16 12:00 | 12:00 | 22 | 38 | 453 |  | caution | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Assistant Crown Attorney Office | [5 empty] | 23 | 41 | 492 |  | 2020-09-16 12:00 | 12:00 | 23 | 41 | 492 |  |  | 2020-09-14 | B14895¦Assistant Crown Attorney Office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 56 | 389 | South side | 2020-09-16 12:00 | 12:00 | 21 | 56 | 389 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 22 | 39 | 463 | entrance | 2020-09-16 12:00 | 12:00 | 22 | 39 | 463 |  | caution | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 206 | [5 empty] | 21 | 57 | 393 | North side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 393 |  |  | 2020-09-14 | B70003¦Courtroom 206¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Waiting Area | [5 empty] | 24 | 43 | 520 |  | 2020-09-16 12:00 | 12:00 | 24 | 43 | 520 |  |  | 2020-09-14 | B14895¦Basement Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 21 | 57 | 390 | South side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 390 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 2nd fl lobby | [5 empty] | 22 | 46 | 416 |  | 2020-09-16 12:00 | 12:00 | 22 | 46 | 416 |  |  | 2020-09-14 | B90636¦2nd fl lobby¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Boardroom | [5 empty] | 24 | 42 | 500 |  | 2020-09-16 12:00 | 12:00 | 24 | 42 | 500 |  |  | 2020-09-14 | B14895¦Basement Boardroom¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 21 | 57 | 390 | North side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 390 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 3rd Floor Elevator Lobby | [5 empty] | 22 | 47 | 403 |  | 2020-09-16 12:00 | 12:00 | 22 | 47 | 403 |  |  | 2020-09-14 | B90636¦3rd Floor Elevator Lobby¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Male Holding Cell | [5 empty] | 24 | 40 | 456 |  | 2020-09-16 12:00 | 12:00 | 24 | 40 | 456 |  | caution | 2020-09-14 | B14895¦Male Holding Cell¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 21 | 57 | 397 | South side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 397 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 22 | 48 | 430 | west | 2020-09-16 12:00 | 12:00 | 22 | 48 | 430 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Female Holding Cell | [5 empty] | 24 | 41 | 452 |  | 2020-09-16 12:00 | 12:00 | 24 | 41 | 452 |  |  | 2020-09-14 | B14895¦Female Holding Cell¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 21 | 57 | 397 | North side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 397 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 22 | 48 | 436 | east | 2020-09-16 12:00 | 12:00 | 22 | 48 | 436 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Outdoors |  |  | 17 | 56 | 407 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B14895¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 21 | 57 | 399 | South side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 399 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 4th floor lobby | [5 empty] | 21 | 47 | 386 |  | 2020-09-16 12:00 | 12:00 | 21 | 47 | 386 |  |  | 2020-09-14 | B90636¦4th floor lobby¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 21 | 57 | 403 | North side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 403 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | courtroom 211 | [5 empty] | 21 | 49 | 372 | north | 2020-09-16 12:00 | 12:00 | 21 | 49 | 372 |  |  | 2020-09-14 | B90636¦courtroom 211¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 21 | 57 | 404 | South side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 404 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 211 | [5 empty] | 21 | 49 | 376 | south | 2020-09-16 12:00 | 12:00 | 21 | 49 | 376 |  |  | 2020-09-14 | B90636¦Courtroom 211¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Northeast corridor | [5 empty] | 21 | 56 | 399 |  | 2020-09-16 12:00 | 12:00 | 21 | 56 | 399 |  |  | 2020-09-14 | B18359¦Northeast corridor¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 21 | 57 | 394 | North side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 394 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | hallway by 211 | [5 empty] | 21 | 49 | 377 |  | 2020-09-16 12:00 | 12:00 | 21 | 49 | 377 |  |  | 2020-09-14 | B90636¦hallway by 211¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 21 | 57 | 393 | South side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 393 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-1 | [5 empty] | 22.4 | 53.7 | 684 |  | 2020-09-16 12:00 | 12:00 | 22.4 | 53.7 | 684 |  |  | 2020-09-14 | B10644¦Courtroom 2-1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 21 | 57 | 390 | North side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 390 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 22 | 49 | 450 | hallway in front of vestibule | 2020-09-16 12:00 | 12:00 | 22 | 49 | 450 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-3 | [5 empty] | 21.1 | 59.2 | 430 |  | 2020-09-16 12:00 | 12:00 | 21.1 | 59.2 | 430 |  |  | 2020-09-14 | B10644¦Courtroom 2-3¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 21 | 57 | 392 | South side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 392 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | outside | [5 empty] | 23 | 49 | 361 |  | 2020-09-16 12:00 | 12:00 | 23 | 49 | 361 |  |  | 2020-09-14 | B90636¦outside¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 21 | 57 | 396 | North side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 396 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-5 | [5 empty] | 22 | 56.9 | 400 |  | 2020-09-16 12:00 | 12:00 | 22 | 56.9 | 400 |  |  | 2020-09-14 | B10644¦Courtroom 2-5¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 21 | 57 | 393 | South side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 393 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 21 | 57 | 397 | North side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 397 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-7 | [5 empty] | 22.3 | 55.8 | 525 |  | 2020-09-16 12:00 | 12:00 | 22.3 | 55.8 | 525 |  |  | 2020-09-14 | B10644¦Courtroom 2-7¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 21 | 57 | 389 | South side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 389 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 21 | 57 | 398 | South side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 398 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-2 | [5 empty] | 21.1 | 57.9 | 545 |  | 2020-09-16 12:00 | 12:00 | 21.1 | 57.9 | 545 |  |  | 2020-09-14 | B10644¦Courtroom 2-2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 214 | [5 empty] | 21 | 58 | 396 | South side | 2020-09-16 12:00 | 12:00 | 21 | 58 | 396 |  |  | 2020-09-14 | B18359¦Courtroom 214¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 215 | [5 empty] | 21 | 57 | 395 | North side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 395 |  |  | 2020-09-14 | B18359¦Courtroom 215¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Outdoors |  |  | 14 | 53 | 468 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10000¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 3-2 | [5 empty] | 21.6 | 56.5 | 365 |  | 2020-09-16 12:00 | 12:00 | 21.6 | 56.5 | 365 |  |  | 2020-09-14 | B10644¦Courtroom 3-2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 215 | [5 empty] | 21 | 57 | 387 | South side | 2020-09-16 12:00 | 12:00 | 21 | 57 | 387 |  |  | 2020-09-14 | B18359¦Courtroom 215¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Outdoors |  |  | 14 | 49 | 487 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10000¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Outdoors |  |  | 20 | 60 | 381 |  |  |  | Outside of 15 Grosvenor Ave. | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B18359¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-1 | [5 empty] | 22.5 | 58.9 | 483 |  | 2020-09-16 12:00 | 12:00 | 22.5 | 58.9 | 483 |  |  | 2020-09-14 | B10644¦Courtroom 4-1¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Outdoors |  |  | 16 | 51 | 448 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10000¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 1 | [5 empty] | 21.6667 | 55 | 448 |  | 2020-09-16 09:00 | 9:00 | 21.6667 | 55 | 448 |  |  | 2020-09-14 | B10000¦Courtroom 1¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-2 | [5 empty] | 22.3 | 55 | 415 |  | 2020-09-16 12:00 | 12:00 | 22.3 | 55 | 415 |  |  | 2020-09-14 | B10644¦Courtroom 4-2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 1 | [5 empty] | 21.6667 | 53 | 458 |  | 2020-09-16 12:00 | 12:00 | 21.6667 | 53 | 458 |  |  | 2020-09-14 | B10000¦Courtroom 1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-9 | [5 empty] | 21.4 | 53.1 | 400 |  | 2020-09-16 12:00 | 12:00 | 21.4 | 53.1 | 400 |  |  | 2020-09-14 | B10644¦Courtroom 4-9¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 1 | [5 empty] | 21.6667 | 50 | 450 |  | 2020-09-16 15:00 | 15:00 | 21.6667 | 50 | 450 |  |  | 2020-09-14 | B10000¦Courtroom 1¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-3 | [5 empty] | 23.1 | 53.1 | 410 |  | 2020-09-16 12:00 | 12:00 | 23.1 | 53.1 | 410 |  |  | 2020-09-14 | B10644¦Courtroom 4-3¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 2 | [5 empty] | 23.8889 | 48 | 439 |  | 2020-09-16 09:00 | 9:00 | 23.8889 | 48 | 439 |  |  | 2020-09-14 | B10000¦Courtroom 2¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-7 | [5 empty] | 22.5 | 56.2 | 389 |  | 2020-09-16 12:00 | 12:00 | 22.5 | 56.2 | 389 |  |  | 2020-09-14 | B10644¦Courtroom 4-7¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 2 | [5 empty] | 23.3333 | 44 | 506 |  | 2020-09-16 12:00 | 12:00 | 23.3333 | 44 | 506 |  |  | 2020-09-14 | B10000¦Courtroom 2¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 2 | [5 empty] | 22.7778 | 42 | 422 |  | 2020-09-16 15:00 | 15:00 | 22.7778 | 42 | 422 |  |  | 2020-09-14 | B10000¦Courtroom 2¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-4 | [5 empty] | 22.3 | 58.1 | 510 |  | 2020-09-16 12:00 | 12:00 | 22.3 | 58.1 | 510 |  |  | 2020-09-14 | B10644¦Courtroom 4-4¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 3 | [5 empty] | 21.6667 | 51 | 428 |  | 2020-09-16 09:00 | 9:00 | 21.6667 | 51 | 428 |  |  | 2020-09-14 | B10000¦Courtroom 3¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 1 | [5 empty] | 22 | 46 | 454 |  | 2020-09-16 15:00 | 15:00 | 22 | 46 | 454 |  |  | 2020-09-14 | B25602¦Courtroom 1¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-5 | [5 empty] | 21.4 | 56.7 | 400 |  | 2020-09-16 12:00 | 12:00 | 21.4 | 56.7 | 400 |  |  | 2020-09-14 | B10644¦Courtroom 4-5¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 3 | [5 empty] | 21.6667 | 49 | 431 |  | 2020-09-16 12:00 | 12:00 | 21.6667 | 49 | 431 |  |  | 2020-09-14 | B10000¦Courtroom 3¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 | [5 empty] | 22 | 48 | 445 |  | 2020-09-16 15:00 | 15:00 | 22 | 48 | 445 |  |  | 2020-09-14 | B12948¦Courtroom 2¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Reception area | [5 empty] | 22 | 54 | 534 |  | 2020-09-16 12:00 | 12:00 | 22 | 54 | 534 |  |  | 2020-09-14 | B70003¦Reception area¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 3 | [5 empty] | 21.6667 | 46 | 429 |  | 2020-09-16 15:00 | 15:00 | 21.6667 | 46 | 429 |  |  | 2020-09-14 | B10000¦Courtroom 3¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-6 | [5 empty] | 22.6 | 57.9 | 392 |  | 2020-09-16 12:00 | 12:00 | 22.6 | 57.9 | 392 |  |  | 2020-09-14 | B10644¦Courtroom 4-6¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 4 | [5 empty] | 20.5556 | 40 | 454 |  | 2020-09-16 09:00 | 9:00 | 20.5556 | 40 | 454 |  | caution | 2020-09-14 | B10000¦Courtroom 4¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 3 | [5 empty] | 22 | 45 | 495 |  | 2020-09-16 15:00 | 15:00 | 22 | 45 | 495 |  |  | 2020-09-14 | B25602¦Courtroom 3¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 4 | [5 empty] | 22.7778 | 38 | 457 |  | 2020-09-16 12:00 | 12:00 | 22.7778 | 38 | 457 |  | caution | 2020-09-14 | B10000¦Courtroom 4¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 4 | [5 empty] | 22.7778 | 34 | 443 |  | 2020-09-16 15:00 | 15:00 | 22.7778 | 34 | 443 |  | low | 2020-09-14 | B10000¦Courtroom 4¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Front of Main Hallway | [5 empty] | 22 | 54 | 525 |  | 2020-09-16 12:00 | 12:00 | 22 | 54 | 525 |  |  | 2020-09-14 | B70003¦Front of Main Hallway¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 4 | [5 empty] | 23 | 46 | 651 |  | 2020-09-16 15:00 | 15:00 | 23 | 46 | 651 |  |  | 2020-09-14 | B25602¦Courtroom 4¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Superior Court | [5 empty] | 21 | 39 | 453 |  | 2020-09-16 09:00 | 9:00 | 21 | 39 | 453 |  | caution | 2020-09-14 | B19523¦Superior Court¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 55 | 521 | Outside of 502 | 2020-09-16 12:00 | 12:00 | 21 | 55 | 521 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 4 | [5 empty] | 22.2222 | 51 | 437 |  | 2020-09-16 09:00 | 9:00 | 22.2222 | 51 | 437 |  |  | 2020-09-14 | B10000¦Courtroom 4¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 5 | [5 empty] | 22 | 48 | 540 |  | 2020-09-16 15:00 | 15:00 | 22 | 48 | 540 |  |  | 2020-09-14 | B25602¦Courtroom 5¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 55 | 517 | Public area | 2020-09-16 12:00 | 12:00 | 21 | 55 | 517 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 5 | [5 empty] | 22.7778 | 50 | 458 |  | 2020-09-16 12:00 | 12:00 | 22.7778 | 50 | 458 |  |  | 2020-09-14 | B10000¦Courtroom 5¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 55 | 510 | Judge area | 2020-09-16 12:00 | 12:00 | 21 | 55 | 510 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 313 | [5 empty] | 21 | 40 | 470 |  | 2020-09-16 09:00 | 9:00 | 21 | 40 | 470 |  | caution | 2020-09-14 | B19523¦Office Room 313¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 5 | [5 empty] | 22.2222 | 49 | 454 |  | 2020-09-16 15:00 | 15:00 | 22.2222 | 49 | 454 |  |  | 2020-09-14 | B10000¦Courtroom 5¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 57 | 526 | Outside of 503 | 2020-09-16 12:00 | 12:00 | 21 | 57 | 526 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 6 | [5 empty] | 24 | 41 | 437 |  | 2020-09-16 15:00 | 15:00 | 24 | 41 | 437 |  |  | 2020-09-14 | B25602¦Courtroom 6¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 312 | [5 empty] | 21 | 39 | 431 |  | 2020-09-16 09:00 | 9:00 | 21 | 39 | 431 |  | caution | 2020-09-14 | B19523¦Office Room 312¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 57 | 535 | Public area | 2020-09-16 12:00 | 12:00 | 21 | 57 | 535 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-8 | [5 empty] | 23.4 | 54.6 | 380 |  | 2020-09-16 12:00 | 12:00 | 23.4 | 54.6 | 380 |  |  | 2020-09-14 | B10644¦Courtroom 4-8¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 6 | [5 empty] | 21.1111 | 51 | 437 |  | 2020-09-16 09:00 | 9:00 | 21.1111 | 51 | 437 |  |  | 2020-09-14 | B10000¦Courtroom 6¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 7 | [5 empty] | 22 | 44 | 425 |  | 2020-09-16 15:00 | 15:00 | 22 | 44 | 425 |  |  | 2020-09-14 | B25602¦Courtroom 7¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 57 | 544 | Judge area | 2020-09-16 12:00 | 12:00 | 21 | 57 | 544 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 310 | [5 empty] | 21 | 39 | 425 |  | 2020-09-16 09:00 | 9:00 | 21 | 39 | 425 |  | caution | 2020-09-14 | B19523¦Office Room 310¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-9 | [5 empty] | 21.5 | 55 | 401 |  | 2020-09-16 12:00 | 12:00 | 21.5 | 55 | 401 |  |  | 2020-09-14 | B10644¦Courtroom 4-9¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 21 | 58 | 532 | Outside of 506 | 2020-09-16 12:00 | 12:00 | 21 | 58 | 532 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 6 | [5 empty] | 21.1111 | 50 | 458 |  | 2020-09-16 12:00 | 12:00 | 21.1111 | 50 | 458 |  |  | 2020-09-14 | B10000¦Courtroom 6¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Law Association | [5 empty] | 21 | 39 | 414 |  | 2020-09-16 09:00 | 9:00 | 21 | 39 | 414 |  | caution | 2020-09-14 | B19523¦Law Association¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 21 | 58 | 515 | Public area | 2020-09-16 12:00 | 12:00 | 21 | 58 | 515 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Outdoors |  |  | 23 | 43 | 668 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B25602¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-10 | [5 empty] | 22.4 | 58.2 | 494 |  | 2020-09-16 12:00 | 12:00 | 22.4 | 58.2 | 494 |  |  | 2020-09-14 | B10644¦Courtroom 4-10¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 6 | [5 empty] | 21.6667 | 49 | 454 |  | 2020-09-16 15:00 | 15:00 | 21.6667 | 49 | 454 |  |  | 2020-09-14 | B10000¦Courtroom 6¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 58 | 513 | Judge area | 2020-09-16 12:00 | 12:00 | 20 | 58 | 513 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 101 | [5 empty] | 20 | 52 |  |  | 2020-09-16 15:00 | 15:00 | 20 | 52 |  |  |  | 2020-09-14 | B20080¦Courtroom 101¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 7 | [5 empty] | 21.1111 | 49 | 430 |  | 2020-09-16 09:00 | 9:00 | 21.1111 | 49 | 430 |  |  | 2020-09-14 | B10000¦Courtroom 7¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22.5 | 53.2 | 437 |  | 2020-09-16 12:00 | 12:00 | 22.5 | 53.2 | 437 |  |  | 2020-09-14 | B10644¦Courtroom 5-1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 59 | 520 | Outside of 509 | 2020-09-16 12:00 | 12:00 | 20 | 59 | 520 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 201 | [5 empty] | 22 | 51 | 468 |  | 2020-09-16 15:00 | 15:00 | 22 | 51 | 468 |  |  | 2020-09-14 | B20080¦Courtroom 201¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 7 | [5 empty] | 22.2222 | 44 | 509 |  | 2020-09-16 12:00 | 12:00 | 22.2222 | 44 | 509 |  |  | 2020-09-14 | B10000¦Courtroom 7¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 59 | 522 | Public area | 2020-09-16 12:00 | 12:00 | 20 | 59 | 522 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Main Lobby | [5 empty] | 19 | 46 | 408 |  | 2020-09-16 09:00 | 9:00 | 19 | 46 | 408 |  |  | 2020-09-14 | B19523¦Main Lobby¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 202 | [5 empty] | 22 | 51 | 469 |  | 2020-09-16 15:00 | 15:00 | 22 | 51 | 469 |  |  | 2020-09-14 | B20080¦Courtroom 202¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 7 | [5 empty] | 22.2222 | 46 | 453 |  | 2020-09-16 15:00 | 15:00 | 22.2222 | 46 | 453 |  |  | 2020-09-14 | B10000¦Courtroom 7¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Holding Cell | [5 empty] | 20 | 43 | 408 |  | 2020-09-16 09:00 | 9:00 | 20 | 43 | 408 |  |  | 2020-09-14 | B19523¦Holding Cell¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-1 | [5 empty] | 22.1 | 56.7 | 384 |  | 2020-09-16 12:00 | 12:00 | 22.1 | 56.7 | 384 |  |  | 2020-09-14 | B10644¦Courtroom 6-1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 59 | 510 | Judge area | 2020-09-16 12:00 | 12:00 | 20 | 59 | 510 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 1 | [5 empty] | 21 | 42 | 407 |  | 2020-09-16 09:00 | 9:00 | 21 | 42 | 407 |  |  | 2020-09-14 | B19523¦Courtroom 1¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 301 | [5 empty] | 22 | 51 | 502 |  | 2020-09-16 15:00 | 15:00 | 22 | 51 | 502 |  |  | 2020-09-14 | B20080¦Courtroom 301¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 59 | 524 | Outside of 510 | 2020-09-16 12:00 | 12:00 | 20 | 59 | 524 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 8 | [5 empty] | 22.2222 | 48 | 439 |  | 2020-09-16 09:00 | 9:00 | 22.2222 | 48 | 439 |  |  | 2020-09-14 | B10000¦Courtroom 8¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-3 | [5 empty] | 22.5 | 56.3 | 558 |  | 2020-09-16 12:00 | 12:00 | 22.5 | 56.3 | 558 |  |  | 2020-09-14 | B10644¦Courtroom 6-3¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 59 | 522 | Public area | 2020-09-16 12:00 | 12:00 | 20 | 59 | 522 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 302 | [5 empty] | 23 | 51 | 544 |  | 2020-09-16 15:00 | 15:00 | 23 | 51 | 544 |  |  | 2020-09-14 | B20080¦Courtroom 302¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Court Services | [5 empty] | 21 | 40 | 410 |  | 2020-09-16 09:00 | 9:00 | 21 | 40 | 410 |  | caution | 2020-09-14 | B19523¦Court Services¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 59 | 533 | Judge area | 2020-09-16 12:00 | 12:00 | 20 | 59 | 533 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 8 | [5 empty] | 21.6667 | 44 | 506 |  | 2020-09-16 12:00 | 12:00 | 21.6667 | 44 | 506 |  |  | 2020-09-14 | B10000¦Courtroom 8¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | JP Office | [5 empty] | 20 | 41 | 408 |  | 2020-09-16 09:00 | 9:00 | 20 | 41 | 408 |  |  | 2020-09-14 | B19523¦JP Office¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Back of main hallway | [5 empty] | 20 | 59 | 521 |  | 2020-09-16 12:00 | 12:00 | 20 | 59 | 521 |  |  | 2020-09-14 | B70003¦Back of main hallway¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | OPP Office | [5 empty] | 20 | 41 | 404 |  | 2020-09-16 09:00 | 9:00 | 20 | 41 | 404 |  |  | 2020-09-14 | B19523¦OPP Office¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Elevator area | [5 empty] | 20 | 59 | 548 |  | 2020-09-16 12:00 | 12:00 | 20 | 59 | 548 |  |  | 2020-09-14 | B70003¦Elevator area¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 8 | [5 empty] | 21.1111 | 42 | 422 |  | 2020-09-16 15:00 | 15:00 | 21.1111 | 42 | 422 |  |  | 2020-09-14 | B10000¦Courtroom 8¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Crown Attorney Office | [5 empty] | 21 | 41 | 406 |  | 2020-09-16 09:00 | 9:00 | 21 | 41 | 406 |  |  | 2020-09-14 | B19523¦Crown Attorney Office¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Outdoors |  |  | 21 | 59 | 392 |  |  |  | Outside of 444 Yonge St. | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70003¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 41 | 422 |  | 2020-09-16 09:00 | 9:00 | 22 | 41 | 422 |  |  | 2020-09-14 | B19523¦VWAP Office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 9 | [5 empty] | 21.1111 | 51 | 437 |  | 2020-09-16 09:00 | 9:00 | 21.1111 | 51 | 437 |  |  | 2020-09-14 | B10000¦Courtroom 9¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 303 | [5 empty] | 22 | 51 | 475 |  | 2020-09-16 15:00 | 15:00 | 22 | 51 | 475 |  |  | 2020-09-14 | B20080¦Courtroom 303¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 39 | 425 |  | 2020-09-16 09:00 | 9:00 | 22 | 39 | 425 |  | caution | 2020-09-14 | B19523¦VWAP Office¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd fl lobby | [5 empty] | 21 | 40 | 670 |  | 2020-09-16 15:00 | 15:00 | 21 | 40 | 670 |  | caution | 2020-09-14 | B20226¦2nd fl lobby¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 9 | [5 empty] | 21.1111 | 50 | 458 |  | 2020-09-16 12:00 | 12:00 | 21.1111 | 50 | 458 |  |  | 2020-09-14 | B10000¦Courtroom 9¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 9 | [5 empty] | 21.1111 | 49 | 454 |  | 2020-09-16 15:00 | 15:00 | 21.1111 | 49 | 454 |  |  | 2020-09-14 | B10000¦Courtroom 9¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Outdoors |  |  | 22 | 56 | 461 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20080¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 5 | [5 empty] | 20 | 40 | 417 |  | 2020-09-16 09:00 | 9:00 | 20 | 40 | 417 |  | caution | 2020-09-14 | B19523¦Courtroom 5¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Outdoors |  |  | 21 | 58 | 430 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70510¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 2 | [5 empty] | 21 | 43 | 601 |  | 2020-09-16 15:00 | 15:00 | 21 | 43 | 601 |  |  | 2020-09-14 | B20226¦Courtroom 2¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Remote Testimony Room | [5 empty] | 20 | 41 | 412 |  | 2020-09-16 09:00 | 9:00 | 20 | 41 | 412 |  |  | 2020-09-14 | B19523¦Remote Testimony Room¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Conference Room 2 | [5 empty] | 20 | 40 | 420 |  | 2020-09-16 09:00 | 9:00 | 20 | 40 | 420 |  | caution | 2020-09-14 | B19523¦Conference Room 2¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | entry/waiting | [5 empty] | 23 | 54 | 470 |  | 2020-09-16 15:00 | 15:00 | 23 | 54 | 470 |  |  | 2020-09-14 | B70510¦entry/waiting¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 | [5 empty] | 21 | 40 | 411 |  | 2020-09-16 09:00 | 9:00 | 21 | 40 | 411 |  | caution | 2020-09-14 | B19523¦Courtroom 3¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 1 | [5 empty] | 21 | 45 | 638 |  | 2020-09-16 15:00 | 15:00 | 21 | 45 | 638 |  |  | 2020-09-14 | B20226¦Courtroom 1¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 Waiting Area | [5 empty] | 21 | 40 | 424 |  | 2020-09-16 09:00 | 9:00 | 21 | 40 | 424 |  | caution | 2020-09-14 | B19523¦Courtroom 3 Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room A | [5 empty] | 23 | 53 | 450 |  | 2020-09-16 12:00 | 12:00 | 23 | 53 | 450 |  |  | 2020-09-14 | B70510¦Mediation Room A¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 21 | 40 | 422 |  | 2020-09-16 09:00 | 9:00 | 21 | 40 | 422 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 21 | 47 | 641 |  | 2020-09-16 15:00 | 15:00 | 21 | 47 | 641 |  |  | 2020-09-14 | B20226¦2nd Floor Holding Cell¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Information Desk | [5 empty] | 23 | 53 | 457 |  | 2020-09-16 12:00 | 12:00 | 23 | 53 | 457 |  |  | 2020-09-14 | B70510¦Information Desk¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 40 | 435 |  | 2020-09-16 09:00 | 9:00 | 20 | 40 | 435 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 41 | 447 |  | 2020-09-16 09:00 | 9:00 | 20 | 41 | 447 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Lunch Room 454 | [5 empty] | 23 | 53 | 439 |  | 2020-09-16 15:00 | 15:00 | 23 | 53 | 439 |  |  | 2020-09-14 | B70510¦Lunch Room 454¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B20893 | B20893 - 75 Mulcaster St. - Barrie | Courtroom 7,8,9 | [5 empty] | 21.7 | 39 | 438 |  | 2020-09-16 09:00 | 9:00 | 21.7 | 39 | 438 |  | caution | 2020-09-14 | B20893¦Courtroom 7,8,9¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 2 | [5 empty] | 20 | 41 | 416 |  | 2020-09-16 09:00 | 9:00 | 20 | 41 | 416 |  |  | 2020-09-14 | B19523¦Courtroom 2¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 3 | [5 empty] | 22 | 44 | 560 |  | 2020-09-16 15:00 | 15:00 | 22 | 44 | 560 |  |  | 2020-09-14 | B20226¦Courtroom 3¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Copy Room 455 | [5 empty] | 23 | 53 | 437 |  | 2020-09-16 15:00 | 15:00 | 23 | 53 | 437 |  |  | 2020-09-14 | B70510¦Copy Room 455¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B92347 | B92347 - 75 Mulcaster Street - Barrie | Courtroom 15 | [5 empty] | 20.7 | 46 | 415 |  | 2020-09-16 09:00 | 9:00 | 20.7 | 46 | 415 |  |  | 2020-09-14 | B92347¦Courtroom 15¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Outdoors |  |  | 13 | 10 | 399 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20226¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room B | [5 empty] | 23 | 54 | 470 |  | 2020-09-16 15:00 | 15:00 | 23 | 54 | 470 |  |  | 2020-09-14 | B70510¦Mediation Room B¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Outdoors |  |  | 24 | 54 | 397 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B12948¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B20893 | B20893 - 75 Mulcaster St. - Barrie | Courtroom 7,8,9 | [5 empty] | 21.7 | 41 | 504 |  | 2020-09-16 12:00 | 12:00 | 21.7 | 41 | 504 |  |  | 2020-09-14 | B20893¦Courtroom 7,8,9¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 459 | [5 empty] | 23 | 54 | 477 |  | 2020-09-16 15:00 | 15:00 | 23 | 54 | 477 |  |  | 2020-09-14 | B70510¦Office 459¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 1 | [5 empty] | 23 | 52 | 448 |  | 2020-09-16 15:00 | 15:00 | 23 | 52 | 448 |  |  | 2020-09-14 | B12948¦Courtroom 1¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | office 467 | [5 empty] | 23 | 54 | 450 |  | 2020-09-16 15:00 | 15:00 | 23 | 54 | 450 |  |  | 2020-09-14 | B70510¦office 467¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B20893 | B20893 - 75 Mulcaster St. - Barrie | Courtroom 15 | [5 empty] | 21.1 | 48 | 537 |  | 2020-09-16 12:00 | 12:00 | 21.1 | 48 | 537 |  |  | 2020-09-14 | B20893¦Courtroom 15¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 | [5 empty] | 22 | 58 | 452 |  | 2020-09-16 15:00 | 15:00 | 22 | 58 | 452 |  |  | 2020-09-14 | B12948¦Courtroom 3¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 469 | [5 empty] | 23 | 54 | 459 |  | 2020-09-16 15:00 | 15:00 | 23 | 54 | 459 |  |  | 2020-09-14 | B70510¦Office 469¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 | [5 empty] | 22 | 58 | 450 |  | 2020-09-16 15:00 | 15:00 | 22 | 58 | 450 |  |  | 2020-09-14 | B12948¦Courtroom 4¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20893 | B20893 - 75 Mulcaster St. - Barrie | Courtroom 7,8,9 | [5 empty] | 21.8 | 45 | 499 |  | 2020-09-16 15:00 | 15:00 | 21.8 | 45 | 499 |  |  | 2020-09-14 | B20893¦Courtroom 7,8,9¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 6 | [5 empty] | 21 | 59 | 416 |  | 2020-09-16 15:00 | 15:00 | 21 | 59 | 416 |  |  | 2020-09-14 | B12948¦Courtroom 6¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Main Lobby | [5 empty] | 20 | 13 | 578 |  | 2020-09-16 15:00 | 15:00 | 20 | 13 | 578 |  | low | 2020-09-14 | B70050¦Main Lobby¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B92347 | B92347 - 75 Mulcaster Street - Barrie | Courtroom 15 | [5 empty] | 21.2 | 49 | 557 |  | 2020-09-16 15:00 | 15:00 | 21.2 | 49 | 557 |  |  | 2020-09-14 | B92347¦Courtroom 15¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | room 473 (printer) | [5 empty] | 23 | 54 | 455 |  | 2020-09-16 15:00 | 15:00 | 23 | 54 | 455 |  |  | 2020-09-14 | B70510¦room 473 (printer)¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 | [5 empty] | 21 | 60 | 418 |  | 2020-09-16 15:00 | 15:00 | 21 | 60 | 418 |  | caution | 2020-09-14 | B12948¦Courtroom 5¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 301 | [5 empty] | 19 | 60 | 500 |  | 2020-09-16 09:00 | 9:00 | 19 | 60 | 500 |  | caution | 2020-09-14 | B25671¦Courtroom 301¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 8 | [5 empty] | 23 | 55 | 428 |  | 2020-09-16 15:00 | 15:00 | 23 | 55 | 428 |  |  | 2020-09-14 | B25683¦Courtroom 8¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hall 475 or 466 | [5 empty] | 22 | 54 | 450 |  | 2020-09-16 15:00 | 15:00 | 22 | 54 | 450 |  |  | 2020-09-14 | B70510¦Hall 475 or 466¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 1 | [5 empty] | 20 | 23 | 534 |  | 2020-09-16 15:00 | 15:00 | 20 | 23 | 534 |  | low | 2020-09-14 | B70050¦Courtroom 1¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 101 | [5 empty] | 20 | 59 | 696 |  | 2020-09-16 12:00 | 12:00 | 20 | 59 | 696 |  |  | 2020-09-14 | B25671¦Courtroom 101¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 11 | [5 empty] | 23 | 55 | 428 |  | 2020-09-16 15:00 | 15:00 | 23 | 55 | 428 |  |  | 2020-09-14 | B25683¦Courtroom 11¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 1 | [5 empty] | 22 | 54 | 470 |  | 2020-09-16 15:00 | 15:00 | 22 | 54 | 470 |  |  | 2020-09-14 | B70510¦Hearing Room 1¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Holding Cell | [5 empty] | 21 | 61 | 449 |  | 2020-09-16 15:00 | 15:00 | 21 | 61 | 449 |  | caution | 2020-09-14 | B12948¦Holding Cell¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 20 | 30 | 532 |  | 2020-09-16 15:00 | 15:00 | 20 | 30 | 532 |  | low | 2020-09-14 | B70050¦2nd Floor Holding Cell¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 9 | [5 empty] | 23 | 52 | 441 |  | 2020-09-16 15:00 | 15:00 | 23 | 52 | 441 |  |  | 2020-09-14 | B25683¦Courtroom 9¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Admin Office Waiting Area | [5 empty] | 21 | 61 | 430 |  | 2020-09-16 15:00 | 15:00 | 21 | 61 | 430 |  | caution | 2020-09-14 | B12948¦Admin Office Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Meeting Rooms 1/2 | [5 empty] | 22 | 55 | 444 |  | 2020-09-16 15:00 | 15:00 | 22 | 55 | 444 |  |  | 2020-09-14 | B70510¦Vestibule at Meeting Rooms 1/2¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 201 | [5 empty] | 20 | 60 | 549 |  | 2020-09-16 12:00 | 12:00 | 20 | 60 | 549 |  | caution | 2020-09-14 | B25671¦Courtroom 201¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration office | [5 empty] | 22 | 59 | 423 |  | 2020-09-16 15:00 | 15:00 | 22 | 59 | 423 |  |  | 2020-09-14 | B12948¦Administration office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Hearing Room 1 | [5 empty] | 22 | 54 | 428 |  | 2020-09-16 15:00 | 15:00 | 22 | 54 | 428 |  |  | 2020-09-14 | B70510¦Vestibule at Hearing Room 1¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Yannick Bedard Office - 2nd Floor | [5 empty] | 21 | 29 | 611 |  | 2020-09-16 15:00 | 15:00 | 21 | 29 | 611 |  | low | 2020-09-14 | B70050¦Yannick Bedard Office - 2nd Floor¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 301 | [5 empty] | 22 | 57 | 532 |  | 2020-09-16 12:00 | 12:00 | 22 | 57 | 532 |  |  | 2020-09-14 | B25671¦Courtroom 301¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 1 | [5 empty] | 22 | 55 | 449 |  | 2020-09-16 15:00 | 15:00 | 22 | 55 | 449 |  |  | 2020-09-14 | B70510¦Hearing Room 1¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 1 | [5 empty] | 24 | 52 | 390 |  | 2020-09-16 15:00 | 15:00 | 24 | 52 | 390 |  |  | 2020-09-14 | B24638¦Courtroom 1¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 439 | [5 empty] | 22 | 55 | 450 |  | 2020-09-16 15:00 | 15:00 | 22 | 55 | 450 |  |  | 2020-09-14 | B70510¦Office 439¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Crown attorney admin area | [5 empty] | 22 | 61 | 457 |  | 2020-09-16 15:00 | 15:00 | 22 | 61 | 457 |  | caution | 2020-09-14 | B12948¦Crown attorney admin area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | First Aid Desk | [5 empty] | 22 | 55 | 450 |  | 2020-09-16 15:00 | 15:00 | 22 | 55 | 450 |  |  | 2020-09-14 | B70510¦First Aid Desk¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-3 OTHER | [5 empty] | 22 | 50 | 637 |  | 2020-09-16 12:00 | 12:00 | 22 | 50 | 637 |  |  | 2020-09-14 | B25398¦Courtroom 16-3 OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 2 | [5 empty] | 22 | 37 | 578 |  | 2020-09-16 15:00 | 15:00 | 22 | 37 | 578 |  | caution | 2020-09-14 | B70050¦Courtroom 2¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 436 | [5 empty] | 22 | 55 | 486 |  | 2020-09-16 15:00 | 15:00 | 22 | 55 | 486 |  |  | 2020-09-14 | B70510¦Office 436¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main entrance | [5 empty] | 21 | 60 | 429 |  | 2020-09-16 15:00 | 15:00 | 21 | 60 | 429 |  | caution | 2020-09-14 | B12948¦Main entrance¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Outdoors |  |  | 22 | 52 | [5 empty] | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20619¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd fl lobby | [5 empty] | 21 | 35 | 567 |  | 2020-09-16 15:00 | 15:00 | 21 | 35 | 567 |  | caution | 2020-09-14 | B70050¦2nd fl lobby¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-2, West OTHER | [5 empty] | 21 | 53 | 644 |  | 2020-09-16 12:00 | 12:00 | 21 | 53 | 644 |  |  | 2020-09-14 | B25398¦Courtroom 16-2, West OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 432 | [5 empty] | 22 | 54 | 454 |  | 2020-09-16 15:00 | 15:00 | 22 | 54 | 454 |  |  | 2020-09-14 | B70510¦Office 432¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 3 | [5 empty] | 24 | 51 | 365 |  | 2020-09-16 15:00 | 15:00 | 24 | 51 | 365 |  |  | 2020-09-14 | B24638¦Courtroom 3¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Courtroom 1-14 | [5 empty] | 23 | 58 | 566 |  | 2020-09-16 15:00 | 15:00 | 23 | 58 | 566 |  |  | 2020-09-14 | B20619¦Courtroom 1-14¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main Entrance Waiting Area | [5 empty] | 22 | 60 | 424 |  | 2020-09-16 15:00 | 15:00 | 22 | 60 | 424 |  | caution | 2020-09-14 | B12948¦Main Entrance Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 429 | [5 empty] | 23 | 54 | 468 |  | 2020-09-16 15:00 | 15:00 | 23 | 54 | 468 |  |  | 2020-09-14 | B70510¦Office 429¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Court Room 1 Waiting Area | [5 empty] | 21 | 61 | 440 |  | 2020-09-16 15:00 | 15:00 | 21 | 61 | 440 |  | caution | 2020-09-14 | B12948¦Court Room 1 Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 427 | [5 empty] | 23 | 54 | 472 |  | 2020-09-16 15:00 | 15:00 | 23 | 54 | 472 |  |  | 2020-09-14 | B70510¦Office 427¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Outdoors |  |  | 24 | 48 | 295 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B24638¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-2, East OTHER | [5 empty] | 23 | 53 | 640 |  | 2020-09-16 12:00 | 12:00 | 23 | 53 | 640 |  |  | 2020-09-14 | B25398¦Courtroom 16-2, East OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mail Room | [5 empty] | 23 | 53 | 463 |  | 2020-09-16 15:00 | 15:00 | 23 | 53 | 463 |  |  | 2020-09-14 | B70510¦Mail Room¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Outdoors |  |  | 25 | 45 | 329 |  |  |  | Base Readings | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B25165¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 Waiting Area | [5 empty] | 21 | 61 | 427 |  | 2020-09-16 15:00 | 15:00 | 21 | 61 | 427 |  | caution | 2020-09-14 | B12948¦Courtroom 2 Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 420 | [5 empty] | 23 | 53 | 481 |  | 2020-09-16 15:00 | 15:00 | 23 | 53 | 481 |  |  | 2020-09-14 | B70510¦Office 420¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-1B OTHER | [5 empty] | 22 | 55 | 632 |  | 2020-09-16 12:00 | 12:00 | 22 | 55 | 632 |  |  | 2020-09-14 | B25398¦Courtroom 16-1B OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 Waiting Area | [5 empty] | 22 | 60 | 451 |  | 2020-09-16 15:00 | 15:00 | 22 | 60 | 451 |  | caution | 2020-09-14 | B12948¦Courtroom 3 Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 418 | [5 empty] | 23 | 53 | 485 |  | 2020-09-16 15:00 | 15:00 | 23 | 53 | 485 |  |  | 2020-09-14 | B70510¦Office 418¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 308 | [5 empty] | 22 | 52 | 431 |  | 2020-09-16 15:00 | 15:00 | 22 | 52 | 431 |  |  | 2020-09-14 | B25165¦Courtroom 308¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 Waiting Area | [5 empty] | 22 | 59 | 436 |  | 2020-09-16 15:00 | 15:00 | 22 | 59 | 436 |  |  | 2020-09-14 | B12948¦Courtroom 5 Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-1A, North OTHER | [5 empty] | 20 | 56 | 629 |  | 2020-09-16 12:00 | 12:00 | 20 | 56 | 629 |  |  | 2020-09-14 | B25398¦Courtroom 16-1A, North OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | File Room | [5 empty] | 23 | 53 | 466 |  | 2020-09-16 15:00 | 15:00 | 23 | 53 | 466 |  |  | 2020-09-14 | B70510¦File Room¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 and 6 Waiting Area | [5 empty] | 22 | 59 | 432 |  | 2020-09-16 15:00 | 15:00 | 22 | 59 | 432 |  |  | 2020-09-14 | B12948¦Courtroom 4 and 6 Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 306 | [5 empty] | 22 | 51 | 672 |  | 2020-09-16 15:00 | 15:00 | 22 | 51 | 672 |  |  | 2020-09-14 | B25165¦Courtroom 306¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Health Room | [5 empty] | 23 | 53 | 467 |  | 2020-09-16 15:00 | 15:00 | 23 | 53 | 467 |  |  | 2020-09-14 | B70510¦Health Room¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-1A, South OTHER | [5 empty] | 20 | 57 | 631 |  | 2020-09-16 12:00 | 12:00 | 20 | 57 | 631 |  |  | 2020-09-14 | B25398¦Courtroom 16-1A, South OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 302 | [5 empty] | 21 | 52 | 421 |  | 2020-09-16 15:00 | 15:00 | 21 | 52 | 421 |  |  | 2020-09-14 | B25165¦Courtroom 302¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 | [5 empty] | 22 | 54 | 470 |  | 2020-09-16 15:00 | 15:00 | 22 | 54 | 470 |  |  | 2020-09-14 | B70510¦Hearing Room 3¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Police Court Bureau | [5 empty] | 21 | 49 | 526 |  | 2020-09-16 12:00 | 12:00 | 21 | 49 | 526 |  |  | 2020-09-14 | B19523¦Police Court Bureau¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 208 | [5 empty] | 21 | 52 | 454 |  | 2020-09-16 15:00 | 15:00 | 21 | 52 | 454 |  |  | 2020-09-14 | B25165¦Courtroom 208¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-1A OTHER | [5 empty] | 20 | 57 | 628 |  | 2020-09-16 12:00 | 12:00 | 20 | 57 | 628 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-1A OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 Waiting Area | [5 empty] | 22 | 54 | 461 |  | 2020-09-16 15:00 | 15:00 | 22 | 54 | 461 |  |  | 2020-09-14 | B70510¦Hearing Room 3 Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 Waiting Area | [5 empty] | 21 | 42 | 523 |  | 2020-09-16 12:00 | 12:00 | 21 | 42 | 523 |  |  | 2020-09-14 | B19523¦Courtroom 4 Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 206 | [5 empty] | 21 | 52 | 464 |  | 2020-09-16 15:00 | 15:00 | 21 | 52 | 464 |  |  | 2020-09-14 | B25165¦Courtroom 206¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 | [5 empty] | 21 | 44 | 509 |  | 2020-09-16 12:00 | 12:00 | 21 | 44 | 509 |  |  | 2020-09-14 | B19523¦Courtroom 4¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 204 | [5 empty] | 22 | 52 | 480 |  | 2020-09-16 15:00 | 15:00 | 22 | 52 | 480 |  |  | 2020-09-14 | B25165¦Courtroom 204¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-3 OTHER | [5 empty] | 20 | 58 | 638 |  | 2020-09-16 12:00 | 12:00 | 20 | 58 | 638 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-3 OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Elevator Lobby | [5 empty] | 22 | 54 | 450 |  | 2020-09-16 15:00 | 15:00 | 22 | 54 | 450 |  |  | 2020-09-14 | B70510¦Elevator Lobby¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 202 | [5 empty] | 21 | 52 | 444 |  | 2020-09-16 15:00 | 15:00 | 21 | 52 | 444 |  |  | 2020-09-14 | B25165¦Courtroom 202¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 47 | 550 |  | 2020-09-16 12:00 | 12:00 | 20 | 47 | 550 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 200 | [5 empty] | 22 | 52 | 474 |  | 2020-09-16 15:00 | 15:00 | 22 | 52 | 474 |  |  | 2020-09-14 | B25165¦Courtroom 200¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 49 | 533 |  | 2020-09-16 12:00 | 12:00 | 19 | 49 | 533 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Wasrooms, 16th Floor OTHER | [5 empty] | 21 | 57 | 636 |  | 2020-09-16 12:00 | 12:00 | 21 | 57 | 636 |  |  | 2020-09-14 | B25398¦Corridor adj. to Wasrooms, 16th Floor OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Outdoors |  |  | 24 | 52 | 436 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70510¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 100 | [5 empty] | 22 | 51 | 457 |  | 2020-09-16 15:00 | 15:00 | 22 | 51 | 457 |  |  | 2020-09-14 | B25165¦Courtroom 100¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 49 | 519 |  | 2020-09-16 12:00 | 12:00 | 19 | 49 | 519 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Outdoors |  |  | 21 | 58 | 430 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70510¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Jury Room | [5 empty] | 20 | 47 | 507 |  | 2020-09-16 12:00 | 12:00 | 20 | 47 | 507 |  |  | 2020-09-14 | B19523¦Jury Room¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 16th Floor OTHER | [5 empty] | 20 | 58 | 635 |  | 2020-09-16 12:00 | 12:00 | 20 | 58 | 635 |  |  | 2020-09-14 | B25398¦Elevator Lobby, 16th Floor OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Ontario Court | [5 empty] | 21 | 44 | 498 |  | 2020-09-16 12:00 | 12:00 | 21 | 44 | 498 |  |  | 2020-09-14 | B19523¦Ontario Court¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Women's Washroom, 16th Floor | [5 empty] | 20 | 54 | 637 |  | 2020-09-16 12:00 | 12:00 | 20 | 54 | 637 |  |  | 2020-09-14 | B25398¦OTHER Women's Washroom, 16th Floor¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Judicial Library | [5 empty] | 21 | 43 | 504 |  | 2020-09-16 12:00 | 12:00 | 21 | 43 | 504 |  |  | 2020-09-14 | B19523¦Judicial Library¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 315 | [5 empty] | 21 | 43 | 491 |  | 2020-09-16 12:00 | 12:00 | 21 | 43 | 491 |  |  | 2020-09-14 | B19523¦Office Room 315¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Mediation Centre, 16th Floor OTHER | [5 empty] | 21 | 55 | 630 |  | 2020-09-16 12:00 | 12:00 | 21 | 55 | 630 |  |  | 2020-09-14 | B25398¦Corridor adj. to Mediation Centre, 16th Floor OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 316 | [5 empty] | 21 | 43 | 493 |  | 2020-09-16 12:00 | 12:00 | 21 | 43 | 493 |  |  | 2020-09-14 | B19523¦Office Room 316¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 317 | [5 empty] | 21 | 44 | 548 |  | 2020-09-16 12:00 | 12:00 | 21 | 44 | 548 |  |  | 2020-09-14 | B19523¦Office Room 317¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Outdoors |  |  | 21 | 56 | 630 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B25398¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Superior Court | [5 empty] | 22 | 42 | 532 |  | 2020-09-16 12:00 | 12:00 | 22 | 42 | 532 |  |  | 2020-09-14 | B19523¦Superior Court¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 313 | [5 empty] | 21 | 43 | 515 |  | 2020-09-16 12:00 | 12:00 | 21 | 43 | 515 |  |  | 2020-09-14 | B19523¦Office Room 313¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 312 | [5 empty] | 22 | 42 | 483 |  | 2020-09-16 12:00 | 12:00 | 22 | 42 | 483 |  |  | 2020-09-14 | B19523¦Office Room 312¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-3 OTHER | [5 empty] | 21 | 58 | 637 |  | 2020-09-16 15:00 | 15:00 | 21 | 58 | 637 |  |  | 2020-09-14 | B25398¦Courtroom 16-3 OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 310 | [5 empty] | 22 | 42 | 484 |  | 2020-09-16 12:00 | 12:00 | 22 | 42 | 484 |  |  | 2020-09-14 | B19523¦Office Room 310¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Law Association | [5 empty] | 21 | 43 | 483 |  | 2020-09-16 12:00 | 12:00 | 21 | 43 | 483 |  |  | 2020-09-14 | B19523¦Law Association¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-2, West OTHER | [5 empty] | 21 | 57 | 636 |  | 2020-09-16 15:00 | 15:00 | 21 | 57 | 636 |  |  | 2020-09-14 | B25398¦Courtroom 16-2, West OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Main Lobby | [5 empty] | 21 | 42 | 497 |  | 2020-09-16 12:00 | 12:00 | 21 | 42 | 497 |  |  | 2020-09-14 | B19523¦Main Lobby¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Holding Cell | [5 empty] | 21 | 42 | 512 |  | 2020-09-16 12:00 | 12:00 | 21 | 42 | 512 |  |  | 2020-09-14 | B19523¦Holding Cell¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-2, East OTHER | [5 empty] | 21 | 57 | 636 |  | 2020-09-16 15:00 | 15:00 | 21 | 57 | 636 |  |  | 2020-09-14 | B25398¦Courtroom 16-2, East OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 1 | [5 empty] | 21 | 42 | 500 |  | 2020-09-16 12:00 | 12:00 | 21 | 42 | 500 |  |  | 2020-09-14 | B19523¦Courtroom 1¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 101 | [5 empty] | 20 | 56 | 513 | Bas online | 2020-09-16 15:00 | 15:00 | 20 | 56 | 513 |  |  | 2020-09-14 | B19512¦Courtroom 101¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Court Services | [5 empty] | 21 | 42 | 479 |  | 2020-09-16 12:00 | 12:00 | 21 | 42 | 479 |  |  | 2020-09-14 | B19523¦Court Services¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 200 | [5 empty] | 22 | 48 | 588 | Bas online | 2020-09-16 15:00 | 15:00 | 22 | 48 | 588 |  |  | 2020-09-14 | B19512¦Courtroom 200¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | JP Office | [5 empty] | 21 | 42 | 503 |  | 2020-09-16 12:00 | 12:00 | 21 | 42 | 503 |  |  | 2020-09-14 | B19523¦JP Office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | OPP Office | [5 empty] | 21 | 42 | 500 |  | 2020-09-16 12:00 | 12:00 | 21 | 42 | 500 |  |  | 2020-09-14 | B19523¦OPP Office¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 201 | [5 empty] | 24 | 48 | 580 | Bas online | 2020-09-16 15:00 | 15:00 | 24 | 48 | 580 |  |  | 2020-09-14 | B19512¦Courtroom 201¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Crown Attorney Office | [5 empty] | 21 | 44 | 494 |  | 2020-09-16 12:00 | 12:00 | 21 | 44 | 494 |  |  | 2020-09-14 | B19523¦Crown Attorney Office¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-1A, North OTHER | [5 empty] | 20 | 57 | 636 |  | 2020-09-16 15:00 | 15:00 | 20 | 57 | 636 |  |  | 2020-09-14 | B25398¦Courtroom 16-1A, North OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 42 | 493 |  | 2020-09-16 12:00 | 12:00 | 22 | 42 | 493 |  |  | 2020-09-14 | B19523¦VWAP Office¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Outdoors |  |  | 23 | 50 |  |  |  |  | Bas online | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B19512¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 43 | 520 |  | 2020-09-16 12:00 | 12:00 | 22 | 43 | 520 |  |  | 2020-09-14 | B19523¦VWAP Office¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-1A, North OTHER | [5 empty] | 20 | 57 | 633 |  | 2020-09-16 15:00 | 15:00 | 20 | 57 | 633 |  |  | 2020-09-14 | B25398¦Courtroom 16-1A, North OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Courtroom 16-1B, South OTHER | [5 empty] | 20 | 57 | 630 |  | 2020-09-16 15:00 | 15:00 | 20 | 57 | 630 |  |  | 2020-09-14 | B25398¦Courtroom 16-1B, South OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-1A OTHER | [5 empty] | 20 | 57 | 634 |  | 2020-09-16 15:00 | 15:00 | 20 | 57 | 634 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-1A OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-3 OTHER | [5 empty] | 20 | 57 | 631 |  | 2020-09-16 15:00 | 15:00 | 20 | 57 | 631 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-3 OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Washrooms, 16th Floor OTHER | [5 empty] | 21 | 57 | 637 |  | 2020-09-16 15:00 | 15:00 | 21 | 57 | 637 |  |  | 2020-09-14 | B25398¦Corridor adj. to Washrooms, 16th Floor OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 16th Floor OTHER | [5 empty] | 20 | 58 | 636 |  | 2020-09-16 15:00 | 15:00 | 20 | 58 | 636 |  |  | 2020-09-14 | B25398¦Elevator Lobby, 16th Floor OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Women's Washroom, 16th Floor | [5 empty] | 21 | 56 | 632 |  | 2020-09-16 15:00 | 15:00 | 21 | 56 | 632 |  |  | 2020-09-14 | B25398¦OTHER Women's Washroom, 16th Floor¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Mediation Centre, 16th Floor OTHER | [5 empty] | 20 | 58 | 631 |  | 2020-09-16 15:00 | 15:00 | 20 | 58 | 631 |  |  | 2020-09-14 | B25398¦Corridor adj. to Mediation Centre, 16th Floor OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Outdoors |  |  | 22 | 52 | 635 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B25398¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 101 | [5 empty] | 20 | 59 | 638 |  | 2020-09-16 15:00 | 15:00 | 20 | 59 | 638 |  |  | 2020-09-14 | B25671¦Courtroom 101¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 5 | [5 empty] | 21 | 42 | 494 |  | 2020-09-16 12:00 | 12:00 | 21 | 42 | 494 |  |  | 2020-09-14 | B19523¦Courtroom 5¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 201 | [5 empty] | 20 | 60 | 507 |  | 2020-09-16 15:00 | 15:00 | 20 | 60 | 507 |  | caution | 2020-09-14 | B25671¦Courtroom 201¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Remote Testimony Room | [5 empty] | 21 | 42 | 517 |  | 2020-09-16 12:00 | 12:00 | 21 | 42 | 517 |  |  | 2020-09-14 | B19523¦Remote Testimony Room¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 301 | [5 empty] | 20 | 60 | 499 |  | 2020-09-16 15:00 | 15:00 | 20 | 60 | 499 |  | caution | 2020-09-14 | B25671¦Courtroom 301¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Conference Room 2 | [5 empty] | 21 | 42 | 487 |  | 2020-09-16 12:00 | 12:00 | 21 | 42 | 487 |  |  | 2020-09-14 | B19523¦Conference Room 2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 | [5 empty] | 21 | 42 | 507 |  | 2020-09-16 12:00 | 12:00 | 21 | 42 | 507 |  |  | 2020-09-14 | B19523¦Courtroom 3¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 Waiting Area | [5 empty] | 21 | 44 | 501 |  | 2020-09-16 12:00 | 12:00 | 21 | 44 | 501 |  |  | 2020-09-14 | B19523¦Courtroom 3 Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 21 | 45 | 549 |  | 2020-09-16 12:00 | 12:00 | 21 | 45 | 549 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 21 | 45 | 538 |  | 2020-09-16 12:00 | 12:00 | 21 | 45 | 538 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 46 | 549 |  | 2020-09-16 12:00 | 12:00 | 20 | 46 | 549 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Outdoors |  |  | 24 | 46 | 238 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20289¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 2 | [5 empty] | 21 | 44 | 539 |  | 2020-09-16 12:00 | 12:00 | 21 | 44 | 539 |  |  | 2020-09-14 | B19523¦Courtroom 2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Legal Aid Ontario | [5 empty] | 25 | 39 | 458 |  | 2020-09-16 12:00 | 12:00 | 25 | 39 | 458 |  | caution | 2020-09-14 | B20016¦Legal Aid Ontario¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Duty Counsel Waiting Area | [5 empty] | 25 | 41 | 463 |  | 2020-09-16 12:00 | 12:00 | 25 | 41 | 463 |  |  | 2020-09-14 | B19523¦Duty Counsel Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 24 | 45 | 303 | judge | 2020-09-16 15:00 | 15:00 | 24 | 45 | 303 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 100 Courtroom 202 Courtroom 203 | [5 empty] | 21 | 47 | 457 |  | 2020-09-16 15:00 | 15:00 | 21 | 47 | 457 |  |  | 2020-09-14 | B20616¦Courtroom 100 Courtroom 202 Courtroom 203¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel | [5 empty] | 23 | 43 | 501 |  | 2020-09-16 12:00 | 12:00 | 23 | 43 | 501 |  |  | 2020-09-14 | B20016¦Duty Counsel¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 24 | 45 | 282 | public | 2020-09-16 15:00 | 15:00 | 24 | 45 | 282 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lobby Courtroom 1 - 2 | [5 empty] | 23 | 46 | 484 |  | 2020-09-16 12:00 | 12:00 | 23 | 46 | 484 |  |  | 2020-09-14 | B20016¦Lobby Courtroom 1 - 2¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office North | [5 empty] | 24 | 44 | 650 |  | 2020-09-16 15:00 | 15:00 | 24 | 44 | 650 |  |  | 2020-09-14 | B14895¦Administration Office North¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 23 | 45 | 276 | judge | 2020-09-16 15:00 | 15:00 | 23 | 45 | 276 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Main Lobby | [5 empty] | 23 | 47 | 523 |  | 2020-09-16 12:00 | 12:00 | 23 | 47 | 523 |  |  | 2020-09-14 | B20016¦Main Lobby¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office South | [5 empty] | 22 | 46 | 525 |  | 2020-09-16 15:00 | 15:00 | 22 | 46 | 525 |  |  | 2020-09-14 | B14895¦Administration Office South¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lower Hallway | [5 empty] | 22 | 47 | 493 |  | 2020-09-16 12:00 | 12:00 | 22 | 47 | 493 |  |  | 2020-09-14 | B20016¦Lower Hallway¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 101 Courtroom 102 Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 200 Courtroom 201 Courtroom 401 Courtroom 402 Courtroom 403 | [5 empty] | 22 | 47 | 457 |  | 2020-09-16 15:00 | 15:00 | 22 | 47 | 457 |  |  | 2020-09-14 | B20616¦Courtroom 101 Courtroom 102 Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 200 Courtroom 201 Courtroom 401 Courtroom 402 Courtroom 403¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main entrance | [5 empty] | 19 | 53 | 538 |  | 2020-09-16 15:00 | 15:00 | 19 | 53 | 538 |  |  | 2020-09-14 | B14895¦Main entrance¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | OTHER | [5 empty] | 22 | 40 | 478 | Courtroom 1-2-3 | 2020-09-16 12:00 | 12:00 | 22 | 40 | 478 |  | caution | 2020-09-14 | B20016¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 23 | 44 | 263 | public | 2020-09-16 15:00 | 15:00 | 23 | 44 | 263 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 | [5 empty] | 23 | 55 | 569 |  | 2020-09-16 15:00 | 15:00 | 23 | 55 | 569 |  |  | 2020-09-14 | B14209¦Courtroom 1¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation | [5 empty] | 22 | 49 | 475 |  | 2020-09-16 12:00 | 12:00 | 22 | 49 | 475 |  |  | 2020-09-14 | B20016¦Family Mediation¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 106 Courtroom 205 | [5 empty] | 20 | 51 | 457 |  | 2020-09-16 15:00 | 15:00 | 20 | 51 | 457 |  |  | 2020-09-14 | B20616¦Courtroom 106 Courtroom 205¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 300 | [5 empty] | 22 | 49 | 331 |  | 2020-09-16 15:00 | 15:00 | 22 | 49 | 331 |  |  | 2020-09-14 | B20289¦Courtroom 300¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation Across Stairs | [5 empty] | 21 | 50 | 478 |  | 2020-09-16 12:00 | 12:00 | 21 | 50 | 478 |  |  | 2020-09-14 | B20016¦Family Mediation Across Stairs¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main Entrance Waiting Area | [5 empty] | 21 | 50 | 540 |  | 2020-09-16 15:00 | 15:00 | 21 | 50 | 540 |  |  | 2020-09-14 | B14895¦Main Entrance Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 301 | [5 empty] | 22 | 49 | 347 |  | 2020-09-16 15:00 | 15:00 | 22 | 49 | 347 |  |  | 2020-09-14 | B20289¦Courtroom 301¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Outdoors |  |  | 22 | 54 | 381 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B19652¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom A | [5 empty] | 22 | 47 | 421 |  | 2020-09-16 15:00 | 15:00 | 22 | 47 | 421 |  |  | 2020-09-14 | B14895¦Courtroom A¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 204 Courtroom 301 Courtroom 303 Courtroom 404 Courtroom 405 | [5 empty] | 21 | 51 | 457 |  | 2020-09-16 15:00 | 15:00 | 21 | 51 | 457 |  |  | 2020-09-14 | B20616¦Courtroom 204 Courtroom 301 Courtroom 303 Courtroom 404 Courtroom 405¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Center) | [5 empty] | 23 | 49 | 468 |  | 2020-09-16 15:00 | 15:00 | 23 | 49 | 468 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Center)¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 302 | [5 empty] | 22 | 49 | 328 |  | 2020-09-16 15:00 | 15:00 | 22 | 49 | 328 |  |  | 2020-09-14 | B20289¦Courtroom 302¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Judge Dias) | [5 empty] | 23 | 49 | 440 |  | 2020-09-16 15:00 | 15:00 | 23 | 49 | 440 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Judge Dias)¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 303 | [5 empty] | 22 | 50 | 322 |  | 2020-09-16 15:00 | 15:00 | 22 | 50 | 322 |  |  | 2020-09-14 | B20289¦Courtroom 303¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 302 | [5 empty] | 22 | 51 | 457 |  | 2020-09-16 15:00 | 15:00 | 22 | 51 | 457 |  |  | 2020-09-14 | B20616¦Courtroom 302¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 50 | 461 | Superior judges chamber | 2020-09-16 15:00 | 15:00 | 22 | 50 | 461 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom A | [5 empty] | 23 | 47 | 369 | in session; measurement taken outside courtroom | 2020-09-16 15:00 | 15:00 | 23 | 47 | 369 |  |  | 2020-09-14 | B20289¦Courtroom A¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 107 Courtroom 108 | [5 empty] | 21 | 54 | 455 |  | 2020-09-16 15:00 | 15:00 | 21 | 54 | 455 |  |  | 2020-09-14 | B20616¦Courtroom 107 Courtroom 108¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 52 | 532 | 3rd floor stairs landing | 2020-09-16 15:00 | 15:00 | 22 | 52 | 532 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom B | [5 empty] | 22 | 46 | 361 |  | 2020-09-16 15:00 | 15:00 | 22 | 46 | 361 |  |  | 2020-09-14 | B20289¦Courtroom B¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 304 | [5 empty] | 22 | 52 | 565 |  | 2020-09-16 15:00 | 15:00 | 22 | 52 | 565 |  |  | 2020-09-14 | B20616¦Courtroom 304¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 52 | 472 | 3rd floor Jury room | 2020-09-16 15:00 | 15:00 | 22 | 52 | 472 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom C (North) | [5 empty] | 22 | 47 | 354 |  | 2020-09-16 15:00 | 15:00 | 22 | 47 | 354 |  |  | 2020-09-14 | B20289¦Courtroom C (North)¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 305 | [5 empty] | 21 | 52 | 565 |  | 2020-09-16 15:00 | 15:00 | 21 | 52 | 565 |  |  | 2020-09-14 | B20616¦Courtroom 305¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 52 | 437 | Justice Macdonald chamber | 2020-09-16 15:00 | 15:00 | 22 | 52 | 437 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom D | [5 empty] | 22 | 47 | 376 |  | 2020-09-16 15:00 | 15:00 | 22 | 47 | 376 |  |  | 2020-09-14 | B20289¦Courtroom D¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom B (North) | [5 empty] | 23 | 39 | 470 |  | 2020-09-16 15:00 | 15:00 | 23 | 39 | 470 |  | caution | 2020-09-14 | B14895¦Courtroom B (North)¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 - waiting area | [5 empty] | 23 | 57 | 529 |  | 2020-09-16 15:00 | 15:00 | 23 | 57 | 529 |  |  | 2020-09-14 | B14209¦Courtroom 1 - waiting area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 53 | 426 | Justice McDonald secretary | 2020-09-16 15:00 | 15:00 | 22 | 53 | 426 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | 2nd Floor Waiting Area | [5 empty] | 23 | 45 | 608 |  | 2020-09-16 15:00 | 15:00 | 23 | 45 | 608 |  |  | 2020-09-14 | B14895¦2nd Floor Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom E | [5 empty] | 22 | 48 | 372 |  | 2020-09-16 15:00 | 15:00 | 22 | 48 | 372 |  |  | 2020-09-14 | B20289¦Courtroom E¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 53 | 417 | SCJTC office | 2020-09-16 15:00 | 15:00 | 22 | 53 | 417 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Crown Attorney Office | [5 empty] | 23 | 42 | 513 |  | 2020-09-16 15:00 | 15:00 | 23 | 42 | 513 |  |  | 2020-09-14 | B14895¦Crown Attorney Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom F | [5 empty] | 22 | 49 | 337 | in session; measurement taken outside courtroom | 2020-09-16 15:00 | 15:00 | 22 | 49 | 337 |  |  | 2020-09-14 | B20289¦Courtroom F¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 53 | 421 | Visiting Justice chamber | 2020-09-16 15:00 | 15:00 | 22 | 53 | 421 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Waiting Area | [5 empty] | 24 | 45 | 605 |  | 2020-09-16 15:00 | 15:00 | 24 | 45 | 605 |  |  | 2020-09-14 | B14895¦Basement Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Center) | [5 empty] | 22 | 53 | 418 |  | 2020-09-16 15:00 | 15:00 | 22 | 53 | 418 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Center)¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Male Holding Cell | [5 empty] | 23 | 41 | 440 |  | 2020-09-16 15:00 | 15:00 | 23 | 41 | 440 |  |  | 2020-09-14 | B14895¦Male Holding Cell¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 | [5 empty] | 22 | 57 | 468 |  | 2020-09-16 15:00 | 15:00 | 22 | 57 | 468 |  |  | 2020-09-14 | B14209¦Courtroom 2¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Judge Dias) | [5 empty] | 22 | 53 | 430 |  | 2020-09-16 15:00 | 15:00 | 22 | 53 | 430 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Judge Dias)¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Female Holding Cell | [5 empty] | 23 | 40 | 448 |  | 2020-09-16 15:00 | 15:00 | 23 | 40 | 448 |  | caution | 2020-09-14 | B14895¦Female Holding Cell¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 - waiting room | [5 empty] | 23 | 58 | 491 |  | 2020-09-16 15:00 | 15:00 | 23 | 58 | 491 |  |  | 2020-09-14 | B14209¦Courtroom 2 - waiting room¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 Waiting Area | [5 empty] | 22 | 54 | 447 |  | 2020-09-16 15:00 | 15:00 | 22 | 54 | 447 |  |  | 2020-09-14 | B19652¦Courtroom 2 Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Center) | [5 empty] | 22 | 56 | 430 |  | 2020-09-16 15:00 | 15:00 | 22 | 56 | 430 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Center)¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Boardroom | [5 empty] | 23 | 42 | 534 |  | 2020-09-16 15:00 | 15:00 | 23 | 42 | 534 |  |  | 2020-09-14 | B14895¦Basement Boardroom¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Judge Dias) | [5 empty] | 22 | 56 | 446 |  | 2020-09-16 15:00 | 15:00 | 22 | 56 | 446 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Judge Dias)¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room | [5 empty] | 23 | 59 | 424 |  | 2020-09-16 15:00 | 15:00 | 23 | 59 | 424 |  |  | 2020-09-14 | B14209¦Hearing Room¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Outdoors |  |  | 18 | 49 | 366 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B14895¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 54 | 504 | Justice peace chamber | 2020-09-16 15:00 | 15:00 | 23 | 54 | 504 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room, Judge’s Chamber | [5 empty] | 23 | 59 | 440 |  | 2020-09-16 15:00 | 15:00 | 23 | 59 | 440 |  |  | 2020-09-14 | B14209¦Hearing Room, Judge’s Chamber¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 52 | 420 | Council chamber dias | 2020-09-16 15:00 | 15:00 | 23 | 52 | 420 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room - Waiting area | [5 empty] | 23 | 58 | 531 |  | 2020-09-16 15:00 | 15:00 | 23 | 58 | 531 |  |  | 2020-09-14 | B14209¦Hearing Room - Waiting area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 52 | 421 | Council chamber center | 2020-09-16 15:00 | 15:00 | 23 | 52 | 421 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Front desk | [5 empty] | 23 | 58 | 526 |  | 2020-09-16 15:00 | 15:00 | 23 | 58 | 526 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Front desk¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 50 | 465 | 2nd floor lunchroom | 2020-09-16 15:00 | 15:00 | 22 | 50 | 465 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 53 | 473 | 2nd floor stairs landing | 2020-09-16 15:00 | 15:00 | 22 | 53 | 473 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 51 | 459 | Court services kitchenette | 2020-09-16 15:00 | 15:00 | 22 | 51 | 459 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 24 | 51 | 684 | Court service north | 2020-09-16 15:00 | 15:00 | 24 | 51 | 684 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown attorney admin area | [5 empty] | 23 | 57 | 532 |  | 2020-09-16 15:00 | 15:00 | 23 | 57 | 532 |  |  | 2020-09-14 | B14209¦Crown attorney admin area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 52 | 672 | Court service south | 2020-09-16 15:00 | 15:00 | 23 | 52 | 672 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Print Room | [5 empty] | 22 | 57 | 534 |  | 2020-09-16 15:00 | 15:00 | 22 | 57 | 534 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Print Room¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 51 | 651 | Court service entrance vestibule | 2020-09-16 15:00 | 15:00 | 23 | 51 | 651 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 52 | 565 | 1st floor stair landing | 2020-09-16 15:00 | 15:00 | 23 | 52 | 565 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office | [5 empty] | 22 | 57 | 505 |  | 2020-09-16 15:00 | 15:00 | 22 | 57 | 505 |  |  | 2020-09-14 | B14209¦Crown Attorney Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Assistant Crown Attorney Office (236) | [5 empty] | 22 | 57 | 521 |  | 2020-09-16 15:00 | 15:00 | 22 | 57 | 521 |  |  | 2020-09-14 | B14209¦Assistant Crown Attorney Office (236)¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Meeting Room (232) | [5 empty] | 22 | 58 | 509 |  | 2020-09-16 15:00 | 15:00 | 22 | 58 | 509 |  |  | 2020-09-14 | B14209¦Crown Attorney Meeting Room (232)¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Cubicles | [5 empty] | 23 | 58 | 537 |  | 2020-09-16 15:00 | 15:00 | 23 | 58 | 537 |  |  | 2020-09-14 | B14209¦Court Admin Office Cubicles¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Lobby | [5 empty] | 23 | 56 | 538 |  | 2020-09-16 15:00 | 15:00 | 23 | 56 | 538 |  |  | 2020-09-14 | B14209¦Court Admin Office Lobby¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Holding Cell corridor | [5 empty] | 23 | 56 | 501 |  | 2020-09-16 15:00 | 15:00 | 23 | 56 | 501 |  |  | 2020-09-14 | B14209¦Holding Cell corridor¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Crown Attorney Office | [5 empty] | 22 | 50 | 469 |  | 2020-09-16 15:00 | 15:00 | 22 | 50 | 469 |  |  | 2020-09-14 | B20016¦Crown Attorney Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Legal Aid Ontario | [5 empty] | 22 | 46 | 442 |  | 2020-09-16 15:00 | 15:00 | 22 | 46 | 442 |  |  | 2020-09-14 | B20016¦Legal Aid Ontario¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel Waiting Area | [5 empty] | 22 | 46 | 491 |  | 2020-09-16 15:00 | 15:00 | 22 | 46 | 491 |  |  | 2020-09-14 | B20016¦Duty Counsel Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel | [5 empty] | 22 | 47 | 457 |  | 2020-09-16 15:00 | 15:00 | 22 | 47 | 457 |  |  | 2020-09-14 | B20016¦Duty Counsel¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lobby Courtroom 1 - 2 | [5 empty] | 22 | 47 | 484 |  | 2020-09-16 15:00 | 15:00 | 22 | 47 | 484 |  |  | 2020-09-14 | B20016¦Lobby Courtroom 1 - 2¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Main Lobby | [5 empty] | 22 | 48 | 450 |  | 2020-09-16 15:00 | 15:00 | 22 | 48 | 450 |  |  | 2020-09-14 | B20016¦Main Lobby¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lower Hallway | [5 empty] | 22 | 48 | 451 |  | 2020-09-16 15:00 | 15:00 | 22 | 48 | 451 |  |  | 2020-09-14 | B20016¦Lower Hallway¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | OTHER | [5 empty] | 21 | 50 | 481 | Courtroom 1-2-3 | 2020-09-16 15:00 | 15:00 | 21 | 50 | 481 |  |  | 2020-09-14 | B20016¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Police Control Room | [5 empty] | 23 | 57 | 525 |  | 2020-09-16 15:00 | 15:00 | 23 | 57 | 525 |  |  | 2020-09-14 | B14209¦Police Control Room¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation | [5 empty] | 21 | 49 | 457 |  | 2020-09-16 15:00 | 15:00 | 21 | 49 | 457 |  |  | 2020-09-14 | B20016¦Family Mediation¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation Across Stairs | [5 empty] | 21 | 50 | 460 |  | 2020-09-16 15:00 | 15:00 | 21 | 50 | 460 |  |  | 2020-09-14 | B20016¦Family Mediation Across Stairs¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Main entrance | [5 empty] | 23 | 41 | 466 |  | 2020-09-16 15:00 | 15:00 | 23 | 41 | 466 |  |  | 2020-09-14 | B20979¦Main entrance¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 23 | 43 | 461 | north | 2020-09-16 15:00 | 15:00 | 23 | 43 | 461 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Justice of the Peace Office | [5 empty] | 22 | 48 | 440 |  | 2020-09-16 15:00 | 15:00 | 22 | 48 | 440 |  |  | 2020-09-14 | B20016¦Justice of the Peace Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Intake Court | [5 empty] | 23 | 52 | 477 |  | 2020-09-16 15:00 | 15:00 | 23 | 52 | 477 |  |  | 2020-09-14 | B14209¦Intake Court¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 23 | 43 | 451 | south | 2020-09-16 15:00 | 15:00 | 23 | 43 | 451 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Holding Cell | [5 empty] | 21 | 50 | 436 |  | 2020-09-16 15:00 | 15:00 | 21 | 50 | 436 |  |  | 2020-09-14 | B20016¦Holding Cell¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 23 | 44 | 535 | south | 2020-09-16 15:00 | 15:00 | 23 | 44 | 535 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Level 1 Corridor by room 103 | [5 empty] | 24 | 55 | 532 |  | 2020-09-16 15:00 | 15:00 | 24 | 55 | 532 |  |  | 2020-09-14 | B14209¦Level 1 Corridor by room 103¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Courtroom 1 | [5 empty] | 22 | 49 | 438 |  | 2020-09-16 15:00 | 15:00 | 22 | 49 | 438 |  |  | 2020-09-14 | B20016¦Courtroom 1¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 23 | 43 | 532 | north | 2020-09-16 15:00 | 15:00 | 23 | 43 | 532 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Main Lobby | [5 empty] | 22 | 41 | 499 |  | 2020-09-16 15:00 | 15:00 | 22 | 41 | 499 |  |  | 2020-09-14 | B19523¦Main Lobby¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | courtroom 307 | [5 empty] | 22 | 45 | 581 | south | 2020-09-16 15:00 | 15:00 | 22 | 45 | 581 |  |  | 2020-09-14 | B20979¦courtroom 307¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Holding Cell | [5 empty] | 22 | 43 | 501 |  | 2020-09-16 15:00 | 15:00 | 22 | 43 | 501 |  |  | 2020-09-14 | B19523¦Holding Cell¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Library | [5 empty] | 23 | 55 | 514 |  | 2020-09-16 15:00 | 15:00 | 23 | 55 | 514 |  |  | 2020-09-14 | B14209¦Library¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-1 | [6 empty] | 50.9 | 699 |  | 2020-09-16 12:00 | 12:00 |  | 50.9 | 699 |  |  | 2020-09-14 | B10644¦Courtroom 2-1¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | courtroom 307 | [5 empty] | 22 | 45 | 595 | north | 2020-09-16 15:00 | 15:00 | 22 | 45 | 595 |  |  | 2020-09-14 | B20979¦courtroom 307¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Law Library Meeting Room (028B) | [5 empty] | 23 | 52 | 554 |  | 2020-09-16 15:00 | 15:00 | 23 | 52 | 554 |  |  | 2020-09-14 | B14209¦Law Library Meeting Room (028B)¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 1 | [5 empty] | 22 | 42 | 509 |  | 2020-09-16 15:00 | 15:00 | 22 | 42 | 509 |  |  | 2020-09-14 | B19523¦Courtroom 1¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 41 | 403 | south | 2020-09-16 15:00 | 15:00 | 22 | 41 | 403 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Lunch Room | [5 empty] | 22 | 55 | 497 |  | 2020-09-16 15:00 | 15:00 | 22 | 55 | 497 |  |  | 2020-09-14 | B14209¦Lunch Room¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-3 | [5 empty] | 20.5 | 69 | 418 |  | 2020-09-16 12:00 | 12:00 | 20.5 | 69 | 418 |  | high | 2020-09-14 | B10644¦Courtroom 2-3¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Court Services | [5 empty] | 21 | 43 | 498 |  | 2020-09-16 15:00 | 15:00 | 21 | 43 | 498 |  |  | 2020-09-14 | B19523¦Court Services¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 46 | 400 | north | 2020-09-16 15:00 | 15:00 | 22 | 46 | 400 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | JP Office | [5 empty] | 21 | 42 | 507 |  | 2020-09-16 15:00 | 15:00 | 21 | 42 | 507 |  |  | 2020-09-14 | B19523¦JP Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Entrance by Stair G | [5 empty] | 24 | 57 | 478 |  | 2020-09-16 15:00 | 15:00 | 24 | 57 | 478 |  |  | 2020-09-14 | B14209¦Entrance by Stair G¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | OPP Office | [5 empty] | 21 | 44 | 516 |  | 2020-09-16 15:00 | 15:00 | 21 | 44 | 516 |  |  | 2020-09-14 | B19523¦OPP Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | hallway by courtroom 302 | [5 empty] | 22 | 45 | 441 |  | 2020-09-16 15:00 | 15:00 | 22 | 45 | 441 |  |  | 2020-09-14 | B20979¦hallway by courtroom 302¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Main Lobby | [5 empty] | 24 | 59 | 618 |  | 2020-09-16 15:00 | 15:00 | 24 | 59 | 618 |  |  | 2020-09-14 | B14209¦Main Lobby¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-5 | [5 empty] | 21 | 60.2 | 418 |  | 2020-09-16 12:00 | 12:00 | 21 | 60.2 | 418 |  | caution | 2020-09-14 | B10644¦Courtroom 2-5¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | hallway by courtroom 307 | [5 empty] | 22 | 46 | 445 |  | 2020-09-16 15:00 | 15:00 | 22 | 46 | 445 |  |  | 2020-09-14 | B20979¦hallway by courtroom 307¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Crown Attorney Office | [5 empty] | 22 | 47 | 522 |  | 2020-09-16 15:00 | 15:00 | 22 | 47 | 522 |  |  | 2020-09-14 | B19523¦Crown Attorney Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 23 | 43 | 585 |  | 2020-09-16 15:00 | 15:00 | 23 | 43 | 585 |  |  | 2020-09-14 | B19523¦VWAP Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 22 | 49 | 764 | north | 2020-09-16 15:00 | 15:00 | 22 | 49 | 764 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 23 | 46 | 585 |  | 2020-09-16 15:00 | 15:00 | 23 | 46 | 585 |  |  | 2020-09-14 | B19523¦VWAP Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 23 | 47 | 731 | south | 2020-09-16 15:00 | 15:00 | 23 | 47 | 731 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-7 | [5 empty] | 21.7 | 59.3 | 560 |  | 2020-09-16 12:00 | 12:00 | 21.7 | 59.3 | 560 |  |  | 2020-09-14 | B10644¦Courtroom 2-7¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Outdoors |  |  | 23 | 59 | 382 |  |  |  | sunny | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B14209¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Basement cells - hallway | [5 empty] | 23 | 44 | 383 |  | 2020-09-16 15:00 | 15:00 | 23 | 44 | 383 |  |  | 2020-09-14 | B20979¦Basement cells - hallway¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 5 | [5 empty] | 22 | 40 | 507 |  | 2020-09-16 15:00 | 15:00 | 22 | 40 | 507 |  | caution | 2020-09-14 | B19523¦Courtroom 5¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | police office | [5 empty] | 24 | 45 | 517 |  | 2020-09-16 15:00 | 15:00 | 24 | 45 | 517 |  |  | 2020-09-14 | B20979¦police office¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-2 | [5 empty] | 19.2 | 59.2 | 543 |  | 2020-09-16 12:00 | 12:00 | 19.2 | 59.2 | 543 |  |  | 2020-09-14 | B10644¦Courtroom 2-2¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | outside | [5 empty] | 27 | 36 | 344 |  | 2020-09-16 15:00 | 15:00 | 27 | 36 | 344 | caution | caution | 2020-09-14 | B20979¦outside¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Remote Testimony Room | [5 empty] | 21 | 43 | 516 |  | 2020-09-16 15:00 | 15:00 | 21 | 43 | 516 |  |  | 2020-09-14 | B19523¦Remote Testimony Room¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Conference Room 2 | [5 empty] | 21 | 42 | 507 |  | 2020-09-16 15:00 | 15:00 | 21 | 42 | 507 |  |  | 2020-09-14 | B19523¦Conference Room 2¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Main entrance | [5 empty] | 25 | 36 | 435 |  | 2020-09-16 15:00 | 15:00 | 25 | 36 | 435 |  | caution | 2020-09-14 | B90636¦Main entrance¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 | [5 empty] | 21 | 44 | 512 |  | 2020-09-16 15:00 | 15:00 | 21 | 44 | 512 |  |  | 2020-09-14 | B19523¦Courtroom 3¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 3-2 | [5 empty] | 22.9 | 64 | 692 |  | 2020-09-16 12:00 | 12:00 | 22.9 | 64 | 692 |  | caution | 2020-09-14 | B10644¦Courtroom 3-2¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 24 | 38 | 390 | north | 2020-09-16 15:00 | 15:00 | 24 | 38 | 390 |  | caution | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 Waiting Area | [5 empty] | 21 | 44 | 520 |  | 2020-09-16 15:00 | 15:00 | 21 | 44 | 520 |  |  | 2020-09-14 | B19523¦Courtroom 3 Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 23 | 39 | 390 | south | 2020-09-16 15:00 | 15:00 | 23 | 39 | 390 |  | caution | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 21 | 44 | 545 |  | 2020-09-16 15:00 | 15:00 | 21 | 44 | 545 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-1 | [5 empty] | 22.7 | 59.6 | 492 |  | 2020-09-16 12:00 | 12:00 | 22.7 | 59.6 | 492 |  |  | 2020-09-14 | B10644¦Courtroom 4-1¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 21 | 45 | 529 |  | 2020-09-16 15:00 | 15:00 | 21 | 45 | 529 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 22 | 40 | 441 | vestibule - lobby | 2020-09-16 15:00 | 15:00 | 22 | 40 | 441 |  | caution | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 46 | 554 |  | 2020-09-16 15:00 | 15:00 | 20 | 46 | 554 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 22 | 41 | 457 | entrance to main room | 2020-09-16 15:00 | 15:00 | 22 | 41 | 457 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-2 | [5 empty] | 21.5 | 57.3 | 432 |  | 2020-09-16 12:00 | 12:00 | 21.5 | 57.3 | 432 |  |  | 2020-09-14 | B10644¦Courtroom 4-2¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 2 | [5 empty] | 21 | 46 | 531 |  | 2020-09-16 15:00 | 15:00 | 21 | 46 | 531 |  |  | 2020-09-14 | B19523¦Courtroom 2¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | hallway outside courtroom 203 | [5 empty] | 22 | 43 | 425 |  | 2020-09-16 15:00 | 15:00 | 22 | 43 | 425 |  |  | 2020-09-14 | B90636¦hallway outside courtroom 203¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Police Court Bureau | [5 empty] | 21 | 46 | 540 |  | 2020-09-16 15:00 | 15:00 | 21 | 46 | 540 |  |  | 2020-09-14 | B19523¦Police Court Bureau¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-9 | [5 empty] | 21.3 | 60 | 410 |  | 2020-09-16 12:00 | 12:00 | 21.3 | 60 | 410 |  | caution | 2020-09-14 | B10644¦Courtroom 4-9¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 2nd fl lobby | [5 empty] | 22 | 46 | 397 |  | 2020-09-16 15:00 | 15:00 | 22 | 46 | 397 |  |  | 2020-09-14 | B90636¦2nd fl lobby¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 Waiting Area | [5 empty] | 21 | 45 | 537 |  | 2020-09-16 15:00 | 15:00 | 21 | 45 | 537 |  |  | 2020-09-14 | B19523¦Courtroom 4 Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 3rd Floor Elevator Lobby | [5 empty] | 22 | 44 | 398 |  | 2020-09-16 15:00 | 15:00 | 22 | 44 | 398 |  |  | 2020-09-14 | B90636¦3rd Floor Elevator Lobby¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 | [5 empty] | 21 | 44 | 509 |  | 2020-09-16 15:00 | 15:00 | 21 | 44 | 509 |  |  | 2020-09-14 | B19523¦Courtroom 4¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-3 | [5 empty] | 25.2 | 57.7 | 405 |  | 2020-09-16 12:00 | 12:00 | 25.2 | 57.7 | 405 |  |  | 2020-09-14 | B10644¦Courtroom 4-3¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 4th floor lobby | [5 empty] | 21 | 45 | 389 |  | 2020-09-16 15:00 | 15:00 | 21 | 45 | 389 |  |  | 2020-09-14 | B90636¦4th floor lobby¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 43 | 555 |  | 2020-09-16 15:00 | 15:00 | 20 | 43 | 555 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 211 | [5 empty] | 21 | 48 | 372 | north | 2020-09-16 15:00 | 15:00 | 21 | 48 | 372 |  |  | 2020-09-14 | B90636¦Courtroom 211¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 50 | 550 |  | 2020-09-16 15:00 | 15:00 | 19 | 50 | 550 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 211 | [5 empty] | 21 | 48 | 378 | south | 2020-09-16 15:00 | 15:00 | 21 | 48 | 378 |  |  | 2020-09-14 | B90636¦Courtroom 211¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-7 | [5 empty] | 23.2 | 61.3 | 370 |  | 2020-09-16 12:00 | 12:00 | 23.2 | 61.3 | 370 |  | caution | 2020-09-14 | B10644¦Courtroom 4-7¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 54 | 546 |  | 2020-09-16 15:00 | 15:00 | 19 | 54 | 546 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | hallway by courtroom 211 | [5 empty] | 21 | 45 | 381 |  | 2020-09-16 15:00 | 15:00 | 21 | 45 | 381 |  |  | 2020-09-14 | B90636¦hallway by courtroom 211¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Jury Room | [5 empty] | 20 | 49 | 518 |  | 2020-09-16 15:00 | 15:00 | 20 | 49 | 518 |  |  | 2020-09-14 | B19523¦Jury Room¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Ontario Court | [5 empty] | 21 | 46 | 522 |  | 2020-09-16 15:00 | 15:00 | 21 | 46 | 522 |  |  | 2020-09-14 | B19523¦Ontario Court¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 205 | [5 empty] | 21 | 45 | 421 | north | 2020-09-16 15:00 | 15:00 | 21 | 45 | 421 |  |  | 2020-09-14 | B90636¦Courtroom 205¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-4 | [5 empty] | 22.7 | 59 | 504 |  | 2020-09-16 15:00 | 15:00 | 22.7 | 59 | 504 |  |  | 2020-09-14 | B10644¦Courtroom 4-4¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Judicial Library | [5 empty] | 21 | 44 | 501 |  | 2020-09-16 15:00 | 15:00 | 21 | 44 | 501 |  |  | 2020-09-14 | B19523¦Judicial Library¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 205 | [5 empty] | 21 | 44 | 424 | south | 2020-09-16 15:00 | 15:00 | 21 | 44 | 424 |  |  | 2020-09-14 | B90636¦Courtroom 205¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 315 | [5 empty] | 21 | 45 | 493 |  | 2020-09-16 15:00 | 15:00 | 21 | 45 | 493 |  |  | 2020-09-14 | B19523¦Office Room 315¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | outside | [5 empty] | 27 | 36 | 344 |  | 2020-09-16 15:00 | 15:00 | 27 | 36 | 344 | caution | caution | 2020-09-14 | B90636¦outside¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 316 | [5 empty] | 21 | 45 | 483 |  | 2020-09-16 15:00 | 15:00 | 21 | 45 | 483 |  |  | 2020-09-14 | B19523¦Office Room 316¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-5 | [5 empty] | 22.7 | 60.1 | 387 |  | 2020-09-16 12:00 | 12:00 | 22.7 | 60.1 | 387 |  | caution | 2020-09-14 | B10644¦Courtroom 4-5¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 317 | [5 empty] | 21 | 44 | 531 |  | 2020-09-16 15:00 | 15:00 | 21 | 44 | 531 |  |  | 2020-09-14 | B19523¦Office Room 317¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Superior Court | [5 empty] | 22 | 44 | 551 |  | 2020-09-16 15:00 | 15:00 | 22 | 44 | 551 |  |  | 2020-09-14 | B19523¦Superior Court¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 313 | [5 empty] | 22 | 43 | 519 |  | 2020-09-16 15:00 | 15:00 | 22 | 43 | 519 |  |  | 2020-09-14 | B19523¦Office Room 313¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 312 | [5 empty] | 22 | 43 | 504 |  | 2020-09-16 15:00 | 15:00 | 22 | 43 | 504 |  |  | 2020-09-14 | B19523¦Office Room 312¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 310 | [5 empty] | 22 | 42 | 507 |  | 2020-09-16 15:00 | 15:00 | 22 | 42 | 507 |  |  | 2020-09-14 | B19523¦Office Room 310¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Law Association | [5 empty] | 21 | 45 | 505 |  | 2020-09-16 15:00 | 15:00 | 21 | 45 | 505 |  |  | 2020-09-14 | B19523¦Law Association¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-6 | [5 empty] | 23 | 60.1 | 387 |  | 2020-09-16 12:00 | 12:00 | 23 | 60.1 | 387 |  | caution | 2020-09-14 | B10644¦Courtroom 4-6¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-8 | [5 empty] | 23.1 | 55.3 | 409 |  | 2020-09-16 12:00 | 12:00 | 23.1 | 55.3 | 409 |  |  | 2020-09-14 | B10644¦Courtroom 4-8¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-8 | [5 empty] | 23.1 | 55.3 | 409 |  | 2020-09-16 12:00 | 12:00 | 23.1 | 55.3 | 409 |  |  | 2020-09-14 | B10644¦Courtroom 4-8¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-9 | [5 empty] | 21.2 | 60 | 410 |  | 2020-09-16 12:00 | 12:00 | 21.2 | 60 | 410 |  | caution | 2020-09-14 | B10644¦Courtroom 4-9¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-10 | [5 empty] | 22.1 | 60.3 | 407 |  | 2020-09-16 15:00 | 15:00 | 22.1 | 60.3 | 407 |  | caution | 2020-09-14 | B10644¦Courtroom 4-10¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 24.2 | 58 | 420 |  | 2020-09-16 12:00 | 12:00 | 24.2 | 58 | 420 |  |  | 2020-09-14 | B10644¦Courtroom 5-1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-1 | [5 empty] | 17.2 | 56.7 | 454 |  | 2020-09-16 12:00 | 12:00 | 17.2 | 56.7 | 454 |  |  | 2020-09-14 | B10644¦Courtroom 6-1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-3 | [5 empty] | 19.6 | 53.2 | 627 |  | 2020-09-16 12:00 | 12:00 | 19.6 | 53.2 | 627 |  |  | 2020-09-14 | B10644¦Courtroom 6-3¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Outdoors |  |  | 18 | 70 | 405 |  |  |  | overcast | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70485¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Social Benefits Tribunal Reception | [5 empty] | 21 | 56 | 403 |  | 2020-09-16 09:00 | 9:00 | 21 | 56 | 403 |  |  | 2020-09-14 | B70485¦Social Benefits Tribunal Reception¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | OTHER | [5 empty] | 21 | 56 | 404 |  | 2020-09-16 09:00 | 9:00 | 21 | 56 | 404 |  |  | 2020-09-14 | B70485¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #4 | [5 empty] | 22 | 55 | 407 |  | 2020-09-16 09:00 | 9:00 | 22 | 55 | 407 |  |  | 2020-09-14 | B70485¦SBT Hearing Room #4¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | LTB Hearing Room #1 | [5 empty] | 21 | 54 | 405 |  | 2020-09-16 09:00 | 9:00 | 21 | 54 | 405 |  |  | 2020-09-14 | B70485¦LTB Hearing Room #1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Regional Managers Office | [5 empty] | 21 | 54 | 408 | open door, plants | 2020-09-16 09:00 | 9:00 | 21 | 54 | 408 |  |  | 2020-09-14 | B70485¦Regional Managers Office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Cubes outside RM Office | [5 empty] | 21 | 54 | 411 | plants | 2020-09-16 09:00 | 9:00 | 21 | 54 | 411 |  |  | 2020-09-14 | B70485¦Cubes outside RM Office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #1 | [5 empty] | 22 | 54 | 410 | open door | 2020-09-16 09:00 | 9:00 | 22 | 54 | 410 |  |  | 2020-09-14 | B70485¦Mediation Room #1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #2 | [5 empty] | 22 | 53 | 409 | open door | 2020-09-16 09:00 | 9:00 | 22 | 53 | 409 |  |  | 2020-09-14 | B70485¦Mediation Room #2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Reception/ Administration LTB | [5 empty] | 22 | 53 | 406 |  | 2020-09-16 09:00 | 9:00 | 22 | 53 | 406 |  |  | 2020-09-14 | B70485¦Reception/ Administration LTB¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mail Room area | [5 empty] | 22 | 52 | 412 |  | 2020-09-16 09:00 | 9:00 | 22 | 52 | 412 |  |  | 2020-09-14 | B70485¦Mail Room area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Copy Room | [5 empty] | 22 | 53 | 413 |  | 2020-09-16 09:00 | 9:00 | 22 | 53 | 413 |  |  | 2020-09-14 | B70485¦Copy Room¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #3 | [5 empty] | 22 | 52 | 425 | open door | 2020-09-16 09:00 | 9:00 | 22 | 52 | 425 |  |  | 2020-09-14 | B70485¦Mediation Room #3¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Corner Office | [5 empty] | 22 | 52 | 415 | open door | 2020-09-16 09:00 | 9:00 | 22 | 52 | 415 |  |  | 2020-09-14 | B70485¦Corner Office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Side Entry Door | [5 empty] | 21 | 52 | 410 |  | 2020-09-16 09:00 | 9:00 | 21 | 52 | 410 |  |  | 2020-09-14 | B70485¦Side Entry Door¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Filing Area | [5 empty] | 21 | 52 | 413 |  | 2020-09-16 09:00 | 9:00 | 21 | 52 | 413 |  |  | 2020-09-14 | B70485¦Filing Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Staff Kitchen | [5 empty] | 22 | 52 | 412 |  | 2020-09-16 09:00 | 9:00 | 22 | 52 | 412 |  |  | 2020-09-14 | B70485¦Staff Kitchen¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Hearing Room #2 | [5 empty] | 22 | 52 | 415 | closed door | 2020-09-16 09:00 | 9:00 | 22 | 52 | 415 |  |  | 2020-09-14 | B70485¦Hearing Room #2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Elevators | [5 empty] | 22 | 52 | 409 |  | 2020-09-16 09:00 | 9:00 | 22 | 52 | 409 |  |  | 2020-09-14 | B70485¦Elevators¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Outdoors |  |  | 21 | 57 | 395 |  |  |  | sunny | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70485¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Social Benefits Tribunal Reception | [5 empty] | 22 | 52 | 418 |  | 2020-09-16 15:00 | 15:00 | 22 | 52 | 418 |  |  | 2020-09-14 | B70485¦Social Benefits Tribunal Reception¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | OTHER | [5 empty] | 22 | 52 | 418 | sbt hearing room 3 | 2020-09-16 15:00 | 15:00 | 22 | 52 | 418 |  |  | 2020-09-14 | B70485¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #4 | [5 empty] | 22 | 52 | 417 |  | 2020-09-16 15:00 | 15:00 | 22 | 52 | 417 |  |  | 2020-09-14 | B70485¦SBT Hearing Room #4¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | LTB Hearing Room #1 | [5 empty] | 21 | 53 | 411 |  | 2020-09-16 09:00 | 9:00 | 21 | 53 | 411 |  |  | 2020-09-14 | B70485¦LTB Hearing Room #1¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Regional Managers Office | [5 empty] | 21 | 54 | 428 | open door, plants | 2020-09-16 15:00 | 15:00 | 21 | 54 | 428 |  |  | 2020-09-14 | B70485¦Regional Managers Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Cubes outside RM Office | [5 empty] | 21 | 54 | 424 | plants | 2020-09-16 15:00 | 15:00 | 21 | 54 | 424 |  |  | 2020-09-14 | B70485¦Cubes outside RM Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #1 | [5 empty] | 21 | 54 | 415 | open door | 2020-09-16 15:00 | 15:00 | 21 | 54 | 415 |  |  | 2020-09-14 | B70485¦Mediation Room #1¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #2 | [5 empty] | 21 | 54 | 424 | open door | 2020-09-16 15:00 | 15:00 | 21 | 54 | 424 |  |  | 2020-09-14 | B70485¦Mediation Room #2¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Reception/ Administration LTB | [5 empty] | 21 | 54 | 428 |  | 2020-09-16 15:00 | 15:00 | 21 | 54 | 428 |  |  | 2020-09-14 | B70485¦Reception/ Administration LTB¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mail Room area | [5 empty] | 21 | 53 | 426 |  | 2020-09-16 15:00 | 15:00 | 21 | 53 | 426 |  |  | 2020-09-14 | B70485¦Mail Room area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Copy Room | [5 empty] | 21 | 53 | 419 |  | 2020-09-16 15:00 | 15:00 | 21 | 53 | 419 |  |  | 2020-09-14 | B70485¦Copy Room¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #3 | [5 empty] | 21 | 53 | 425 | open door | 2020-09-16 15:00 | 15:00 | 21 | 53 | 425 |  |  | 2020-09-14 | B70485¦Mediation Room #3¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Corner Office | [5 empty] | 21 | 53 | 430 | open door | 2020-09-16 15:00 | 15:00 | 21 | 53 | 430 |  |  | 2020-09-14 | B70485¦Corner Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Side Entry Door | [5 empty] | 21 | 54 | 423 |  | 2020-09-16 15:00 | 15:00 | 21 | 54 | 423 |  |  | 2020-09-14 | B70485¦Side Entry Door¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Filing Area | [5 empty] | 21 | 54 | 458 |  | 2020-09-16 15:00 | 15:00 | 21 | 54 | 458 |  |  | 2020-09-14 | B70485¦Filing Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Staff Kitchen | [5 empty] | 21 | 54 | 423 |  | 2020-09-16 15:00 | 15:00 | 21 | 54 | 423 |  |  | 2020-09-14 | B70485¦Staff Kitchen¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Hearing Room #2 | [5 empty] | 22 | 51 | 421 | closed door | 2020-09-16 15:00 | 15:00 | 22 | 51 | 421 |  |  | 2020-09-14 | B70485¦Hearing Room #2¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Elevators | [5 empty] | 21 | 54 | 419 |  | 2020-09-16 15:00 | 15:00 | 21 | 54 | 419 |  |  | 2020-09-14 | B70485¦Elevators¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Outdoors |  |  | 24 | 53 | 384 |  |  |  | sunny | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70485¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Social Benefits Tribunal Reception | [5 empty] | 22 | 50 | 410 |  | 2020-09-16 12:00 | 12:00 | 22 | 50 | 410 |  |  | 2020-09-14 | B70485¦Social Benefits Tribunal Reception¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | OTHER | [5 empty] | 22 | 51 | 409 |  | 2020-09-16 12:00 | 12:00 | 22 | 51 | 409 |  |  | 2020-09-14 | B70485¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #4 | [5 empty] | 22 | 51 | 411 |  | 2020-09-16 12:00 | 12:00 | 22 | 51 | 411 |  |  | 2020-09-14 | B70485¦SBT Hearing Room #4¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | LTB Hearing Room #1 | [5 empty] | 22 | 53 | 415 |  | 2020-09-16 12:00 | 12:00 | 22 | 53 | 415 |  |  | 2020-09-14 | B70485¦LTB Hearing Room #1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Regional Managers Office | [5 empty] | 22 | 53 | 413 | open door, plants | 2020-09-16 12:00 | 12:00 | 22 | 53 | 413 |  |  | 2020-09-14 | B70485¦Regional Managers Office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Cubes outside RM Office | [5 empty] | 22 | 53 | 430 | plants | 2020-09-16 12:00 | 12:00 | 22 | 53 | 430 |  |  | 2020-09-14 | B70485¦Cubes outside RM Office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #1 | [5 empty] | 21 | 54 | 412 | open door | 2020-09-16 12:00 | 12:00 | 21 | 54 | 412 |  |  | 2020-09-14 | B70485¦Mediation Room #1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #2 | [5 empty] | 21 | 54 | 413 | open door | 2020-09-16 12:00 | 12:00 | 21 | 54 | 413 |  |  | 2020-09-14 | B70485¦Mediation Room #2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Reception/ Administration LTB | [5 empty] | 21 | 54 | 411 |  | 2020-09-16 12:00 | 12:00 | 21 | 54 | 411 |  |  | 2020-09-14 | B70485¦Reception/ Administration LTB¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mail Room area | [5 empty] | 21 | 54 | 421 |  | 2020-09-16 12:00 | 12:00 | 21 | 54 | 421 |  |  | 2020-09-14 | B70485¦Mail Room area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Copy Room | [5 empty] | 21 | 54 | 429 |  | 2020-09-16 12:00 | 12:00 | 21 | 54 | 429 |  |  | 2020-09-14 | B70485¦Copy Room¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #3 | [5 empty] | 21 | 55 | 420 | open door | 2020-09-16 12:00 | 12:00 | 21 | 55 | 420 |  |  | 2020-09-14 | B70485¦Mediation Room #3¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Corner Office | [5 empty] | 21 | 54 | 417 | open door | 2020-09-16 12:00 | 12:00 | 21 | 54 | 417 |  |  | 2020-09-14 | B70485¦Corner Office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Side Entry Door | [5 empty] | 21 | 55 | 414 |  | 2020-09-16 12:00 | 12:00 | 21 | 55 | 414 |  |  | 2020-09-14 | B70485¦Side Entry Door¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Filing Area | [5 empty] | 21 | 55 | 412 |  | 2020-09-16 12:00 | 12:00 | 21 | 55 | 412 |  |  | 2020-09-14 | B70485¦Filing Area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Staff Kitchen | [5 empty] | 21 | 55 | 435 |  | 2020-09-16 12:00 | 12:00 | 21 | 55 | 435 |  |  | 2020-09-14 | B70485¦Staff Kitchen¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Hearing Room #2 | [5 empty] | 21 | 55 | 421 | closed door | 2020-09-16 12:00 | 12:00 | 21 | 55 | 421 |  |  | 2020-09-14 | B70485¦Hearing Room #2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Elevators | [5 empty] | 21 | 54 | 413 |  | 2020-09-16 12:00 | 12:00 | 21 | 54 | 413 |  |  | 2020-09-14 | B70485¦Elevators¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Outdoors |  |  | 21 | 56 | 398 |  |  |  | side walk construction | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20705¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 55 | 452 | front security desk | 2020-09-16 09:00 | 9:00 | 22 | 55 | 452 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 53 | 449 | family law reception area | 2020-09-16 09:00 | 9:00 | 22 | 53 | 449 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 53 | 465 | criminal court inquiry area | 2020-09-16 09:00 | 9:00 | 22 | 53 | 465 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 491 | family/civil division waiting area | 2020-09-16 09:00 | 9:00 | 22 | 52 | 491 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 473 |  | 2020-09-16 09:00 | 9:00 | 22 | 52 | 473 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 445 | Court 20 - 24 Waiting Areas | 2020-09-16 09:00 | 9:00 | 22 | 52 | 445 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 51 | 455 | Court 25 - 26 Waiting Areas | 2020-09-16 09:00 | 9:00 | 23 | 51 | 455 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 463 | Court 4 - 6 Waiting Areas | 2020-09-16 09:00 | 9:00 | 22 | 52 | 463 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 496 | Court 1 - 3 Waiting Areas | 2020-09-16 09:00 | 9:00 | 22 | 52 | 496 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 460 | Court 7 - 9 Waiting Areas | 2020-09-16 09:00 | 9:00 | 22 | 52 | 460 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 460 | Court 10 - 12 Waiting Areas | 2020-09-16 09:00 | 9:00 | 22 | 52 | 460 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 52 | 468 |  | 2020-09-16 09:00 | 9:00 | 23 | 52 | 468 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 52 | 459 |  | 2020-09-16 09:00 | 9:00 | 23 | 52 | 459 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 50 | 430 | Court 30 - 33 Waiting Areas | 2020-09-16 09:00 | 9:00 | 22 | 50 | 430 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 52 | 448 | Crown Attourney wing entrance | 2020-09-16 09:00 | 9:00 | 23 | 52 | 448 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 51 | 441 | Probation / Parole Waiting Areas | 2020-09-16 09:00 | 9:00 | 23 | 51 | 441 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 50 | 457 | Land Registry Office | 2020-09-16 09:00 | 9:00 | 23 | 50 | 457 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 4th floor waiting area | [5 empty] | 23 | 50 | 442 |  | 2020-09-16 09:00 | 9:00 | 23 | 50 | 442 |  |  | 2020-09-14 | B20705¦4th floor waiting area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 50 | 450 | Court 53 - 55 Waiting Areas | 2020-09-16 09:00 | 9:00 | 23 | 50 | 450 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 51 | 450 | Court 51 - 52 Waiting Areas | 2020-09-16 09:00 | 9:00 | 22 | 51 | 450 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 434 | 6th Floor Waiting Area | 2020-09-16 09:00 | 9:00 | 22 | 52 | 434 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Outdoors |  |  | 22.7 | 57 | 392 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20705¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 24 | 48 | 495 | front security desk | 2020-09-16 12:00 | 12:00 | 24 | 48 | 495 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 48 | 491 | family law reception area | 2020-09-16 12:00 | 12:00 | 23 | 48 | 491 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 49 | 495 | criminal court inquiry area | 2020-09-16 12:00 | 12:00 | 23 | 49 | 495 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 50 | 496 | family/civil division waiting area | 2020-09-16 12:00 | 12:00 | 23 | 50 | 496 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 50 | 499 | court support services | 2020-09-16 12:00 | 12:00 | 23 | 50 | 499 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 51 | 478 | Court 20 - 24 Waiting Areas | 2020-09-16 12:00 | 12:00 | 23 | 51 | 478 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 50 | 466 | Court 25 - 26 Waiting Areas | 2020-09-16 12:00 | 12:00 | 23 | 50 | 466 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 54 | 520 | Court 4 - 6 Waiting Areas | 2020-09-16 12:00 | 12:00 | 23 | 54 | 520 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 530 | Court 1 - 3 Waiting Areas | 2020-09-16 12:00 | 12:00 | 22 | 52 | 530 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 53 | 502 | Court 7 - 9 Waiting Areas | 2020-09-16 12:00 | 12:00 | 22 | 53 | 502 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 512 | Court 10 - 12 Waiting Areas | 2020-09-16 12:00 | 12:00 | 22 | 52 | 512 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 50 | 476 | Court 13 - 14 Waiting Areas | 2020-09-16 12:00 | 12:00 | 23 | 50 | 476 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 496 | Court 34 - 36 Waiting Areas | 2020-09-16 12:00 | 12:00 | 22 | 52 | 496 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 51 | 486 | Court 30 - 33 Waiting Areas | 2020-09-16 12:00 | 12:00 | 23 | 51 | 486 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 52 | 495 | Crown Attourney wing entrance | 2020-09-16 12:00 | 12:00 | 23 | 52 | 495 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 52 | 522 | Crown Attorney wing entrance | 2020-09-16 12:00 | 12:00 | 23 | 52 | 522 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 52 | 522 | Probation / Parole Waiting Areas | 2020-09-16 12:00 | 12:00 | 23 | 52 | 522 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 4th floor waiting area | [5 empty] | 23 | 50 | 507 |  | 2020-09-16 12:00 | 12:00 | 23 | 50 | 507 |  |  | 2020-09-14 | B20705¦4th floor waiting area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 51 | 497 | Court 53 - 55 Waiting Areas | 2020-09-16 12:00 | 12:00 | 23 | 51 | 497 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 51 | 498 | Court 51 - 52 Waiting Areas | 2020-09-16 12:00 | 12:00 | 22 | 51 | 498 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 487 | 6th Floor Waiting Area | 2020-09-16 12:00 | 12:00 | 22 | 52 | 487 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Outdoors |  |  | 23 | 54 | 379 |  |  |  | sidewalk construction | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20705¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 49 | 500 | front security desk | 2020-09-16 15:00 | 15:00 | 23 | 49 | 500 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 49 | 506 | family law reception area | 2020-09-16 15:00 | 15:00 | 23 | 49 | 506 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 50 | 505 | criminal court inquiry area | 2020-09-16 15:00 | 15:00 | 23 | 50 | 505 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 50 | 513 | family/civil division waiting area | 2020-09-16 15:00 | 15:00 | 23 | 50 | 513 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 50 | 506 | court support services | 2020-09-16 15:00 | 15:00 | 23 | 50 | 506 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 51 | 523 | Court 20 - 24 Waiting Areas | 2020-09-16 15:00 | 15:00 | 23 | 51 | 523 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 51 | 505 | Court 25 - 26 Waiting Areas | 2020-09-16 15:00 | 15:00 | 23 | 51 | 505 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 515 | Court 4 - 6 Waiting Areas | 2020-09-16 15:00 | 15:00 | 22 | 52 | 515 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 565 | Court 1 - 3 Waiting Areas | 2020-09-16 15:00 | 15:00 | 22 | 52 | 565 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 505 | Court 7 - 9 Waiting Areas | 2020-09-16 15:00 | 15:00 | 22 | 52 | 505 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 527 | Court 10 - 12 Waiting Areas | 2020-09-16 15:00 | 15:00 | 22 | 52 | 527 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 51 | 523 | Crown Attourney wing entrance | 2020-09-16 15:00 | 15:00 | 23 | 51 | 523 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 23 | 51 | 522 | Probation / Parole Waiting Areas | 2020-09-16 15:00 | 15:00 | 23 | 51 | 522 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 4th floor waiting area | [5 empty] | 22 | 51 | 510 |  | 2020-09-16 15:00 | 15:00 | 22 | 51 | 510 |  |  | 2020-09-14 | B20705¦4th floor waiting area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 506 | Court 53 - 55 Waiting Areas | 2020-09-16 15:00 | 15:00 | 22 | 52 | 506 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 51 | 494 | Court 51 - 52 Waiting Areas | 2020-09-16 15:00 | 15:00 | 22 | 51 | 494 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | OTHER | [5 empty] | 22 | 52 | 523 | 6th Floor Waiting Area | 2020-09-16 15:00 | 15:00 | 22 | 52 | 523 |  |  | 2020-09-14 | B20705¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Front seating area | [5 empty] | 23 | 53 | 387 |  | 2020-09-16 15:00 | 15:00 | 23 | 53 | 387 |  |  | 2020-09-14 | B18359¦Front seating area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Northwest corridor | [5 empty] | 22 | 56 | 389 |  | 2020-09-16 15:00 | 15:00 | 22 | 56 | 389 |  |  | 2020-09-14 | B18359¦Northwest corridor¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 22 | 54 | 387 | North side | 2020-09-16 15:00 | 15:00 | 22 | 54 | 387 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 22 | 54 | 387 | south side | 2020-09-16 15:00 | 15:00 | 22 | 54 | 387 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 22 | 54 | 388 | north side | 2020-09-16 15:00 | 15:00 | 22 | 54 | 388 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 22 | 55 | 387 | south side | 2020-09-16 15:00 | 15:00 | 22 | 55 | 387 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 22 | 56 | 385 | north side | 2020-09-16 15:00 | 15:00 | 22 | 56 | 385 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 22 | 56 | 397 | south side | 2020-09-16 15:00 | 15:00 | 22 | 56 | 397 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 22 | 54 | 390 | north side | 2020-09-16 15:00 | 15:00 | 22 | 54 | 390 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 22 | 54 | 389 | south side | 2020-09-16 15:00 | 15:00 | 22 | 54 | 389 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 22 | 55 | 390 | north side | 2020-09-16 15:00 | 15:00 | 22 | 55 | 390 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 22 | 56 | 387 | south side | 2020-09-16 15:00 | 15:00 | 22 | 56 | 387 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 22 | 56 | 391 | north side | 2020-09-16 15:00 | 15:00 | 22 | 56 | 391 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 22 | 56 | 390 | south side | 2020-09-16 15:00 | 15:00 | 22 | 56 | 390 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 22 | 56 | 391 | north side | 2020-09-16 15:00 | 15:00 | 22 | 56 | 391 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 22 | 57 | 392 | south side | 2020-09-16 15:00 | 15:00 | 22 | 57 | 392 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 22 | 57 | 396 | north side | 2020-09-16 15:00 | 15:00 | 22 | 57 | 396 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 22 | 57 | 396 | south side | 2020-09-16 15:00 | 15:00 | 22 | 57 | 396 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 22 | 57 | 392 | north side | 2020-09-16 15:00 | 15:00 | 22 | 57 | 392 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 22 | 57 | 391 | south side | 2020-09-16 15:00 | 15:00 | 22 | 57 | 391 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | northeast corridor | [5 empty] | 22 | 56 | 400 |  | 2020-09-16 15:00 | 15:00 | 22 | 56 | 400 |  |  | 2020-09-14 | B18359¦northeast corridor¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 22 | 57 | 383 | north side | 2020-09-16 15:00 | 15:00 | 22 | 57 | 383 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 22 | 57 | 390 | south side | 2020-09-16 15:00 | 15:00 | 22 | 57 | 390 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 22 | 57 | 386 | north side | 2020-09-16 15:00 | 15:00 | 22 | 57 | 386 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 22 | 57 | 386 | south side | 2020-09-16 15:00 | 15:00 | 22 | 57 | 386 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 22 | 57 | 395 | north side | 2020-09-16 15:00 | 15:00 | 22 | 57 | 395 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 22 | 57 | 388 | south side | 2020-09-16 15:00 | 15:00 | 22 | 57 | 388 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 22 | 58 | 383 | north side | 2020-09-16 15:00 | 15:00 | 22 | 58 | 383 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 22 | 58 | 390 | south side | 2020-09-16 15:00 | 15:00 | 22 | 58 | 390 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 22 | 58 | 386 | north side | 2020-09-16 15:00 | 15:00 | 22 | 58 | 386 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 22 | 58 | 384 | south side | 2020-09-16 15:00 | 15:00 | 22 | 58 | 384 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 22 | 58 | 385 | north side | 2020-09-16 15:00 | 15:00 | 22 | 58 | 385 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 22 | 58 | 381 | judge area | 2020-09-16 15:00 | 15:00 | 22 | 58 | 381 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Outdoors |  |  | 22 | 66 | 381 |  |  |  | Outside of 15 Grosvenor Ave. | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B18359¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | reception area | [5 empty] | 22 | 55 | 552 |  | 2020-09-16 15:00 | 15:00 | 22 | 55 | 552 |  |  | 2020-09-14 | B70003¦reception area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Front of main hallway | [5 empty] | 22 | 56 | 556 |  | 2020-09-16 15:00 | 15:00 | 22 | 56 | 556 |  |  | 2020-09-14 | B70003¦Front of main hallway¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 56 | 553 | outside of 502 | 2020-09-16 15:00 | 15:00 | 21 | 56 | 553 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 20 | 56 | 466 | north section | 2020-09-16 09:00 | 9:00 | 20 | 56 | 466 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 20 | 56 | 445 | south section | 2020-09-16 09:00 | 9:00 | 20 | 56 | 445 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 1E | [5 empty] | 20 | 57 | 460 | ground floor | 2020-09-16 09:00 | 9:00 | 20 | 57 | 460 |  |  | 2020-09-14 | B14164¦Hallway by courtroom 1E¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 19 | 57 | 439 | north section | 2020-09-16 09:00 | 9:00 | 19 | 57 | 439 |  |  | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 19 | 57 | 427 | south section | 2020-09-16 09:00 | 9:00 | 19 | 57 | 427 |  |  | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 6 | [5 empty] | 19 | 59 | 438 | second floor | 2020-09-16 09:00 | 9:00 | 19 | 59 | 438 |  |  | 2020-09-14 | B14164¦Hallway by courtroom 6¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 20 | 59 | 443 | north section | 2020-09-16 09:00 | 9:00 | 20 | 59 | 443 |  |  | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 20 | 58 | 425 | south section | 2020-09-16 09:00 | 9:00 | 20 | 58 | 425 |  |  | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 10 | [5 empty] | 20 | 59 | 436 | basement | 2020-09-16 09:00 | 9:00 | 20 | 59 | 436 |  |  | 2020-09-14 | B14164¦Hallway by courtroom 10¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, Basement | [5 empty] | 20 | 58 | 470 |  | 2020-09-16 09:00 | 9:00 | 20 | 58 | 470 |  |  | 2020-09-14 | B14164¦Common area by elevator, Basement¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, ground floor | [5 empty] | 20 | 57 | 443 |  | 2020-09-16 09:00 | 9:00 | 20 | 57 | 443 |  |  | 2020-09-14 | B14164¦Common area by elevator, ground floor¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Youth office, ground floor | [5 empty] | 20 | 57 | 486 |  | 2020-09-16 09:00 | 9:00 | 20 | 57 | 486 |  |  | 2020-09-14 | B14164¦Youth office, ground floor¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Family office, ground floor | [5 empty] | 20 | 57 | 520 |  | 2020-09-16 09:00 | 9:00 | 20 | 57 | 520 |  |  | 2020-09-14 | B14164¦Family office, ground floor¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, second floor | [5 empty] | 20 | 57 | 439 |  | 2020-09-16 09:00 | 9:00 | 20 | 57 | 439 |  |  | 2020-09-14 | B14164¦Common area by elevator, second floor¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Outdoors |  |  | 18 | 70 | 421 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B14164¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Library | [5 empty] | 21.1111 | 63 | 561 |  | 2020-09-16 09:00 | 9:00 | 21.1111 | 63 | 561 |  | caution | 2020-09-14 | B10246¦Library¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 20.5556 | 59 | 491 | Justice Wilcox Chambers | 2020-09-16 09:00 | 9:00 | 20.5556 | 59 | 491 |  |  | 2020-09-14 | B10246¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 2nd fl lobby | [5 empty] | 17 | 54 | 426 | Windows closed, no plants | 2020-09-16 09:00 | 9:00 | 17 | 54 | 426 |  |  | 2020-09-14 | B13049¦2nd fl lobby¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 250 | [5 empty] | 20 | 43 | 371 | No windows, no plants | 2020-09-16 09:00 | 9:00 | 20 | 43 | 371 |  |  | 2020-09-14 | B13049¦Courtroom 250¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | 2nd fl lobby | [5 empty] | 21.1111 | 58 | 475 | Middle of hallway | 2020-09-16 09:00 | 9:00 | 21.1111 | 58 | 475 |  |  | 2020-09-14 | B10246¦2nd fl lobby¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Administration office | [5 empty] | 20 | 39 | 398 | Windows closed, 4 plants total at various locations. | 2020-09-16 09:00 | 9:00 | 20 | 39 | 398 |  | caution | 2020-09-14 | B13049¦Administration office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 2 | [5 empty] | 21.1111 | 57 | 475 |  | 2020-09-16 09:00 | 9:00 | 21.1111 | 57 | 475 |  |  | 2020-09-14 | B10246¦Courtroom 2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 1st Floor Lobby next to courtroom 122 | [5 empty] | 21 | 40 | 379 | Windows closed, no plants | 2020-09-16 09:00 | 9:00 | 21 | 40 | 379 |  | caution | 2020-09-14 | B13049¦1st Floor Lobby next to courtroom 122¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 122 | [5 empty] | 21 | 39 | 404 | No windows, no plants | 2020-09-16 09:00 | 9:00 | 21 | 39 | 404 |  | caution | 2020-09-14 | B13049¦Courtroom 122¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Trial Co-ordinators Office | [5 empty] | 21.1111 | 58 | 566 |  | 2020-09-16 09:00 | 9:00 | 21.1111 | 58 | 566 |  |  | 2020-09-14 | B10246¦Trial Co-ordinators Office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Main Floor Entrance Lobby | [5 empty] | 21.6667 | 57 | 488 | Middle of hallway | 2020-09-16 09:00 | 9:00 | 21.6667 | 57 | 488 |  |  | 2020-09-14 | B10246¦Main Floor Entrance Lobby¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Court Security office #142 | [5 empty] | 22 | 38 | 428 | No windows, no plants | 2020-09-16 09:00 | 9:00 | 22 | 38 | 428 |  | caution | 2020-09-14 | B13049¦Court Security office #142¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 140 | [5 empty] | 22 | 37 | 407 | No windows, no plants | 2020-09-16 09:00 | 9:00 | 22 | 37 | 407 |  | caution | 2020-09-14 | B13049¦Courtroom 140¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 21.6667 | 56 | 567 | Office to the left of office 10 | 2020-09-16 09:00 | 9:00 | 21.6667 | 56 | 567 |  |  | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown attorney admin area | [5 empty] | 21.6667 | 55 | 511 |  | 2020-09-16 09:00 | 9:00 | 21.6667 | 55 | 511 |  |  | 2020-09-14 | B10246¦Crown attorney admin area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 1st floor cell holding area | [5 empty] | 21 | 33 | 420 | Across from door #3 - no windows, no plants | 2020-09-16 09:00 | 9:00 | 21 | 33 | 420 |  | low | 2020-09-14 | B13049¦1st floor cell holding area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Administration office | [5 empty] | 21.6667 | 56 | 570 |  | 2020-09-16 09:00 | 9:00 | 21.6667 | 56 | 570 |  |  | 2020-09-14 | B10246¦Administration office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 21.1111 | 57 | 503 | Basement cells - hallway | 2020-09-16 09:00 | 9:00 | 21.1111 | 57 | 503 |  |  | 2020-09-14 | B10246¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 21.1111 | 58 | 489 | Basement lobby - bottom of stairs | 2020-09-16 09:00 | 9:00 | 21.1111 | 58 | 489 |  |  | 2020-09-14 | B10246¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown Attorney Office | [5 empty] | 23 | 35 | 406 | Office #1 - east side - windows closed, no plants | 2020-09-16 09:00 | 9:00 | 23 | 35 | 406 |  | caution | 2020-09-14 | B13049¦Crown Attorney Office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 1 (Center) | [5 empty] | 21.6667 | 60 | 514 |  | 2020-09-16 09:00 | 9:00 | 21.6667 | 60 | 514 |  | caution | 2020-09-14 | B10246¦Courtroom 1 (Center)¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown Attorney Office | [5 empty] | 23 | 36 | 486 | Office #2 - north side - windows closed, no plants | 2020-09-16 09:00 | 9:00 | 23 | 36 | 486 |  | caution | 2020-09-14 | B13049¦Crown Attorney Office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown attorney admin area | [5 empty] | 24 | 35 | 541 | Windows closed, no plants | 2020-09-16 09:00 | 9:00 | 24 | 35 | 541 |  | caution | 2020-09-14 | B13049¦Crown attorney admin area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Outdoors |  |  | 11 | 44 | 402 |  |  |  | East entrance - partly cloudy, windy | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B13095¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Outdoors |  |  | 17.7778 | 75 | 419 |  |  |  | Directly outside main entrance - overcast | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10246¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Hallway | [5 empty] | 20 | 43 | 530 | Window closed, no plants | 2020-09-16 09:00 | 9:00 | 20 | 43 | 530 |  |  | 2020-09-14 | B13095¦Hallway¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | office - B04A | [5 empty] | 20 | 41 | 451 | Windows closed, no plants | 2020-09-16 09:00 | 9:00 | 20 | 41 | 451 |  |  | 2020-09-14 | B13049¦office - B04A¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Outdoors |  |  | 18 | 64 | 432 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10639¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Lunch Room | [5 empty] | 23 | 57 | 535 |  | 2020-09-16 09:00 | 9:00 | 23 | 57 | 535 |  |  | 2020-09-14 | B70451¦Lunch Room¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Main Lobby | [5 empty] | 22 | 29 | 495 | Windows closed, no plants | 2020-09-16 09:00 | 9:00 | 22 | 29 | 495 |  | low | 2020-09-14 | B13095¦Main Lobby¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 23 | 56 | 511 | east | 2020-09-16 09:00 | 9:00 | 23 | 56 | 511 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 6 North Side | [5 empty] | 21 | 55 | 440 |  | 2020-09-16 09:00 | 9:00 | 21 | 55 | 440 |  |  | 2020-09-14 | B10639¦Courtroom 6 North Side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 23 | 56 | 508 | west | 2020-09-16 09:00 | 9:00 | 23 | 56 | 508 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 602 | [5 empty] | 23 | 57 | 563 |  | 2020-09-16 09:00 | 9:00 | 23 | 57 | 563 |  |  | 2020-09-14 | B70451¦hallway by courtroom 602¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 6 South side | [5 empty] | 21 | 55 | 436 |  | 2020-09-16 09:00 | 9:00 | 21 | 55 | 436 |  |  | 2020-09-14 | B10639¦Courtroom 6 South side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 603 | [5 empty] | 23 | 57 | 523 |  | 2020-09-16 09:00 | 9:00 | 23 | 57 | 523 |  |  | 2020-09-14 | B70451¦hallway by courtroom 603¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | conference room 4 | [5 empty] | 23 | 57 | 494 |  | 2020-09-16 09:00 | 9:00 | 23 | 57 | 494 |  |  | 2020-09-14 | B70451¦conference room 4¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 6 | [5 empty] | 21 | 54 | 468 |  | 2020-09-16 09:00 | 9:00 | 21 | 54 | 468 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 6¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 56 | 484 | east | 2020-09-16 09:00 | 9:00 | 23 | 56 | 484 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 56 | 496 | west | 2020-09-16 09:00 | 9:00 | 23 | 56 | 496 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 5 North side | [5 empty] | 21 | 55 | 528 |  | 2020-09-16 09:00 | 9:00 | 21 | 55 | 528 |  |  | 2020-09-14 | B10639¦Courtroom 5 North side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 607 | [5 empty] | 23 | 56 | 515 |  | 2020-09-16 09:00 | 9:00 | 23 | 56 | 515 |  |  | 2020-09-14 | B70451¦hallway by courtroom 607¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 5 South side | [5 empty] | 21 | 54 | 500 |  | 2020-09-16 09:00 | 9:00 | 21 | 54 | 500 |  |  | 2020-09-14 | B10639¦Courtroom 5 South side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | enforcement/finance office | [5 empty] | 23 | 59 | 525 |  | 2020-09-16 09:00 | 9:00 | 23 | 59 | 525 |  |  | 2020-09-14 | B70451¦enforcement/finance office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 23 | 56 | 491 | east | 2020-09-16 09:00 | 9:00 | 23 | 56 | 491 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 5 | [5 empty] | 21 | 54 | 481 |  | 2020-09-16 09:00 | 9:00 | 21 | 54 | 481 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 5¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 23 | 56 | 489 | west | 2020-09-16 09:00 | 9:00 | 23 | 56 | 489 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 3 Southeast side | [5 empty] | 21 | 59 | 479 |  | 2020-09-16 09:00 | 9:00 | 21 | 59 | 479 |  |  | 2020-09-14 | B10639¦Courtroom 3 Southeast side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 605 | [5 empty] | 23 | 56 | 499 |  | 2020-09-16 09:00 | 9:00 | 23 | 56 | 499 |  |  | 2020-09-14 | B70451¦hallway by courtroom 605¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters administration office | [5 empty] | 23 | 57 | 505 |  | 2020-09-16 09:00 | 9:00 | 23 | 57 | 505 |  |  | 2020-09-14 | B70451¦masters administration office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 3 Northeast side | [5 empty] | 21 | 58 | 452 |  | 2020-09-16 09:00 | 9:00 | 21 | 58 | 452 |  |  | 2020-09-14 | B10639¦Courtroom 3 Northeast side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-10 | [5 empty] | 22 | 57 | 491 |  | 2020-09-16 09:00 | 9:00 | 22 | 57 | 491 |  |  | 2020-09-14 | B70451¦room 6-10¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | hallway by courtroom 3 | [5 empty] | 21 | 57 | 450 |  | 2020-09-16 09:00 | 9:00 | 21 | 57 | 450 |  |  | 2020-09-14 | B10639¦hallway by courtroom 3¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-9 | [5 empty] | 22 | 57 | 500 |  | 2020-09-16 09:00 | 9:00 | 22 | 57 | 500 |  |  | 2020-09-14 | B70451¦room 6-9¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters library | [5 empty] | 22 | 59 | 495 |  | 2020-09-16 09:00 | 9:00 | 22 | 59 | 495 |  |  | 2020-09-14 | B70451¦masters library¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Outdoors |  |  | 18 | 80 | 387 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B11586¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Lobby by the statue | [5 empty] | 21 | 54 | 439 |  | 2020-09-16 09:00 | 9:00 | 21 | 54 | 439 |  |  | 2020-09-14 | B10639¦Lobby by the statue¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-4 | [5 empty] | 22 | 59 | 491 |  | 2020-09-16 09:00 | 9:00 | 22 | 59 | 491 |  |  | 2020-09-14 | B70451¦room 6-4¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 2 | [5 empty] | 20 | 72 | 455 |  | 2020-09-16 09:00 | 9:00 | 20 | 72 | 455 |  | high | 2020-09-14 | B11586¦Courtroom 2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | reception area-masters | [5 empty] | 22 | 59 | 493 |  | 2020-09-16 09:00 | 9:00 | 22 | 59 | 493 |  |  | 2020-09-14 | B70451¦reception area-masters¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby East Side | [5 empty] | 21 | 54 | 440 |  | 2020-09-16 09:00 | 9:00 | 21 | 54 | 440 |  |  | 2020-09-14 | B10639¦Entrance Lobby East Side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Outdoors |  |  | 13 | 64 | 374 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B12955¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Outdoors |  |  | 20 | 64 | 502 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70451¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown Attorney Beaton Office | [5 empty] | 21 | 68 | 462 |  | 2020-09-16 09:00 | 9:00 | 21 | 68 | 462 |  | high | 2020-09-14 | B11586¦Crown Attorney Beaton Office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Main Floor Entrance Lobby | [5 empty] | 14 | 60 | 353 | front lobby | 2020-09-16 09:00 | 9:00 | 14 | 60 | 353 |  | caution | 2020-09-14 | B12955¦Main Floor Entrance Lobby¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby West Side | [5 empty] | 21 | 53 | 446 |  | 2020-09-16 09:00 | 9:00 | 21 | 53 | 446 |  |  | 2020-09-14 | B10639¦Entrance Lobby West Side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by COA intake office | [5 empty] | 21 | 53 | 452 |  | 2020-09-16 09:00 | 9:00 | 21 | 53 | 452 |  |  | 2020-09-14 | B10639¦Hallway by COA intake office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown Attorney Huneault Office | [5 empty] | 21 | 67 | 444 |  | 2020-09-16 09:00 | 9:00 | 21 | 67 | 444 |  | high | 2020-09-14 | B11586¦Crown Attorney Huneault Office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | OTHER | [5 empty] | 18 | 62 | 420 | Waiting area | 2020-09-16 09:00 | 9:00 | 18 | 62 | 420 |  | caution | 2020-09-14 | B12955¦OTHER¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by Law Society of Ontario | [5 empty] | 21 | 53 | 450 |  | 2020-09-16 09:00 | 9:00 | 21 | 53 | 450 |  |  | 2020-09-14 | B10639¦Hallway by Law Society of Ontario¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Administration office | [5 empty] | 20 | 58 | 429 |  | 2020-09-16 09:00 | 9:00 | 20 | 58 | 429 |  |  | 2020-09-14 | B12955¦Administration office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown Attorney Administration Area | [5 empty] | 21 | 66 | 457 |  | 2020-09-16 09:00 | 9:00 | 21 | 66 | 457 |  | high | 2020-09-14 | B11586¦Crown Attorney Administration Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 Waiting Area | [5 empty] | 21 | 65 | 452 |  | 2020-09-16 09:00 | 9:00 | 21 | 65 | 452 |  | caution | 2020-09-14 | B11586¦Courtroom 1 Waiting Area¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Outdoors |  |  | 18 | 67 | 440 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20265¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 203 | [5 empty] | 19 | 56 | 421 | room was being prepared for court | 2020-09-16 09:00 | 9:00 | 19 | 56 | 421 |  |  | 2020-09-14 | B12955¦Courtroom 203¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 | [5 empty] | 21 | 66 | 436 |  | 2020-09-16 09:00 | 9:00 | 21 | 66 | 436 |  | high | 2020-09-14 | B11586¦Courtroom 1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 103 | [5 empty] | 20 | 52 | 381 |  | 2020-09-16 09:00 | 9:00 | 20 | 52 | 381 |  |  | 2020-09-14 | B12955¦Courtroom 103¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 north side | [5 empty] | 22 | 52 | 455 |  | 2020-09-16 09:00 | 9:00 | 22 | 52 | 455 |  |  | 2020-09-14 | B20265¦courtroom M1 north side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | 2nd Floor Holding Cell | [5 empty] | 21 | 65 | 419 |  | 2020-09-16 09:00 | 9:00 | 21 | 65 | 419 |  | caution | 2020-09-14 | B11586¦2nd Floor Holding Cell¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Judge office | [5 empty] | 22 | 62 | 466 |  | 2020-09-16 09:00 | 9:00 | 22 | 62 | 466 |  | caution | 2020-09-14 | B11586¦Judge office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 south side | [5 empty] | 22 | 52 | 448 |  | 2020-09-16 09:00 | 9:00 | 22 | 52 | 448 |  |  | 2020-09-14 | B20265¦courtroom M1 south side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courthouse Administration Office | [5 empty] | 22 | 64 | 485 |  | 2020-09-16 09:00 | 9:00 | 22 | 64 | 485 |  | caution | 2020-09-14 | B11586¦Courthouse Administration Office¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by Courtroom M1 | [5 empty] | 22 | 52 | 460 |  | 2020-09-16 09:00 | 9:00 | 22 | 52 | 460 |  |  | 2020-09-14 | B20265¦hallway by Courtroom M1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | 1st Floor Lobby | [5 empty] | 22 | 64 | 492 |  | 2020-09-16 09:00 | 9:00 | 22 | 64 | 492 |  | caution | 2020-09-14 | B11586¦1st Floor Lobby¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom J South side | [5 empty] | 22 | 53 | 462 |  | 2020-09-16 09:00 | 9:00 | 22 | 53 | 462 |  |  | 2020-09-14 | B20265¦Courtroom J South side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | ourtroom J North side | [5 empty] | 22 | 52 | 460 |  | 2020-09-16 09:00 | 9:00 | 22 | 52 | 460 |  |  | 2020-09-14 | B20265¦ourtroom J North side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom J | [5 empty] | 22 | 51 | 485 |  | 2020-09-16 09:00 | 9:00 | 22 | 51 | 485 |  |  | 2020-09-14 | B20265¦hallway by courtroom J¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G south side | [5 empty] | 22 | 48 | 486 |  | 2020-09-16 09:00 | 9:00 | 22 | 48 | 486 |  |  | 2020-09-14 | B20265¦courtroom G south side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G north side | [5 empty] | 22 | 48 | 476 |  | 2020-09-16 09:00 | 9:00 | 22 | 48 | 476 |  |  | 2020-09-14 | B20265¦courtroom G north side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 121 West side | [5 empty] | 22 | 45 | 500 |  | 2020-09-16 09:00 | 9:00 | 22 | 45 | 500 |  |  | 2020-09-14 | B20265¦Courtroom 121 West side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 121 East side | [5 empty] | 22 | 46 | 448 |  | 2020-09-16 09:00 | 9:00 | 22 | 46 | 448 |  |  | 2020-09-14 | B20265¦Courtroom 121 East side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 123 East side | [5 empty] | 22 | 49 | 469 |  | 2020-09-16 09:00 | 9:00 | 22 | 49 | 469 |  |  | 2020-09-14 | B20265¦Courtroom 123 East side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 123 West side | [5 empty] | 22 | 50 | 456 |  | 2020-09-16 09:00 | 9:00 | 22 | 50 | 456 |  |  | 2020-09-14 | B20265¦Courtroom 123 West side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 east side | [5 empty] | 22 | 52 | 470 |  | 2020-09-16 09:00 | 9:00 | 22 | 52 | 470 |  |  | 2020-09-14 | B20265¦courtroom 124 east side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 west side | [5 empty] | 22 | 50 | 455 |  | 2020-09-16 09:00 | 9:00 | 22 | 50 | 455 |  |  | 2020-09-14 | B20265¦courtroom 124 west side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 125 South side | [5 empty] | 22 | 50 | 512 |  | 2020-09-16 09:00 | 9:00 | 22 | 50 | 512 |  |  | 2020-09-14 | B20265¦Courtroom 125 South side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 125 North side | [5 empty] | 21 | 52 | 490 |  | 2020-09-16 09:00 | 9:00 | 21 | 52 | 490 |  |  | 2020-09-14 | B20265¦Courtroom 125 North side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 126 south side | [5 empty] | 22 | 50 | 455 |  | 2020-09-16 09:00 | 9:00 | 22 | 50 | 455 |  |  | 2020-09-14 | B20265¦courtroom 126 south side¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom 126 | [5 empty] | 22 | 50 | 485 |  | 2020-09-16 09:00 | 9:00 | 22 | 50 | 485 |  |  | 2020-09-14 | B20265¦hallway by courtroom 126¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Hallway by Receiving | [5 empty] | 20 | 62 | 478 |  | 2020-09-16 09:00 | 9:00 | 20 | 62 | 478 |  | caution | 2020-09-14 | B20265¦Hallway by Receiving¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 21 | 57 | 566 | north section | 2020-09-16 12:00 | 12:00 | 21 | 57 | 566 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 21 | 57 | 561 | south section | 2020-09-16 12:00 | 12:00 | 21 | 57 | 561 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 1E | [5 empty] | 21 | 57 | 480 | ground floor | 2020-09-16 12:00 | 12:00 | 21 | 57 | 480 |  |  | 2020-09-14 | B14164¦Hallway by courtroom 1E¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 20 | 58 | 492 | north section | 2020-09-16 12:00 | 12:00 | 20 | 58 | 492 |  |  | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 20 | 58 | 496 | south section | 2020-09-16 12:00 | 12:00 | 20 | 58 | 496 |  |  | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 6 | [5 empty] | 20 | 59 | 497 | second floor | 2020-09-16 12:00 | 12:00 | 20 | 59 | 497 |  |  | 2020-09-14 | B14164¦Hallway by courtroom 6¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 20 | 60 | 458 | north section | 2020-09-16 12:00 | 12:00 | 20 | 60 | 458 |  | caution | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 21 | 58 | 448 | south section | 2020-09-16 12:00 | 12:00 | 21 | 58 | 448 |  |  | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by Courtroom 10 | [5 empty] | 21 | 58 | 437 | Basement | 2020-09-16 12:00 | 12:00 | 21 | 58 | 437 |  |  | 2020-09-14 | B14164¦Hallway by Courtroom 10¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, basement | [5 empty] | 21 | 58 | 474 |  | 2020-09-16 12:00 | 12:00 | 21 | 58 | 474 |  |  | 2020-09-14 | B14164¦Common area by elevator, basement¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, ground floor | [5 empty] | 21 | 58 | 460 |  | 2020-09-16 12:00 | 12:00 | 21 | 58 | 460 |  |  | 2020-09-14 | B14164¦Common area by elevator, ground floor¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Youth office, ground floor | [5 empty] | 21 | 58 | 579 |  | 2020-09-16 12:00 | 12:00 | 21 | 58 | 579 |  |  | 2020-09-14 | B14164¦Youth office, ground floor¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Family office, ground floor | [5 empty] | 21 | 58 | 533 |  | 2020-09-16 12:00 | 12:00 | 21 | 58 | 533 |  |  | 2020-09-14 | B14164¦Family office, ground floor¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, second floor | [5 empty] | 21 | 58 | 482 |  | 2020-09-16 12:00 | 12:00 | 21 | 58 | 482 |  |  | 2020-09-14 | B14164¦Common area by elevator, second floor¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Outdoors |  |  | 20 | 64 | 436 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B14164¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Lobby | [5 empty] | 21 | 53 | 543 |  | 2020-09-16 12:00 | 12:00 | 21 | 53 | 543 |  |  | 2020-09-14 | B10002¦Lobby¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Skeggs | [5 empty] | 21 | 57 | 589 | Door closed | 2020-09-16 12:00 | 12:00 | 21 | 57 | 589 |  |  | 2020-09-14 | B10002¦Office Skeggs¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Cubicle Office | [5 empty] | 22 | 54 | 598 | Door Open | 2020-09-16 12:00 | 12:00 | 22 | 54 | 598 |  |  | 2020-09-14 | B10002¦Cubicle Office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Outdoors |  |  | 21 | 62 | 421 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10639¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 6 North side | [5 empty] | 21 | 56 | 457 |  | 2020-09-16 12:00 | 12:00 | 21 | 56 | 457 |  |  | 2020-09-14 | B10639¦Courtroom 6 North side¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 6 South side | [5 empty] | 21 | 56 | 434 |  | 2020-09-16 12:00 | 12:00 | 21 | 56 | 434 |  |  | 2020-09-14 | B10639¦Courtroom 6 South side¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | File Room | [5 empty] | 22 | 52 | 602 |  | 2020-09-16 12:00 | 12:00 | 22 | 52 | 602 |  |  | 2020-09-14 | B10002¦File Room¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 6 | [5 empty] | 21 | 55 | 448 |  | 2020-09-16 12:00 | 12:00 | 21 | 55 | 448 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 6¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Outdoors |  |  | 11 | 44 | 385 |  |  |  | North entrance - cloudy, windy | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B21030¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 5 North side | [5 empty] | 21 | 55 | 477 |  | 2020-09-16 12:00 | 12:00 | 21 | 55 | 477 |  |  | 2020-09-14 | B10639¦Courtroom 5 North side¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Courtroom 113 | [5 empty] | 22 | 40 | 525 | Windows closed, no plants | 2020-09-16 09:00 | 9:00 | 22 | 40 | 525 |  | caution | 2020-09-14 | B21030¦Courtroom 113¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 5 South side | [5 empty] | 21 | 54 | 460 |  | 2020-09-16 12:00 | 12:00 | 21 | 54 | 460 |  |  | 2020-09-14 | B10639¦Courtroom 5 South side¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Administration office | [5 empty] | 24 | 38 | 549 | Windows closed, 4 plants along South window | 2020-09-16 09:00 | 9:00 | 24 | 38 | 549 |  | caution | 2020-09-14 | B21030¦Administration office¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Didiodato | [5 empty] | 22 | 53 | 597 | Door Closed | 2020-09-16 12:00 | 12:00 | 22 | 53 | 597 |  |  | 2020-09-14 | B10002¦Office Didiodato¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 5 | [5 empty] | 21 | 55 | 462 |  | 2020-09-16 12:00 | 12:00 | 21 | 55 | 462 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 5¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 58 | 471 | east | 2020-09-16 09:00 | 9:00 | 22 | 58 | 471 |  |  | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 58 | 471 | west | 2020-09-16 09:00 | 9:00 | 22 | 58 | 471 |  |  | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 21 | 61 | 488 | east | 2020-09-16 09:00 | 9:00 | 21 | 61 | 488 |  | caution | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 21 | 60 | 479 | west | 2020-09-16 09:00 | 9:00 | 21 | 60 | 479 |  | caution | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 21 | 61 | 480 | east | 2020-09-16 09:00 | 9:00 | 21 | 61 | 480 |  | caution | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 3 Southeast side | [5 empty] | 21 | 57 | 457 |  | 2020-09-16 12:00 | 12:00 | 21 | 57 | 457 |  |  | 2020-09-14 | B10639¦Courtroom 3 Southeast side¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Outdoors |  |  | 16 | 64 | 388 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10002¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 21 | 61 | 480 | west | 2020-09-16 09:00 | 9:00 | 21 | 61 | 480 |  | caution | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 21 | 61 | 473 | east | 2020-09-16 09:00 | 9:00 | 21 | 61 | 473 |  | caution | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 3 Northeast side | [5 empty] | 21 | 57 | 447 |  | 2020-09-16 12:00 | 12:00 | 21 | 57 | 447 |  |  | 2020-09-14 | B10639¦Courtroom 3 Northeast side¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 21 | 61 | 467 | west | 2020-09-16 09:00 | 9:00 | 21 | 61 | 467 |  | caution | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Library | [5 empty] | 21.6667 | 59 | 555 |  | 2020-09-16 12:00 | 12:00 | 21.6667 | 59 | 555 |  |  | 2020-09-14 | B10246¦Library¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | hallway by courtroom 3 | [5 empty] | 21 | 56 | 445 |  | 2020-09-16 12:00 | 12:00 | 21 | 56 | 445 |  |  | 2020-09-14 | B10639¦hallway by courtroom 3¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 21 | 56 | 474 | east | 2020-09-16 09:00 | 9:00 | 21 | 56 | 474 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | 2nd Floor Holding Cell (hallway) | [5 empty] | 23 | 35 | 470 | Windows closed, no plants | 2020-09-16 09:00 | 9:00 | 23 | 35 | 470 |  | caution | 2020-09-14 | B21030¦2nd Floor Holding Cell (hallway)¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 56 | 486 | west | 2020-09-16 09:00 | 9:00 | 22 | 56 | 486 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 56 | 483 | east | 2020-09-16 09:00 | 9:00 | 22 | 56 | 483 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Lobby by the Statue | [5 empty] | 21 | 58 | 448 |  | 2020-09-16 12:00 | 12:00 | 21 | 58 | 448 |  |  | 2020-09-14 | B10639¦Lobby by the Statue¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Lobby Administration | [5 empty] | 18 | 61 | 505 |  | 2020-09-16 12:00 | 12:00 | 18 | 61 | 505 |  | caution | 2020-09-14 | B10003¦Lobby Administration¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 21.1111 | 59 | 531 | Justice Wilcox chambers | 2020-09-16 12:00 | 12:00 | 21.1111 | 59 | 531 |  |  | 2020-09-14 | B10246¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 55 | 481 | west | 2020-09-16 09:00 | 9:00 | 22 | 55 | 481 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby East Side | [5 empty] | 21 | 56 | 458 |  | 2020-09-16 12:00 | 12:00 | 21 | 56 | 458 |  |  | 2020-09-14 | B10639¦Entrance Lobby East Side¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 56 | 566 | east | 2020-09-16 09:00 | 9:00 | 21 | 56 | 566 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 56 | 501 | west | 2020-09-16 09:00 | 9:00 | 21 | 56 | 501 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | 2nd fl lobby | [5 empty] | 21.6667 | 60 | 517 | Middle of hallway | 2020-09-16 12:00 | 12:00 | 21.6667 | 60 | 517 |  | caution | 2020-09-14 | B10246¦2nd fl lobby¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby West Side | [5 empty] | 21 | 56 | 464 |  | 2020-09-16 12:00 | 12:00 | 21 | 56 | 464 |  |  | 2020-09-14 | B10639¦Entrance Lobby West Side¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 56 | 535 | east | 2020-09-16 09:00 | 9:00 | 22 | 56 | 535 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 55 | 522 | west | 2020-09-16 09:00 | 9:00 | 22 | 55 | 522 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by COA intake office | [5 empty] | 21 | 56 | 467 |  | 2020-09-16 12:00 | 12:00 | 21 | 56 | 467 |  |  | 2020-09-14 | B10639¦Hallway by COA intake office¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Boardroom used as a courtroom | [5 empty] | 24 | 37 | 544 | Windows closed, no plants | 2020-09-16 09:00 | 9:00 | 24 | 37 | 544 |  | caution | 2020-09-14 | B21030¦Boardroom used as a courtroom¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 22 | 62 | 476 | east | 2020-09-16 09:00 | 9:00 | 22 | 62 | 476 |  | caution | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Library | [5 empty] | 18 | 59 | 506 | Wall mount AC unit running | 2020-09-16 12:00 | 12:00 | 18 | 59 | 506 |  |  | 2020-09-14 | B10003¦Library¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 22 | 62 | 474 | west | 2020-09-16 09:00 | 9:00 | 22 | 62 | 474 |  | caution | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by Law Society of Ontario | [5 empty] | 21 | 55 | 466 |  | 2020-09-16 12:00 | 12:00 | 21 | 55 | 466 |  |  | 2020-09-14 | B10639¦Hallway by Law Society of Ontario¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 22 | 62 | 474 | east | 2020-09-16 09:00 | 9:00 | 22 | 62 | 474 |  | caution | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Outdoors |  |  | 21 | 60 | 444 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20265¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 22 | 62 | 492 | west | 2020-09-16 09:00 | 9:00 | 22 | 62 | 492 |  | caution | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 21 | 53 | 488 | east | 2020-09-16 09:00 | 9:00 | 21 | 53 | 488 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | crown main lobby | [5 empty] | 24 | 37 | 643 | No windows, no plants | 2020-09-16 09:00 | 9:00 | 24 | 37 | 643 |  | caution | 2020-09-14 | B21030¦crown main lobby¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 north side | [5 empty] | 22 | 52 | 554 |  | 2020-09-16 12:00 | 12:00 | 22 | 52 | 554 |  |  | 2020-09-14 | B20265¦courtroom M1 north side¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Basement Library | [5 empty] | 18 | 62 | 446 |  | 2020-09-16 12:00 | 12:00 | 18 | 62 | 446 |  | caution | 2020-09-14 | B10003¦Basement Library¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 21 | 53 | 490 | west | 2020-09-16 09:00 | 9:00 | 21 | 53 | 490 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 63 | 526 | east | 2020-09-16 09:00 | 9:00 | 21 | 63 | 526 |  | caution | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 2 | [5 empty] | 21.6667 | 61 | 540 |  | 2020-09-16 12:00 | 12:00 | 21.6667 | 61 | 540 |  | caution | 2020-09-14 | B10246¦Courtroom 2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 south side | [5 empty] | 22 | 52 | 556 |  | 2020-09-16 12:00 | 12:00 | 22 | 52 | 556 |  |  | 2020-09-14 | B20265¦courtroom M1 south side¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 62 | 505 | west | 2020-09-16 09:00 | 9:00 | 21 | 62 | 505 |  | caution | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Trial Co-ordinators Office | [5 empty] | 21.6667 | 59 | 600 |  | 2020-09-16 12:00 | 12:00 | 21.6667 | 59 | 600 |  |  | 2020-09-14 | B10246¦Trial Co-ordinators Office¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Outdoors |  |  | 20 | 64 | 502 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B91122¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by Courtroom M1 | [5 empty] | 22 | 52 | 499 |  | 2020-09-16 12:00 | 12:00 | 22 | 52 | 499 |  |  | 2020-09-14 | B20265¦hallway by Courtroom M1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Outdoors |  |  | 16 | 64 | 391 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10003¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom J South side | [5 empty] | 22 | 53 | 507 |  | 2020-09-16 12:00 | 12:00 | 22 | 53 | 507 |  |  | 2020-09-14 | B20265¦Courtroom J South side¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 61 | 634 | east | 2020-09-16 12:00 | 12:00 | 22 | 61 | 634 |  | caution | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 61 | 631 | west | 2020-09-16 12:00 | 12:00 | 22 | 61 | 631 |  | caution | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Main Floor Entrance Lobby | [5 empty] | 21.6667 | 58 | 525 | Middle of hallway | 2020-09-16 12:00 | 12:00 | 21.6667 | 58 | 525 |  |  | 2020-09-14 | B10246¦Main Floor Entrance Lobby¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 22 | 61 | 593 | east | 2020-09-16 12:00 | 12:00 | 22 | 61 | 593 |  | caution | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom J North side | [5 empty] | 22 | 53 | 510 |  | 2020-09-16 12:00 | 12:00 | 22 | 53 | 510 |  |  | 2020-09-14 | B20265¦Courtroom J North side¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 22 | 60 | 510 | west | 2020-09-16 12:00 | 12:00 | 22 | 60 | 510 |  | caution | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | 58 | [5 empty] | 21.6667 | 58 | 509 | Office to the left of the office 10 | 2020-09-16 12:00 | 12:00 | 21.6667 | 58 | 509 |  |  | 2020-09-14 | B10246¦58¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 21 | 61 | 491 | east | 2020-09-16 12:00 | 12:00 | 21 | 61 | 491 |  | caution | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown attorney admin area | [5 empty] | 24 | 36 | 542 | Windows closed, no plants | 2020-09-16 09:00 | 9:00 | 24 | 36 | 542 |  | caution | 2020-09-14 | B21030¦Crown attorney admin area¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom J | [5 empty] | 22 | 52 | 515 |  | 2020-09-16 12:00 | 12:00 | 22 | 52 | 515 |  |  | 2020-09-14 | B20265¦hallway by courtroom J¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 22 | 62 | 493 | west | 2020-09-16 12:00 | 12:00 | 22 | 62 | 493 |  | caution | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 22 | 62 | 505 | east | 2020-09-16 12:00 | 12:00 | 22 | 62 | 505 |  | caution | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G south side | [5 empty] | 22 | 49 | 595 |  | 2020-09-16 12:00 | 12:00 | 22 | 49 | 595 |  |  | 2020-09-14 | B20265¦courtroom G south side¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 24 | 34 | 457 | Office #1 - SW corner - windows closed, no plants | 2020-09-16 09:00 | 9:00 | 24 | 34 | 457 |  | low | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 21.6667 | 59 | 501 | Office to the right of office 10 | 2020-09-16 12:00 | 12:00 | 21.6667 | 59 | 501 |  |  | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 22 | 62 | 495 | west | 2020-09-16 12:00 | 12:00 | 22 | 62 | 495 |  | caution | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 56 | 521 | east | 2020-09-16 12:00 | 12:00 | 22 | 56 | 521 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G north side | [5 empty] | 22 | 48 | 597 |  | 2020-09-16 12:00 | 12:00 | 22 | 48 | 597 |  |  | 2020-09-14 | B20265¦courtroom G north side¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 56 | 519 | west | 2020-09-16 12:00 | 12:00 | 22 | 56 | 519 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 121 West side | [5 empty] | 22 | 46 | 516 |  | 2020-09-16 12:00 | 12:00 | 22 | 46 | 516 |  |  | 2020-09-14 | B20265¦Courtroom 121 West side¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 56 | 528 | east | 2020-09-16 12:00 | 12:00 | 22 | 56 | 528 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 56 | 522 | west | 2020-09-16 12:00 | 12:00 | 22 | 56 | 522 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 57 | 526 | east | 2020-09-16 12:00 | 12:00 | 21 | 57 | 526 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 121 East side | [5 empty] | 22 | 46 | 497 |  | 2020-09-16 12:00 | 12:00 | 22 | 46 | 497 |  |  | 2020-09-14 | B20265¦Courtroom 121 East side¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 56 | 527 | west | 2020-09-16 12:00 | 12:00 | 21 | 56 | 527 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Outdoors |  |  | 20 | 76 | 381 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B11586¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 56 | 552 | east | 2020-09-16 12:00 | 12:00 | 22 | 56 | 552 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 123 East side | [5 empty] | 22 | 50 | 500 |  | 2020-09-16 12:00 | 12:00 | 22 | 50 | 500 |  |  | 2020-09-14 | B20265¦Courtroom 123 East side¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 55 | 549 | west | 2020-09-16 12:00 | 12:00 | 22 | 55 | 549 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | 1st Floor Lobby | [5 empty] | 21 | 72 | 562 |  | 2020-09-16 12:00 | 12:00 | 21 | 72 | 562 |  | high | 2020-09-14 | B11586¦1st Floor Lobby¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 22 | 65 | 467 | east | 2020-09-16 12:00 | 12:00 | 22 | 65 | 467 |  | caution | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 123 West | [5 empty] | 22 | 50 | 456 |  | 2020-09-16 12:00 | 12:00 | 22 | 50 | 456 |  |  | 2020-09-14 | B20265¦Courtroom 123 West¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 22 | 65 | 461 | west | 2020-09-16 12:00 | 12:00 | 22 | 65 | 461 |  | caution | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courthouse Administration Office | [5 empty] | 21 | 66 | 632 |  | 2020-09-16 12:00 | 12:00 | 21 | 66 | 632 |  | high | 2020-09-14 | B11586¦Courthouse Administration Office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 21 | 66 | 469 | west | 2020-09-16 12:00 | 12:00 | 21 | 66 | 469 |  | high | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 east side | [5 empty] | 22 | 49 | 501 |  | 2020-09-16 12:00 | 12:00 | 22 | 49 | 501 |  |  | 2020-09-14 | B20265¦courtroom 124 east side¦¦Sep-16-2020 12:00
2020-09-16 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 24 | 38 | 710 | No windows, no plants | 2020-09-16 09:00 | 9:00 | 24 | 38 | 710 |  | caution | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 21 | 54 | 548 | east | 2020-09-16 12:00 | 12:00 | 21 | 54 | 548 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 2 | [5 empty] | 22 | 68 | 581 |  | 2020-09-16 12:00 | 12:00 | 22 | 68 | 581 |  | high | 2020-09-14 | B11586¦Courtroom 2¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 21 | 54 | 523 | west | 2020-09-16 12:00 | 12:00 | 21 | 54 | 523 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 west side | [5 empty] | 22 | 48 | 466 |  | 2020-09-16 12:00 | 12:00 | 22 | 48 | 466 |  |  | 2020-09-14 | B20265¦courtroom 124 west side¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown Attorney Beaton Office | [5 empty] | 22 | 67 | 586 |  | 2020-09-16 12:00 | 12:00 | 22 | 67 | 586 |  | high | 2020-09-14 | B11586¦Crown Attorney Beaton Office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 62 | 487 | east | 2020-09-16 12:00 | 12:00 | 21 | 62 | 487 |  | caution | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 62 | 487 | west | 2020-09-16 12:00 | 12:00 | 21 | 62 | 487 |  | caution | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown Attorney Huneault Office | [5 empty] | 22 | 67 | 585 |  | 2020-09-16 12:00 | 12:00 | 22 | 67 | 585 |  | high | 2020-09-14 | B11586¦Crown Attorney Huneault Office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Outdoors |  |  | 20 | 70 | 476 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B91122¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 125 South side | [5 empty] | 22 | 50 | 554 |  | 2020-09-16 12:00 | 12:00 | 22 | 50 | 554 |  |  | 2020-09-14 | B20265¦Courtroom 125 South side¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 1 (Center) | [5 empty] | 21.6667 | 62 | 545 |  | 2020-09-16 12:00 | 12:00 | 21.6667 | 62 | 545 |  | caution | 2020-09-14 | B10246¦Courtroom 1 (Center)¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown Attorney Administartion Area | [5 empty] | 22 | 66 | 639 |  | 2020-09-16 12:00 | 12:00 | 22 | 66 | 639 |  | high | 2020-09-14 | B11586¦Crown Attorney Administartion Area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown attorney admin area | [5 empty] | 22.2222 | 59 | 553 |  | 2020-09-16 12:00 | 12:00 | 22.2222 | 59 | 553 |  |  | 2020-09-14 | B10246¦Crown attorney admin area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Administration office | [5 empty] | 22.2222 | 59 | 555 |  | 2020-09-16 12:00 | 12:00 | 22.2222 | 59 | 555 |  |  | 2020-09-14 | B10246¦Administration office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 Waiting Area | [5 empty] | 22 | 65 | 559 |  | 2020-09-16 12:00 | 12:00 | 22 | 65 | 559 |  | caution | 2020-09-14 | B11586¦Courtroom 1 Waiting Area¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Lunch Room | [5 empty] | 24 | 57 | 521 |  | 2020-09-16 12:00 | 12:00 | 24 | 57 | 521 |  |  | 2020-09-14 | B70451¦Lunch Room¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 125 North side | [5 empty] | 22 | 50 | 540 |  | 2020-09-16 12:00 | 12:00 | 22 | 50 | 540 |  |  | 2020-09-14 | B20265¦Courtroom 125 North side¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 | [5 empty] | 22 | 67 | 524 |  | 2020-09-16 12:00 | 12:00 | 22 | 67 | 524 |  | high | 2020-09-14 | B11586¦Courtroom 1¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 23 | 56 | 519 | east | 2020-09-16 12:00 | 12:00 | 23 | 56 | 519 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | 2nd Floor Holding Cell | [5 empty] | 22 | 67 | 511 |  | 2020-09-16 12:00 | 12:00 | 22 | 67 | 511 |  | high | 2020-09-14 | B11586¦2nd Floor Holding Cell¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 23 | 57 | 511 | west | 2020-09-16 12:00 | 12:00 | 23 | 57 | 511 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 21.6667 | 57 | 514 | Basement lobby - bottom of the stairs | 2020-09-16 12:00 | 12:00 | 21.6667 | 57 | 514 |  |  | 2020-09-14 | B10246¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 126 south side | [5 empty] | 22 | 48 | 500 |  | 2020-09-16 12:00 | 12:00 | 22 | 48 | 500 |  |  | 2020-09-14 | B20265¦courtroom 126 south side¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Judge Office | [5 empty] | 22 | 66 | 523 |  | 2020-09-16 12:00 | 12:00 | 22 | 66 | 523 |  | high | 2020-09-14 | B11586¦Judge Office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 602 | [5 empty] | 23 | 58 | 530 |  | 2020-09-16 12:00 | 12:00 | 23 | 58 | 530 |  |  | 2020-09-14 | B70451¦hallway by courtroom 602¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 603 | [5 empty] | 23 | 58 | 532 |  | 2020-09-16 12:00 | 12:00 | 23 | 58 | 532 |  |  | 2020-09-14 | B70451¦hallway by courtroom 603¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 21.1111 | 60 | 540 | Basement cells - hallway | 2020-09-16 12:00 | 12:00 | 21.1111 | 60 | 540 |  | caution | 2020-09-14 | B10246¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom 126 | [5 empty] | 23 | 49 | 578 |  | 2020-09-16 12:00 | 12:00 | 23 | 49 | 578 |  |  | 2020-09-14 | B20265¦hallway by courtroom 126¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | conference room 4 | [5 empty] | 23 | 58 | 498 |  | 2020-09-16 12:00 | 12:00 | 23 | 58 | 498 |  |  | 2020-09-14 | B70451¦conference room 4¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 57 | 495 | east | 2020-09-16 12:00 | 12:00 | 23 | 57 | 495 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 56 | 495 | west | 2020-09-16 12:00 | 12:00 | 23 | 56 | 495 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Hallway by Receiving | [5 empty] | 22 | 54 | 524 |  | 2020-09-16 12:00 | 12:00 | 22 | 54 | 524 |  |  | 2020-09-14 | B20265¦Hallway by Receiving¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 607 | [5 empty] | 23 | 57 | 573 |  | 2020-09-16 12:00 | 12:00 | 23 | 57 | 573 |  |  | 2020-09-14 | B70451¦hallway by courtroom 607¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | enforcement/finance office | [5 empty] | 24 | 56 | 524 |  | 2020-09-16 12:00 | 12:00 | 24 | 56 | 524 |  |  | 2020-09-14 | B70451¦enforcement/finance office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 23 | 57 | 506 | east | 2020-09-16 12:00 | 12:00 | 23 | 57 | 506 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 23 | 57 | 497 | west | 2020-09-16 12:00 | 12:00 | 23 | 57 | 497 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 605 | [5 empty] | 23 | 58 | 558 |  | 2020-09-16 12:00 | 12:00 | 23 | 58 | 558 |  |  | 2020-09-14 | B70451¦hallway by courtroom 605¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters administration office | [5 empty] | 23 | 57 | 514 |  | 2020-09-16 12:00 | 12:00 | 23 | 57 | 514 |  |  | 2020-09-14 | B70451¦masters administration office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-10 | [5 empty] | 23 | 58 | 495 |  | 2020-09-16 12:00 | 12:00 | 23 | 58 | 495 |  |  | 2020-09-14 | B70451¦room 6-10¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-9 | [5 empty] | 22 | 58 | 501 |  | 2020-09-16 12:00 | 12:00 | 22 | 58 | 501 |  |  | 2020-09-14 | B70451¦room 6-9¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters library | [5 empty] | 23 | 57 | 514 |  | 2020-09-16 12:00 | 12:00 | 23 | 57 | 514 |  |  | 2020-09-14 | B70451¦masters library¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-4 | [5 empty] | 22 | 58 | 503 |  | 2020-09-16 12:00 | 12:00 | 22 | 58 | 503 |  |  | 2020-09-14 | B70451¦room 6-4¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | reception area-masters | [5 empty] | 22 | 59 | 503 |  | 2020-09-16 12:00 | 12:00 | 22 | 59 | 503 |  |  | 2020-09-14 | B70451¦reception area-masters¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Outdoors |  |  | 20 | 70 | 476 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70451¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Outdoors |  |  | 17.2222 | 75 | 451 |  |  |  | Directly outside main entrance - Rain | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10246¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Outdoors |  |  | 10 | 46 | 400 |  |  |  | North entrance - partly cloudy, windy | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B21030¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | 2nd Floor Holding Cell (hallway) | [5 empty] | 22 | 40 | 462 | Windows closed, no plants | 2020-09-16 15:00 | 15:00 | 22 | 40 | 462 |  | caution | 2020-09-14 | B21030¦2nd Floor Holding Cell (hallway)¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Boardroom used as a courtroom | [5 empty] | 25 | 33 | 504 | Windows closed, no plants | 2020-09-16 15:00 | 15:00 | 25 | 33 | 504 |  | low | 2020-09-14 | B21030¦Boardroom used as a courtroom¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Courtroom 113 | [5 empty] | 25 | 33 | 504 | Windows closed, no plants | 2020-09-16 15:00 | 15:00 | 25 | 33 | 504 |  | low | 2020-09-14 | B21030¦Courtroom 113¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | crown main lobby | [5 empty] | 24 | 36 | 650 | No windows, no plants | 2020-09-16 15:00 | 15:00 | 24 | 36 | 650 |  | caution | 2020-09-14 | B21030¦crown main lobby¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown attorney admin area | [5 empty] | 24 | 34 | 549 | Windows closed, no plants | 2020-09-16 15:00 | 15:00 | 24 | 34 | 549 |  | low | 2020-09-14 | B21030¦Crown attorney admin area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 21 | 57 | 512 | north section | 2020-09-16 15:00 | 15:00 | 21 | 57 | 512 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 21 | 57 | 496 | south section | 2020-09-16 15:00 | 15:00 | 21 | 57 | 496 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by Courtroom 1E | [5 empty] | 21 | 57 | 480 | ground floor | 2020-09-16 15:00 | 15:00 | 21 | 57 | 480 |  |  | 2020-09-14 | B14164¦Hallway by Courtroom 1E¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 20 | 58 | 520 | north section | 2020-09-16 15:00 | 15:00 | 20 | 58 | 520 |  |  | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 24 | 33 | 476 | Office #1 - SW corner - Windows closed, no plants | 2020-09-16 15:00 | 15:00 | 24 | 33 | 476 |  | low | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 20 | 58 | 499 | south section | 2020-09-16 15:00 | 15:00 | 20 | 58 | 499 |  |  | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 6 | [5 empty] | 20 | 59 | 481 | second floor | 2020-09-16 15:00 | 15:00 | 20 | 59 | 481 |  |  | 2020-09-14 | B14164¦Hallway by courtroom 6¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 21 | 60 | 460 | north section | 2020-09-16 15:00 | 15:00 | 21 | 60 | 460 |  | caution | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 21 | 59 | 456 | south section | 2020-09-16 15:00 | 15:00 | 21 | 59 | 456 |  |  | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by Courtroom 10 | [5 empty] | 21 | 58 | 458 | basement | 2020-09-16 15:00 | 15:00 | 21 | 58 | 458 |  |  | 2020-09-14 | B14164¦Hallway by Courtroom 10¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, basement | [5 empty] | 21 | 59 | 485 |  | 2020-09-16 15:00 | 15:00 | 21 | 59 | 485 |  |  | 2020-09-14 | B14164¦Common area by elevator, basement¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, ground floor | [5 empty] | 21 | 60 | 493 |  | 2020-09-16 15:00 | 15:00 | 21 | 60 | 493 |  | caution | 2020-09-14 | B14164¦Common area by elevator, ground floor¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Youth office, ground floor | [5 empty] | 21 | 60 | 588 |  | 2020-09-16 15:00 | 15:00 | 21 | 60 | 588 |  | caution | 2020-09-14 | B14164¦Youth office, ground floor¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Family office, Ground floor | [5 empty] | 21 | 59 | 543 |  | 2020-09-16 15:00 | 15:00 | 21 | 59 | 543 |  |  | 2020-09-14 | B14164¦Family office, Ground floor¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, second floor | [5 empty] | 21 | 59 | 491 |  | 2020-09-16 15:00 | 15:00 | 21 | 59 | 491 |  |  | 2020-09-14 | B14164¦Common area by elevator, second floor¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Outdoors |  |  | 22 | 60 | 393 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B14164¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 24 | 35 | 531 | Office #2 - NE corner - no windows, no plants | 2020-09-16 15:00 | 15:00 | 24 | 35 | 531 |  | caution | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-16-2020 15:00
2020-09-16 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Outdoors |  |  | 16 | 43 | 401 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B12955¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Main Floor Entrance Lobby | [5 empty] | 13 | 48 | 465 | front lobby | 2020-09-16 12:00 | 12:00 | 13 | 48 | 465 |  |  | 2020-09-14 | B12955¦Main Floor Entrance Lobby¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | OTHER | [5 empty] | 15 | 62 | 496 | waiting area | 2020-09-16 12:00 | 12:00 | 15 | 62 | 496 |  | caution | 2020-09-14 | B12955¦OTHER¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Administration office | [5 empty] | 18 | 61 | 464 |  | 2020-09-16 12:00 | 12:00 | 18 | 61 | 464 |  | caution | 2020-09-14 | B12955¦Administration office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 103 | [5 empty] | 20 | 46 | 418 |  | 2020-09-16 12:00 | 12:00 | 20 | 46 | 418 |  |  | 2020-09-14 | B12955¦Courtroom 103¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 203 | [5 empty] | 21 | 41 | 432 |  | 2020-09-16 12:00 | 12:00 | 21 | 41 | 432 |  |  | 2020-09-14 | B12955¦Courtroom 203¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Lobby | [5 empty] | 23 | 46 | 569 |  | 2020-09-16 15:00 | 15:00 | 23 | 46 | 569 |  |  | 2020-09-14 | B10002¦Lobby¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Skeggs | [5 empty] | 22 | 43 | 604 |  | 2020-09-16 15:00 | 15:00 | 22 | 43 | 604 |  |  | 2020-09-14 | B10002¦Office Skeggs¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Cubicle Office | [5 empty] | 22 | 47 | 606 | Door Open | 2020-09-16 15:00 | 15:00 | 22 | 47 | 606 |  |  | 2020-09-14 | B10002¦Cubicle Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | File Room | [5 empty] | 23 | 54 | 791 | Two employees moving things around | 2020-09-16 15:00 | 15:00 | 23 | 54 | 791 |  |  | 2020-09-14 | B10002¦File Room¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Didiodato | [5 empty] | 22 | 51 | 643 | Door Open | 2020-09-16 15:00 | 15:00 | 22 | 51 | 643 |  |  | 2020-09-14 | B10002¦Office Didiodato¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Library | [5 empty] | 21.1111 | 59 | 516 |  | 2020-09-16 15:00 | 15:00 | 21.1111 | 59 | 516 |  |  | 2020-09-14 | B10246¦Library¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Outdoors |  |  | 16 | 59 | 382 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10002¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 20.5556 | 60 | 473 | Justice Wilcox chambers | 2020-09-16 15:00 | 15:00 | 20.5556 | 60 | 473 |  | caution | 2020-09-14 | B10246¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | 2nd fl lobby | [5 empty] | 21.1111 | 59 | 477 | Middle of hallway | 2020-09-16 15:00 | 15:00 | 21.1111 | 59 | 477 |  |  | 2020-09-14 | B10246¦2nd fl lobby¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 2 | [5 empty] | 21.1111 | 59 | 473 |  | 2020-09-16 15:00 | 15:00 | 21.1111 | 59 | 473 |  |  | 2020-09-14 | B10246¦Courtroom 2¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Lobby Administration | [5 empty] | 19 | 58 | 604 |  | 2020-09-16 15:00 | 15:00 | 19 | 58 | 604 |  |  | 2020-09-14 | B10003¦Lobby Administration¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Trial Co-ordinators Office | [5 empty] | 21.6667 | 58 | 540 |  | 2020-09-16 15:00 | 15:00 | 21.6667 | 58 | 540 |  |  | 2020-09-14 | B10246¦Trial Co-ordinators Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Library | [5 empty] | 19 | 58 | 597 | Wall mounted AC unit running | 2020-09-16 15:00 | 15:00 | 19 | 58 | 597 |  |  | 2020-09-14 | B10003¦Library¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Main Floor Entrance Lobby | [5 empty] | 21.6667 | 57 | 487 | Middle of hallway | 2020-09-16 15:00 | 15:00 | 21.6667 | 57 | 487 |  |  | 2020-09-14 | B10246¦Main Floor Entrance Lobby¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 21.1111 | 55 | 462 | Office to the left of office 10 | 2020-09-16 15:00 | 15:00 | 21.1111 | 55 | 462 |  |  | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Basement Library | [5 empty] | 18 | 61 | 469 |  | 2020-09-16 15:00 | 15:00 | 18 | 61 | 469 |  | caution | 2020-09-14 | B10003¦Basement Library¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 21.1111 | 55 | 450 | Office to the right of office 10 | 2020-09-16 15:00 | 15:00 | 21.1111 | 55 | 450 |  |  | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 1 (Center) | [5 empty] | 21.1111 | 60 | 541 |  | 2020-09-16 15:00 | 15:00 | 21.1111 | 60 | 541 |  | caution | 2020-09-14 | B10246¦Courtroom 1 (Center)¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Outdoors |  |  | 16 | 58 | 402 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10003¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown attorney admin area | [5 empty] | 21.6667 | 56 | 455 |  | 2020-09-16 15:00 | 15:00 | 21.6667 | 56 | 455 |  |  | 2020-09-14 | B10246¦Crown attorney admin area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Administration office | [5 empty] | 21.6667 | 55 | 518 |  | 2020-09-16 15:00 | 15:00 | 21.6667 | 55 | 518 |  |  | 2020-09-14 | B10246¦Administration office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 21.6667 | 56 | 466 | Basement lobby - bottom of the stairs | 2020-09-16 15:00 | 15:00 | 21.6667 | 56 | 466 |  |  | 2020-09-14 | B10246¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 20.5556 | 59 | 487 | Basement cells - hallway | 2020-09-16 15:00 | 15:00 | 20.5556 | 59 | 487 |  |  | 2020-09-14 | B10246¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Outdoors |  |  | 16.1111 | 65 | 394 |  |  |  | Directly outside main entrance: partly cloudy/sun | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10246¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Security Desk | [5 empty] | 22 | 58 | 495 |  | 2020-09-16 09:00 | 9:00 | 22 | 58 | 495 |  |  | 2020-09-14 | B11589¦Security Desk¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom A | [5 empty] | 22 | 54 | 435 |  | 2020-09-16 09:00 | 9:00 | 22 | 54 | 435 |  |  | 2020-09-14 | B11589¦Courtroom A¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Outdoors |  |  | 15 | 23 | 402 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B12955¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom B | [5 empty] | 22 | 60 | 420 |  | 2020-09-16 09:00 | 9:00 | 22 | 60 | 420 |  | caution | 2020-09-14 | B11589¦Courtroom B¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Main Floor Entrance Lobby | [5 empty] | 15 | 33 | 435 | front lobby | 2020-09-16 15:00 | 15:00 | 15 | 33 | 435 |  | low | 2020-09-14 | B12955¦Main Floor Entrance Lobby¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom C | [5 empty] | 22 | 59 | 416 |  | 2020-09-16 09:00 | 9:00 | 22 | 59 | 416 |  |  | 2020-09-14 | B11589¦Courtroom C¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | OTHER | [5 empty] | 17 | 46 | 489 | waiting area | 2020-09-16 15:00 | 15:00 | 17 | 46 | 489 |  |  | 2020-09-14 | B12955¦OTHER¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom D | [5 empty] | 22 | 57 | 480 |  | 2020-09-16 09:00 | 9:00 | 22 | 57 | 480 |  |  | 2020-09-14 | B11589¦Courtroom D¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Administration office | [5 empty] | 21 | 41 | 456 |  | 2020-09-16 15:00 | 15:00 | 21 | 41 | 456 |  |  | 2020-09-14 | B12955¦Administration office¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom E | [5 empty] | 22 | 65 | 438 |  | 2020-09-16 09:00 | 9:00 | 22 | 65 | 438 |  | caution | 2020-09-14 | B11589¦Courtroom E¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Walker | [5 empty] | 22 | 61 | 420 |  | 2020-09-16 09:00 | 9:00 | 22 | 61 | 420 |  | caution | 2020-09-14 | B11589¦Office Walker¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Martin | [5 empty] | 21 | 63 | 424 |  | 2020-09-16 09:00 | 9:00 | 21 | 63 | 424 |  | caution | 2020-09-14 | B11589¦Office Martin¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 103 | [5 empty] | 21 | 47 | 425 |  | 2020-09-16 15:00 | 15:00 | 21 | 47 | 425 |  |  | 2020-09-14 | B12955¦Courtroom 103¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Baker | [5 empty] | 21 | 59 | 428 |  | 2020-09-16 09:00 | 9:00 | 21 | 59 | 428 |  |  | 2020-09-14 | B11589¦Office Baker¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Attorney General Administration Office | [5 empty] | 22 | 62 | 473 |  | 2020-09-16 09:00 | 9:00 | 22 | 62 | 473 |  | caution | 2020-09-14 | B11589¦Attorney General Administration Office¦¦Sep-16-2020 09:00
2020-09-16 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 203 | [5 empty] | 20 | 45 | 432 |  | 2020-09-16 15:00 | 15:00 | 20 | 45 | 432 |  |  | 2020-09-14 | B12955¦Courtroom 203¦¦Sep-16-2020 15:00
2020-09-16 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Hallway | [5 empty] | 22 | 59 | 442 |  | 2020-09-16 09:00 | 9:00 | 22 | 59 | 442 |  |  | 2020-09-14 | B11589¦Hallway¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom H | [5 empty] | 22 | 60 | 401 |  | 2020-09-16 09:00 | 9:00 | 22 | 60 | 401 |  | caution | 2020-09-14 | B11589¦Courtroom H¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom J | [5 empty] | 21 | 66 | 399 |  | 2020-09-16 09:00 | 9:00 | 21 | 66 | 399 |  | high | 2020-09-14 | B11589¦Courtroom J¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Outdoors |  |  | 19 | 74 | 399 |  |  |  |  | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B11589¦Outdoors¦¦Sep-16-2020 09:00
2020-09-16 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Security Desk | [5 empty] | 21 | 61 | 612 |  | 2020-09-16 12:00 | 12:00 | 21 | 61 | 612 |  | caution | 2020-09-14 | B11589¦Security Desk¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom A | [5 empty] | 21 | 58 | 459 |  | 2020-09-16 12:00 | 12:00 | 21 | 58 | 459 |  |  | 2020-09-14 | B11589¦Courtroom A¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom B | [5 empty] | 22 | 66 | 535 |  | 2020-09-16 12:00 | 12:00 | 22 | 66 | 535 |  | high | 2020-09-14 | B11589¦Courtroom B¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom C | [5 empty] | 21 | 65 | 582 |  | 2020-09-16 12:00 | 12:00 | 21 | 65 | 582 |  | caution | 2020-09-14 | B11589¦Courtroom C¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom D | [5 empty] | 21 | 59 | 521 |  | 2020-09-16 12:00 | 12:00 | 21 | 59 | 521 |  |  | 2020-09-14 | B11589¦Courtroom D¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom E | [8 empty] | No Access | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B11589¦Courtroom E¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Walker | [5 empty] | 21 | 62 | 580 |  | 2020-09-16 12:00 | 12:00 | 21 | 62 | 580 |  | caution | 2020-09-14 | B11589¦Office Walker¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Martin | [5 empty] | 21 | 65 | 521 |  | 2020-09-16 12:00 | 12:00 | 21 | 65 | 521 |  | caution | 2020-09-14 | B11589¦Office Martin¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Baker | [5 empty] | 21 | 67 | 454 |  | 2020-09-16 12:00 | 12:00 | 21 | 67 | 454 |  | high | 2020-09-14 | B11589¦Office Baker¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Attorney General Administration Office | [5 empty] | 22 | 63 | 465 |  | 2020-09-16 12:00 | 12:00 | 22 | 63 | 465 |  | caution | 2020-09-14 | B11589¦Attorney General Administration Office¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Hallway | [5 empty] | 22 | 62 | 471 |  | 2020-09-16 12:00 | 12:00 | 22 | 62 | 471 |  | caution | 2020-09-14 | B11589¦Hallway¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom H | [5 empty] | 22 | 63 | 418 |  | 2020-09-16 12:00 | 12:00 | 22 | 63 | 418 |  | caution | 2020-09-14 | B11589¦Courtroom H¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom J | [5 empty] | 20 | 66 | 393 |  | 2020-09-16 12:00 | 12:00 | 20 | 66 | 393 |  | high | 2020-09-14 | B11589¦Courtroom J¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Outdoors |  |  | 20 | 71 | 387 |  |  |  |  | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B11589¦Outdoors¦¦Sep-16-2020 12:00
2020-09-16 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Outdoors |  |  | 19 | 58 | 365 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B11586¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | 1st Floor Lobby | [5 empty] | 21 | 68 | 542 |  | 2020-09-16 15:00 | 15:00 | 21 | 68 | 542 |  | high | 2020-09-14 | B11586¦1st Floor Lobby¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courthouse Administration Office | [5 empty] | 22 | 67 | 572 |  | 2020-09-16 15:00 | 15:00 | 22 | 67 | 572 |  | high | 2020-09-14 | B11586¦Courthouse Administration Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 2 | [5 empty] | 21 | 54 | 549 |  | 2020-09-16 15:00 | 15:00 | 21 | 54 | 549 |  |  | 2020-09-14 | B11586¦Courtroom 2¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown Attorney Beaton Office | [5 empty] | 22 | 64 | 541 |  | 2020-09-16 15:00 | 15:00 | 22 | 64 | 541 |  | caution | 2020-09-14 | B11586¦Crown Attorney Beaton Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown Attorney Huneault Office | [5 empty] | 22 | 64 | 541 |  | 2020-09-16 15:00 | 15:00 | 22 | 64 | 541 |  | caution | 2020-09-14 | B11586¦Crown Attorney Huneault Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown Attorney Administration Area | [5 empty] | 22 | 64 | 570 |  | 2020-09-16 15:00 | 15:00 | 22 | 64 | 570 |  | caution | 2020-09-14 | B11586¦Crown Attorney Administration Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 Waiting Area | [5 empty] | 22 | 62 | 525 |  | 2020-09-16 15:00 | 15:00 | 22 | 62 | 525 |  | caution | 2020-09-14 | B11586¦Courtroom 1 Waiting Area¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 | [5 empty] | 22 | 62 | 501 |  | 2020-09-16 15:00 | 15:00 | 22 | 62 | 501 |  | caution | 2020-09-14 | B11586¦Courtroom 1¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | 2nd Floor Holding Cell | [5 empty] | 22 | 62 | 494 |  | 2020-09-16 15:00 | 15:00 | 22 | 62 | 494 |  | caution | 2020-09-14 | B11586¦2nd Floor Holding Cell¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Judge Office | [5 empty] | 22 | 62 | 484 |  | 2020-09-16 15:00 | 15:00 | 22 | 62 | 484 |  | caution | 2020-09-14 | B11586¦Judge Office¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Outdoors |  |  | 23 | 57 | 422 |  |  |  |  | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10639¦Outdoors¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Security Desk | [5 empty] | 22 | 61 | 565 |  | 2020-09-16 15:00 | 15:00 | 22 | 61 | 565 |  | caution | 2020-09-14 | B11589¦Security Desk¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom A | [5 empty] | 22 | 60 | 502 |  | 2020-09-16 15:00 | 15:00 | 22 | 60 | 502 |  | caution | 2020-09-14 | B11589¦Courtroom A¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 6 North side | [5 empty] | 21 | 56 | 442 |  | 2020-09-16 15:00 | 15:00 | 21 | 56 | 442 |  |  | 2020-09-14 | B10639¦Courtroom 6 North side¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom B | [5 empty] | 22 | 64 | 465 |  | 2020-09-16 15:00 | 15:00 | 22 | 64 | 465 |  | caution | 2020-09-14 | B11589¦Courtroom B¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom C | [5 empty] | 22 | 65 | 470 |  | 2020-09-16 15:00 | 15:00 | 22 | 65 | 470 |  | caution | 2020-09-14 | B11589¦Courtroom C¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom D | [5 empty] | 22 | 61 | 510 |  | 2020-09-16 15:00 | 15:00 | 22 | 61 | 510 |  | caution | 2020-09-14 | B11589¦Courtroom D¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom E | [5 empty] | 22 | 61 | 411 |  | 2020-09-16 15:00 | 15:00 | 22 | 61 | 411 |  | caution | 2020-09-14 | B11589¦Courtroom E¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 6 south side | [5 empty] | 21 | 56 | 432 |  | 2020-09-16 15:00 | 15:00 | 21 | 56 | 432 |  |  | 2020-09-14 | B10639¦courtroom 6 south side¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Walker | [5 empty] | 22 | 64 | 497 |  | 2020-09-16 15:00 | 15:00 | 22 | 64 | 497 |  | caution | 2020-09-14 | B11589¦Office Walker¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Martin | [5 empty] | 22 | 66 | 499 |  | 2020-09-16 15:00 | 15:00 | 22 | 66 | 499 |  | high | 2020-09-14 | B11589¦Office Martin¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 6 | [5 empty] | 21 | 56 | 423 |  | 2020-09-16 15:00 | 15:00 | 21 | 56 | 423 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 6¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Baker | [5 empty] | 22 | 64 | 445 |  | 2020-09-16 15:00 | 15:00 | 22 | 64 | 445 |  | caution | 2020-09-14 | B11589¦Office Baker¦¦Sep-16-2020 15:00
2020-09-16 | 0:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 17.7917 | 58.9167 | 543.1333 | Average of the hour | 2020-09-16 | 0:00 | 17.7917 | 58.9167 | 543.1333 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.9 | 48.7083 | 598.4583 | Average of the hour | 2020-09-16 | 0:00 | 20.9 | 48.7083 | 598.4583 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 18.5792 | 66.2958 | 415.6667 | Average of the hour | 2020-09-16 | 0:00 | 18.5792 | 66.2958 | 415.6667 |  | high | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.4583 | 55.9983 | 407.25 | Average of the hour | 2020-09-16 | 0:00 | 22.4583 | 55.9983 | 407.25 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 19.6567 | 70.3242 | 448.8333 | Average of the hour | 2020-09-16 | 0:00 | 19.6567 | 70.3242 | 448.8333 |  | high | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 23.2142 | 51.3892 | 463.5833 | Average of the hour | 2020-09-16 | 0:00 | 23.2142 | 51.3892 | 463.5833 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.6033 | 45.1104 | 416.1667 | Average of the hour | 2020-09-16 | 0:00 | 24.6033 | 45.1104 | 416.1667 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.3733 | 54.7396 | 414.8333 | Average of the hour | 2020-09-16 | 0:00 | 22.3733 | 54.7396 | 414.8333 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.64 | 50.7026 | 511.9489 | Average of the hour | 2020-09-16 | 0:00 | 21.64 | 50.7026 | 511.9489 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 24.2916 | 45.9293 | 305.5044 | Average of the hour | 2020-09-16 | 0:00 | 24.2916 | 45.9293 | 305.5044 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.352 | 47.0112 | 370.8535 | Average of the hour | 2020-09-16 | 0:00 | 23.352 | 47.0112 | 370.8535 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 23.13 | 52.9571 | 616.8333 | Average of the hour | 2020-09-16 | 0:00 | 23.13 | 52.9571 | 616.8333 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 22.3375 | 50.3942 | 415.5833 | Average of the hour | 2020-09-16 | 0:00 | 22.3375 | 50.3942 | 415.5833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.7058 | 54.4304 | 412.5833 | Average of the hour | 2020-09-16 | 0:00 | 22.7058 | 54.4304 | 412.5833 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.95 | 46.5 | 448.2833 | Average of the hour | 2020-09-16 | 0:00 | 21.95 | 46.5 | 448.2833 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 20.7 | 51.1925 | 416.2833 | Average of the hour | 2020-09-16 | 0:00 | 20.7 | 51.1925 | 416.2833 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 14.6417 |  |  | Average of the hour | 2020-09-16 | 0:00 | 14.6417 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 15.5583 |  |  | Average of the hour | 2020-09-16 | 0:00 | 15.5583 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 15.1526 |  | 448.4667 | Average of the hour | 2020-09-16 | 0:00 | 15.1526 |  | 448.4667 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 15.0577 |  | 379.4167 | Average of the hour | 2020-09-16 | 0:00 | 15.0577 |  | 379.4167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 48.8083 |  | Average of the hour | 2020-09-16 | 0:00 |  | 48.8083 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 48.5 |  | Average of the hour | 2020-09-16 | 0:00 |  | 48.5 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.4634 | 44.9387 | 439.6806 | Average of the hour | 2020-09-16 | 0:00 | 22.4634 | 44.9387 | 439.6806 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 53.3695 | 687.5106 | Average of the hour | 2020-09-16 | 0:00 |  | 53.3695 | 687.5106 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.2986 | 45.2558 |  | Average of the hour | 2020-09-16 | 0:00 | 21.2986 | 45.2558 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 00:00
2020-09-16 | 0:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 | 0:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 00:00
2020-09-16 | 1:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 17.525 | 58.625 | 478.5 | Average of the hour | 2020-09-16 01:00 | 1:00 | 17.525 | 58.625 | 478.5 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.9 | 48.5 | 597.5 | Average of the hour | 2020-09-16 01:00 | 1:00 | 20.9 | 48.5 | 597.5 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 18.525 | 65.1517 | 410.1667 | Average of the hour | 2020-09-16 01:00 | 1:00 | 18.525 | 65.1517 | 410.1667 |  | high | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.495 | 54.7917 | 394.5 | Average of the hour | 2020-09-16 01:00 | 1:00 | 22.495 | 54.7917 | 394.5 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 19.65 | 68.8383 | 437.75 | Average of the hour | 2020-09-16 01:00 | 1:00 | 19.65 | 68.8383 | 437.75 |  | high | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 23.4125 | 51.6558 | 463.4167 | Average of the hour | 2020-09-16 01:00 | 1:00 | 23.4125 | 51.6558 | 463.4167 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.64 | 45.4042 | 415.5833 | Average of the hour | 2020-09-16 01:00 | 1:00 | 24.64 | 45.4042 | 415.5833 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.3833 | 55.5375 | 414.3333 | Average of the hour | 2020-09-16 01:00 | 1:00 | 22.3833 | 55.5375 | 414.3333 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.7236 | 50.7877 | 510.6118 | Average of the hour | 2020-09-16 01:00 | 1:00 | 21.7236 | 50.7877 | 510.6118 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 24.3254 | 46.1597 | 303.1896 | Average of the hour | 2020-09-16 01:00 | 1:00 | 24.3254 | 46.1597 | 303.1896 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.352 | 47.063 | 369.7206 | Average of the hour | 2020-09-16 01:00 | 1:00 | 23.352 | 47.063 | 369.7206 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 23.1267 | 53.1825 | 613 | Average of the hour | 2020-09-16 01:00 | 1:00 | 23.1267 | 53.1825 | 613 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 22.4067 | 50.8767 | 412.1667 | Average of the hour | 2020-09-16 01:00 | 1:00 | 22.4067 | 50.8767 | 412.1667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.6933 | 54.7479 | 410.1667 | Average of the hour | 2020-09-16 01:00 | 1:00 | 22.6933 | 54.7479 | 410.1667 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.9 | 46.875 | 441.0917 | Average of the hour | 2020-09-16 01:00 | 1:00 | 21.9 | 46.875 | 441.0917 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 20.925 | 50.7733 | 415.3417 | Average of the hour | 2020-09-16 01:00 | 1:00 | 20.925 | 50.7733 | 415.3417 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 14.7417 |  |  | Average of the hour | 2020-09-16 01:00 | 1:00 | 14.7417 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 15.55 |  |  | Average of the hour | 2020-09-16 01:00 | 1:00 | 15.55 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 15.167 |  | 440.2083 | Average of the hour | 2020-09-16 01:00 | 1:00 | 15.167 |  | 440.2083 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 15.0875 |  | 379.25 | Average of the hour | 2020-09-16 01:00 | 1:00 | 15.0875 |  | 379.25 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 49.1167 |  | Average of the hour | 2020-09-16 01:00 | 1:00 |  | 49.1167 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 49.0667 |  | Average of the hour | 2020-09-16 01:00 | 1:00 |  | 49.0667 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.3344 | 45.4725 | 440.5156 | Average of the hour | 2020-09-16 01:00 | 1:00 | 22.3344 | 45.4725 | 440.5156 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 52.53 | 687.0548 | Average of the hour | 2020-09-16 01:00 | 1:00 |  | 52.53 | 687.0548 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.4743 | 45.8039 |  | Average of the hour | 2020-09-16 01:00 | 1:00 | 21.4743 | 45.8039 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 01:00
2020-09-16 | 1:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 01:00 | 1:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 01:00
2020-09-16 | 2:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 16.9583 | 61.2083 | 440.7 | Average of the hour | 2020-09-16 02:00 | 2:00 | 16.9583 | 61.2083 | 440.7 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.875 | 48.7917 | 576.25 | Average of the hour | 2020-09-16 02:00 | 2:00 | 20.875 | 48.7917 | 576.25 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 18.4242 | 60.375 | 411 | Average of the hour | 2020-09-16 02:00 | 2:00 | 18.4242 | 60.375 | 411 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.3258 | 50.8333 | 399.8333 | Average of the hour | 2020-09-16 02:00 | 2:00 | 22.3258 | 50.8333 | 399.8333 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 19.5892 | 63.5367 | 440.6667 | Average of the hour | 2020-09-16 02:00 | 2:00 | 19.5892 | 63.5367 | 440.6667 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 23.6083 | 51.7333 | 463.5 | Average of the hour | 2020-09-16 02:00 | 2:00 | 23.6083 | 51.7333 | 463.5 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.6733 | 45.6954 | 414 | Average of the hour | 2020-09-16 02:00 | 2:00 | 24.6733 | 45.6954 | 414 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.37 | 56.5042 | 413 | Average of the hour | 2020-09-16 02:00 | 2:00 | 22.37 | 56.5042 | 413 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.7236 | 51.0947 | 509.4175 | Average of the hour | 2020-09-16 02:00 | 2:00 | 21.7236 | 51.0947 | 509.4175 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 24.3931 | 46.6703 | 303.0194 | Average of the hour | 2020-09-16 02:00 | 2:00 | 24.3931 | 46.6703 | 303.0194 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.352 | 47.2419 | 367.1177 | Average of the hour | 2020-09-16 02:00 | 2:00 | 23.352 | 47.2419 | 367.1177 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 23.15 | 53.6517 | 611.5833 | Average of the hour | 2020-09-16 02:00 | 2:00 | 23.15 | 53.6517 | 611.5833 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 22.4817 | 51.5092 | 409.6667 | Average of the hour | 2020-09-16 02:00 | 2:00 | 22.4817 | 51.5092 | 409.6667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.8233 | 55.1458 | 410.6667 | Average of the hour | 2020-09-16 02:00 | 2:00 | 22.8233 | 55.1458 | 410.6667 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.9 | 47.375 | 444.2417 | Average of the hour | 2020-09-16 02:00 | 2:00 | 21.9 | 47.375 | 444.2417 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 20.9333 | 51.2358 | 414.7167 | Average of the hour | 2020-09-16 02:00 | 2:00 | 20.9333 | 51.2358 | 414.7167 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 14.925 |  |  | Average of the hour | 2020-09-16 02:00 | 2:00 | 14.925 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 15.4333 |  |  | Average of the hour | 2020-09-16 02:00 | 2:00 | 15.4333 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 15.1092 |  | 443.4083 | Average of the hour | 2020-09-16 02:00 | 2:00 | 15.1092 |  | 443.4083 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 15.0726 |  | 379.75 | Average of the hour | 2020-09-16 02:00 | 2:00 | 15.0726 |  | 379.75 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 49.7167 |  | Average of the hour | 2020-09-16 02:00 | 2:00 |  | 49.7167 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 49.8 |  | Average of the hour | 2020-09-16 02:00 | 2:00 |  | 49.8 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.2175 | 46.0767 | 437.4976 | Average of the hour | 2020-09-16 02:00 | 2:00 | 22.2175 | 46.0767 | 437.4976 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 52.2613 | 687.0677 | Average of the hour | 2020-09-16 02:00 | 2:00 |  | 52.2613 | 687.0677 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.5057 | 45.5147 |  | Average of the hour | 2020-09-16 02:00 | 2:00 | 21.5057 | 45.5147 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 02:00
2020-09-16 | 2:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 02:00 | 2:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 02:00
2020-09-16 | 3:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 16.625 | 63.125 | 431.8917 | Average of the hour | 2020-09-16 03:00 | 3:00 | 16.625 | 63.125 | 431.8917 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.6667 | 49.125 | 538.25 | Average of the hour | 2020-09-16 03:00 | 3:00 | 20.6667 | 49.125 | 538.25 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 18.2125 | 55.3075 | 407 | Average of the hour | 2020-09-16 03:00 | 3:00 | 18.2125 | 55.3075 | 407 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.0533 | 46.5867 | 394.5 | Average of the hour | 2020-09-16 03:00 | 3:00 | 22.0533 | 46.5867 | 394.5 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 19.2975 | 58.6875 | 441.1667 | Average of the hour | 2020-09-16 03:00 | 3:00 | 19.2975 | 58.6875 | 441.1667 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 23.8442 | 51.4125 | 462.25 | Average of the hour | 2020-09-16 03:00 | 3:00 | 23.8442 | 51.4125 | 462.25 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.7 | 45.9571 | 413.9167 | Average of the hour | 2020-09-16 03:00 | 3:00 | 24.7 | 45.9571 | 413.9167 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.3167 | 57.1254 | 414.5 | Average of the hour | 2020-09-16 03:00 | 3:00 | 22.3167 | 57.1254 | 414.5 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.7236 | 51.4367 | 508.2596 | Average of the hour | 2020-09-16 03:00 | 3:00 | 21.7236 | 51.4367 | 508.2596 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 24.3931 | 47.05 | 301.3955 | Average of the hour | 2020-09-16 03:00 | 3:00 | 24.3931 | 47.05 | 301.3955 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.3103 | 47.525 | 366.1486 | Average of the hour | 2020-09-16 03:00 | 3:00 | 23.3103 | 47.525 | 366.1486 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 23.16 | 54.1167 | 608.8333 | Average of the hour | 2020-09-16 03:00 | 3:00 | 23.16 | 54.1167 | 608.8333 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 22.5008 | 51.9329 | 406.5833 | Average of the hour | 2020-09-16 03:00 | 3:00 | 22.5008 | 51.9329 | 406.5833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.8408 | 55.5279 | 411.9167 | Average of the hour | 2020-09-16 03:00 | 3:00 | 22.8408 | 55.5279 | 411.9167 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.9 | 48.0417 | 441.7 | Average of the hour | 2020-09-16 03:00 | 3:00 | 21.9 | 48.0417 | 441.7 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 20.3417 | 54.205 | 415.6167 | Average of the hour | 2020-09-16 03:00 | 3:00 | 20.3417 | 54.205 | 415.6167 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 15.25 |  |  | Average of the hour | 2020-09-16 03:00 | 3:00 | 15.25 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 15.5917 |  |  | Average of the hour | 2020-09-16 03:00 | 3:00 | 15.5917 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 15.2174 |  | 441.975 | Average of the hour | 2020-09-16 03:00 | 3:00 | 15.2174 |  | 441.975 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 15.2052 |  | 379.8333 | Average of the hour | 2020-09-16 03:00 | 3:00 | 15.2052 |  | 379.8333 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 50.175 |  | Average of the hour | 2020-09-16 03:00 | 3:00 |  | 50.175 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 50.8083 |  | Average of the hour | 2020-09-16 03:00 | 3:00 |  | 50.8083 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.3309 | 45.9284 | 438.2887 | Average of the hour | 2020-09-16 03:00 | 3:00 | 22.3309 | 45.9284 | 438.2887 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 52.173 | 686.9633 | Average of the hour | 2020-09-16 03:00 | 3:00 |  | 52.173 | 686.9633 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.1827 | 46.0748 |  | Average of the hour | 2020-09-16 03:00 | 3:00 | 21.1827 | 46.0748 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 03:00
2020-09-16 | 3:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 03:00 | 3:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 03:00
2020-09-16 | 4:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 17.3583 | 60.3333 | 441.1417 | Average of the hour | 2020-09-16 04:00 | 4:00 | 17.3583 | 60.3333 | 441.1417 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.3667 | 50.2083 | 542.9583 | Average of the hour | 2020-09-16 04:00 | 4:00 | 20.3667 | 50.2083 | 542.9583 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 18.6417 | 52.995 | 407.0833 | Average of the hour | 2020-09-16 04:00 | 4:00 | 18.6417 | 52.995 | 407.0833 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 24.6058 | 43.1617 | 396.5833 | Average of the hour | 2020-09-16 04:00 | 4:00 | 24.6058 | 43.1617 | 396.5833 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.2833 | 53.3458 | 437.5833 | Average of the hour | 2020-09-16 04:00 | 4:00 | 22.2833 | 53.3458 | 437.5833 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 23.0642 | 49.3167 | 462.8333 | Average of the hour | 2020-09-16 04:00 | 4:00 | 23.0642 | 49.3167 | 462.8333 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.6867 | 46.1558 | 412.5 | Average of the hour | 2020-09-16 04:00 | 4:00 | 24.6867 | 46.1558 | 412.5 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.3667 | 57.1171 | 413.25 | Average of the hour | 2020-09-16 04:00 | 4:00 | 22.3667 | 57.1171 | 413.25 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.7236 | 51.6219 | 508.0986 | Average of the hour | 2020-09-16 04:00 | 4:00 | 21.7236 | 51.6219 | 508.0986 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 24.2337 | 47.9967 | 302.7305 | Average of the hour | 2020-09-16 04:00 | 4:00 | 24.2337 | 47.9967 | 302.7305 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.252 | 47.6689 | 366.9743 | Average of the hour | 2020-09-16 04:00 | 4:00 | 23.252 | 47.6689 | 366.9743 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 23.195 | 54.205 | 607.6667 | Average of the hour | 2020-09-16 04:00 | 4:00 | 23.195 | 54.205 | 607.6667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 22.4983 | 51.9692 | 406.5833 | Average of the hour | 2020-09-16 04:00 | 4:00 | 22.4983 | 51.9692 | 406.5833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.7533 | 55.6975 | 410.5 | Average of the hour | 2020-09-16 04:00 | 4:00 | 22.7533 | 55.6975 | 410.5 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.9 | 48.75 | 437.3333 | Average of the hour | 2020-09-16 04:00 | 4:00 | 21.9 | 48.75 | 437.3333 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 20.125 | 56.0075 | 413.6833 | Average of the hour | 2020-09-16 04:00 | 4:00 | 20.125 | 56.0075 | 413.6833 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 15.5667 |  |  | Average of the hour | 2020-09-16 04:00 | 4:00 | 15.5667 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 15.775 |  |  | Average of the hour | 2020-09-16 04:00 | 4:00 | 15.775 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 15.4474 |  | 437.5917 | Average of the hour | 2020-09-16 04:00 | 4:00 | 15.4474 |  | 437.5917 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 15.4355 |  | 379.5833 | Average of the hour | 2020-09-16 04:00 | 4:00 | 15.4355 |  | 379.5833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 51.1333 |  | Average of the hour | 2020-09-16 04:00 | 4:00 |  | 51.1333 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 51.8083 |  | Average of the hour | 2020-09-16 04:00 | 4:00 |  | 51.8083 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.5205 | 45.5473 | 435.7456 | Average of the hour | 2020-09-16 04:00 | 4:00 | 22.5205 | 45.5473 | 435.7456 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 52.1896 | 686.9591 | Average of the hour | 2020-09-16 04:00 | 4:00 |  | 52.1896 | 686.9591 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.4173 | 47.6665 |  | Average of the hour | 2020-09-16 04:00 | 4:00 | 21.4173 | 47.6665 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 04:00
2020-09-16 | 4:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 04:00 | 4:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 04:00
2020-09-16 | 5:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.6917 | 51.4167 | 434.9833 | Average of the hour | 2020-09-16 05:00 | 5:00 | 19.6917 | 51.4167 | 434.9833 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.4833 | 52.2083 | 541.625 | Average of the hour | 2020-09-16 05:00 | 5:00 | 20.4833 | 52.2083 | 541.625 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.16 | 52.6425 | 403.9167 | Average of the hour | 2020-09-16 05:00 | 5:00 | 21.16 | 52.6425 | 403.9167 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.5017 | 46.705 | 400.25 | Average of the hour | 2020-09-16 05:00 | 5:00 | 23.5017 | 46.705 | 400.25 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.1667 | 52.7825 | 439.5833 | Average of the hour | 2020-09-16 05:00 | 5:00 | 22.1667 | 52.7825 | 439.5833 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.28 | 47.93 | 461.6667 | Average of the hour | 2020-09-16 05:00 | 5:00 | 22.28 | 47.93 | 461.6667 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.6217 | 45.8517 | 409.6667 | Average of the hour | 2020-09-16 05:00 | 5:00 | 24.6217 | 45.8517 | 409.6667 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.4333 | 56.5683 | 412.3333 | Average of the hour | 2020-09-16 05:00 | 5:00 | 22.4333 | 56.5683 | 412.3333 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.7396 | 51.5686 | 506.4041 | Average of the hour | 2020-09-16 05:00 | 5:00 | 21.7396 | 51.5686 | 506.4041 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.9213 | 48.7827 | 299.3275 | Average of the hour | 2020-09-16 05:00 | 5:00 | 23.9213 | 48.7827 | 299.3275 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.3102 | 47.343 | 367.3327 | Average of the hour | 2020-09-16 05:00 | 5:00 | 23.3102 | 47.343 | 367.3327 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 23.185 | 54.0008 | 611.0833 | Average of the hour | 2020-09-16 05:00 | 5:00 | 23.185 | 54.0008 | 611.0833 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 22.0883 | 52.8762 | 412.25 | Average of the hour | 2020-09-16 05:00 | 5:00 | 22.0883 | 52.8762 | 412.25 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.5975 | 56.2983 | 406.8333 | Average of the hour | 2020-09-16 05:00 | 5:00 | 22.5975 | 56.2983 | 406.8333 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.8167 | 49.5833 | 441.6167 | Average of the hour | 2020-09-16 05:00 | 5:00 | 21.8167 | 49.5833 | 441.6167 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 20.35 | 55.6008 | 416.45 | Average of the hour | 2020-09-16 05:00 | 5:00 | 20.35 | 55.6008 | 416.45 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 15.225 |  |  | Average of the hour | 2020-09-16 05:00 | 5:00 | 15.225 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 15.6333 |  |  | Average of the hour | 2020-09-16 05:00 | 5:00 | 15.6333 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 15.3829 |  | 441.425 | Average of the hour | 2020-09-16 05:00 | 5:00 | 15.3829 |  | 441.425 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 15.3924 |  | 380.1667 | Average of the hour | 2020-09-16 05:00 | 5:00 | 15.3924 |  | 380.1667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 52.1833 |  | Average of the hour | 2020-09-16 05:00 | 5:00 |  | 52.1833 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 52.7167 |  | Average of the hour | 2020-09-16 05:00 | 5:00 |  | 52.7167 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.6162 | 43.9537 | 454.1283 | Average of the hour | 2020-09-16 05:00 | 5:00 | 22.6162 | 43.9537 | 454.1283 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 52.3879 | 687.185 | Average of the hour | 2020-09-16 05:00 | 5:00 |  | 52.3879 | 687.185 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.5292 | 48.1387 |  | Average of the hour | 2020-09-16 05:00 | 5:00 | 21.5292 | 48.1387 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 05:00
2020-09-16 | 5:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 05:00 | 5:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 05:00
2020-09-16 | 6:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.7 | 51.75 | 427.9333 | Average of the hour | 2020-09-16 06:00 | 6:00 | 19.7 | 51.75 | 427.9333 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.0667 | 54.1667 | 531.7083 | Average of the hour | 2020-09-16 06:00 | 6:00 | 20.0667 | 54.1667 | 531.7083 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.3383 | 51.0092 | 401.75 | Average of the hour | 2020-09-16 06:00 | 6:00 | 21.3383 | 51.0092 | 401.75 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.9692 | 50.07 | 406.3333 | Average of the hour | 2020-09-16 06:00 | 6:00 | 22.9692 | 50.07 | 406.3333 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.845 | 53.3542 | 438.1667 | Average of the hour | 2020-09-16 06:00 | 6:00 | 21.845 | 53.3542 | 438.1667 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.2217 | 47.7225 | 460.1667 | Average of the hour | 2020-09-16 06:00 | 6:00 | 22.2217 | 47.7225 | 460.1667 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.105 | 46.7913 | 409.3333 | Average of the hour | 2020-09-16 06:00 | 6:00 | 24.105 | 46.7913 | 409.3333 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.885 | 57.1258 | 412.5 | Average of the hour | 2020-09-16 06:00 | 6:00 | 21.885 | 57.1258 | 412.5 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.1989 | 52.3626 | 508.0433 | Average of the hour | 2020-09-16 06:00 | 6:00 | 21.1989 | 52.3626 | 508.0433 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.4299 | 48.5424 | 295.4619 | Average of the hour | 2020-09-16 06:00 | 6:00 | 23.4299 | 48.5424 | 295.4619 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.443 | 45.6019 | 365.6002 | Average of the hour | 2020-09-16 06:00 | 6:00 | 23.443 | 45.6019 | 365.6002 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.6917 | 54.0171 | 606.75 | Average of the hour | 2020-09-16 06:00 | 6:00 | 22.6917 | 54.0171 | 606.75 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.9042 | 53.2658 | 417.1667 | Average of the hour | 2020-09-16 06:00 | 6:00 | 20.9042 | 53.2658 | 417.1667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.3467 | 58.4208 | 406.5833 | Average of the hour | 2020-09-16 06:00 | 6:00 | 21.3467 | 58.4208 | 406.5833 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.3667 | 51.6667 | 440.9833 | Average of the hour | 2020-09-16 06:00 | 6:00 | 21.3667 | 51.6667 | 440.9833 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.7167 | 50.9692 | 432.35 | Average of the hour | 2020-09-16 06:00 | 6:00 | 21.7167 | 50.9692 | 432.35 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.075 |  |  | Average of the hour | 2020-09-16 06:00 | 6:00 | 22.075 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.1417 |  |  | Average of the hour | 2020-09-16 06:00 | 6:00 | 20.1417 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 19.1662 |  | 440.5583 | Average of the hour | 2020-09-16 06:00 | 6:00 | 19.1662 |  | 440.5583 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 18.0719 |  | 379.5 | Average of the hour | 2020-09-16 06:00 | 6:00 | 18.0719 |  | 379.5 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 52.65 |  | Average of the hour | 2020-09-16 06:00 | 6:00 |  | 52.65 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 53.625 |  | Average of the hour | 2020-09-16 06:00 | 6:00 |  | 53.625 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.376 | 47 | 451.6066 | Average of the hour | 2020-09-16 06:00 | 6:00 | 22.376 | 47 | 451.6066 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 54.0527 | 687.5277 | Average of the hour | 2020-09-16 06:00 | 6:00 |  | 54.0527 | 687.5277 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.4182 | 48.7147 |  | Average of the hour | 2020-09-16 06:00 | 6:00 | 21.4182 | 48.7147 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 06:00
2020-09-16 | 6:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 06:00 | 6:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 06:00
2020-09-16 | 7:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.7083 | 52.25 | 427.975 | Average of the hour | 2020-09-16 07:00 | 7:00 | 19.7083 | 52.25 | 427.975 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 19.925 | 55.2917 | 530.5417 | Average of the hour | 2020-09-16 07:00 | 7:00 | 19.925 | 55.2917 | 530.5417 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.3408 | 50.5883 | 406.3333 | Average of the hour | 2020-09-16 07:00 | 7:00 | 21.3408 | 50.5883 | 406.3333 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.9542 | 49.6275 | 405.5833 | Average of the hour | 2020-09-16 07:00 | 7:00 | 22.9542 | 49.6275 | 405.5833 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.87 | 53.0692 | 438.4167 | Average of the hour | 2020-09-16 07:00 | 7:00 | 21.87 | 53.0692 | 438.4167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.16 | 47.1925 | 464.8333 | Average of the hour | 2020-09-16 07:00 | 7:00 | 22.16 | 47.1925 | 464.8333 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.1108 | 47.5883 | 410.3333 | Average of the hour | 2020-09-16 07:00 | 7:00 | 24.1108 | 47.5883 | 410.3333 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.0267 | 57.3421 | 412.3333 | Average of the hour | 2020-09-16 07:00 | 7:00 | 22.0267 | 57.3421 | 412.3333 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.0573 | 53.6078 | 509.4456 | Average of the hour | 2020-09-16 07:00 | 7:00 | 21.0573 | 53.6078 | 509.4456 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.303 | 48.94 | 294.5756 | Average of the hour | 2020-09-16 07:00 | 7:00 | 23.303 | 48.94 | 294.5756 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.34 | 45.5636 | 364.9458 | Average of the hour | 2020-09-16 07:00 | 7:00 | 23.34 | 45.5636 | 364.9458 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.5258 | 55.2046 | 605.75 | Average of the hour | 2020-09-16 07:00 | 7:00 | 22.5258 | 55.2046 | 605.75 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.8717 | 52.1579 | 408.0833 | Average of the hour | 2020-09-16 07:00 | 7:00 | 20.8717 | 52.1579 | 408.0833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.145 | 60.1412 | 402.5 | Average of the hour | 2020-09-16 07:00 | 7:00 | 21.145 | 60.1412 | 402.5 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.2 | 52.5 | 439.6417 | Average of the hour | 2020-09-16 07:00 | 7:00 | 21.2 | 52.5 | 439.6417 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.7083 | 51.255 | 429.9833 | Average of the hour | 2020-09-16 07:00 | 7:00 | 21.7083 | 51.255 | 429.9833 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 21.05 |  |  | Average of the hour | 2020-09-16 07:00 | 7:00 | 21.05 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.6 |  |  | Average of the hour | 2020-09-16 07:00 | 7:00 | 20.6 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 19.6466 |  | 440.4417 | Average of the hour | 2020-09-16 07:00 | 7:00 | 19.6466 |  | 440.4417 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 18.5668 |  | 380.1667 | Average of the hour | 2020-09-16 07:00 | 7:00 | 18.5668 |  | 380.1667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 52.0167 |  | Average of the hour | 2020-09-16 07:00 | 7:00 |  | 52.0167 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 52.275 |  | Average of the hour | 2020-09-16 07:00 | 7:00 |  | 52.275 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.1797 | 49.6948 | 452.4702 | Average of the hour | 2020-09-16 07:00 | 7:00 | 22.1797 | 49.6948 | 452.4702 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 55.4456 | 687.5291 | Average of the hour | 2020-09-16 07:00 | 7:00 |  | 55.4456 | 687.5291 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.3194 | 48.9457 |  | Average of the hour | 2020-09-16 07:00 | 7:00 | 21.3194 | 48.9457 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 07:00
2020-09-16 | 7:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 07:00 | 7:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 07:00
2020-09-16 | 8:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.8333 | 53.5 | 426.0167 | Average of the hour | 2020-09-16 08:00 | 8:00 | 19.8333 | 53.5 | 426.0167 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.0333 | 56.625 | 533.875 | Average of the hour | 2020-09-16 08:00 | 8:00 | 20.0333 | 56.625 | 533.875 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.4175 | 50.4467 | 428.25 | Average of the hour | 2020-09-16 08:00 | 8:00 | 21.4175 | 50.4467 | 428.25 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.9808 | 49.37 | 414.5 | Average of the hour | 2020-09-16 08:00 | 8:00 | 22.9808 | 49.37 | 414.5 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.0208 | 52.6708 | 442.0833 | Average of the hour | 2020-09-16 08:00 | 8:00 | 22.0208 | 52.6708 | 442.0833 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.0692 | 47.3233 | 464.8333 | Average of the hour | 2020-09-16 08:00 | 8:00 | 22.0692 | 47.3233 | 464.8333 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.0525 | 47.6283 | 416 | Average of the hour | 2020-09-16 08:00 | 8:00 | 24.0525 | 47.6283 | 416 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.9767 | 57.1729 | 418.0833 | Average of the hour | 2020-09-16 08:00 | 8:00 | 21.9767 | 57.1729 | 418.0833 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.0654 | 54.6702 | 514.4445 | Average of the hour | 2020-09-16 08:00 | 8:00 | 21.0654 | 54.6702 | 514.4445 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.22 | 49.1975 | 297.7338 | Average of the hour | 2020-09-16 08:00 | 8:00 | 23.22 | 49.1975 | 297.7338 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.1535 | 45.8291 | 364.5611 | Average of the hour | 2020-09-16 08:00 | 8:00 | 23.1535 | 45.8291 | 364.5611 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.3792 | 55.6496 | 623.9167 | Average of the hour | 2020-09-16 08:00 | 8:00 | 22.3792 | 55.6496 | 623.9167 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.8017 | 52.1371 | 410.3333 | Average of the hour | 2020-09-16 08:00 | 8:00 | 20.8017 | 52.1371 | 410.3333 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.0517 | 60.5608 | 412.0833 | Average of the hour | 2020-09-16 08:00 | 8:00 | 21.0517 | 60.5608 | 412.0833 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.2 | 52.5 | 446.6083 | Average of the hour | 2020-09-16 08:00 | 8:00 | 21.2 | 52.5 | 446.6083 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.7583 | 51.1425 | 429.9167 | Average of the hour | 2020-09-16 08:00 | 8:00 | 21.7583 | 51.1425 | 429.9167 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 21.825 |  |  | Average of the hour | 2020-09-16 08:00 | 8:00 | 21.825 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.7417 |  |  | Average of the hour | 2020-09-16 08:00 | 8:00 | 20.7417 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 19.7976 |  | 445.5167 | Average of the hour | 2020-09-16 08:00 | 8:00 | 19.7976 |  | 445.5167 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 18.73 |  | 379.25 | Average of the hour | 2020-09-16 08:00 | 8:00 | 18.73 |  | 379.25 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 51.65 |  | Average of the hour | 2020-09-16 08:00 | 8:00 |  | 51.65 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 51.675 |  | Average of the hour | 2020-09-16 08:00 | 8:00 |  | 51.675 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.0807 | 50.872 | 455.7073 | Average of the hour | 2020-09-16 08:00 | 8:00 | 22.0807 | 50.872 | 455.7073 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 55.3882 | 687.4203 | Average of the hour | 2020-09-16 08:00 | 8:00 |  | 55.3882 | 687.4203 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.3903 | 48.3352 |  | Average of the hour | 2020-09-16 08:00 | 8:00 | 21.3903 | 48.3352 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 08:00
2020-09-16 | 8:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 08:00 | 8:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 08:00
2020-09-16 | 9:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.7583 | 55.2083 | 441.3583 | Average of the hour | 2020-09-16 09:00 | 9:00 | 19.7583 | 55.2083 | 441.3583 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.2417 | 57.7917 | 534.9167 | Average of the hour | 2020-09-16 09:00 | 9:00 | 20.2417 | 57.7917 | 534.9167 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.4842 | 50.4775 | 482.5833 | Average of the hour | 2020-09-16 09:00 | 9:00 | 21.4842 | 50.4775 | 482.5833 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.1267 | 49.0158 | 446.75 | Average of the hour | 2020-09-16 09:00 | 9:00 | 23.1267 | 49.0158 | 446.75 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.0858 | 52.605 | 464.75 | Average of the hour | 2020-09-16 09:00 | 9:00 | 22.0858 | 52.605 | 464.75 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.9892 | 47.515 | 471.3333 | Average of the hour | 2020-09-16 09:00 | 9:00 | 21.9892 | 47.515 | 471.3333 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.0692 | 48.4013 | 421.3333 | Average of the hour | 2020-09-16 09:00 | 9:00 | 24.0692 | 48.4013 | 421.3333 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.99 | 57.705 | 423.1667 | Average of the hour | 2020-09-16 09:00 | 9:00 | 21.99 | 57.705 | 423.1667 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.1151 | 54.5183 | 525.8443 | Average of the hour | 2020-09-16 09:00 | 9:00 | 21.1151 | 54.5183 | 525.8443 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.1619 | 49.567 | 302.1033 | Average of the hour | 2020-09-16 09:00 | 9:00 | 23.1619 | 49.567 | 302.1033 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.9782 | 45.721 | 380.3818 | Average of the hour | 2020-09-16 09:00 | 9:00 | 22.9782 | 45.721 | 380.3818 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.3142 | 56.3846 | 642.8333 | Average of the hour | 2020-09-16 09:00 | 9:00 | 22.3142 | 56.3846 | 642.8333 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.7083 | 52.4275 | 421.3333 | Average of the hour | 2020-09-16 09:00 | 9:00 | 20.7083 | 52.4275 | 421.3333 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.0067 | 60.9858 | 415 | Average of the hour | 2020-09-16 09:00 | 9:00 | 21.0067 | 60.9858 | 415 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.35 | 52.3333 | 466.4333 | Average of the hour | 2020-09-16 09:00 | 9:00 | 21.35 | 52.3333 | 466.4333 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.9583 | 50.7883 | 428.5083 | Average of the hour | 2020-09-16 09:00 | 9:00 | 21.9583 | 50.7883 | 428.5083 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 21.0083 |  |  | Average of the hour | 2020-09-16 09:00 | 9:00 | 21.0083 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.9167 |  |  | Average of the hour | 2020-09-16 09:00 | 9:00 | 20.9167 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.3967 |  | 465.875 | Average of the hour | 2020-09-16 09:00 | 9:00 | 20.3967 |  | 465.875 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 19.2705 |  | 379.1667 | Average of the hour | 2020-09-16 09:00 | 9:00 | 19.2705 |  | 379.1667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 51.2583 |  | Average of the hour | 2020-09-16 09:00 | 9:00 |  | 51.2583 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 51.2667 |  | Average of the hour | 2020-09-16 09:00 | 9:00 |  | 51.2667 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.1365 | 51.8899 | 465.3428 | Average of the hour | 2020-09-16 09:00 | 9:00 | 22.1365 | 51.8899 | 465.3428 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 54.5174 | 689.0654 | Average of the hour | 2020-09-16 09:00 | 9:00 |  | 54.5174 | 689.0654 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.4745 | 47.4536 |  | Average of the hour | 2020-09-16 09:00 | 9:00 | 21.4745 | 47.4536 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 09:00
2020-09-16 | 9:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 09:00 | 9:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 09:00
2020-09-16 | 10:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.9833 | 56 | 431.2417 | Average of the hour | 2020-09-16 10:00 | 10:00 | 19.9833 | 56 | 431.2417 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.2 | 58.4583 | 553.5 | Average of the hour | 2020-09-16 10:00 | 10:00 | 20.2 | 58.4583 | 553.5 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.4292 | 50.785 | 509.6667 | Average of the hour | 2020-09-16 10:00 | 10:00 | 21.4292 | 50.785 | 509.6667 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.1275 | 48.9708 | 465.75 | Average of the hour | 2020-09-16 10:00 | 10:00 | 23.1275 | 48.9708 | 465.75 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.99 | 53.2217 | 498.1667 | Average of the hour | 2020-09-16 10:00 | 10:00 | 21.99 | 53.2217 | 498.1667 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.8658 | 47.7133 | 485.5 | Average of the hour | 2020-09-16 10:00 | 10:00 | 21.8658 | 47.7133 | 485.5 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.9725 | 49.0392 | 423.75 | Average of the hour | 2020-09-16 10:00 | 10:00 | 23.9725 | 49.0392 | 423.75 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22 | 58.1933 | 428.1667 | Average of the hour | 2020-09-16 10:00 | 10:00 | 22 | 58.1933 | 428.1667 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.1151 | 55.1621 | 530.84 | Average of the hour | 2020-09-16 10:00 | 10:00 | 21.1151 | 55.1621 | 530.84 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.0785 | 49.5753 | 304.1884 | Average of the hour | 2020-09-16 10:00 | 10:00 | 23.0785 | 49.5753 | 304.1884 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.8539 | 46.358 | 408.4857 | Average of the hour | 2020-09-16 10:00 | 10:00 | 22.8539 | 46.358 | 408.4857 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.2333 | 57.0417 | 643.3333 | Average of the hour | 2020-09-16 10:00 | 10:00 | 22.2333 | 57.0417 | 643.3333 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.7583 | 52.7096 | 416.4167 | Average of the hour | 2020-09-16 10:00 | 10:00 | 20.7583 | 52.7096 | 416.4167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.875 | 61.3554 | 417.6667 | Average of the hour | 2020-09-16 10:00 | 10:00 | 20.875 | 61.3554 | 417.6667 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.5583 | 51.5417 | 472.8417 | Average of the hour | 2020-09-16 10:00 | 10:00 | 21.5583 | 51.5417 | 472.8417 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.1333 | 50.5708 | 429.3917 | Average of the hour | 2020-09-16 10:00 | 10:00 | 22.1333 | 50.5708 | 429.3917 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 20.6167 |  |  | Average of the hour | 2020-09-16 10:00 | 10:00 | 20.6167 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.7583 |  |  | Average of the hour | 2020-09-16 10:00 | 10:00 | 20.7583 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.9849 |  | 471.8333 | Average of the hour | 2020-09-16 10:00 | 10:00 | 20.9849 |  | 471.8333 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 19.8596 |  | 379.5833 | Average of the hour | 2020-09-16 10:00 | 10:00 | 19.8596 |  | 379.5833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 51.025 |  | Average of the hour | 2020-09-16 10:00 | 10:00 |  | 51.025 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 51.1167 |  | Average of the hour | 2020-09-16 10:00 | 10:00 |  | 51.1167 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.1793 | 52.8736 | 465.9135 | Average of the hour | 2020-09-16 10:00 | 10:00 | 22.1793 | 52.8736 | 465.9135 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 53.6208 | 690.3936 | Average of the hour | 2020-09-16 10:00 | 10:00 |  | 53.6208 | 690.3936 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.3871 | 46.0582 |  | Average of the hour | 2020-09-16 10:00 | 10:00 | 21.3871 | 46.0582 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 10:00
2020-09-16 | 10:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 10:00 | 10:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 10:00
2020-09-16 | 11:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.825 | 56.9583 | 463.6 | Average of the hour | 2020-09-16 11:00 | 11:00 | 19.825 | 56.9583 | 463.6 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.1417 | 58.5417 | 564.75 | Average of the hour | 2020-09-16 11:00 | 11:00 | 20.1417 | 58.5417 | 564.75 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.1042 | 51.6075 | 524.1667 | Average of the hour | 2020-09-16 11:00 | 11:00 | 21.1042 | 51.6075 | 524.1667 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.9633 | 49.2825 | 465.3333 | Average of the hour | 2020-09-16 11:00 | 11:00 | 22.9633 | 49.2825 | 465.3333 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.5242 | 54.4275 | 506.8333 | Average of the hour | 2020-09-16 11:00 | 11:00 | 21.5242 | 54.4275 | 506.8333 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.6933 | 48.0467 | 500.4167 | Average of the hour | 2020-09-16 11:00 | 11:00 | 21.6933 | 48.0467 | 500.4167 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.95 | 49.1621 | 421 | Average of the hour | 2020-09-16 11:00 | 11:00 | 23.95 | 49.1621 | 421 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.9667 | 58.4142 | 425.8333 | Average of the hour | 2020-09-16 11:00 | 11:00 | 21.9667 | 58.4142 | 425.8333 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.1151 | 55.3226 | 527.1086 | Average of the hour | 2020-09-16 11:00 | 11:00 | 21.1151 | 55.3226 | 527.1086 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.0013 | 49.5753 | 301.4856 | Average of the hour | 2020-09-16 11:00 | 11:00 | 23.0013 | 49.5753 | 301.4856 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.8456 | 46.8629 | 409.845 | Average of the hour | 2020-09-16 11:00 | 11:00 | 22.8456 | 46.8629 | 409.845 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.1808 | 57.4975 | 643 | Average of the hour | 2020-09-16 11:00 | 11:00 | 22.1808 | 57.4975 | 643 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.6042 | 52.9333 | 418.3333 | Average of the hour | 2020-09-16 11:00 | 11:00 | 20.6042 | 52.9333 | 418.3333 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.8067 | 61.5225 | 416.9167 | Average of the hour | 2020-09-16 11:00 | 11:00 | 20.8067 | 61.5225 | 416.9167 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.8 | 51.2083 | 491.4417 | Average of the hour | 2020-09-16 11:00 | 11:00 | 21.8 | 51.2083 | 491.4417 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.325 | 50.1942 | 428.2083 | Average of the hour | 2020-09-16 11:00 | 11:00 | 22.325 | 50.1942 | 428.2083 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 19.4417 |  |  | Average of the hour | 2020-09-16 11:00 | 11:00 | 19.4417 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.9083 |  |  | Average of the hour | 2020-09-16 11:00 | 11:00 | 20.9083 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 21.3368 |  | 492.6417 | Average of the hour | 2020-09-16 11:00 | 11:00 | 21.3368 |  | 492.6417 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 20.627 |  | 379.9167 | Average of the hour | 2020-09-16 11:00 | 11:00 | 20.627 |  | 379.9167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 50.7583 |  | Average of the hour | 2020-09-16 11:00 | 11:00 |  | 50.7583 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 49.8833 |  | Average of the hour | 2020-09-16 11:00 | 11:00 |  | 49.8833 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.253 | 53.6875 | 472.105 | Average of the hour | 2020-09-16 11:00 | 11:00 | 22.253 | 53.6875 | 472.105 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 53.903 | 690.3566 | Average of the hour | 2020-09-16 11:00 | 11:00 |  | 53.903 | 690.3566 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.1264 | 47.1144 |  | Average of the hour | 2020-09-16 11:00 | 11:00 | 21.1264 | 47.1144 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 11:00
2020-09-16 | 11:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 11:00 | 11:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 11:00
2020-09-16 | 12:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.0083 | 57.375 | 440.55 | Average of the hour | 2020-09-16 12:00 | 12:00 | 20.0083 | 57.375 | 440.55 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.1167 | 58.875 | 567 | Average of the hour | 2020-09-16 12:00 | 12:00 | 20.1167 | 58.875 | 567 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.9775 | 52.0175 | 523.8333 | Average of the hour | 2020-09-16 12:00 | 12:00 | 20.9775 | 52.0175 | 523.8333 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.9292 | 49.6842 | 466.75 | Average of the hour | 2020-09-16 12:00 | 12:00 | 22.9292 | 49.6842 | 466.75 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.5408 | 54.9433 | 504.4167 | Average of the hour | 2020-09-16 12:00 | 12:00 | 21.5408 | 54.9433 | 504.4167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.695 | 48.35 | 490.5833 | Average of the hour | 2020-09-16 12:00 | 12:00 | 21.695 | 48.35 | 490.5833 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.8392 | 48.8254 | 421.8333 | Average of the hour | 2020-09-16 12:00 | 12:00 | 23.8392 | 48.8254 | 421.8333 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.9183 | 57.9975 | 421.75 | Average of the hour | 2020-09-16 12:00 | 12:00 | 21.9183 | 57.9975 | 421.75 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.1912 | 54.6103 | 529.3074 | Average of the hour | 2020-09-16 12:00 | 12:00 | 21.1912 | 54.6103 | 529.3074 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.9581 | 49.1219 | 298.9792 | Average of the hour | 2020-09-16 12:00 | 12:00 | 22.9581 | 49.1219 | 298.9792 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.5043 | 48.0245 | 407.0485 | Average of the hour | 2020-09-16 12:00 | 12:00 | 22.5043 | 48.0245 | 407.0485 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.0692 | 57.4071 | 628 | Average of the hour | 2020-09-16 12:00 | 12:00 | 22.0692 | 57.4071 | 628 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.5608 | 53.2063 | 406.5833 | Average of the hour | 2020-09-16 12:00 | 12:00 | 20.5608 | 53.2063 | 406.5833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.6033 | 61.4279 | 416 | Average of the hour | 2020-09-16 12:00 | 12:00 | 20.6033 | 61.4279 | 416 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22.1417 | 49.5833 | 503.3833 | Average of the hour | 2020-09-16 12:00 | 12:00 | 22.1417 | 49.5833 | 503.3833 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.4583 | 49.465 | 426.95 | Average of the hour | 2020-09-16 12:00 | 12:00 | 22.4583 | 49.465 | 426.95 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 20.4333 |  |  | Average of the hour | 2020-09-16 12:00 | 12:00 | 20.4333 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.9667 |  |  | Average of the hour | 2020-09-16 12:00 | 12:00 | 20.9667 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 21.5376 |  | 503.525 | Average of the hour | 2020-09-16 12:00 | 12:00 | 21.5376 |  | 503.525 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 21.2569 |  | 380 | Average of the hour | 2020-09-16 12:00 | 12:00 | 21.2569 |  | 380 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 49.775 |  | Average of the hour | 2020-09-16 12:00 | 12:00 |  | 49.775 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 48.55 |  | Average of the hour | 2020-09-16 12:00 | 12:00 |  | 48.55 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.9054 | 53.4432 | 457.2026 | Average of the hour | 2020-09-16 12:00 | 12:00 | 21.9054 | 53.4432 | 457.2026 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 54.051 | 690.3528 | Average of the hour | 2020-09-16 12:00 | 12:00 |  | 54.051 | 690.3528 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.1513 | 46.9823 |  | Average of the hour | 2020-09-16 12:00 | 12:00 | 21.1513 | 46.9823 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 12:00
2020-09-16 | 12:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 12:00 | 12:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 12:00
2020-09-16 | 13:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.1667 | 57.6667 | 426.2167 | Average of the hour | 2020-09-16 13:00 | 13:00 | 20.1667 | 57.6667 | 426.2167 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.175 | 59.5833 | 565.8333 | Average of the hour | 2020-09-16 13:00 | 13:00 | 20.175 | 59.5833 | 565.8333 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.9308 | 52.4533 | 511.75 | Average of the hour | 2020-09-16 13:00 | 13:00 | 20.9308 | 52.4533 | 511.75 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.8908 | 50.2142 | 469.75 | Average of the hour | 2020-09-16 13:00 | 13:00 | 22.8908 | 50.2142 | 469.75 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.6717 | 55.1833 | 492.9167 | Average of the hour | 2020-09-16 13:00 | 13:00 | 21.6717 | 55.1833 | 492.9167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.5258 | 47.9883 | 480.4167 | Average of the hour | 2020-09-16 13:00 | 13:00 | 21.5258 | 47.9883 | 480.4167 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.7333 | 48.2325 | 418.5 | Average of the hour | 2020-09-16 13:00 | 13:00 | 23.7333 | 48.2325 | 418.5 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.7867 | 57.3646 | 418.8333 | Average of the hour | 2020-09-16 13:00 | 13:00 | 21.7867 | 57.3646 | 418.8333 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.2166 | 54.0004 | 518.409 | Average of the hour | 2020-09-16 13:00 | 13:00 | 21.2166 | 54.0004 | 518.409 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.8587 | 48.7547 | 297.094 | Average of the hour | 2020-09-16 13:00 | 13:00 | 22.8587 | 48.7547 | 297.094 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.4433 | 47.8258 | 404.1251 | Average of the hour | 2020-09-16 13:00 | 13:00 | 22.4433 | 47.8258 | 404.1251 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.9967 | 57.0896 | 632 | Average of the hour | 2020-09-16 13:00 | 13:00 | 21.9967 | 57.0896 | 632 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.4908 | 52.9617 | 404.25 | Average of the hour | 2020-09-16 13:00 | 13:00 | 20.4908 | 52.9617 | 404.25 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.43 | 60.9988 | 413.5833 | Average of the hour | 2020-09-16 13:00 | 13:00 | 20.43 | 60.9988 | 413.5833 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.5833 | 49.7083 | 487.125 | Average of the hour | 2020-09-16 13:00 | 13:00 | 21.5833 | 49.7083 | 487.125 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22 | 49.8275 | 421.6417 | Average of the hour | 2020-09-16 13:00 | 13:00 | 22 | 49.8275 | 421.6417 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.225 |  |  | Average of the hour | 2020-09-16 13:00 | 13:00 | 23.225 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.6667 |  |  | Average of the hour | 2020-09-16 13:00 | 13:00 | 20.6667 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 21.8315 |  | 486.925 | Average of the hour | 2020-09-16 13:00 | 13:00 | 21.8315 |  | 486.925 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 21.791 |  | 379.8333 | Average of the hour | 2020-09-16 13:00 | 13:00 | 21.791 |  | 379.8333 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-16 13:00 | 13:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-16 13:00 | 13:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.7518 | 53.0809 | 455.4674 | Average of the hour | 2020-09-16 13:00 | 13:00 | 21.7518 | 53.0809 | 455.4674 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 53.6895 | 690.3144 | Average of the hour | 2020-09-16 13:00 | 13:00 |  | 53.6895 | 690.3144 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9968 | 46.6077 |  | Average of the hour | 2020-09-16 13:00 | 13:00 | 20.9968 | 46.6077 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 13:00
2020-09-16 | 13:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 13:00 | 13:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 13:00
2020-09-16 | 14:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.175 | 58.4167 | 423.2 | Average of the hour | 2020-09-16 14:00 | 14:00 | 20.175 | 58.4167 | 423.2 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.2333 | 60.5417 | 564 | Average of the hour | 2020-09-16 14:00 | 14:00 | 20.2333 | 60.5417 | 564 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.8875 | 53.0425 | 524.25 | Average of the hour | 2020-09-16 14:00 | 14:00 | 20.8875 | 53.0425 | 524.25 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.84 | 50.9408 | 466.9167 | Average of the hour | 2020-09-16 14:00 | 14:00 | 22.84 | 50.9408 | 466.9167 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.7883 | 55.5392 | 489.1667 | Average of the hour | 2020-09-16 14:00 | 14:00 | 21.7883 | 55.5392 | 489.1667 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.6492 | 48.61 | 477.5833 | Average of the hour | 2020-09-16 14:00 | 14:00 | 21.6492 | 48.61 | 477.5833 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.7292 | 48.2396 | 417.5833 | Average of the hour | 2020-09-16 14:00 | 14:00 | 23.7292 | 48.2396 | 417.5833 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.6583 | 57.2733 | 411 | Average of the hour | 2020-09-16 14:00 | 14:00 | 21.6583 | 57.2733 | 411 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.2774 | 53.6069 | 522.6313 | Average of the hour | 2020-09-16 14:00 | 14:00 | 21.2774 | 53.6069 | 522.6313 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.8157 | 48.5883 | 304.5891 | Average of the hour | 2020-09-16 14:00 | 14:00 | 22.8157 | 48.5883 | 304.5891 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.5212 | 47.6763 | 418.7675 | Average of the hour | 2020-09-16 14:00 | 14:00 | 22.5212 | 47.6763 | 418.7675 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.96 | 57.005 | 633.6667 | Average of the hour | 2020-09-16 14:00 | 14:00 | 21.96 | 57.005 | 633.6667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.3308 | 53.2604 | 404.1667 | Average of the hour | 2020-09-16 14:00 | 14:00 | 20.3308 | 53.2604 | 404.1667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.2158 | 60.9258 | 416.4167 | Average of the hour | 2020-09-16 14:00 | 14:00 | 20.2158 | 60.9258 | 416.4167 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.4 | 48.5833 | 471.075 | Average of the hour | 2020-09-16 14:00 | 14:00 | 21.4 | 48.5833 | 471.075 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.5333 | 49.91 | 418.2833 | Average of the hour | 2020-09-16 14:00 | 14:00 | 21.5333 | 49.91 | 418.2833 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 24.4333 |  |  | Average of the hour | 2020-09-16 14:00 | 14:00 | 24.4333 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.5333 |  |  | Average of the hour | 2020-09-16 14:00 | 14:00 | 20.5333 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 21.9711 |  | 470.6333 | Average of the hour | 2020-09-16 14:00 | 14:00 | 21.9711 |  | 470.6333 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 22.3047 |  | 379.5 | Average of the hour | 2020-09-16 14:00 | 14:00 | 22.3047 |  | 379.5 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-16 14:00 | 14:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-16 14:00 | 14:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.6787 | 53.0717 | 459.054 | Average of the hour | 2020-09-16 14:00 | 14:00 | 21.6787 | 53.0717 | 459.054 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 52.8469 | 690.1574 | Average of the hour | 2020-09-16 14:00 | 14:00 |  | 52.8469 | 690.1574 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9759 | 45.6752 |  | Average of the hour | 2020-09-16 14:00 | 14:00 | 20.9759 | 45.6752 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 14:00
2020-09-16 | 14:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 14:00 | 14:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 14:00
2020-09-16 | 15:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.1583 | 59.375 | 420.5417 | Average of the hour | 2020-09-16 15:00 | 15:00 | 20.1583 | 59.375 | 420.5417 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.525 | 60.5417 | 591.6667 | Average of the hour | 2020-09-16 15:00 | 15:00 | 20.525 | 60.5417 | 591.6667 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.8783 | 53.7608 | 530.9167 | Average of the hour | 2020-09-16 15:00 | 15:00 | 20.8783 | 53.7608 | 530.9167 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.8517 | 51.5733 | 467.1667 | Average of the hour | 2020-09-16 15:00 | 15:00 | 22.8517 | 51.5733 | 467.1667 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.9217 | 55.4125 | 490.5833 | Average of the hour | 2020-09-16 15:00 | 15:00 | 21.9217 | 55.4125 | 490.5833 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.5967 | 49.56 | 476.1667 | Average of the hour | 2020-09-16 15:00 | 15:00 | 21.5967 | 49.56 | 476.1667 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.6875 | 48.3888 | 426 | Average of the hour | 2020-09-16 15:00 | 15:00 | 23.6875 | 48.3888 | 426 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.5925 | 57.2508 | 419.0833 | Average of the hour | 2020-09-16 15:00 | 15:00 | 21.5925 | 57.2508 | 419.0833 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.3209 | 53.5312 | 539.9376 | Average of the hour | 2020-09-16 15:00 | 15:00 | 21.3209 | 53.5312 | 539.9376 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.7556 | 48.5272 | 308.5352 | Average of the hour | 2020-09-16 15:00 | 15:00 | 22.7556 | 48.5272 | 308.5352 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.5212 | 47.8551 | 421.0553 | Average of the hour | 2020-09-16 15:00 | 15:00 | 22.5212 | 47.8551 | 421.0553 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.9933 | 57.0992 | 641.3333 | Average of the hour | 2020-09-16 15:00 | 15:00 | 21.9933 | 57.0992 | 641.3333 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.2833 | 53.9571 | 409.5833 | Average of the hour | 2020-09-16 15:00 | 15:00 | 20.2833 | 53.9571 | 409.5833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.1167 | 60.7554 | 412.1667 | Average of the hour | 2020-09-16 15:00 | 15:00 | 20.1167 | 60.7554 | 412.1667 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.45 | 47.9583 | 469.1 | Average of the hour | 2020-09-16 15:00 | 15:00 | 21.45 | 47.9583 | 469.1 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.375 | 49.7692 | 423.8583 | Average of the hour | 2020-09-16 15:00 | 15:00 | 21.375 | 49.7692 | 423.8583 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.1667 |  |  | Average of the hour | 2020-09-16 15:00 | 15:00 | 23.1667 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.525 |  |  | Average of the hour | 2020-09-16 15:00 | 15:00 | 20.525 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 22.1742 |  | 469.2833 | Average of the hour | 2020-09-16 15:00 | 15:00 | 22.1742 |  | 469.2833 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 22.6024 |  | 379.5833 | Average of the hour | 2020-09-16 15:00 | 15:00 | 22.6024 |  | 379.5833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.6147 | 53.1693 | 455.5433 | Average of the hour | 2020-09-16 15:00 | 15:00 | 21.6147 | 53.1693 | 455.5433 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 52.69 | 690.3207 | Average of the hour | 2020-09-16 15:00 | 15:00 |  | 52.69 | 690.3207 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9836 | 44.9927 |  | Average of the hour | 2020-09-16 15:00 | 15:00 | 20.9836 | 44.9927 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 15:00
2020-09-16 | 15:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 15:00 | 15:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 15:00
2020-09-16 | 16:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.2583 | 59.8333 | 418.85 | Average of the hour | 2020-09-16 16:00 | 16:00 | 20.2583 | 59.8333 | 418.85 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.3083 | 62.75 | 568.2917 | Average of the hour | 2020-09-16 16:00 | 16:00 | 20.3083 | 62.75 | 568.2917 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.8317 | 54.3342 | 510 | Average of the hour | 2020-09-16 16:00 | 16:00 | 20.8317 | 54.3342 | 510 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.8458 | 52.2275 | 457.4167 | Average of the hour | 2020-09-16 16:00 | 16:00 | 22.8458 | 52.2275 | 457.4167 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.0225 | 55.6667 | 488.4167 | Average of the hour | 2020-09-16 16:00 | 16:00 | 22.0225 | 55.6667 | 488.4167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.6325 | 50.38 | 472.8333 | Average of the hour | 2020-09-16 16:00 | 16:00 | 21.6325 | 50.38 | 472.8333 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.6075 | 49.0792 | 428.8333 | Average of the hour | 2020-09-16 16:00 | 16:00 | 23.6075 | 49.0792 | 428.8333 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.5625 | 57.7246 | 425 | Average of the hour | 2020-09-16 16:00 | 16:00 | 21.5625 | 57.7246 | 425 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.3209 | 54.6845 | 545.8825 | Average of the hour | 2020-09-16 16:00 | 16:00 | 21.3209 | 54.6845 | 545.8825 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.7556 | 49.1435 | 308.2252 | Average of the hour | 2020-09-16 16:00 | 16:00 | 22.7556 | 49.1435 | 308.2252 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.563 | 48.6183 | 423.8666 | Average of the hour | 2020-09-16 16:00 | 16:00 | 22.563 | 48.6183 | 423.8666 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.9217 | 58.5679 | 648.8333 | Average of the hour | 2020-09-16 16:00 | 16:00 | 21.9217 | 58.5679 | 648.8333 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.3467 | 55.4904 | 417.9167 | Average of the hour | 2020-09-16 16:00 | 16:00 | 20.3467 | 55.4904 | 417.9167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 19.9783 | 60.66 | 412.75 | Average of the hour | 2020-09-16 16:00 | 16:00 | 19.9783 | 60.66 | 412.75 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.6 | 47.875 | 465.125 | Average of the hour | 2020-09-16 16:00 | 16:00 | 21.6 | 47.875 | 465.125 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.35 | 49.9808 | 425.3667 | Average of the hour | 2020-09-16 16:00 | 16:00 | 21.35 | 49.9808 | 425.3667 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.775 |  |  | Average of the hour | 2020-09-16 16:00 | 16:00 | 23.775 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.3667 |  |  | Average of the hour | 2020-09-16 16:00 | 16:00 | 20.3667 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 22.4877 |  | 464.7667 | Average of the hour | 2020-09-16 16:00 | 16:00 | 22.4877 |  | 464.7667 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 22.7753 |  | 379.6667 | Average of the hour | 2020-09-16 16:00 | 16:00 | 22.7753 |  | 379.6667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-16 16:00 | 16:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-16 16:00 | 16:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.5685 | 52.8719 | 447.1155 | Average of the hour | 2020-09-16 16:00 | 16:00 | 21.5685 | 52.8719 | 447.1155 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 52.8021 | 690.7611 | Average of the hour | 2020-09-16 16:00 | 16:00 |  | 52.8021 | 690.7611 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9621 | 45.0581 |  | Average of the hour | 2020-09-16 16:00 | 16:00 | 20.9621 | 45.0581 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 16:00
2020-09-16 | 16:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 16:00 | 16:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 16:00
2020-09-16 | 17:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.2083 | 60.4583 | 443.0167 | Average of the hour | 2020-09-16 17:00 | 17:00 | 20.2083 | 60.4583 | 443.0167 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.3 | 63.9167 | 567.25 | Average of the hour | 2020-09-16 17:00 | 17:00 | 20.3 | 63.9167 | 567.25 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.7492 | 54.605 | 460.5 | Average of the hour | 2020-09-16 17:00 | 17:00 | 20.7492 | 54.605 | 460.5 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.7058 | 52.8917 | 440.75 | Average of the hour | 2020-09-16 17:00 | 17:00 | 22.7058 | 52.8917 | 440.75 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.0883 | 55.67 | 477.0833 | Average of the hour | 2020-09-16 17:00 | 17:00 | 22.0883 | 55.67 | 477.0833 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.6742 | 51.0375 | 466.1667 | Average of the hour | 2020-09-16 17:00 | 17:00 | 21.6742 | 51.0375 | 466.1667 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.6167 | 50.0196 | 429.6667 | Average of the hour | 2020-09-16 17:00 | 17:00 | 23.6167 | 50.0196 | 429.6667 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.57 | 58.3875 | 426.1667 | Average of the hour | 2020-09-16 17:00 | 17:00 | 21.57 | 58.3875 | 426.1667 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.3209 | 55.7685 | 539.1603 | Average of the hour | 2020-09-16 17:00 | 17:00 | 21.3209 | 55.7685 | 539.1603 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.7556 | 50.0092 | 311.8714 | Average of the hour | 2020-09-16 17:00 | 17:00 | 22.7556 | 50.0092 | 311.8714 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.6381 | 49.1496 | 410.3259 | Average of the hour | 2020-09-16 17:00 | 17:00 | 22.6381 | 49.1496 | 410.3259 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.8 | 59.2446 | 631 | Average of the hour | 2020-09-16 17:00 | 17:00 | 21.8 | 59.2446 | 631 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.4075 | 56.9646 | 410.5 | Average of the hour | 2020-09-16 17:00 | 17:00 | 20.4075 | 56.9646 | 410.5 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 19.8775 | 61.1579 | 427.1667 | Average of the hour | 2020-09-16 17:00 | 17:00 | 19.8775 | 61.1579 | 427.1667 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.575 | 48.7917 | 469.7333 | Average of the hour | 2020-09-16 17:00 | 17:00 | 21.575 | 48.7917 | 469.7333 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.25 | 50.2808 | 419.15 | Average of the hour | 2020-09-16 17:00 | 17:00 | 21.25 | 50.2808 | 419.15 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.0333 |  |  | Average of the hour | 2020-09-16 17:00 | 17:00 | 23.0333 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.4083 |  |  | Average of the hour | 2020-09-16 17:00 | 17:00 | 20.4083 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 22.377 |  | 469.4917 | Average of the hour | 2020-09-16 17:00 | 17:00 | 22.377 |  | 469.4917 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 22.6496 |  | 379.0833 | Average of the hour | 2020-09-16 17:00 | 17:00 | 22.6496 |  | 379.0833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-16 17:00 | 17:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-16 17:00 | 17:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.5027 | 50.1598 | 434.3576 | Average of the hour | 2020-09-16 17:00 | 17:00 | 21.5027 | 50.1598 | 434.3576 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 53.1803 | 690.7341 | Average of the hour | 2020-09-16 17:00 | 17:00 |  | 53.1803 | 690.7341 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9326 | 45.759 |  | Average of the hour | 2020-09-16 17:00 | 17:00 | 20.9326 | 45.759 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 17:00
2020-09-16 | 17:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 17:00 | 17:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 17:00
2020-09-16 | 18:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.15 | 60.5417 | 436.325 | Average of the hour | 2020-09-16 18:00 | 18:00 | 20.15 | 60.5417 | 436.325 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.4833 | 63.4583 | 596.125 | Average of the hour | 2020-09-16 18:00 | 18:00 | 20.4833 | 63.4583 | 596.125 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.6633 | 54.9142 | 424.75 | Average of the hour | 2020-09-16 18:00 | 18:00 | 20.6633 | 54.9142 | 424.75 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.6267 | 53.1475 | 423.75 | Average of the hour | 2020-09-16 18:00 | 18:00 | 22.6267 | 53.1475 | 423.75 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.135 | 55.6508 | 459.5833 | Average of the hour | 2020-09-16 18:00 | 18:00 | 22.135 | 55.6508 | 459.5833 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.605 | 51.0142 | 463.1667 | Average of the hour | 2020-09-16 18:00 | 18:00 | 21.605 | 51.0142 | 463.1667 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.7617 | 51.1596 | 428 | Average of the hour | 2020-09-16 18:00 | 18:00 | 23.7617 | 51.1596 | 428 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.8617 | 59.2583 | 421.9167 | Average of the hour | 2020-09-16 18:00 | 18:00 | 21.8617 | 59.2583 | 421.9167 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.246 | 56.5923 | 528.7575 | Average of the hour | 2020-09-16 18:00 | 18:00 | 21.246 | 56.5923 | 528.7575 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.0074 | 53.6841 | 305.2661 | Average of the hour | 2020-09-16 18:00 | 18:00 | 23.0074 | 53.6841 | 305.2661 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.756 | 50.2025 | 391.2091 | Average of the hour | 2020-09-16 18:00 | 18:00 | 22.756 | 50.2025 | 391.2091 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.8533 | 60.5325 | 629.0833 | Average of the hour | 2020-09-16 18:00 | 18:00 | 21.8533 | 60.5325 | 629.0833 |  | caution | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.5825 | 58.4792 | 420.4167 | Average of the hour | 2020-09-16 18:00 | 18:00 | 20.5825 | 58.4792 | 420.4167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.3825 | 62.6054 | 427.25 | Average of the hour | 2020-09-16 18:00 | 18:00 | 20.3825 | 62.6054 | 427.25 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.4 | 50.0417 | 456.4833 | Average of the hour | 2020-09-16 18:00 | 18:00 | 21.4 | 50.0417 | 456.4833 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.2 | 50.485 | 417.9833 | Average of the hour | 2020-09-16 18:00 | 18:00 | 21.2 | 50.485 | 417.9833 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.5083 |  |  | Average of the hour | 2020-09-16 18:00 | 18:00 | 23.5083 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.35 |  |  | Average of the hour | 2020-09-16 18:00 | 18:00 | 20.35 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 21.6926 |  | 456.8667 | Average of the hour | 2020-09-16 18:00 | 18:00 | 21.6926 |  | 456.8667 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 22.0553 |  | 379.1667 | Average of the hour | 2020-09-16 18:00 | 18:00 | 22.0553 |  | 379.1667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-16 18:00 | 18:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-16 18:00 | 18:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.7011 | 47.4979 | 446.7173 | Average of the hour | 2020-09-16 18:00 | 18:00 | 21.7011 | 47.4979 | 446.7173 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 53.6145 | 690.4289 | Average of the hour | 2020-09-16 18:00 | 18:00 |  | 53.6145 | 690.4289 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9321 | 47.1066 |  | Average of the hour | 2020-09-16 18:00 | 18:00 | 20.9321 | 47.1066 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 18:00
2020-09-16 | 18:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 18:00 | 18:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 18:00
2020-09-16 | 19:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.25 | 62.125 | 432.5917 | Average of the hour | 2020-09-16 19:00 | 19:00 | 20.25 | 62.125 | 432.5917 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.6167 | 63.1667 | 580 | Average of the hour | 2020-09-16 19:00 | 19:00 | 20.6167 | 63.1667 | 580 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.58 | 55.0575 | 411.6667 | Average of the hour | 2020-09-16 19:00 | 19:00 | 20.58 | 55.0575 | 411.6667 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.5983 | 53.4933 | 410.0833 | Average of the hour | 2020-09-16 19:00 | 19:00 | 22.5983 | 53.4933 | 410.0833 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.33 | 60.0942 | 445.75 | Average of the hour | 2020-09-16 19:00 | 19:00 | 22.33 | 60.0942 | 445.75 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.5758 | 51.1833 | 463.5833 | Average of the hour | 2020-09-16 19:00 | 19:00 | 21.5758 | 51.1833 | 463.5833 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.2625 | 50.9104 | 428.5 | Average of the hour | 2020-09-16 19:00 | 19:00 | 24.2625 | 50.9104 | 428.5 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.5675 | 58.5883 | 426.9167 | Average of the hour | 2020-09-16 19:00 | 19:00 | 22.5675 | 58.5883 | 426.9167 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.357 | 56.3378 | 529.6966 | Average of the hour | 2020-09-16 19:00 | 19:00 | 21.357 | 56.3378 | 529.6966 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.6041 | 54.9826 | 304.3707 | Average of the hour | 2020-09-16 19:00 | 19:00 | 23.6041 | 54.9826 | 304.3707 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.9511 | 52.0128 | 384.0752 | Average of the hour | 2020-09-16 19:00 | 19:00 | 22.9511 | 52.0128 | 384.0752 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.1833 | 61.6908 | 632.5 | Average of the hour | 2020-09-16 19:00 | 19:00 | 22.1833 | 61.6908 | 632.5 |  | caution | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.2983 | 58.5467 | 419 | Average of the hour | 2020-09-16 19:00 | 19:00 | 21.2983 | 58.5467 | 419 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.1308 | 62.0275 | 434.75 | Average of the hour | 2020-09-16 19:00 | 19:00 | 21.1308 | 62.0275 | 434.75 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.2333 | 52.1667 | 444.3333 | Average of the hour | 2020-09-16 19:00 | 19:00 | 21.2333 | 52.1667 | 444.3333 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.25 | 51.5083 | 415.3417 | Average of the hour | 2020-09-16 19:00 | 19:00 | 21.25 | 51.5083 | 415.3417 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.1583 |  |  | Average of the hour | 2020-09-16 19:00 | 19:00 | 23.1583 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.4083 |  |  | Average of the hour | 2020-09-16 19:00 | 19:00 | 20.4083 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.8836 |  | 445 | Average of the hour | 2020-09-16 19:00 | 19:00 | 20.8836 |  | 445 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 20.9715 |  | 379 | Average of the hour | 2020-09-16 19:00 | 19:00 | 20.9715 |  | 379 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-16 19:00 | 19:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-16 19:00 | 19:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.9358 | 47.1503 | 450.0864 | Average of the hour | 2020-09-16 19:00 | 19:00 | 21.9358 | 47.1503 | 450.0864 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 54.2128 | 689.3898 | Average of the hour | 2020-09-16 19:00 | 19:00 |  | 54.2128 | 689.3898 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.8919 | 48.9886 |  | Average of the hour | 2020-09-16 19:00 | 19:00 | 20.8919 | 48.9886 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 19:00
2020-09-16 | 19:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 19:00 | 19:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 19:00
2020-09-16 | 20:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.8917 | 63.5833 | 433.25 | Average of the hour | 2020-09-16 20:00 | 20:00 | 19.8917 | 63.5833 | 433.25 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.9417 | 61.75 | 584.0417 | Average of the hour | 2020-09-16 20:00 | 20:00 | 20.9417 | 61.75 | 584.0417 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.5483 | 55.285 | 411.5833 | Average of the hour | 2020-09-16 20:00 | 20:00 | 20.5483 | 55.285 | 411.5833 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.545 | 52.2117 | 405.4167 | Average of the hour | 2020-09-16 20:00 | 20:00 | 22.545 | 52.2117 | 405.4167 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.9292 | 65.14 | 448.1667 | Average of the hour | 2020-09-16 20:00 | 20:00 | 21.9292 | 65.14 | 448.1667 |  | high | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.5017 | 51.6608 | 468.5 | Average of the hour | 2020-09-16 20:00 | 20:00 | 21.5017 | 51.6608 | 468.5 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.515 | 50.7033 | 428.75 | Average of the hour | 2020-09-16 20:00 | 20:00 | 24.515 | 50.7033 | 428.75 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.8625 | 58.2146 | 425.0833 | Average of the hour | 2020-09-16 20:00 | 20:00 | 22.8625 | 58.2146 | 425.0833 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.4745 | 56.0991 | 526.0184 | Average of the hour | 2020-09-16 20:00 | 20:00 | 21.4745 | 56.0991 | 526.0184 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.7959 | 55.2279 | 303.7907 | Average of the hour | 2020-09-16 20:00 | 20:00 | 23.7959 | 55.2279 | 303.7907 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.0354 | 53.0032 | 377.0282 | Average of the hour | 2020-09-16 20:00 | 20:00 | 23.0354 | 53.0032 | 377.0282 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.3583 | 61.7875 | 633.4167 | Average of the hour | 2020-09-16 20:00 | 20:00 | 22.3583 | 61.7875 | 633.4167 |  | caution | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.5792 | 58.3671 | 425.6667 | Average of the hour | 2020-09-16 20:00 | 20:00 | 21.5792 | 58.3671 | 425.6667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.4883 | 61.9962 | 437.25 | Average of the hour | 2020-09-16 20:00 | 20:00 | 21.4883 | 61.9962 | 437.25 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.5333 | 53.1667 | 436.525 | Average of the hour | 2020-09-16 20:00 | 20:00 | 21.5333 | 53.1667 | 436.525 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.6583 | 52.8842 | 413.0333 | Average of the hour | 2020-09-16 20:00 | 20:00 | 21.6583 | 52.8842 | 413.0333 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 21.9 |  |  | Average of the hour | 2020-09-16 20:00 | 20:00 | 21.9 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 19.8833 |  |  | Average of the hour | 2020-09-16 20:00 | 20:00 | 19.8833 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 19.797 |  | 436.425 | Average of the hour | 2020-09-16 20:00 | 20:00 | 19.797 |  | 436.425 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 19.8819 |  | 379.4167 | Average of the hour | 2020-09-16 20:00 | 20:00 | 19.8819 |  | 379.4167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-16 20:00 | 20:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-16 20:00 | 20:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.1089 | 46.909 | 451.5509 | Average of the hour | 2020-09-16 20:00 | 20:00 | 22.1089 | 46.909 | 451.5509 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 55.8059 | 688.6557 | Average of the hour | 2020-09-16 20:00 | 20:00 |  | 55.8059 | 688.6557 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9693 | 50.0344 |  | Average of the hour | 2020-09-16 20:00 | 20:00 | 20.9693 | 50.0344 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 20:00
2020-09-16 | 20:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 20:00 | 20:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 20:00
2020-09-16 | 21:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.7833 | 62.4167 | 564.3417 | Average of the hour | 2020-09-16 21:00 | 21:00 | 19.7833 | 62.4167 | 564.3417 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 19.7333 | 70.25 | 538.0833 | Average of the hour | 2020-09-16 21:00 | 21:00 | 19.7333 | 70.25 | 538.0833 |  | high | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.5108 | 55.8117 | 410.8333 | Average of the hour | 2020-09-16 21:00 | 21:00 | 20.5108 | 55.8117 | 410.8333 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.4483 | 53.0358 | 405.25 | Average of the hour | 2020-09-16 21:00 | 21:00 | 22.4483 | 53.0358 | 405.25 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.6242 | 68.1683 | 446.9167 | Average of the hour | 2020-09-16 21:00 | 21:00 | 21.6242 | 68.1683 | 446.9167 |  | high | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.4908 | 52.5883 | 472.5833 | Average of the hour | 2020-09-16 21:00 | 21:00 | 21.4908 | 52.5883 | 472.5833 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.6683 | 50.5392 | 428.5833 | Average of the hour | 2020-09-16 21:00 | 21:00 | 24.6683 | 50.5392 | 428.5833 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 23.1025 | 57.9304 | 425.25 | Average of the hour | 2020-09-16 21:00 | 21:00 | 23.1025 | 57.9304 | 425.25 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.6168 | 55.9116 | 525.0607 | Average of the hour | 2020-09-16 21:00 | 21:00 | 21.6168 | 55.9116 | 525.0607 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.9295 | 55.2197 | 300.4664 | Average of the hour | 2020-09-16 21:00 | 21:00 | 23.9295 | 55.2197 | 300.4664 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.1022 | 52.9868 | 375.8081 | Average of the hour | 2020-09-16 21:00 | 21:00 | 23.1022 | 52.9868 | 375.8081 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.5133 | 61.7442 | 633 | Average of the hour | 2020-09-16 21:00 | 21:00 | 22.5133 | 61.7442 | 633 |  | caution | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.875 | 58.2079 | 427.5 | Average of the hour | 2020-09-16 21:00 | 21:00 | 21.875 | 58.2079 | 427.5 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.5558 | 62.0413 | 431.4167 | Average of the hour | 2020-09-16 21:00 | 21:00 | 21.5558 | 62.0413 | 431.4167 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.7333 | 53.75 | 433.675 | Average of the hour | 2020-09-16 21:00 | 21:00 | 21.7333 | 53.75 | 433.675 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.8 | 52.6908 | 417.1 | Average of the hour | 2020-09-16 21:00 | 21:00 | 21.8 | 52.6908 | 417.1 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 20.9833 |  |  | Average of the hour | 2020-09-16 21:00 | 21:00 | 20.9833 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 19.2583 |  |  | Average of the hour | 2020-09-16 21:00 | 21:00 | 19.2583 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 19.0521 |  | 435.1833 | Average of the hour | 2020-09-16 21:00 | 21:00 | 19.0521 |  | 435.1833 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 19.1725 |  | 379.9167 | Average of the hour | 2020-09-16 21:00 | 21:00 | 19.1725 |  | 379.9167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-16 21:00 | 21:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-16 21:00 | 21:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.2182 | 46.7222 | 448.5981 | Average of the hour | 2020-09-16 21:00 | 21:00 | 22.2182 | 46.7222 | 448.5981 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 57.8939 | 688.1702 | Average of the hour | 2020-09-16 21:00 | 21:00 |  | 57.8939 | 688.1702 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.8957 | 50.7619 |  | Average of the hour | 2020-09-16 21:00 | 21:00 | 20.8957 | 50.7619 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 21:00
2020-09-16 | 21:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 21:00 | 21:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 21:00
2020-09-16 | 22:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.8 | 60.5417 | 536.175 | Average of the hour | 2020-09-16 22:00 | 22:00 | 19.8 | 60.5417 | 536.175 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 17.8917 | 80.2083 | 539.2917 | Average of the hour | 2020-09-16 22:00 | 22:00 | 17.8917 | 80.2083 | 539.2917 |  | high | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.4 | 59.9458 | 413.3333 | Average of the hour | 2020-09-16 22:00 | 22:00 | 20.4 | 59.9458 | 413.3333 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.0525 | 55.6067 | 405.75 | Average of the hour | 2020-09-16 22:00 | 22:00 | 23.0525 | 55.6067 | 405.75 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.6525 | 66.2567 | 447 | Average of the hour | 2020-09-16 22:00 | 22:00 | 21.6525 | 66.2567 | 447 |  | high | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.7967 | 52.735 | 474.5 | Average of the hour | 2020-09-16 22:00 | 22:00 | 21.7967 | 52.735 | 474.5 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.7733 | 50.3108 | 428.3333 | Average of the hour | 2020-09-16 22:00 | 22:00 | 24.7733 | 50.3108 | 428.3333 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 23.1408 | 57.8137 | 424.9167 | Average of the hour | 2020-09-16 22:00 | 22:00 | 23.1408 | 57.8137 | 424.9167 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.7252 | 55.8043 | 522.3005 | Average of the hour | 2020-09-16 22:00 | 22:00 | 21.7252 | 55.8043 | 522.3005 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 24.0207 | 54.962 | 302.0821 | Average of the hour | 2020-09-16 22:00 | 22:00 | 24.0207 | 54.962 | 302.0821 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.1356 | 52.7987 | 371.4885 | Average of the hour | 2020-09-16 22:00 | 22:00 | 23.1356 | 52.7987 | 371.4885 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.5958 | 61.8321 | 627.5 | Average of the hour | 2020-09-16 22:00 | 22:00 | 22.5958 | 61.8321 | 627.5 |  | caution | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.9833 | 57.9567 | 420.6667 | Average of the hour | 2020-09-16 22:00 | 22:00 | 21.9833 | 57.9567 | 420.6667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.9742 | 62.0183 | 431.75 | Average of the hour | 2020-09-16 22:00 | 22:00 | 21.9742 | 62.0183 | 431.75 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.9583 | 54.2917 | 438.6167 | Average of the hour | 2020-09-16 22:00 | 22:00 | 21.9583 | 54.2917 | 438.6167 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.8 | 52.9367 | 417.5333 | Average of the hour | 2020-09-16 22:00 | 22:00 | 21.8 | 52.9367 | 417.5333 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 18.9667 |  |  | Average of the hour | 2020-09-16 22:00 | 22:00 | 18.9667 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 19.0333 |  |  | Average of the hour | 2020-09-16 22:00 | 22:00 | 19.0333 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 18.8724 |  | 438.1667 | Average of the hour | 2020-09-16 22:00 | 22:00 | 18.8724 |  | 438.1667 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 18.8651 |  | 379.5833 | Average of the hour | 2020-09-16 22:00 | 22:00 | 18.8651 |  | 379.5833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-16 22:00 | 22:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-16 22:00 | 22:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.2574 | 46.2314 | 446.9266 | Average of the hour | 2020-09-16 22:00 | 22:00 | 22.2574 | 46.2314 | 446.9266 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 59.5489 | 687.8951 | Average of the hour | 2020-09-16 22:00 | 22:00 |  | 59.5489 | 687.8951 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9286 | 51.813 |  | Average of the hour | 2020-09-16 22:00 | 22:00 | 20.9286 | 51.813 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 22:00
2020-09-16 | 22:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 22:00 | 22:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 22:00
2020-09-16 | 23:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.8 | 61.0417 | 567.75 | Average of the hour | 2020-09-16 23:00 | 23:00 | 19.8 | 61.0417 | 567.75 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 17.2417 | 79.5833 | 540.9583 | Average of the hour | 2020-09-16 23:00 | 23:00 | 17.2417 | 79.5833 | 540.9583 |  | high | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.4333 | 63.8242 | 412.75 | Average of the hour | 2020-09-16 23:00 | 23:00 | 20.4333 | 63.8242 | 412.75 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.36 | 57.9108 | 400.3333 | Average of the hour | 2020-09-16 23:00 | 23:00 | 23.36 | 57.9108 | 400.3333 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.7958 | 67.955 | 446.25 | Average of the hour | 2020-09-16 23:00 | 23:00 | 21.7958 | 67.955 | 446.25 |  | high | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.16 | 54.1625 | 468.25 | Average of the hour | 2020-09-16 23:00 | 23:00 | 22.16 | 54.1625 | 468.25 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.8792 | 49.9125 | 428.5833 | Average of the hour | 2020-09-16 23:00 | 23:00 | 24.8792 | 49.9125 | 428.5833 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 23.0733 | 57.9625 | 425.3333 | Average of the hour | 2020-09-16 23:00 | 23:00 | 23.0733 | 57.9625 | 425.3333 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.7252 | 55.8043 | 520.4681 | Average of the hour | 2020-09-16 23:00 | 23:00 | 21.7252 | 55.8043 | 520.4681 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 24.1458 | 54.3752 | 305.179 | Average of the hour | 2020-09-16 23:00 | 23:00 | 24.1458 | 54.3752 | 305.179 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.1786 | 52.6746 | 373.2938 | Average of the hour | 2020-09-16 23:00 | 23:00 | 23.1786 | 52.6746 | 373.2938 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.7408 | 61.7625 | 623 | Average of the hour | 2020-09-16 23:00 | 23:00 | 22.7408 | 61.7625 | 623 |  | caution | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 22.2425 | 57.36 | 429.5 | Average of the hour | 2020-09-16 23:00 | 23:00 | 22.2425 | 57.36 | 429.5 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.9992 | 62.03 | 428.0833 | Average of the hour | 2020-09-16 23:00 | 23:00 | 21.9992 | 62.03 | 428.0833 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22.2583 | 54.4583 | 439.4083 | Average of the hour | 2020-09-16 23:00 | 23:00 | 22.2583 | 54.4583 | 439.4083 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.8 | 53.3517 | 418.325 | Average of the hour | 2020-09-16 23:00 | 23:00 | 21.8 | 53.3517 | 418.325 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 18.775 |  |  | Average of the hour | 2020-09-16 23:00 | 23:00 | 18.775 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 19.0167 |  |  | Average of the hour | 2020-09-16 23:00 | 23:00 | 19.0167 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 18.8875 |  | 439.7583 | Average of the hour | 2020-09-16 23:00 | 23:00 | 18.8875 |  | 439.7583 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 18.7674 |  | 379.5833 | Average of the hour | 2020-09-16 23:00 | 23:00 | 18.7674 |  | 379.5833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-16 23:00 | 23:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-16 23:00 | 23:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.349 | 45.6693 | 444.5942 | Average of the hour | 2020-09-16 23:00 | 23:00 | 22.349 | 45.6693 | 444.5942 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 60.3607 | 687.761 | Average of the hour | 2020-09-16 23:00 | 23:00 |  | 60.3607 | 687.761 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.8843 | 51.9573 |  | Average of the hour | 2020-09-16 23:00 | 23:00 | 20.8843 | 51.9573 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-16-2020 23:00
2020-09-16 | 23:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-16 23:00 | 23:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-16-2020 23:00
2020-09-17 03:11 | 44091.1324 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Retiring room |  | 1 | 39 | 45 | 380 | 23 | 45 | 380 |  | 2020-09-17 03:11 | 44091.1324 | 23 | 45 | 380 |  |  | 2020-09-14 | B20772¦Retiring room ¦¦Sep-17-2020 03:10
2020-09-17 08:03 | 44091.3352 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 306 |  | 0 | 28 | 38 | 372 | 23.1 | 49.1 | 409 | No | 2020-09-17 08:03 | 44091.3352 | 23.1 | 49.1 | 409 |  |  | 2020-09-14 | B14660¦306¦¦Sep-17-2020 08:02
2020-09-17 08:15 | 44091.3435 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Crown attorneys office |  | 4 | 24.5 | 48.4 | 394 | 22 | 50.1 | 425 | No | 2020-09-17 08:15 | 44091.3435 | 22 | 50.1 | 425 |  |  | 2020-09-14 | B21128¦Crown attorneys office ¦¦Sep-17-2020 08:14
2020-09-17 08:22 | 44091.3488 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NE hall |  | 0 | 17 | 73 | 440 | 21 | 60 | 565 |  | 2020-09-17 08:22 | 44091.3488 | 21 | 60 | 565 |  | caution | 2020-09-14 | B25548¦NE hall¦¦Sep-17-2020 08:22
2020-09-17 08:24 | 44091.3499 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NW Hall |  | 0 | 17 | 73 | 440 | 22 | 58 | 670 |  | 2020-09-17 08:24 | 44091.3499 | 22 | 58 | 670 |  |  | 2020-09-14 | B25548¦NW Hall¦¦Sep-17-2020 08:23
2020-09-17 08:25 | 44091.3508 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | E Hall |  | 0 | 17 | 73 | 440 | 22 | 56 | 585 |  | 2020-09-17 08:25 | 44091.3508 | 22 | 56 | 585 |  |  | 2020-09-14 | B25548¦E Hall¦¦Sep-17-2020 08:25
2020-09-17 08:26 | 44091.3517 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | SE hall |  | 0 | 17 | 73 | 440 | 23 | 56 | 650 |  | 2020-09-17 08:26 | 44091.3517 | 23 | 56 | 650 |  |  | 2020-09-14 | B25548¦SE hall¦¦Sep-17-2020 08:26
2020-09-17 08:28 | 44091.3527 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | SW hall |  | 0 | 17 | 73 | 440 | 23 | 56 | 590 |  | 2020-09-17 08:28 | 44091.3527 | 23 | 56 | 590 |  |  | 2020-09-14 | B25548¦SW hall¦¦Sep-17-2020 08:27
2020-09-17 08:30 | 44091.3541 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | Center hall |  | 0 | 17 | 73 | 440 | 23 | 54 | 620 |  | 2020-09-17 08:30 | 44091.3541 | 23 | 54 | 620 |  |  | 2020-09-14 | B25548¦Center hall¦¦Sep-17-2020 08:29
2020-09-17 08:33 | 44091.3559 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Police Sergeant office |  | 1 | 30 | 35 | 386 | 24 | 49 | 561 |  | 2020-09-17 08:33 | 44091.3559 | 24 | 49 | 561 |  |  | 2020-09-14 | B70235¦Police Sergeant office ¦¦Sep-17-2020 08:32
2020-09-17 08:33 | 44091.356 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- E wall |  | 0 | 17 | 73 | 440 | 23 | 53 | 610 |  | 2020-09-17 08:33 | 44091.356 | 23 | 53 | 610 |  |  | 2020-09-14 | B25548¦1- E wall¦¦Sep-17-2020 08:32
2020-09-17 08:34 | 44091.357 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Front entrance |  | 0 | 14.5 | 74.1 | 427 | 15.8 | 69.3 | 424 |  | 2020-09-17 08:34 | 44091.357 | 15.8 | 69.3 | 424 |  | high | 2020-09-14 | B17477¦Front entrance ¦¦Sep-17-2020 08:34
2020-09-17 08:35 | 44091.3576 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- E wall |  | 0 | 17 | 73 | 440 | 23 | 54 | 600 |  | 2020-09-17 08:35 | 44091.3576 | 23 | 54 | 600 |  |  | 2020-09-14 | B25548¦1- E wall¦¦Sep-17-2020 08:35
2020-09-17 08:37 | 44091.3588 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- E wall |  | 0 | 17 | 73 | 440 | 23 | 53 | 600 |  | 2020-09-17 08:37 | 44091.3588 | 23 | 53 | 600 |  |  | 2020-09-14 | B25548¦1- E wall¦¦Sep-17-2020 08:36
2020-09-17 08:37 | 44091.359 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Administration office |  | 6 | 15.1 | 70.2 | 406 | 20.2 | 58.4 | 467 |  | 2020-09-17 08:37 | 44091.359 | 20.2 | 58.4 | 467 |  |  | 2020-09-14 | B90558¦Administration office¦¦Sep-17-2020 08:36
2020-09-17 08:38 | 44091.3599 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- S wall |  | 0 | 17 | 73 | 440 | 23 | 53 | 600 |  | 2020-09-17 08:38 | 44091.3599 | 23 | 53 | 600 |  |  | 2020-09-14 | B25548¦1- S wall¦¦Sep-17-2020 08:38
2020-09-17 08:39 | 44091.3601 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | OPP office |  | 1 | 15 | 70 | 412 | 19 | 61 | 494 |  | 2020-09-17 08:39 | 44091.3601 | 19 | 61 | 494 |  | caution | 2020-09-14 | B70235¦OPP office ¦¦Sep-17-2020 08:38
2020-09-17 08:39 | 44091.3603 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 128 |  | 0 | 11 | 72 | 385 | 19.6 | 60.2 | 404 | No | 2020-09-17 08:39 | 44091.3603 | 19.6 | 60.2 | 404 |  | caution | 2020-09-14 | B14660¦128¦¦Sep-17-2020 08:38
2020-09-17 08:40 | 44091.3611 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Security |  | 1 | 15.1 | 71 | 43.3 | 20.6 | 58 | 476 |  | 2020-09-17 08:40 | 44091.3611 | 20.6 | 58 | 476 |  |  | 2020-09-14 | B17477¦Security ¦¦Sep-17-2020 08:39
2020-09-17 08:40 | 44091.3611 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- S wall |  | 0 | 17 | 73 | 440 | 23 | 53 | 600 |  | 2020-09-17 08:40 | 44091.3611 | 23 | 53 | 600 |  |  | 2020-09-14 | B25548¦1- S wall¦¦Sep-17-2020 08:40
2020-09-17 08:41 | 44091.3615 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office E |  | 2 | 15 | 70 | 412 | 21 | 53 | 454 |  | 2020-09-17 08:41 | 44091.3615 | 21 | 53 | 454 |  |  | 2020-09-14 | B70235¦Main office E ¦¦Sep-17-2020 08:40
2020-09-17 08:42 | 44091.3624 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 1 seating area |  | 0 | 15.1 | 71 | 43.3 | 21.5 | 54.6 | 428 |  | 2020-09-17 08:42 | 44091.3624 | 21.5 | 54.6 | 428 |  |  | 2020-09-14 | B17477¦Level 1 seating area ¦¦Sep-17-2020 08:41
2020-09-17 08:42 | 44091.3627 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- S wall |  | 0 | 17 | 73 | 440 | 23 | 53 | 630 |  | 2020-09-17 08:42 | 44091.3627 | 23 | 53 | 630 |  |  | 2020-09-14 | B25548¦1- S wall¦¦Sep-17-2020 08:42
2020-09-17 08:43 | 44091.3634 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 1 seating area 2 |  | 0 | 15.1 | 71 | 44.3 | 21.7 | 54 | 425 |  | 2020-09-17 08:43 | 44091.3634 | 21.7 | 54 | 425 |  |  | 2020-09-14 | B17477¦Level 1 seating area 2 ¦¦Sep-17-2020 08:43
2020-09-17 08:44 | 44091.3636 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 001 |  | 0 | 11 | 72 | 385 | 19.6 | 51.4 | 398 | No | 2020-09-17 08:44 | 44091.3636 | 19.6 | 51.4 | 398 |  |  | 2020-09-14 | B14660¦001¦¦Sep-17-2020 08:43
2020-09-17 08:45 | 44091.3645 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- S wall |  | 0 | 17 | 53 | 440 | 23 | 53 | 580 |  | 2020-09-17 08:45 | 44091.3645 | 23 | 53 | 580 |  |  | 2020-09-14 | B25548¦1- S wall¦¦Sep-17-2020 08:44
2020-09-17 08:46 | 44091.365 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom#1 |  | 1 | 15.1 | 70.2 | 406 | 21.2 | 50.5 | 433 |  | 2020-09-17 08:46 | 44091.365 | 21.2 | 50.5 | 433 |  |  | 2020-09-14 | B90558¦Courtroom#1¦¦Sep-17-2020 08:45
2020-09-17 08:47 | 44091.3661 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Main entrance |  | 0 | 17.2 | 71.5 | 432 | 19.6 | 64.7 | 485 |  | 2020-09-17 08:47 | 44091.3661 | 19.6 | 64.7 | 485 |  | caution | 2020-09-14 | B25039¦Main entrance¦¦Sep-17-2020 08:47
2020-09-17 08:47 | 44091.3662 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 seating area |  | 0 | 15.1 | 71 | 43.3 | 22.1 | 52.2 | 428 |  | 2020-09-17 08:47 | 44091.3662 | 22.1 | 52.2 | 428 |  |  | 2020-09-14 | B17477¦Courtroom 100 seating area ¦¦Sep-17-2020 08:47
2020-09-17 08:47 | 44091.3662 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- S wall |  | 0 | 17 | 73 | 440 | 23 | 53 | 580 |  | 2020-09-17 08:47 | 44091.3662 | 23 | 53 | 580 |  |  | 2020-09-14 | B25548¦1- S wall¦¦Sep-17-2020 08:47
2020-09-17 08:48 | 44091.3666 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 028 |  | 0 | 11 | 72 | 385 | 20.9 | 46.9 | 415 | No | 2020-09-17 08:48 | 44091.3666 | 20.9 | 46.9 | 415 |  |  | 2020-09-14 | B14660¦028¦¦Sep-17-2020 08:47
2020-09-17 08:49 | 44091.3672 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom#2 |  | 1 | 15.1 | 70.2 | 406 | 20.8 | 50.7 | 427 |  | 2020-09-17 08:49 | 44091.3672 | 20.8 | 50.7 | 427 |  |  | 2020-09-14 | B90558¦Courtroom#2¦¦Sep-17-2020 08:48
2020-09-17 08:49 | 44091.3672 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Office 1 |  | 0 | 17.2 | 71.5 | 432 | 23 | 51.3 | 429 |  | 2020-09-17 08:49 | 44091.3672 | 23 | 51.3 | 429 |  |  | 2020-09-14 | B25039¦Office 1¦¦Sep-17-2020 08:48
2020-09-17 08:49 | 44091.3675 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 seating area 2 |  | 0 | 15.1 | 71 | 43.3 | 22.5 | 52.3 | 431 |  | 2020-09-17 08:49 | 44091.3675 | 22.5 | 52.3 | 431 |  |  | 2020-09-14 | B17477¦Courtroom 100 seating area 2¦¦Sep-17-2020 08:49
2020-09-17 08:49 | 44091.3676 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 3 gallery |  | 0 | 15 | 68 | 421 | 20.2 | 51.4 | 428 | No | 2020-09-17 08:49 | 44091.3676 | 20.2 | 51.4 | 428 |  |  | 2020-09-14 | B20151¦Court room 3 gallery ¦¦Sep-17-2020 08:49
2020-09-17 08:50 | 44091.3677 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- S wall |  | 0 | 17 | 73 | 440 | 23 | 53 | 580 |  | 2020-09-17 08:50 | 44091.3677 | 23 | 53 | 580 |  |  | 2020-09-14 | B25548¦1- S wall¦¦Sep-17-2020 08:49
2020-09-17 08:50 | 44091.3679 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 019 |  | 0 | 11 | 72 | 385 | 21.5 | 46.4 | 409 | No | 2020-09-17 08:50 | 44091.3679 | 21.5 | 46.4 | 409 |  |  | 2020-09-14 | B14660¦019¦¦Sep-17-2020 08:49
2020-09-17 08:50 | 44091.3682 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Copier room |  | 0 | 17.2 | 71.5 | 432 | 22.8 | 51.8 | 430 |  | 2020-09-17 08:50 | 44091.3682 | 22.8 | 51.8 | 430 |  |  | 2020-09-14 | B25039¦Copier room¦¦Sep-17-2020 08:50
2020-09-17 08:51 | 44091.3688 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 3 judge desk |  | 0 | 15 | 68 | 421 | 20.5 | 51 | 432 | No | 2020-09-17 08:51 | 44091.3688 | 20.5 | 51 | 432 |  |  | 2020-09-14 | B20151¦Court room 3 judge desk ¦¦Sep-17-2020 08:51
2020-09-17 08:51 | 44091.3688 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 doors |  | 1 | 15.1 | 71 | 433 | 22.3 | 50.9 | 423 |  | 2020-09-17 08:51 | 44091.3688 | 22.3 | 50.9 | 423 |  |  | 2020-09-14 | B17477¦Courtroom 100 doors ¦¦Sep-17-2020 08:51
2020-09-17 08:52 | 44091.3693 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom#3 |  | 2 | 15.1 | 70.2 | 406 | 21.3 | 50.5 | 433 |  | 2020-09-17 08:52 | 44091.3693 | 21.3 | 50.5 | 433 |  |  | 2020-09-14 | B90558¦Courtroom#3¦¦Sep-17-2020 08:51
2020-09-17 08:52 | 44091.3694 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Office 2 |  | 0 | 17.2 | 71.5 | 432 | 22.7 | 51.7 | 427 |  | 2020-09-17 08:52 | 44091.3694 | 22.7 | 51.7 | 427 |  |  | 2020-09-14 | B25039¦Office 2¦¦Sep-17-2020 08:51
2020-09-17 08:53 | 44091.3698 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- W wall |  | 0 | 17 | 73 | 440 | 23 | 53 | 580 |  | 2020-09-17 08:52 | 44091.3698 | 23 | 53 | 580 |  |  | 2020-09-14 | B25548¦1- W wall¦¦Sep-17-2020 08:52
2020-09-17 08:53 | 44091.3699 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 011 |  | 0 | 11 | 72 | 385 | 21.9 | 45.2 | 415 | No | 2020-09-17 08:53 | 44091.3699 | 21.9 | 45.2 | 415 |  |  | 2020-09-14 | B14660¦011¦¦Sep-17-2020 08:52
2020-09-17 08:53 | 44091.3703 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Judges panel |  | 0 | 17.2 | 71.5 | 432 | 22.6 | 52.1 | 426 |  | 2020-09-17 08:53 | 44091.3703 | 22.6 | 52.1 | 426 |  |  | 2020-09-14 | B25039¦Judges panel¦¦Sep-17-2020 08:53
2020-09-17 08:53 | 44091.3704 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 bench |  | 1 | 15.1 | 71 | 433 | 21.7 | 51.8 | 428 |  | 2020-09-17 08:53 | 44091.3704 | 21.7 | 51.8 | 428 |  |  | 2020-09-14 | B17477¦Courtroom 100 bench¦¦Sep-17-2020 08:53
2020-09-17 08:54 | 44091.3708 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 1 |  | 1 | 15 | 68 | 421 | 20.8 | 49.5 | 457 | No | 2020-09-17 08:54 | 44091.3708 | 20.8 | 49.5 | 457 |  |  | 2020-09-14 | B20151¦Court room 1¦¦Sep-17-2020 08:53
2020-09-17 08:55 | 44091.3712 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- W wall |  | 0 | 17 | 73 | 440 | 22 | 53 | 580 |  | 2020-09-17 08:55 | 44091.3712 | 22 | 53 | 580 |  |  | 2020-09-14 | B25548¦1- W wall¦¦Sep-17-2020 08:54
2020-09-17 08:55 | 44091.3714 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Courtroom front east |  | 0 | 17.2 | 71.5 | 432 | 22.5 | 52.6 | 421 |  | 2020-09-17 08:55 | 44091.3714 | 22.5 | 52.6 | 421 |  |  | 2020-09-14 | B25039¦Courtroom front east¦¦Sep-17-2020 08:54
2020-09-17 08:55 | 44091.3717 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 118 |  | 0 | 11 | 72 | 385 | 22.5 | 45.3 | 409 | No | 2020-09-17 08:55 | 44091.3717 | 22.5 | 45.3 | 409 |  |  | 2020-09-14 | B14660¦118¦¦Sep-17-2020 08:55
2020-09-17 08:55 | 44091.3717 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 1 ramp |  | 0 | 15.1 | 71 | 433 | 22 | 51.4 | 428 |  | 2020-09-17 08:55 | 44091.3717 | 22 | 51.4 | 428 |  |  | 2020-09-14 | B17477¦Level 1 ramp ¦¦Sep-17-2020 08:55
2020-09-17 08:56 | 44091.372 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice O'Brien office |  | 0 | 15.1 | 70.2 | 406 | 20.6 | 46.3 | 440 | Dehumidifier running, set at 17 | 2020-09-17 08:56 | 44091.372 | 20.6 | 46.3 | 440 |  |  | 2020-09-14 | B90558¦Justice O'Brien office¦¦Sep-17-2020 08:55
2020-09-17 08:56 | 44091.3725 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Courtroom front west |  | 0 | 17.2 | 71.5 | 432 | 22.3 | 52.8 | 422 |  | 2020-09-17 08:56 | 44091.3725 | 22.3 | 52.8 | 422 |  |  | 2020-09-14 | B25039¦Courtroom front west¦¦Sep-17-2020 08:56
2020-09-17 08:57 | 44091.373 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 2 seating area |  | 0 | 15.1 | 71 | 433 | 22.3 | 50.6 | 427 |  | 2020-09-17 08:57 | 44091.373 | 22.3 | 50.6 | 427 |  |  | 2020-09-14 | B17477¦Level 2 seating area ¦¦Sep-17-2020 08:57
2020-09-17 08:57 | 44091.3732 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 0 | 13 | 60 | 412 | 20.1 | 53.5 | 556 |  | 2020-09-17 08:57 | 44091.3732 | 20.1 | 53.5 | 556 |  |  | 2020-09-14 | B16187¦Court 3¦¦Sep-17-2020 08:57
2020-09-17 08:58 | 44091.3733 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- W wall |  | 0 | 17 | 73 | 440 | 22 | 54 | 590 |  | 2020-09-17 08:58 | 44091.3733 | 22 | 54 | 590 |  |  | 2020-09-14 | B25548¦1- W wall¦¦Sep-17-2020 08:57
2020-09-17 08:58 | 44091.3733 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice Wheeler office |  | 0 | 15.1 | 70.2 | 406 | 20.4 | 53.4 | 444 |  | 2020-09-17 08:58 | 44091.3733 | 20.4 | 53.4 | 444 |  |  | 2020-09-14 | B90558¦Justice Wheeler office¦¦Sep-17-2020 08:57
2020-09-17 08:58 | 44091.3734 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 115 |  | 0 | 11 | 72 | 385 | 23.2 | 42 | 410 | No | 2020-09-17 08:58 | 44091.3734 | 23.2 | 42 | 410 |  |  | 2020-09-14 | B14660¦115¦¦Sep-17-2020 08:57
2020-09-17 08:58 | 44091.3736 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 0 | 13 | 60 | 412 | 20.8 | 51.1 | 529 |  | 2020-09-17 08:58 | 44091.3736 | 20.8 | 51.1 | 529 |  |  | 2020-09-14 | B16187¦Court 3¦¦Sep-17-2020 08:57
2020-09-17 08:58 | 44091.3736 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Courtroom rear west |  | 0 | 17.2 | 71.5 | 432 | 22.3 | 53 | 423 |  | 2020-09-17 08:58 | 44091.3736 | 22.3 | 53 | 423 |  |  | 2020-09-14 | B25039¦Courtroom rear west¦¦Sep-17-2020 08:57
2020-09-17 08:59 | 44091.374 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 2 ramp |  | 0 | 15.1 | 71 | 433 | 22.3 | 50.7 | 429 |  | 2020-09-17 08:59 | 44091.374 | 22.3 | 50.7 | 429 |  |  | 2020-09-14 | B17477¦Level 2 ramp ¦¦Sep-17-2020 08:58
2020-09-17 08:59 | 44091.3742 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 0 | 13 | 60 | 412 | 21.3 | 46.1 | 469 |  | 2020-09-17 08:59 | 44091.3742 | 21.3 | 46.1 | 469 |  |  | 2020-09-14 | B16187¦Court 3¦¦Sep-17-2020 08:58
2020-09-17 08:59 | 44091.3743 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | S foyer |  | 0 | 17 | 73 | 440 | 22 | 54 | 630 |  | 2020-09-17 08:59 | 44091.3743 | 22 | 54 | 630 |  |  | 2020-09-14 | B25548¦S foyer¦¦Sep-17-2020 08:59
2020-09-17 08:59 | 44091.3745 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 3 gallery |  | 1 | 15 | 68 | 421 | 21.8 | 47.9 | 455 | No | 2020-09-17 08:59 | 44091.3745 | 21.8 | 47.9 | 455 |  |  | 2020-09-14 | B20151¦Court room 3 gallery ¦¦Sep-17-2020 08:59
2020-09-17 08:59 | 44091.3746 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 60 | 412 | 21.3 | 45 | 440 |  | 2020-09-17 08:59 | 44091.3746 | 21.3 | 45 | 440 |  |  | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 08:59
2020-09-17 09:00 | 44091.3747 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice Letourneau office |  | 0 | 15.1 | 70.2 | 406 | 21.1 | 51.8 | 426 |  | 2020-09-17 09:00 | 44091.3747 | 21.1 | 51.8 | 426 |  |  | 2020-09-14 | B90558¦Justice Letourneau office¦¦Sep-17-2020 08:59
2020-09-17 09:00 | 44091.3749 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Courtroom rear east |  | 0 | 17.2 | 71.5 | 432 | 22.2 | 53.2 | 425 |  | 2020-09-17 09:00 | 44091.3749 | 22.2 | 53.2 | 425 |  |  | 2020-09-14 | B25039¦Courtroom rear east¦¦Sep-17-2020 08:59
2020-09-17 09:00 | 44091.3752 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Robing corridor |  | 1 | 13.8 | 71.6 | 478 | 20 | 54.1 | 451 |  | 2020-09-17 09:00 | 44091.3752 | 20 | 54.1 | 451 |  |  | 2020-09-14 | B20474¦Robing corridor¦¦Sep-17-2020 09:00
2020-09-17 09:00 | 44091.3753 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | N foyer |  | 0 | 17 | 73 | 440 | 23 | 54 | 610 |  | 2020-09-17 09:00 | 44091.3753 | 23 | 54 | 610 |  |  | 2020-09-14 | B25548¦N foyer¦¦Sep-17-2020 09:00
2020-09-17 09:00 | 44091.3753 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 3 |  | 1 | 15.2 | 70 | 377 | 20.7 | 60.3 | 436 |  | 2020-09-17 09:00 | 44091.3753 | 20.7 | 60.3 | 436 |  | caution | 2020-09-14 | B20494¦Courtroom 3¦¦Sep-17-2020 09:00
2020-09-17 09:01 | 44091.3754 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 3 seating area |  | 0 | 15.1 | 71 | 433 | 21 | 51.1 | 447 |  | 2020-09-17 09:01 | 44091.3754 | 21 | 51.1 | 447 |  |  | 2020-09-14 | B17477¦Level 3 seating area ¦¦Sep-17-2020 09:00
2020-09-17 09:01 | 44091.3755 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 3 judge desk |  | 1 | 15 | 68 | 421 | 22.2 | 46 | 463 |  | 2020-09-17 09:01 | 44091.3755 | 22.2 | 46 | 463 |  |  | 2020-09-14 | B20151¦Court room 3 judge desk ¦¦Sep-17-2020 09:00
2020-09-17 09:01 | 44091.3756 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 4 |  | 0 | 13 | 60 | 412 | 21.2 | 43.2 | 438 |  | 2020-09-17 09:01 | 44091.3756 | 21.2 | 43.2 | 438 |  |  | 2020-09-14 | B16187¦Court 4¦¦Sep-17-2020 09:00
2020-09-17 09:01 | 44091.3757 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Waiting room |  | 0 | 17.2 | 71.5 | 432 | 22.4 | 52.5 | 423 |  | 2020-09-17 09:01 | 44091.3757 | 22.4 | 52.5 | 423 |  |  | 2020-09-14 | B25039¦Waiting room¦¦Sep-17-2020 09:01
2020-09-17 09:01 | 44091.3758 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 107 |  | 3 | 11 | 72 | 385 | 20.5 | 47.4 | 437 | No | 2020-09-17 09:01 | 44091.3758 | 20.5 | 47.4 | 437 |  |  | 2020-09-14 | B14660¦107¦¦Sep-17-2020 09:01
2020-09-17 09:01 | 44091.376 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 2nd floor SE hall |  | 1 | 14.5 | 74.7 | 397 | 21.6 | 50.3 | 433 |  | 2020-09-17 09:01 | 44091.376 | 21.6 | 50.3 | 433 |  |  | 2020-09-14 | B20494¦2nd floor SE hall¦¦Sep-17-2020 09:01
2020-09-17 09:02 | 44091.3761 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Service desk |  | 2 | 13 | 60 | 412 | 21 | 42 | 434 |  | 2020-09-17 09:02 | 44091.3761 | 21 | 42 | 434 |  |  | 2020-09-14 | B16187¦Service desk¦¦Sep-17-2020 09:01
2020-09-17 09:02 | 44091.3763 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 3 seating area 2 |  | 0 | 15.1 | 71 | 433 | 22.1 | 50.7 | 427 |  | 2020-09-17 09:02 | 44091.3763 | 22.1 | 50.7 | 427 |  |  | 2020-09-14 | B17477¦Level 3 seating area 2 ¦¦Sep-17-2020 09:01
2020-09-17 09:02 | 44091.3763 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- N wall |  | 0 | 17 | 73 | 440 | 23 | 53 | 590 |  | 2020-09-17 09:02 | 44091.3763 | 23 | 53 | 590 |  |  | 2020-09-14 | B25548¦1- N wall¦¦Sep-17-2020 09:01
2020-09-17 09:02 | 44091.3764 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | TC office |  | 2 | 15.1 | 70.2 | 406 | 21.6 | 50.6 | 471 | Air conditioner running | 2020-09-17 09:02 | 44091.3764 | 21.6 | 50.6 | 471 |  |  | 2020-09-14 | B90558¦TC office¦¦Sep-17-2020 09:01
2020-09-17 09:02 | 44091.3766 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 60 | 412 | 21.8 | 45 | 461 |  | 2020-09-17 09:02 | 44091.3766 | 21.8 | 45 | 461 |  |  | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 09:02
2020-09-17 09:02 | 44091.3767 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Mediation room 2 |  | 0 | 17.2 | 71.5 | 432 | 22 | 53.7 | 425 |  | 2020-09-17 09:02 | 44091.3767 | 22 | 53.7 | 425 |  |  | 2020-09-14 | B25039¦Mediation room 2¦¦Sep-17-2020 09:02
2020-09-17 09:03 | 44091.3772 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 seating area |  | 0 | 15.1 | 71 | 433 | 22.5 | 50.6 | 433 |  | 2020-09-17 09:03 | 44091.3772 | 22.5 | 50.6 | 433 |  |  | 2020-09-14 | B17477¦Courtroom 300 seating area ¦¦Sep-17-2020 09:03
2020-09-17 09:03 | 44091.3774 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Second floor hallway nw |  | 1 | 15.2 | 70 | 377 | 21.3 | 59.7 | 438 |  | 2020-09-17 09:03 | 44091.3774 | 21.3 | 59.7 | 438 |  |  | 2020-09-14 | B20494¦Second floor hallway nw¦¦Sep-17-2020 09:03
2020-09-17 09:04 | 44091.3774 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 113 |  | 0 | 11 | 72 | 385 | 22 | 42.5 | 411 | No | 2020-09-17 09:04 | 44091.3774 | 22 | 42.5 | 411 |  |  | 2020-09-14 | B14660¦113¦¦Sep-17-2020 09:03
2020-09-17 09:04 | 44091.3776 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- N wall |  | 0 | 17 | 73 | 440 | 23 | 53 | 580 |  | 2020-09-17 09:04 | 44091.3776 | 23 | 53 | 580 |  |  | 2020-09-14 | B25548¦1- N wall¦¦Sep-17-2020 09:03
2020-09-17 09:04 | 44091.3776 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 1 |  | 0 | 13 | 60 | 412 | 21.2 | 45.9 | 434 |  | 2020-09-17 09:04 | 44091.3776 | 21.2 | 45.9 | 434 |  |  | 2020-09-14 | B16187¦Court 1¦¦Sep-17-2020 09:03
2020-09-17 09:04 | 44091.3777 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Mediation room 1 |  | 0 | 17.2 | 71.5 | 432 | 22.2 | 53.3 | 424 |  | 2020-09-17 09:04 | 44091.3777 | 22.2 | 53.3 | 424 |  |  | 2020-09-14 | B25039¦Mediation room 1¦¦Sep-17-2020 09:03
2020-09-17 09:04 | 44091.3779 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Library |  | 0 | 15.1 | 70.2 | 406 | 20.9 | 50.4 | 417 |  | 2020-09-17 09:04 | 44091.3779 | 20.9 | 50.4 | 417 |  |  | 2020-09-14 | B90558¦Library¦¦Sep-17-2020 09:04
2020-09-17 09:04 | 44091.3779 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Criminal Justice office |  | 2 | 14.5 | 74.4 | 397 | 22.2 | 50.5 | 451 |  | 2020-09-17 09:04 | 44091.3779 | 22.2 | 50.5 | 451 |  |  | 2020-09-14 | B20494¦Criminal Justice office ¦¦Sep-17-2020 09:04
2020-09-17 09:04 | 44091.378 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 60 | 412 | 21.5 | 46.2 | 441 |  | 2020-09-17 09:04 | 44091.378 | 21.5 | 46.2 | 441 |  |  | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 09:04
2020-09-17 09:05 | 44091.3782 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Front lobby |  | 2 | 15.7 | 72 | 404 | 17.8 | 70.5 | 433 |  | 2020-09-17 09:05 | 44091.3782 | 17.8 | 70.5 | 433 |  | high | 2020-09-14 | B11228¦Front lobby¦¦Sep-17-2020 09:04
2020-09-17 09:05 | 44091.3783 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 seating area 2 |  | 0 | 15.1 | 71 | 433 | 22.9 | 48.6 | 426 |  | 2020-09-17 09:05 | 44091.3783 | 22.9 | 48.6 | 426 |  |  | 2020-09-14 | B17477¦Courtroom 300 seating area 2 ¦¦Sep-17-2020 09:04
2020-09-17 09:05 | 44091.3787 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Washroom |  | 0 | 17.2 | 71.5 | 426 | 21.9 | 54 | 426 |  | 2020-09-17 09:05 | 44091.3787 | 21.9 | 54 | 426 |  |  | 2020-09-14 | B25039¦Washroom¦¦Sep-17-2020 09:05
2020-09-17 09:05 | 44091.3788 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Crown attorney |  | 0 | 13 | 60 | 412 | 21.4 | 45.7 | 441 |  | 2020-09-17 09:05 | 44091.3788 | 21.4 | 45.7 | 441 |  |  | 2020-09-14 | B16187¦Crown attorney ¦¦Sep-17-2020 09:05
2020-09-17 09:06 | 44091.3789 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9-bench |  | 2 | 15 | 72 | 367 | 21 | 51 | 387 |  | 2020-09-17 09:06 | 44091.3789 | 21 | 51 | 387 |  |  | 2020-09-14 | B20772¦H9-bench ¦¦Sep-17-2020 09:05
2020-09-17 09:06 | 44091.3791 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- N wall |  | 0 | 17 | 73 | 440 | 23 | 53 | 590 |  | 2020-09-17 09:06 | 44091.3791 | 23 | 53 | 590 |  |  | 2020-09-14 | B25548¦1- N wall¦¦Sep-17-2020 09:05
2020-09-17 09:06 | 44091.3791 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Front staircase |  | 1 | 16.6 | 72 | 404 | 19.1 | 65 | 434 |  | 2020-09-17 09:06 | 44091.3791 | 19.1 | 65 | 434 |  | caution | 2020-09-14 | B11228¦Front staircase¦¦Sep-17-2020 09:05
2020-09-17 09:06 | 44091.3792 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 2 |  | 0 | 13 | 60 | 412 | 21.5 | 45.4 | 442 |  | 2020-09-17 09:06 | 44091.3792 | 21.5 | 45.4 | 442 |  |  | 2020-09-14 | B16187¦Court 2 ¦¦Sep-17-2020 09:06
2020-09-17 09:06 | 44091.3792 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 waiting area |  | 0 | 15 | 68 | 421 | 21.8 | 45.9 | 455 | No | 2020-09-17 09:06 | 44091.3792 | 21.8 | 45.9 | 455 |  |  | 2020-09-14 | B20151¦Court room 2 waiting area ¦¦Sep-17-2020 09:06
2020-09-17 09:06 | 44091.3793 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Second floor hallway sw |  | 1 | 15.2 | 70 | 377 | 21.6 | 53.8 | 439 |  | 2020-09-17 09:06 | 44091.3793 | 21.6 | 53.8 | 439 |  |  | 2020-09-14 | B20494¦Second floor hallway sw¦¦Sep-17-2020 09:06
2020-09-17 09:06 | 44091.3794 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 114 |  | 0 | 11 | 72 | 385 | 22.2 | 44 | 415 | No | 2020-09-17 09:06 | 44091.3794 | 22.2 | 44 | 415 |  |  | 2020-09-14 | B14660¦114¦¦Sep-17-2020 09:06
2020-09-17 09:07 | 44091.3796 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 60 | 412 | 21.3 | 46.6 | 439 |  | 2020-09-17 09:07 | 44091.3796 | 21.3 | 46.6 | 439 |  |  | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 09:06
2020-09-17 09:07 | 44091.3796 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Waiting area 2 |  | 1 | 15.1 | 70.2 | 406 | 21.2 | 50.3 | 434 |  | 2020-09-17 09:07 | 44091.3796 | 21.2 | 50.3 | 434 |  |  | 2020-09-14 | B90558¦Waiting area 2¦¦Sep-17-2020 09:06
2020-09-17 09:07 | 44091.3796 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Main hall |  | 0 | 17.2 | 71.5 | 432 | 22.2 | 54.7 | 433 |  | 2020-09-17 09:07 | 44091.3796 | 22.2 | 54.7 | 433 |  |  | 2020-09-14 | B25039¦Main hall¦¦Sep-17-2020 09:06
2020-09-17 09:07 | 44091.3799 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom waiting area/entrance - right side |  | 2 | 16.2 | 60.9 | 385 | 22.2 | 45.6 | 394 |  | 2020-09-17 09:07 | 44091.3799 | 22.2 | 45.6 | 394 |  |  | 2020-09-14 | B70277¦Courtroom waiting area/entrance - right side¦¦Sep-17-2020 09:06
2020-09-17 09:07 | 44091.3799 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 - defense seat |  | 2 | 15 | 72 | 367 | 21 | 51 | 388 |  | 2020-09-17 09:07 | 44091.3799 | 21 | 51 | 388 |  |  | 2020-09-14 | B20772¦H9 - defense seat¦¦Sep-17-2020 09:07
2020-09-17 09:07 | 44091.38 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 60 | 412 | 21.9 | 49.6 | 445 |  | 2020-09-17 09:07 | 44091.38 | 21.9 | 49.6 | 445 |  |  | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 09:07
2020-09-17 09:07 | 44091.38 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Upper courtroom |  | 1 | 16.6 | 72 | 404 | 20.4 | 63.5 | 431 |  | 2020-09-17 09:07 | 44091.38 | 20.4 | 63.5 | 431 |  | caution | 2020-09-14 | B11228¦Upper courtroom¦¦Sep-17-2020 09:07
2020-09-17 09:07 | 44091.3801 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 2 |  | 1 | 14.5 | 74.7 | 397 | 21.9 | 47.9 | 416 |  | 2020-09-17 09:07 | 44091.3801 | 21.9 | 47.9 | 416 |  |  | 2020-09-14 | B20494¦Courtroom 2¦¦Sep-17-2020 09:07
2020-09-17 09:08 | 44091.3802 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- N wall |  | 0 | 17 | 73 | 440 | 23 | 53 | 600 |  | 2020-09-17 09:08 | 44091.3802 | 23 | 53 | 600 |  |  | 2020-09-14 | B25548¦1- N wall¦¦Sep-17-2020 09:07
2020-09-17 09:08 | 44091.3805 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Lunch room |  | 0 | 17.2 | 71.5 | 432 | 21.8 | 56 | 473 |  | 2020-09-17 09:08 | 44091.3805 | 21.8 | 56 | 473 |  |  | 2020-09-14 | B25039¦Lunch room¦¦Sep-17-2020 09:07
2020-09-17 09:08 | 44091.3805 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 4 |  | 0 | 13 | 60 | 412 | 21.8 | 45.1 | 465 |  | 2020-09-17 09:08 | 44091.3805 | 21.8 | 45.1 | 465 |  |  | 2020-09-14 | B16187¦Court 4¦¦Sep-17-2020 09:07
2020-09-17 09:08 | 44091.3806 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 - middle |  | 2 | 15 | 72 | 367 | 21 | 51 | 380 |  | 2020-09-17 09:08 | 44091.3806 | 21 | 51 | 380 |  |  | 2020-09-14 | B20772¦H9 - middle ¦¦Sep-17-2020 09:08
2020-09-17 09:08 | 44091.3807 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Upper office |  | 1 | 16.6 | 72 | 404 | 21.6 | 60 | 435 |  | 2020-09-17 09:08 | 44091.3807 | 21.6 | 60 | 435 |  | caution | 2020-09-14 | B11228¦Upper office¦¦Sep-17-2020 09:08
2020-09-17 09:09 | 44091.3809 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 60 | 412 | 21.6 | 46.5 | 469 |  | 2020-09-17 09:08 | 44091.3809 | 21.6 | 46.5 | 469 |  |  | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 09:08
2020-09-17 09:09 | 44091.3809 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family court office |  | 3 | 15.2 | 70 | 377 | 22.2 | 53.1 | 901 |  | 2020-09-17 09:09 | 44091.3809 | 22.2 | 53.1 | 901 |  |  | 2020-09-14 | B20494¦Family court office¦¦Sep-17-2020 09:08
2020-09-17 09:09 | 44091.3812 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9-rest left |  | 2 | 15 | 72 | 367 | 21 | 51 | 380 |  | 2020-09-17 09:09 | 44091.3812 | 21 | 51 | 380 |  |  | 2020-09-14 | B20772¦H9-rest left ¦¦Sep-17-2020 09:08
2020-09-17 09:09 | 44091.3812 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 104 |  | 0 | 11 | 72 | 385 | 22.1 | 43.6 | 418 | No | 2020-09-17 09:09 | 44091.3812 | 22.1 | 43.6 | 418 |  |  | 2020-09-14 | B14660¦104¦¦Sep-17-2020 09:08
2020-09-17 09:09 | 44091.3813 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom waiting room/entrance - left side |  | 2 | 16.2 | 60.9 | 385 | 22.3 | 45.4 | 406 |  | 2020-09-17 09:09 | 44091.3813 | 22.3 | 45.4 | 406 |  |  | 2020-09-14 | B70277¦Courtroom waiting room/entrance - left side¦¦Sep-17-2020 09:09
2020-09-17 09:09 | 44091.3814 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Basment common |  | 0 | 13 | 60 | 412 | 21.5 | 48.8 | 512 |  | 2020-09-17 09:09 | 44091.3814 | 21.5 | 48.8 | 512 |  |  | 2020-09-14 | B16187¦Basment common¦¦Sep-17-2020 09:09
2020-09-17 09:09 | 44091.3814 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Lunch room hall |  | 0 | 17.2 | 71.5 | 432 | 22.2 | 54.8 | 466 |  | 2020-09-17 09:09 | 44091.3814 | 22.2 | 54.8 | 466 |  |  | 2020-09-14 | B25039¦Lunch room hall¦¦Sep-17-2020 09:09
2020-09-17 09:09 | 44091.3816 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Upper hallwau |  | 1 | 16.6 | 72 | 404 | 21.3 | 57.7 | 439 |  | 2020-09-17 09:09 | 44091.3816 | 21.3 | 57.7 | 439 |  |  | 2020-09-14 | B11228¦Upper hallwau¦¦Sep-17-2020 09:09
2020-09-17 09:10 | 44091.3818 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9-rear right |  | 2 | 15 | 72 | 367 | 21 | 51 | 380 |  | 2020-09-17 09:10 | 44091.3818 | 21 | 51 | 380 |  |  | 2020-09-14 | B20772¦H9-rear right¦¦Sep-17-2020 09:09
2020-09-17 09:10 | 44091.3818 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Cell waiting area |  | 0 | 13 | 60 | 412 | 21.6 | 45.5 | 474 |  | 2020-09-17 09:10 | 44091.3818 | 21.6 | 45.5 | 474 |  |  | 2020-09-14 | B16187¦Cell waiting area¦¦Sep-17-2020 09:09
2020-09-17 09:10 | 44091.3819 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin waiting area |  | 2 | 15 | 68 | 421 | 21.6 | 46.2 | 485 | No | 2020-09-17 09:10 | 44091.3819 | 21.6 | 46.2 | 485 |  |  | 2020-09-14 | B20151¦Admin waiting area ¦¦Sep-17-2020 09:09
2020-09-17 09:10 | 44091.382 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- N wall |  | 0 | 17 | 73 | 440 | 23 | 52 | 590 |  | 2020-09-17 09:10 | 44091.382 | 23 | 52 | 590 |  |  | 2020-09-14 | B25548¦1- N wall¦¦Sep-17-2020 09:10
2020-09-17 09:10 | 44091.3822 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 2nd floor NE hall |  | 1 | 14.5 | 74.7 | 397 | 21.9 | 50 | 462 |  | 2020-09-17 09:10 | 44091.3822 | 21.9 | 50 | 462 |  |  | 2020-09-14 | B20494¦2nd floor NE hall¦¦Sep-17-2020 09:10
2020-09-17 09:10 | 44091.3822 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Back stairs |  | 1 | 16.6 | 72 | 404 | 21.6 | 58.1 | 467 |  | 2020-09-17 09:10 | 44091.3822 | 21.6 | 58.1 | 467 |  |  | 2020-09-14 | B11228¦Back stairs¦¦Sep-17-2020 09:10
2020-09-17 09:11 | 44091.3823 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Service Ontario |  | 1 | 17.2 | 71.5 | 432 | 22.7 | 52.7 | 451 |  | 2020-09-17 09:11 | 44091.3823 | 22.7 | 52.7 | 451 |  |  | 2020-09-14 | B25039¦Service Ontario¦¦Sep-17-2020 09:10
2020-09-17 09:11 | 44091.3825 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 60 | 412 | 21 | 45.9 | 483 |  | 2020-09-17 09:11 | 44091.3825 | 21 | 45.9 | 483 |  |  | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 09:10
2020-09-17 09:11 | 44091.3829 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Washroom 1st floor |  | 0 | 13 | 60 | 412 | 21.2 | 43.9 | 472 |  | 2020-09-17 09:11 | 44091.3829 | 21.2 | 43.9 | 472 |  |  | 2020-09-14 | B16187¦Washroom 1st floor¦¦Sep-17-2020 09:11
2020-09-17 09:11 | 44091.383 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- N wall |  | 0 | 17 | 73 | 440 | 23 | 52 | 600 |  | 2020-09-17 09:11 | 44091.383 | 23 | 52 | 600 |  |  | 2020-09-14 | B25548¦1- N wall¦¦Sep-17-2020 09:11
2020-09-17 09:12 | 44091.383 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Main entry |  | 3 | 14.5 | 74.7 | 397 | 22.2 | 51.5 | 460 |  | 2020-09-17 09:12 | 44091.383 | 22.2 | 51.5 | 460 |  |  | 2020-09-14 | B20494¦Main entry¦¦Sep-17-2020 09:11
2020-09-17 09:12 | 44091.383 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - back right, facing judge |  | 2 | 16.2 | 60.9 | 385 | 22.3 | 44.5 | 398 |  | 2020-09-17 09:12 | 44091.383 | 22.3 | 44.5 | 398 |  |  | 2020-09-14 | B70277¦Courtroom - back right, facing judge¦¦Sep-17-2020 09:11
2020-09-17 09:12 | 44091.3831 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Lower courtroom lobby |  | 1 | 16.6 | 72 | 404 | 21.6 | 56.3 | 458 |  | 2020-09-17 09:12 | 44091.3831 | 21.6 | 56.3 | 458 |  |  | 2020-09-14 | B11228¦Lower courtroom lobby¦¦Sep-17-2020 09:11
2020-09-17 09:12 | 44091.3832 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 101 |  | 0 | 11 | 72 | 385 | 21.6 | 51.2 | 408 | No | 2020-09-17 09:12 | 44091.3832 | 21.6 | 51.2 | 408 |  |  | 2020-09-14 | B14660¦101¦¦Sep-17-2020 09:11
2020-09-17 09:12 | 44091.3832 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Water fountain |  | 0 | 17.2 | 71.5 | 432 | 22.8 | 52.2 | 494 |  | 2020-09-17 09:12 | 44091.3832 | 22.8 | 52.2 | 494 |  |  | 2020-09-14 | B25039¦Water fountain¦¦Sep-17-2020 09:11
2020-09-17 09:12 | 44091.3833 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Washroom 1st floor |  | 0 | 13 | 60 | 412 | 22 | 43.3 | 461 |  | 2020-09-17 09:12 | 44091.3833 | 22 | 43.3 | 461 |  |  | 2020-09-14 | B16187¦Washroom 1st floor¦¦Sep-17-2020 09:12
2020-09-17 09:13 | 44091.3837 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 60 | 412 | 22 | 43.3 | 459 |  | 2020-09-17 09:12 | 44091.3837 | 22 | 43.3 | 459 |  |  | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 09:12
2020-09-17 09:13 | 44091.3838 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom services office |  | 0 | 15.1 | 71 | 433 | 24.1 | 48.9 | 544 |  | 2020-09-17 09:13 | 44091.3838 | 24.1 | 48.9 | 544 |  |  | 2020-09-14 | B17477¦Courtroom services office¦¦Sep-17-2020 09:12
2020-09-17 09:13 | 44091.384 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Meditation room |  | 0 | 17.2 | 71.5 | 432 | 22.8 | 52.1 | 448 |  | 2020-09-17 09:13 | 44091.384 | 22.8 | 52.1 | 448 |  |  | 2020-09-14 | B25039¦Meditation room ¦¦Sep-17-2020 09:12
2020-09-17 09:13 | 44091.384 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin office |  | 3 | 15 | 68 | 421 | 21.3 | 49.8 | 560 | No | 2020-09-17 09:13 | 44091.384 | 21.3 | 49.8 | 560 |  |  | 2020-09-14 | B20151¦Admin office ¦¦Sep-17-2020 09:13
2020-09-17 09:13 | 44091.384 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - back left, facing judge |  | 2 | 16.2 | 60.9 | 385 | 22.2 | 44.8 | 397 |  | 2020-09-17 09:13 | 44091.384 | 22.2 | 44.8 | 397 |  |  | 2020-09-14 | B70277¦Courtroom - back left, facing judge¦¦Sep-17-2020 09:13
2020-09-17 09:13 | 44091.3841 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 60 | 412 | 22.5 | 42.3 | 455 |  | 2020-09-17 09:13 | 44091.3841 | 22.5 | 42.3 | 455 |  |  | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 09:13
2020-09-17 09:13 | 44091.3842 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Lower courtroom |  | 1 | 16.6 | 72 | 404 | 21.5 | 54 | 455 |  | 2020-09-17 09:13 | 44091.3842 | 21.5 | 54 | 455 |  |  | 2020-09-14 | B11228¦Lower courtroom¦¦Sep-17-2020 09:13
2020-09-17 09:13 | 44091.3843 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family office common area |  | 2 | 15.2 | 70 | 377 | 22.3 | 49.4 | 462 |  | 2020-09-17 09:13 | 44091.3843 | 22.3 | 49.4 | 462 |  |  | 2020-09-14 | B20494¦Family office common area¦¦Sep-17-2020 09:13
2020-09-17 09:14 | 44091.3845 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Washroom 2nd floor |  | 0 | 13 | 60 | 412 | 21.9 | 42 | 459 |  | 2020-09-17 09:14 | 44091.3845 | 21.9 | 42 | 459 |  |  | 2020-09-14 | B16187¦Washroom 2nd floor¦¦Sep-17-2020 09:13
2020-09-17 09:14 | 44091.3847 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- S wall |  | 0 | 17 | 73 | 440 | 23 | 52 | 590 |  | 2020-09-17 09:14 | 44091.3847 | 23 | 52 | 590 |  |  | 2020-09-14 | B25548¦2- S wall¦¦Sep-17-2020 09:14
2020-09-17 09:14 | 44091.3849 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Rear hall |  | 0 | 17.2 | 71.5 | 432 | 22.9 | 52 | 494 |  | 2020-09-17 09:14 | 44091.3849 | 22.9 | 52 | 494 |  |  | 2020-09-14 | B25039¦Rear hall¦¦Sep-17-2020 09:14
2020-09-17 09:14 | 44091.3849 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Washroom 2nd floor |  | 0 | 13 | 60 | 412 | 22 | 43.2 | 458 |  | 2020-09-17 09:14 | 44091.3849 | 22 | 43.2 | 458 |  |  | 2020-09-14 | B16187¦Washroom 2nd floor¦¦Sep-17-2020 09:14
2020-09-17 09:14 | 44091.385 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Front entrance hallway |  | 7 | 19 | 61.3 | 407 | 23.1 | 48.4 | 441 | No | 2020-09-17 09:14 | 44091.385 | 23.1 | 48.4 | 441 |  |  | 2020-09-14 | B21128¦Front entrance hallway ¦¦Sep-17-2020 09:14
2020-09-17 09:15 | 44091.3851 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Office lobby |  | 1 | 16.6 | 72 | 404 | 22.8 | 53 | 461 |  | 2020-09-17 09:15 | 44091.3851 | 22.8 | 53 | 461 |  |  | 2020-09-14 | B11228¦Office lobby¦¦Sep-17-2020 09:14
2020-09-17 09:15 | 44091.3852 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 60 | 412 | 21.4 | 44 | 455 |  | 2020-09-17 09:15 | 44091.3852 | 21.4 | 44 | 455 |  |  | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 09:14
2020-09-17 09:15 | 44091.3852 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Interview Room 1 |  | 1 | 14.5 | 74.7 | 397 | 22.4 | 50 | 487 |  | 2020-09-17 09:15 | 44091.3852 | 22.4 | 50 | 487 |  |  | 2020-09-14 | B20494¦Interview Room 1¦¦Sep-17-2020 09:14
2020-09-17 09:15 | 44091.3855 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Entryway |  | 2 | 15.8 | 82.9 | 409 | 19.2 | 68.5 | 532 |  | 2020-09-17 09:15 | 44091.3855 | 19.2 | 68.5 | 532 |  | high | 2020-09-14 | B20390¦Entryway¦¦Sep-17-2020 09:15
2020-09-17 09:15 | 44091.3855 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | East office second floor |  | 3 | 15.2 | 70 | 377 | 22.5 | 49.8 | 455 |  | 2020-09-17 09:15 | 44091.3855 | 22.5 | 49.8 | 455 |  |  | 2020-09-14 | B20494¦East office second floor ¦¦Sep-17-2020 09:15
2020-09-17 09:15 | 44091.3856 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - middle left, facing judge |  | 2 | 16.2 | 60.9 | 385 | 22.1 | 44.7 | 390 |  | 2020-09-17 09:15 | 44091.3856 | 22.1 | 44.7 | 390 |  |  | 2020-09-14 | B70277¦Courtroom - middle left, facing judge¦¦Sep-17-2020 09:15
2020-09-17 09:16 | 44091.3859 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Handicapped washroom |  | 0 | 17.2 | 71.5 | 432 | 22.8 | 51.9 | 438 |  | 2020-09-17 09:16 | 44091.3859 | 22.8 | 51.9 | 438 |  |  | 2020-09-14 | B25039¦Handicapped washroom¦¦Sep-17-2020 09:15
2020-09-17 09:16 | 44091.386 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- S wall |  | 0 | 17 | 73 | 440 | 23 | 53 | 610 |  | 2020-09-17 09:16 | 44091.386 | 23 | 53 | 610 |  |  | 2020-09-14 | B25548¦2- S wall¦¦Sep-17-2020 09:15
2020-09-17 09:16 | 44091.3864 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin Supervisor |  | 0 | 15 | 68 | 421 | 21.5 | 49 | 563 | No | 2020-09-17 09:16 | 44091.3864 | 21.5 | 49 | 563 |  |  | 2020-09-14 | B20151¦Admin Supervisor ¦¦Sep-17-2020 09:16
2020-09-17 09:17 | 44091.3866 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Office |  | 2 | 16.6 | 72 | 404 | 23.2 | 52.2 | 483 |  | 2020-09-17 09:17 | 44091.3866 | 23.2 | 52.2 | 483 |  |  | 2020-09-14 | B11228¦Office¦¦Sep-17-2020 09:16
2020-09-17 09:17 | 44091.3866 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 134 |  | 0 | 11 | 72 | 385 | 21.4 | 46.3 | 415 | No | 2020-09-17 09:17 | 44091.3866 | 21.4 | 46.3 | 415 |  |  | 2020-09-14 | B14660¦134¦¦Sep-17-2020 09:16
2020-09-17 09:17 | 44091.3868 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - middle right, facing judge |  | 2 | 16.2 | 60.9 | 385 | 22.1 | 44.7 | 388 |  | 2020-09-17 09:17 | 44091.3868 | 22.1 | 44.7 | 388 |  |  | 2020-09-14 | B70277¦Courtroom - middle right, facing judge¦¦Sep-17-2020 09:17
2020-09-17 09:17 | 44091.3869 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Fire extinguisher |  | 0 | 17.2 | 71.5 | 432 | 22.9 | 51.6 | 445 |  | 2020-09-17 09:17 | 44091.3869 | 22.9 | 51.6 | 445 |  |  | 2020-09-14 | B25039¦Fire extinguisher¦¦Sep-17-2020 09:17
2020-09-17 09:17 | 44091.3869 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main floor waiting area |  | 6 | 15.8 | 82.9 | 409 | 20 | 63.2 | 522 |  | 2020-09-17 09:17 | 44091.3869 | 20 | 63.2 | 522 |  | caution | 2020-09-14 | B20390¦Main floor waiting area ¦¦Sep-17-2020 09:17
2020-09-17 09:17 | 44091.3871 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- S wall |  | 0 | 17 | 73 | 440 | 23 | 52 | 580 |  | 2020-09-17 09:17 | 44091.3871 | 23 | 52 | 580 |  |  | 2020-09-14 | B25548¦2- S wall¦¦Sep-17-2020 09:17
2020-09-17 09:18 | 44091.3873 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Second floor landing |  | 1 | 15.2 | 70 | 377 | 21.7 | 52 | 470 |  | 2020-09-17 09:18 | 44091.3873 | 21.7 | 52 | 470 |  |  | 2020-09-14 | B20494¦Second floor landing¦¦Sep-17-2020 09:17
2020-09-17 09:18 | 44091.3875 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Administration office east |  | 2 | 17 | 63 | 433 | 20 | 53 | 515 |  | 2020-09-17 09:18 | 44091.3875 | 20 | 53 | 515 |  |  | 2020-09-14 | B25479¦Administration office east ¦¦Sep-17-2020 09:17
2020-09-17 09:18 | 44091.3876 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Interview room 2 |  | 1 | 14.5 | 74.7 | 397 | 22.5 | 49.8 | 478 |  | 2020-09-17 09:18 | 44091.3876 | 22.5 | 49.8 | 478 |  |  | 2020-09-14 | B20494¦Interview room 2¦¦Sep-17-2020 09:18
2020-09-17 09:18 | 44091.3877 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Common area |  | 0 | 17.2 | 71.5 | 432 | 22.6 | 52 | 452 |  | 2020-09-17 09:18 | 44091.3877 | 22.6 | 52 | 452 |  |  | 2020-09-14 | B25039¦Common area¦¦Sep-17-2020 09:18
2020-09-17 09:19 | 44091.3881 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Administration office west |  | 0 | 17 | 63 | 433 | 21 | 48 | 557 |  | 2020-09-17 09:19 | 44091.3881 | 21 | 48 | 557 |  |  | 2020-09-14 | B25479¦Administration office west ¦¦Sep-17-2020 09:18
2020-09-17 09:19 | 44091.3881 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin file |  | 1 | 15 | 68 | 421 | 21.5 | 48.4 | 545 | No | 2020-09-17 09:19 | 44091.3881 | 21.5 | 48.4 | 545 |  |  | 2020-09-14 | B20151¦Admin file ¦¦Sep-17-2020 09:18
2020-09-17 09:19 | 44091.3882 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 2 |  | 2 | 15.8 | 82.9 | 409 | 20.4 | 60.8 | 511 |  | 2020-09-17 09:19 | 44091.3882 | 20.4 | 60.8 | 511 |  | caution | 2020-09-14 | B20390¦Outside courtroom 2¦¦Sep-17-2020 09:18
2020-09-17 09:19 | 44091.3884 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - judges desk, left side |  | 2 | 16.2 | 60.9 | 385 | 21.8 | 44.5 | 397 |  | 2020-09-17 09:19 | 44091.3884 | 21.8 | 44.5 | 397 |  |  | 2020-09-14 | B70277¦Courtroom - judges desk, left side¦¦Sep-17-2020 09:19
2020-09-17 09:20 | 44091.3886 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- S wall |  | 0 | 17 | 73 | 440 | 23 | 52 | 610 |  | 2020-09-17 09:20 | 44091.3886 | 23 | 52 | 610 |  |  | 2020-09-14 | B25548¦2- S wall¦¦Sep-17-2020 09:19
2020-09-17 09:20 | 44091.3888 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Intake office |  | 1 | 17 | 63 | 433 | 22 | 49 | 602 |  | 2020-09-17 09:20 | 44091.3888 | 22 | 49 | 602 |  |  | 2020-09-14 | B25479¦Intake office ¦¦Sep-17-2020 09:19
2020-09-17 09:20 | 44091.3888 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 136 |  | 4 | 11 | 72 | 385 | 21.9 | 43.6 | 440 | No | 2020-09-17 09:20 | 44091.3888 | 21.9 | 43.6 | 440 |  |  | 2020-09-14 | B14660¦136¦¦Sep-17-2020 09:19
2020-09-17 09:20 | 44091.389 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | 911 entrance |  | 0 | 17.2 | 71.5 | 432 | 22.9 | 51.7 | 444 |  | 2020-09-17 09:20 | 44091.389 | 22.9 | 51.7 | 444 |  |  | 2020-09-14 | B25039¦911 entrance¦¦Sep-17-2020 09:20
2020-09-17 09:21 | 44091.3893 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Supervisors office |  | 1 | 17 | 63 | 433 | 22 | 47 | 548 |  | 2020-09-17 09:21 | 44091.3893 | 22 | 47 | 548 |  |  | 2020-09-14 | B25479¦Supervisors office ¦¦Sep-17-2020 09:20
2020-09-17 09:21 | 44091.3893 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 5 |  | 1 | 15.2 | 70 | 377 | 21.5 | 49.1 | 410 |  | 2020-09-17 09:21 | 44091.3893 | 21.5 | 49.1 | 410 |  |  | 2020-09-14 | B20494¦Courtroom 5¦¦Sep-17-2020 09:20
2020-09-17 09:21 | 44091.3895 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | N.W hallway |  | 2 | 19 | 61.3 | 407 | 24.3 | 45.4 | 458 | No | 2020-09-17 09:21 | 44091.3895 | 24.3 | 45.4 | 458 |  |  | 2020-09-14 | B21128¦N.W hallway ¦¦Sep-17-2020 09:20
2020-09-17 09:21 | 44091.3895 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - judges desk, right side |  | 2 | 16.2 | 60.9 | 385 | 21.9 | 44.1 | 394 |  | 2020-09-17 09:21 | 44091.3895 | 21.9 | 44.1 | 394 |  |  | 2020-09-14 | B70277¦Courtroom - judges desk, right side¦¦Sep-17-2020 09:20
2020-09-17 09:21 | 44091.3896 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 4 |  | 4 | 14.5 | 74.7 | 397 | 22.7 | 49.8 | 511 |  | 2020-09-17 09:21 | 44091.3896 | 22.7 | 49.8 | 511 |  |  | 2020-09-14 | B20494¦Courtroom 4¦¦Sep-17-2020 09:21
2020-09-17 09:21 | 44091.3898 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Lunchroom |  | 0 | 17 | 63 | 433 | 22 | 46 | 545 |  | 2020-09-17 09:21 | 44091.3898 | 22 | 46 | 545 |  |  | 2020-09-14 | B25479¦Lunchroom ¦¦Sep-17-2020 09:21
2020-09-17 09:21 | 44091.3898 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- S wall |  | 0 | 17 | 73 | 440 | 23 | 53 | 590 |  | 2020-09-17 09:21 | 44091.3898 | 23 | 53 | 590 |  |  | 2020-09-14 | B25548¦2- S wall¦¦Sep-17-2020 09:21
2020-09-17 09:21 | 44091.3899 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Emergency exit |  | 0 | 17.2 | 71.5 | 432 | 22.5 | 52.8 | 432 |  | 2020-09-17 09:21 | 44091.3899 | 22.5 | 52.8 | 432 |  |  | 2020-09-14 | B25039¦Emergency exit¦¦Sep-17-2020 09:21
2020-09-17 09:22 | 44091.3902 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 3 |  | 2 | 15.8 | 82.9 | 409 | 20.8 | 58.4 | 483 |  | 2020-09-17 09:22 | 44091.3902 | 20.8 | 58.4 | 483 |  |  | 2020-09-14 | B20390¦Outside courtroom 3¦¦Sep-17-2020 09:21
2020-09-17 09:22 | 44091.3904 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - witness table |  | 2 | 16.2 | 60.9 | 385 | 22 | 44 | 395 |  | 2020-09-17 09:22 | 44091.3904 | 22 | 44 | 395 |  |  | 2020-09-14 | B70277¦Courtroom - witness table¦¦Sep-17-2020 09:22
2020-09-17 09:22 | 44091.3906 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway ne |  | 1 | 15.2 | 70 | 377 | 22 | 52.1 | 439 |  | 2020-09-17 09:22 | 44091.3906 | 22 | 52.1 | 439 |  |  | 2020-09-14 | B20494¦Third floor hallway ne¦¦Sep-17-2020 09:22
2020-09-17 09:23 | 44091.3907 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 405 |  | 3 | 19 | 61.3 | 407 | 23.5 | 45.2 | 451 | No | 2020-09-17 09:23 | 44091.3907 | 23.5 | 45.2 | 451 |  |  | 2020-09-14 | B21128¦405¦¦Sep-17-2020 09:22
2020-09-17 09:23 | 44091.3908 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 2 |  | 0 | 17 | 63 | 433 | 22 | 41 | 475 | Couldn't get into courtroom 1,3,4 and 5 | 2020-09-17 09:23 | 44091.3908 | 22 | 41 | 475 |  |  | 2020-09-14 | B25479¦Courtroom 2¦¦Sep-17-2020 09:22
2020-09-17 09:23 | 44091.3909 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 17 | 73 | 440 | 23 | 52 | 600 |  | 2020-09-17 09:23 | 44091.3909 | 23 | 52 | 600 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-17-2020 09:22
2020-09-17 09:23 | 44091.391 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 144 |  | 0 | 11 | 72 | 385 | 21.8 | 43.7 | 432 | No | 2020-09-17 09:23 | 44091.391 | 21.8 | 43.7 | 432 |  |  | 2020-09-14 | B14660¦144¦¦Sep-17-2020 09:23
2020-09-17 09:24 | 44091.3914 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Library |  | 0 | 17 | 63 | 433 | 22 | 44 | 487 |  | 2020-09-17 09:24 | 44091.3914 | 22 | 44 | 487 |  |  | 2020-09-14 | B25479¦Library ¦¦Sep-17-2020 09:23
2020-09-17 09:24 | 44091.3918 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | TC office |  | 2 | 27 | 63 | 433 | 22 | 44 | 476 |  | 2020-09-17 09:24 | 44091.3918 | 22 | 44 | 476 |  |  | 2020-09-14 | B25479¦TC office ¦¦Sep-17-2020 09:24
2020-09-17 09:24 | 44091.3918 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 406 |  | 4 | 19 | 61.3 | 407 | 23.6 | 46.1 | 430 | No | 2020-09-17 09:24 | 44091.3918 | 23.6 | 46.1 | 430 |  |  | 2020-09-14 | B21128¦406¦¦Sep-17-2020 09:24
2020-09-17 09:24 | 44091.3918 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom services |  | 0 | 15.1 | 71 | 433 | 24.3 | 47.1 | 539 |  | 2020-09-17 09:24 | 44091.3918 | 24.3 | 47.1 | 539 |  |  | 2020-09-14 | B17477¦Courtroom services ¦¦Sep-17-2020 09:24
2020-09-17 09:24 | 44091.3918 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-W wall |  | 0 | 17 | 73 | 440 | 23 | 51 | 620 |  | 2020-09-17 09:24 | 44091.3918 | 23 | 51 | 620 |  |  | 2020-09-14 | B25548¦2-W wall¦¦Sep-17-2020 09:24
2020-09-17 09:24 | 44091.392 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Court services waiting area |  | 2 | 15.8 | 82.9 | 409 | 21.3 | 58.8 | 525 |  | 2020-09-17 09:24 | 44091.392 | 21.3 | 58.8 | 525 |  |  | 2020-09-14 | B20390¦Court services waiting area¦¦Sep-17-2020 09:24
2020-09-17 09:24 | 44091.392 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway se |  | 1 | 15.2 | 70 | 377 | 24 | 49.5 | 459 |  | 2020-09-17 09:24 | 44091.392 | 24 | 49.5 | 459 |  |  | 2020-09-14 | B20494¦Third floor hallway se¦¦Sep-17-2020 09:24
2020-09-17 09:25 | 44091.3921 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Robing corridor |  | 1 | 13.8 | 71.6 | 478 | 20 | 56.5 | 469 |  | 2020-09-17 09:25 | 44091.3921 | 20 | 56.5 | 469 |  |  | 2020-09-14 | B20474¦Robing corridor¦¦Sep-17-2020 09:24
2020-09-17 09:25 | 44091.3922 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family services |  | 1 | 14.5 | 74.7 | 397 | 23 | 52 | 438 |  | 2020-09-17 09:25 | 44091.3922 | 23 | 52 | 438 |  |  | 2020-09-14 | B20494¦Family services ¦¦Sep-17-2020 09:24
2020-09-17 09:25 | 44091.3923 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | JP lobby |  | 0 | 17 | 63 | 433 | 23 | 46 | 536 |  | 2020-09-17 09:25 | 44091.3923 | 23 | 46 | 536 |  |  | 2020-09-14 | B25479¦JP lobby ¦¦Sep-17-2020 09:24
2020-09-17 09:25 | 44091.3923 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Judges Chamber - front desk |  | 1 | 16.2 | 60.9 | 385 | 22.3 | 44.6 | 395 |  | 2020-09-17 09:25 | 44091.3923 | 22.3 | 44.6 | 395 |  |  | 2020-09-14 | B70277¦Judges Chamber - front desk¦¦Sep-17-2020 09:24
2020-09-17 09:25 | 44091.3926 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 122 |  | 0 | 11 | 72 | 385 | 22.1 | 43.2 | 430 | No | 2020-09-17 09:25 | 44091.3926 | 22.1 | 43.2 | 430 |  |  | 2020-09-14 | B14660¦122¦¦Sep-17-2020 09:25
2020-09-17 09:25 | 44091.3927 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office C |  | 2 | 15 | 70 | 412 | 21 | 52 | 447 |  | 2020-09-17 09:25 | 44091.3927 | 21 | 52 | 447 |  |  | 2020-09-14 | B70235¦Main office C ¦¦Sep-17-2020 09:25
2020-09-17 09:26 | 44091.3928 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | Main lobby |  | 6 | 14.1 | 60.7 | 419 | 18.8 | 57 | 507 | No | 2020-09-17 09:26 | 44091.3928 | 18.8 | 57 | 507 |  |  | 2020-09-14 | B70496¦Main lobby¦¦Sep-17-2020 09:25
2020-09-17 09:26 | 44091.393 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Front Lobby |  | 2 | 16 | 64 | 400 | 20.6 | 55.7 | 446 |  | 2020-09-17 09:26 | 44091.393 | 20.6 | 55.7 | 446 |  |  | 2020-09-14 | B20550¦Front Lobby¦¦Sep-17-2020 09:25
2020-09-17 09:26 | 44091.3932 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Main lobby south |  | 5 | 17 | 63 | 433 | 22 | 43 | 519 |  | 2020-09-17 09:26 | 44091.3932 | 22 | 43 | 519 |  |  | 2020-09-14 | B25479¦Main lobby south ¦¦Sep-17-2020 09:26
2020-09-17 09:26 | 44091.3932 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- W Wall |  | 0 | 17 | 73 | 440 | 23 | 51 | 610 |  | 2020-09-17 09:26 | 44091.3932 | 23 | 51 | 610 |  |  | 2020-09-14 | B25548¦2- W Wall¦¦Sep-17-2020 09:26
2020-09-17 09:26 | 44091.3933 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Judges chamber - behind desk, back door |  | 1 | 16.2 | 60.9 | 385 | 22.5 | 44.3 | 396 |  | 2020-09-17 09:26 | 44091.3933 | 22.5 | 44.3 | 396 |  |  | 2020-09-14 | B70277¦Judges chamber - behind desk, back door¦¦Sep-17-2020 09:26
2020-09-17 09:27 | 44091.3934 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 407 |  | 2 | 19 | 61.3 | 407 | 23.1 | 40.8 | 416 | No | 2020-09-17 09:26 | 44091.3934 | 23.1 | 40.8 | 416 |  |  | 2020-09-14 | B21128¦407¦¦Sep-17-2020 09:26
2020-09-17 09:27 | 44091.3934 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Enforcement/finance waiting area |  | 1 | 15.8 | 82.9 | 409 | 21.7 | 57.5 | 516 |  | 2020-09-17 09:27 | 44091.3934 | 21.7 | 57.5 | 516 |  |  | 2020-09-14 | B20390¦Enforcement/finance waiting area ¦¦Sep-17-2020 09:26
2020-09-17 09:27 | 44091.3936 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Main lobby north |  | 0 | 17 | 63 | 433 | 22 | 43 | 515 |  | 2020-09-17 09:27 | 44091.3936 | 22 | 43 | 515 |  |  | 2020-09-14 | B25479¦Main lobby north ¦¦Sep-17-2020 09:26
2020-09-17 09:27 | 44091.3937 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway nw |  | 1 | 15.2 | 70 | 377 | 23.3 | 48.8 | 431 |  | 2020-09-17 09:27 | 44091.3937 | 23.3 | 48.8 | 431 |  |  | 2020-09-14 | B20494¦Third floor hallway nw¦¦Sep-17-2020 09:26
2020-09-17 09:27 | 44091.3937 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area at mens washroom |  | 1 | 13.8 | 71.6 | 478 | 20.2 | 55.3 | 464 |  | 2020-09-17 09:27 | 44091.3937 | 20.2 | 55.3 | 464 |  |  | 2020-09-14 | B20474¦Basement waiting area at mens washroom¦¦Sep-17-2020 09:26
2020-09-17 09:27 | 44091.3939 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 doors |  | 1 | 15.1 | 71 | 433 | 23.6 | 45.9 | 429 |  | 2020-09-17 09:27 | 44091.3939 | 23.6 | 45.9 | 429 |  |  | 2020-09-14 | B17477¦Courtroom 300 doors ¦¦Sep-17-2020 09:27
2020-09-17 09:28 | 44091.3943 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 105 |  | 0 | 11 | 72 | 385 | 22.1 | 43.3 | 422 | No | 2020-09-17 09:28 | 44091.3943 | 22.1 | 43.3 | 422 |  |  | 2020-09-14 | B14660¦105¦¦Sep-17-2020 09:27
2020-09-17 09:28 | 44091.3944 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation office - desk area |  | 2 | 16.2 | 60.9 | 385 | 22.6 | 43.6 | 401 |  | 2020-09-17 09:28 | 44091.3944 | 22.6 | 43.6 | 401 |  |  | 2020-09-14 | B70277¦Mediation office - desk area¦¦Sep-17-2020 09:27
2020-09-17 09:28 | 44091.3944 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-W wall |  | 0 | 17 | 73 | 440 | 23 | 51 | 610 |  | 2020-09-17 09:28 | 44091.3944 | 23 | 51 | 610 |  |  | 2020-09-14 | B25548¦2-W wall¦¦Sep-17-2020 09:28
2020-09-17 09:28 | 44091.3945 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Fire pump |  | 1 | 14.5 | 74.7 | 397 | 23.1 | 51.2 | 436 |  | 2020-09-17 09:28 | 44091.3945 | 23.1 | 51.2 | 436 |  |  | 2020-09-14 | B20494¦Fire pump¦¦Sep-17-2020 09:28
2020-09-17 09:28 | 44091.3945 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office W |  | 2 | 15 | 70 | 412 | 22 | 49 | 435 |  | 2020-09-17 09:28 | 44091.3945 | 22 | 49 | 435 |  |  | 2020-09-14 | B70235¦Main office W ¦¦Sep-17-2020 09:28
2020-09-17 09:28 | 44091.3947 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 102 |  | 3 | 14.1 | 60.7 | 419 | 21.6 | 46 | 450 | No | 2020-09-17 09:28 | 44091.3947 | 21.6 | 46 | 450 |  |  | 2020-09-14 | B70496¦102¦¦Sep-17-2020 09:28
2020-09-17 09:29 | 44091.3949 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway sw |  | 1 | 15.2 | 70 | 377 | 23.6 | 47.9 | 419 |  | 2020-09-17 09:29 | 44091.3949 | 23.6 | 47.9 | 419 |  |  | 2020-09-14 | B20494¦Third floor hallway sw¦¦Sep-17-2020 09:28
2020-09-17 09:29 | 44091.395 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 106 |  | 0 | 11 | 72 | 385 | 22 | 43.1 | 433 | No | 2020-09-17 09:29 | 44091.395 | 22 | 43.1 | 433 |  |  | 2020-09-14 | B14660¦106¦¦Sep-17-2020 09:28
2020-09-17 09:29 | 44091.395 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 408 |  | 2 | 19 | 61.3 | 407 | 24.4 | 44 | 442 | No | 2020-09-17 09:29 | 44091.395 | 24.4 | 44 | 442 |  |  | 2020-09-14 | B21128¦408¦¦Sep-17-2020 09:28
2020-09-17 09:29 | 44091.395 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Family services waiting area |  | 3 | 15.8 | 82.9 | 409 | 21.7 | 57.8 | 550 |  | 2020-09-17 09:29 | 44091.395 | 21.7 | 57.8 | 550 |  |  | 2020-09-14 | B20390¦Family services waiting area¦¦Sep-17-2020 09:28
2020-09-17 09:29 | 44091.3951 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 bench |  | 1 | 15.1 | 71 | 433 | 23.2 | 46.7 | 423 |  | 2020-09-17 09:29 | 44091.3951 | 23.2 | 46.7 | 423 |  |  | 2020-09-14 | B17477¦Courtroom 300 bench ¦¦Sep-17-2020 09:28
2020-09-17 09:29 | 44091.3951 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Trial office |  | 0 | 15 | 70 | 412 | 22 | 50 | 436 |  | 2020-09-17 09:29 | 44091.3951 | 22 | 50 | 436 |  |  | 2020-09-14 | B70235¦Trial office ¦¦Sep-17-2020 09:28
2020-09-17 09:30 | 44091.3956 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation office - printer area |  | 2 | 16.2 | 60.9 | 385 | 22.7 | 43.6 | 428 |  | 2020-09-17 09:30 | 44091.3956 | 22.7 | 43.6 | 428 |  |  | 2020-09-14 | B70277¦Mediation office - printer area¦¦Sep-17-2020 09:29
2020-09-17 09:30 | 44091.3957 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area courtroom3 |  | 1 | 13.8 | 71.6 | 478 | 20.3 | 53.9 | 465 |  | 2020-09-17 09:30 | 44091.3957 | 20.3 | 53.9 | 465 |  |  | 2020-09-14 | B20474¦Basement waiting area courtroom3¦¦Sep-17-2020 09:29
2020-09-17 09:30 | 44091.3957 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 - judge |  | 2 | 15 | 72 | 367 | 21 | 51 | 412 |  | 2020-09-17 09:30 | 44091.3957 | 21 | 51 | 412 |  |  | 2020-09-14 | B20772¦H15 - judge¦¦Sep-17-2020 09:29
2020-09-17 09:30 | 44091.3957 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- N Wall |  | 0 | 17 | 73 | 440 | 23 | 52 | 640 |  | 2020-09-17 09:30 | 44091.3957 | 23 | 52 | 640 |  |  | 2020-09-14 | B25548¦2- N Wall¦¦Sep-17-2020 09:29
2020-09-17 09:30 | 44091.3958 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Administrative office |  | 1 | 16 | 64 | 400 | 23.5 | 46.1 | 447 |  | 2020-09-17 09:30 | 44091.3958 | 23.5 | 46.1 | 447 |  |  | 2020-09-14 | B20550¦Administrative office¦¦Sep-17-2020 09:29
2020-09-17 09:30 | 44091.3958 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jennifer Munby office |  | 1 | 15 | 70 | 412 |  |  |  | Occupied, no access | 2020-09-17 09:30 | 44091.3958 | [5 empty] | 2020-09-14 | B70235¦Jennifer Munby office ¦¦Sep-17-2020 09:29
2020-09-17 09:30 | 44091.396 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 3 ramp |  | 0 | 15.1 | 71 | 433 | 23.1 | 47.5 | 442 |  | 2020-09-17 09:30 | 44091.396 | 23.1 | 47.5 | 442 |  |  | 2020-09-14 | B17477¦Level 3 ramp ¦¦Sep-17-2020 09:30
2020-09-17 09:30 | 44091.3962 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 111 |  | 0 | 11 | 72 | 385 | 22.6 | 43.2 | 416 | No | 2020-09-17 09:30 | 44091.3962 | 22.6 | 43.2 | 416 |  |  | 2020-09-14 | B14660¦111¦¦Sep-17-2020 09:30
2020-09-17 09:31 | 44091.3963 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 1 |  | 1 | 15.2 | 70 | 377 | 23.4 | 43.1 | 396 |  | 2020-09-17 09:31 | 44091.3963 | 23.4 | 43.1 | 396 |  |  | 2020-09-14 | B20494¦Courtroom 1¦¦Sep-17-2020 09:30
2020-09-17 09:31 | 44091.3964 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 102 |  | 3 | 14.1 | 60.7 | 419 | 21.3 | 46.8 | 452 | No | 2020-09-17 09:31 | 44091.3964 | 21.3 | 46.8 | 452 |  |  | 2020-09-14 | B70496¦102¦¦Sep-17-2020 09:30
2020-09-17 09:31 | 44091.3966 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jason Mariasine office |  | 0 | 15 | 70 | 412 | 22 | 47 | 430 |  | 2020-09-17 09:31 | 44091.3966 | 22 | 47 | 430 |  |  | 2020-09-14 | B70235¦Jason Mariasine office ¦¦Sep-17-2020 09:31
2020-09-17 09:31 | 44091.3967 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 2nd floor hallway |  | 2 | 15 | 68 | 421 | 18.6 | 60.5 | 451 | No | 2020-09-17 09:31 | 44091.3967 | 18.6 | 60.5 | 451 |  | caution | 2020-09-14 | B20489¦2nd floor hallway ¦¦Sep-17-2020 09:31
2020-09-17 09:31 | 44091.3968 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Lunch room/kitchen - counter area |  | 1 | 16.2 | 60.9 | 385 | 23.9 | 41.5 | 411 |  | 2020-09-17 09:31 | 44091.3968 | 23.9 | 41.5 | 411 |  |  | 2020-09-14 | B70277¦Lunch room/kitchen - counter area¦¦Sep-17-2020 09:31
2020-09-17 09:31 | 44091.3968 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 - plaintiff |  | 2 | 15 | 72 | 367 | 21 | 51 | 396 |  | 2020-09-17 09:31 | 44091.3968 | 21 | 51 | 396 |  |  | 2020-09-14 | B20772¦H15 - plaintiff¦¦Sep-17-2020 09:31
2020-09-17 09:32 | 44091.3969 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 414 |  | 2 | 19 | 61.3 | 407 | 23.7 | 45 | 407 | No | 2020-09-17 09:32 | 44091.3969 | 23.7 | 45 | 407 |  |  | 2020-09-14 | B21128¦414¦¦Sep-17-2020 09:31
2020-09-17 09:32 | 44091.3969 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom waiting room |  | 0 | 24.4 | 51.6 | 401 | 21.2 | 52.6 | 803 |  | 2020-09-17 09:32 | 44091.3969 | 21.2 | 52.6 | 803 |  |  | 2020-09-14 | B90631¦Courtroom waiting room ¦¦Sep-17-2020 09:31
2020-09-17 09:32 | 44091.397 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell - first floor |  | 1 | 15.8 | 82.9 | 409 | 21.8 | 53.1 | 421 |  | 2020-09-17 09:32 | 44091.397 | 21.8 | 53.1 | 421 |  |  | 2020-09-14 | B20390¦Main stairwell - first floor¦¦Sep-17-2020 09:31
2020-09-17 09:32 | 44091.3972 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jennifer Broderick office |  | 0 | 15 | 70 | 412 | 22 | 46 | 439 |  | 2020-09-17 09:32 | 44091.3972 | 22 | 46 | 439 |  |  | 2020-09-14 | B70235¦Jennifer Broderick office ¦¦Sep-17-2020 09:31
2020-09-17 09:32 | 44091.3973 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Waiting area small |  | 0 | 16 | 64 | 400 | 23.2 | 45.2 | 436 |  | 2020-09-17 09:32 | 44091.3973 | 23.2 | 45.2 | 436 |  |  | 2020-09-14 | B20550¦Waiting area small¦¦Sep-17-2020 09:32
2020-09-17 09:32 | 44091.3974 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15-defense |  | 2 | 15 | 72 | 367 | 21 | 51 | 402 |  | 2020-09-17 09:32 | 44091.3974 | 21 | 51 | 402 |  |  | 2020-09-14 | B20772¦H15-defense¦¦Sep-17-2020 09:32
2020-09-17 09:32 | 44091.3974 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 17 | 73 | 440 | 23 | 51 | 630 |  | 2020-09-17 09:32 | 44091.3974 | 23 | 51 | 630 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-17-2020 09:32
2020-09-17 09:32 | 44091.3975 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 4 seating area |  | 0 | 15.1 | 71 | 433 | 23.1 | 47.5 | 441 |  | 2020-09-17 09:32 | 44091.3975 | 23.1 | 47.5 | 441 |  |  | 2020-09-14 | B17477¦Level 4 seating area ¦¦Sep-17-2020 09:32
2020-09-17 09:33 | 44091.3977 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Foyers |  | 2 | 13.7 | 69.4 | 419 | 20.7 | 51.7 | 525 |  | 2020-09-17 09:33 | 44091.3977 | 20.7 | 51.7 | 525 |  |  | 2020-09-14 | B20367¦Foyers ¦¦Sep-17-2020 09:32
2020-09-17 09:33 | 44091.3978 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area inside double doors |  | 1 | 13.8 | 71.6 | 478 | 20.2 | 54.6 | 467 |  | 2020-09-17 09:33 | 44091.3978 | 20.2 | 54.6 | 467 |  |  | 2020-09-14 | B20474¦Basement waiting area inside double doors ¦¦Sep-17-2020 09:32
2020-09-17 09:33 | 44091.398 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Robert Beninger office |  | 0 | 15 | 70 | 412 | 22 | 48 | 433 |  | 2020-09-17 09:33 | 44091.398 | 22 | 48 | 433 |  |  | 2020-09-14 | B70235¦Robert Beninger office ¦¦Sep-17-2020 09:33
2020-09-17 09:33 | 44091.3981 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15-rear right |  | 2 | 15 | 72 | 367 | 21 | 51 | 392 |  | 2020-09-17 09:33 | 44091.3981 | 21 | 51 | 392 |  |  | 2020-09-14 | B20772¦H15-rear right ¦¦Sep-17-2020 09:33
2020-09-17 09:33 | 44091.3982 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 101 |  | 4 | 14.1 | 60.7 | 419 | 21.8 | 45.3 | 442 | No | 2020-09-17 09:33 | 44091.3982 | 21.8 | 45.3 | 442 |  |  | 2020-09-14 | B70496¦101¦¦Sep-17-2020 09:33
2020-09-17 09:33 | 44091.3982 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Min stairwell - second floor |  | 1 | 15.8 | 82.9 | 409 | 22 | 52.6 | 418 |  | 2020-09-17 09:33 | 44091.3982 | 22 | 52.6 | 418 |  |  | 2020-09-14 | B20390¦Min stairwell - second floor¦¦Sep-17-2020 09:33
2020-09-17 09:33 | 44091.3982 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Crown attorney waiting area |  | 0 | 15 | 68 | 421 | 20.5 | 58.2 | 528 | No | 2020-09-17 09:33 | 44091.3982 | 20.5 | 58.2 | 528 |  |  | 2020-09-14 | B20489¦Crown attorney waiting area ¦¦Sep-17-2020 09:33
2020-09-17 09:34 | 44091.3983 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 203 |  | 0 | 11 | 72 | 385 | 22.2 | 47.1 | 476 | No | 2020-09-17 09:34 | 44091.3983 | 22.2 | 47.1 | 476 |  |  | 2020-09-14 | B14660¦203¦¦Sep-17-2020 09:33
2020-09-17 09:34 | 44091.3983 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - kitchen entrance |  | 2 | 16.2 | 60.9 | 385 | 23.1 | 42.5 | 417 |  | 2020-09-17 09:34 | 44091.3983 | 23.1 | 42.5 | 417 |  |  | 2020-09-14 | B70277¦Mediation room - kitchen entrance¦¦Sep-17-2020 09:33
2020-09-17 09:34 | 44091.3984 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 4 seating area 2 |  | 0 | 15.1 | 71 | 433 | 23.1 | 46.8 | 436 |  | 2020-09-17 09:34 | 44091.3984 | 23.1 | 46.8 | 436 |  |  | 2020-09-14 | B17477¦Level 4 seating area 2 ¦¦Sep-17-2020 09:33
2020-09-17 09:34 | 44091.3986 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Stuart Konyer office |  | 0 | 15 | 70 | 412 | 22 | 49 | 427 |  | 2020-09-17 09:34 | 44091.3986 | 22 | 49 | 427 |  |  | 2020-09-14 | B70235¦Stuart Konyer office ¦¦Sep-17-2020 09:33
2020-09-17 09:34 | 44091.3988 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 17 | 73 | 440 | 24 | 52 | 670 |  | 2020-09-17 09:34 | 44091.3988 | 24 | 52 | 670 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-17-2020 09:34
2020-09-17 09:35 | 44091.399 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Court operations |  | 0 | 13.7 | 69.4 | 419 | 20.7 | 50.4 | 435 |  | 2020-09-17 09:35 | 44091.399 | 20.7 | 50.4 | 435 |  |  | 2020-09-14 | B20367¦Court operations ¦¦Sep-17-2020 09:34
2020-09-17 09:35 | 44091.399 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Bottom stairs foyer |  | 1 | 13.8 | 71.6 | 478 | 20.1 | 54.9 | 471 |  | 2020-09-17 09:35 | 44091.399 | 20.1 | 54.9 | 471 |  |  | 2020-09-14 | B20474¦Bottom stairs foyer¦¦Sep-17-2020 09:34
2020-09-17 09:35 | 44091.3991 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15-tear left |  | 2 | 15 | 72 | 367 | 21 | 51 | 393 |  | 2020-09-17 09:35 | 44091.3991 | 21 | 51 | 393 |  |  | 2020-09-14 | B20772¦H15-tear left¦¦Sep-17-2020 09:34
2020-09-17 09:35 | 44091.3991 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Second floor waiting area |  | 1 | 15.8 | 82.9 | 409 | 22.3 | 51.1 | 414 |  | 2020-09-17 09:35 | 44091.3991 | 22.3 | 51.1 | 414 |  |  | 2020-09-14 | B20390¦Second floor waiting area¦¦Sep-17-2020 09:34
2020-09-17 09:35 | 44091.3991 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Lunch room |  | 1 | 15 | 70 | 412 | 22 | 49 | 440 |  | 2020-09-17 09:35 | 44091.3991 | 22 | 49 | 440 |  |  | 2020-09-14 | B70235¦Lunch room ¦¦Sep-17-2020 09:34
2020-09-17 09:35 | 44091.3992 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Waiting area big |  | 0 | 16 | 64 | 400 | 23.7 | 45.2 | 443 |  | 2020-09-17 09:35 | 44091.3992 | 23.7 | 45.2 | 443 |  |  | 2020-09-14 | B20550¦Waiting area big¦¦Sep-17-2020 09:34
2020-09-17 09:35 | 44091.3993 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 413 |  | 2 | 19 | 61.3 | 407 | 23.1 | 48.8 | 476 | No | 2020-09-17 09:35 | 44091.3993 | 23.1 | 48.8 | 476 |  |  | 2020-09-14 | B21128¦413¦¦Sep-17-2020 09:35
2020-09-17 09:35 | 44091.3994 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st floor hallway |  | 2 | 14.1 | 60.7 | 419 | 21.8 | 44.6 | 440 | No | 2020-09-17 09:35 | 44091.3994 | 21.8 | 44.6 | 440 |  |  | 2020-09-14 | B70496¦1st floor hallway¦¦Sep-17-2020 09:35
2020-09-17 09:35 | 44091.3995 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Public seating area |  | 0 | 16.5 | 40.7 | 428 | 21.5 | 49.5 | 564 |  | 2020-09-17 09:35 | 44091.3995 | 21.5 | 49.5 | 564 |  |  | 2020-09-14 | B19890¦Public seating area¦¦Sep-17-2020 09:35
2020-09-17 09:35 | 44091.3996 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 seating area |  | 0 | 15.1 | 71 | 433 | 23.1 | 46.6 | 435 |  | 2020-09-17 09:35 | 44091.3996 | 23.1 | 46.6 | 435 |  |  | 2020-09-14 | B17477¦Courtroom 400 seating area ¦¦Sep-17-2020 09:35
2020-09-17 09:35 | 44091.3996 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - centre table |  | 2 | 16.2 | 60.9 | 385 | 23 | 42.5 | 409 |  | 2020-09-17 09:35 | 44091.3996 | 23 | 42.5 | 409 |  |  | 2020-09-14 | B70277¦Mediation room - centre table¦¦Sep-17-2020 09:35
2020-09-17 09:36 | 44091.3998 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court support office |  | 0 | 15 | 70 | 412 | 22 | 48 | 432 |  | 2020-09-17 09:36 | 44091.3998 | 22 | 48 | 432 |  |  | 2020-09-14 | B70235¦Court support office ¦¦Sep-17-2020 09:35
2020-09-17 09:36 | 44091.3998 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Motion office |  | 2 | 15 | 68 | 421 | 20.6 | 54.7 | 459 | No | 2020-09-17 09:36 | 44091.3998 | 20.6 | 54.7 | 459 |  |  | 2020-09-14 | B20489¦Motion office ¦¦Sep-17-2020 09:35
2020-09-17 09:36 | 44091.4 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 1 |  | 0 | 13.7 | 69.4 | 419 | 21.4 | 47.1 | 438 |  | 2020-09-17 09:36 | 44091.4 | 21.4 | 47.1 | 438 |  |  | 2020-09-14 | B20367¦Waiting room 1¦¦Sep-17-2020 09:35
2020-09-17 09:36 | 44091.4002 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 17 | 73 | 440 | 24 | 51 | 620 |  | 2020-09-17 09:36 | 44091.4002 | 24 | 51 | 620 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-17-2020 09:36
2020-09-17 09:36 | 44091.4002 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Main entrance |  | 0 | 16.5 | 40.7 | 428 | 21.8 | 49.5 | 563 |  | 2020-09-17 09:36 | 44091.4002 | 21.8 | 49.5 | 563 |  |  | 2020-09-14 | B19890¦Main entrance ¦¦Sep-17-2020 09:36
2020-09-17 09:36 | 44091.4003 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside museum |  | 1 | 15.8 | 82.9 | 409 | 22.6 | 50.2 | 414 |  | 2020-09-17 09:36 | 44091.4003 | 22.6 | 50.2 | 414 |  |  | 2020-09-14 | B20390¦Outside museum¦¦Sep-17-2020 09:36
2020-09-17 09:36 | 44091.4003 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 1st floor hall by elevator |  | 1 | 14.5 | 74.7 | 397 | 24.3 | 44.9 | 452 |  | 2020-09-17 09:36 | 44091.4003 | 24.3 | 44.9 | 452 |  |  | 2020-09-14 | B20494¦1st floor hall by elevator¦¦Sep-17-2020 09:36
2020-09-17 09:37 | 44091.4004 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Crown staff room |  | 1 | 15 | 70 | 412 | 22 | 49 | 500 |  | 2020-09-17 09:37 | 44091.4004 | 22 | 49 | 500 |  |  | 2020-09-14 | B70235¦Crown staff room ¦¦Sep-17-2020 09:36
2020-09-17 09:37 | 44091.4005 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Security desk |  | 1 | 16 | 64 | 400 | 23.5 | 44.3 | 442 |  | 2020-09-17 09:37 | 44091.4005 | 23.5 | 44.3 | 442 |  |  | 2020-09-14 | B20550¦Security desk¦¦Sep-17-2020 09:36
2020-09-17 09:37 | 44091.4005 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - hallway entrance |  | 2 | 16.2 | 60.9 | 385 | 23.1 | 42.5 | 416 |  | 2020-09-17 09:37 | 44091.4005 | 23.1 | 42.5 | 416 |  |  | 2020-09-14 | B70277¦Mediation room - hallway entrance¦¦Sep-17-2020 09:36
2020-09-17 09:37 | 44091.4005 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | Stairwell |  | 1 | 14.1 | 60.7 | 419 | 22.5 | 45.3 | 524 | No | 2020-09-17 09:37 | 44091.4005 | 22.5 | 45.3 | 524 |  |  | 2020-09-14 | B70496¦Stairwell¦¦Sep-17-2020 09:36
2020-09-17 09:37 | 44091.4005 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Lower landing of stairs |  | 1 | 13.8 | 71.6 | 478 | 20 | 53.8 | 478 |  | 2020-09-17 09:37 | 44091.4005 | 20 | 53.8 | 478 |  |  | 2020-09-14 | B20474¦Lower landing of stairs¦¦Sep-17-2020 09:36
2020-09-17 09:37 | 44091.4009 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Staff area |  | 3 | 16.5 | 40.7 | 428 | 22 | 48.7 | 551 |  | 2020-09-17 09:37 | 44091.4009 | 22 | 48.7 | 551 |  |  | 2020-09-14 | B19890¦Staff area ¦¦Sep-17-2020 09:37
2020-09-17 09:37 | 44091.4009 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judges chamber foyers |  | 0 | 13.7 | 69.4 | 419 | 21.9 | 47.4 | 446 |  | 2020-09-17 09:37 | 44091.4009 | 21.9 | 47.4 | 446 |  |  | 2020-09-14 | B20367¦Judges chamber foyers ¦¦Sep-17-2020 09:37
2020-09-17 09:38 | 44091.4011 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 412 |  | 2 | 19 | 61.3 | 407 | 22.3 | 39.4 | 422 | No | 2020-09-17 09:38 | 44091.4011 | 22.3 | 39.4 | 422 |  | caution | 2020-09-14 | B21128¦412¦¦Sep-17-2020 09:37
2020-09-17 09:38 | 44091.4011 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 seating area 2 |  | 0 | 15.1 | 71 | 433 | 22 | 47 | 430 |  | 2020-09-17 09:38 | 44091.4011 | 22 | 47 | 430 |  |  | 2020-09-14 | B17477¦Courtroom 400 seating area 2 ¦¦Sep-17-2020 09:37
2020-09-17 09:38 | 44091.4011 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 17 | 73 | 440 | 24 | 50 | 670 |  | 2020-09-17 09:38 | 44091.4011 | 24 | 50 | 670 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-17-2020 09:37
2020-09-17 09:38 | 44091.4012 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Peterborough Police office |  | 1 | 15 | 70 | 412 | 22 | 50 | 538 |  | 2020-09-17 09:38 | 44091.4012 | 22 | 50 | 538 |  |  | 2020-09-14 | B70235¦Peterborough Police office ¦¦Sep-17-2020 09:37
2020-09-17 09:38 | 44091.4014 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Museum |  | 1 | 15.8 | 82.9 | 409 | 21.9 | 51.3 | 409 |  | 2020-09-17 09:38 | 44091.4014 | 21.9 | 51.3 | 409 |  |  | 2020-09-14 | B20390¦Museum ¦¦Sep-17-2020 09:37
2020-09-17 09:38 | 44091.4017 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 2nd floor elevator lobby |  | 1 | 14.1 | 60.7 | 419 | 23 | 43.6 | 468 | No | 2020-09-17 09:38 | 44091.4017 | 23 | 43.6 | 468 |  |  | 2020-09-14 | B70496¦2nd floor elevator lobby¦¦Sep-17-2020 09:38
2020-09-17 09:38 | 44091.4017 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judges chamber foyers |  | 0 | 13.7 | 69.4 | 419 | 21.9 | 47.2 | 457 |  | 2020-09-17 09:38 | 44091.4017 | 21.9 | 47.2 | 457 |  |  | 2020-09-14 | B20367¦Judges chamber foyers ¦¦Sep-17-2020 09:38
2020-09-17 09:39 | 44091.4018 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 judge |  | 1 | 15 | 70 | 412 |  |  |  | Occupied, no access | 2020-09-17 09:39 | 44091.4018 | [5 empty] | 2020-09-14 | B70235¦Court #4 judge ¦¦Sep-17-2020 09:38
2020-09-17 09:39 | 44091.4019 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 17 | 73 | 440 | 23 | 51 | 630 |  | 2020-09-17 09:39 | 44091.4019 | 23 | 51 | 630 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-17-2020 09:38
2020-09-17 09:39 | 44091.402 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Crown office |  | 2 | 16.5 | 40.7 | 428 | 22.3 | 47.5 | 504 |  | 2020-09-17 09:39 | 44091.402 | 22.3 | 47.5 | 504 |  |  | 2020-09-14 | B19890¦Crown office¦¦Sep-17-2020 09:38
2020-09-17 09:39 | 44091.4022 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 411 |  | 2 | 19 | 61.3 | 407 | 22.5 | 51.8 | 420 | No | 2020-09-17 09:39 | 44091.4022 | 22.5 | 51.8 | 420 |  |  | 2020-09-14 | B21128¦411¦¦Sep-17-2020 09:39
2020-09-17 09:39 | 44091.4023 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 doors |  | 2 | 15.1 | 71 | 433 | 22.9 | 46.9 | 424 |  | 2020-09-17 09:39 | 44091.4023 | 22.9 | 46.9 | 424 |  |  | 2020-09-14 | B17477¦Courtroom 400 doors ¦¦Sep-17-2020 09:39
2020-09-17 09:39 | 44091.4023 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 lawyer |  | 1 | 15 | 70 | 412 |  |  |  | Occupied, no access | 2020-09-17 09:39 | 44091.4023 | [5 empty] | 2020-09-14 | B70235¦Court #4 lawyer ¦¦Sep-17-2020 09:39
2020-09-17 09:39 | 44091.4023 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Main floor at stairway |  | 1 | 13.8 | 71.6 | 478 | 20.1 | 57.1 | 512 |  | 2020-09-17 09:39 | 44091.4023 | 20.1 | 57.1 | 512 |  |  | 2020-09-14 | B20474¦Main floor at stairway¦¦Sep-17-2020 09:39
2020-09-17 09:40 | 44091.4026 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown Attorney waiting room |  | 1 | 14.5 | 74.7 | 397 | 23.8 | 48.6 | 466 |  | 2020-09-17 09:40 | 44091.4026 | 23.8 | 48.6 | 466 |  |  | 2020-09-14 | B20494¦Crown Attorney waiting room¦¦Sep-17-2020 09:39
2020-09-17 09:40 | 44091.4026 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 6 |  | 1 | 15.8 | 82.9 | 409 | 22.2 | 53.3 | 411 |  | 2020-09-17 09:40 | 44091.4026 | 22.2 | 53.3 | 411 |  |  | 2020-09-14 | B20390¦Outside courtroom 6¦¦Sep-17-2020 09:39
2020-09-17 09:40 | 44091.4026 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Crown attorney office |  | 2 | 15 | 68 | 421 | 21.2 | 51.8 | 484 | No | 2020-09-17 09:40 | 44091.4026 | 21.2 | 51.8 | 484 |  |  | 2020-09-14 | B20489¦Crown attorney office ¦¦Sep-17-2020 09:39
2020-09-17 09:40 | 44091.4027 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-E wall |  | 0 | 17 | 73 | 440 | 23 | 51 | 610 |  | 2020-09-17 09:40 | 44091.4027 | 23 | 51 | 610 |  |  | 2020-09-14 | B25548¦2-E wall¦¦Sep-17-2020 09:39
2020-09-17 09:40 | 44091.4028 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Duty council office - desk area |  | 2 | 16.2 | 60.9 | 385 | 23.1 | 41.8 | 398 |  | 2020-09-17 09:40 | 44091.4028 | 23.1 | 41.8 | 398 |  |  | 2020-09-14 | B70277¦Duty council office - desk area¦¦Sep-17-2020 09:40
2020-09-17 09:40 | 44091.4029 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 2 |  | 0 | 13.7 | 69.4 | 419 | 21.5 | 46.4 | 462 |  | 2020-09-17 09:40 | 44091.4029 | 21.5 | 46.4 | 462 |  |  | 2020-09-14 | B20367¦Waiting room 2¦¦Sep-17-2020 09:40
2020-09-17 09:41 | 44091.4032 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 vestibule |  | 0 | 15 | 70 | 412 | 22 | 48 | 468 |  | 2020-09-17 09:41 | 44091.4032 | 22 | 48 | 468 |  |  | 2020-09-14 | B70235¦Court #4 vestibule ¦¦Sep-17-2020 09:40
2020-09-17 09:41 | 44091.4032 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Public seating area 2 |  | 0 | 16.5 | 40.7 | 428 | 22.1 | 47.5 | 537 |  | 2020-09-17 09:41 | 44091.4032 | 22.1 | 47.5 | 537 |  |  | 2020-09-14 | B19890¦Public seating area 2¦¦Sep-17-2020 09:40
2020-09-17 09:41 | 44091.4035 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 410 |  | 2 | 19 | 61.3 | 407 | 23.1 | 46.7 | 428 | No | 2020-09-17 09:41 | 44091.4035 | 23.1 | 46.7 | 428 |  |  | 2020-09-14 | B21128¦410¦¦Sep-17-2020 09:40
2020-09-17 09:41 | 44091.4037 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Duty council office - back right |  | 2 | 16.2 | 60.9 | 385 | 23.1 | 41.5 | 396 |  | 2020-09-17 09:41 | 44091.4037 | 23.1 | 41.5 | 396 |  |  | 2020-09-14 | B70277¦Duty council office - back right¦¦Sep-17-2020 09:41
2020-09-17 09:41 | 44091.4037 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 bench |  | 2 | 15.1 | 71 | 433 | 22.3 | 47.7 | 422 |  | 2020-09-17 09:41 | 44091.4037 | 22.3 | 47.7 | 422 |  |  | 2020-09-14 | B17477¦Courtroom 400 bench ¦¦Sep-17-2020 09:41
2020-09-17 09:41 | 44091.4037 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 204 |  | 1 | 14.1 | 60.7 | 419 | 22.1 | 41.7 | 417 | No | 2020-09-17 09:41 | 44091.4037 | 22.1 | 41.7 | 417 |  |  | 2020-09-14 | B70496¦204¦¦Sep-17-2020 09:41
2020-09-17 09:41 | 44091.4037 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Jury room waiting area |  | 3 | 15.8 | 82.9 | 409 | 22.5 | 50.6 | 409 |  | 2020-09-17 09:41 | 44091.4037 | 22.5 | 50.6 | 409 |  |  | 2020-09-14 | B20390¦Jury room waiting area¦¦Sep-17-2020 09:41
2020-09-17 09:42 | 44091.4039 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom4 corridor |  | 1 | 13.8 | 71.6 | 478 | 19.8 | 57.6 | 484 |  | 2020-09-17 09:42 | 44091.4039 | 19.8 | 57.6 | 484 |  |  | 2020-09-14 | B20474¦Courtroom4 corridor¦¦Sep-17-2020 09:41
2020-09-17 09:42 | 44091.4039 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview room #4 |  | 0 | 15 | 70 | 412 | 22 | 48 | 464 |  | 2020-09-17 09:42 | 44091.4039 | 22 | 48 | 464 |  |  | 2020-09-14 | B70235¦Interview room #4 ¦¦Sep-17-2020 09:41
2020-09-17 09:42 | 44091.4039 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-E wall |  | 0 | 17 | 73 | 440 | 24 | 51 | 610 |  | 2020-09-17 09:42 | 44091.4039 | 24 | 51 | 610 |  |  | 2020-09-14 | B25548¦2-E wall¦¦Sep-17-2020 09:41
2020-09-17 09:42 | 44091.4041 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12- rear right |  | 2 | 15 | 72 | 367 | 23 | 43 | 396 |  | 2020-09-17 09:42 | 44091.4041 | 23 | 43 | 396 |  |  | 2020-09-14 | B20772¦H12- rear right ¦¦Sep-17-2020 09:41
2020-09-17 09:42 | 44091.4042 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Courtroom 2 |  | 0 | 16.5 | 40.7 | 428 | 22.2 | 47.3 | 478 |  | 2020-09-17 09:42 | 44091.4042 | 22.2 | 47.3 | 478 |  |  | 2020-09-14 | B19890¦Courtroom 2¦¦Sep-17-2020 09:42
2020-09-17 09:42 | 44091.4043 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 2 |  | 0 | 13.7 | 69.4 | 419 | 21.3 | 47.4 | 450 |  | 2020-09-17 09:42 | 44091.4043 | 21.3 | 47.4 | 450 |  |  | 2020-09-14 | B20367¦Courtroom 2¦¦Sep-17-2020 09:42
2020-09-17 09:42 | 44091.4043 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 409 |  | 2 | 19 | 61.3 | 407 | 23.1 | 47.5 | 414 | No | 2020-09-17 09:42 | 44091.4043 | 23.1 | 47.5 | 414 |  |  | 2020-09-14 | B21128¦409¦¦Sep-17-2020 09:42
2020-09-17 09:42 | 44091.4044 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 11 |  | 2 | 19 | 57 | 420 | 21.6 | 50 | 430 |  | 2020-09-17 09:42 | 44091.4044 | 21.6 | 50 | 430 |  |  | 2020-09-14 | B70740¦11¦¦Sep-17-2020 09:42
2020-09-17 09:43 | 44091.4045 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 judge |  | 0 | 15 | 70 | 412 | 22 | 44 | 432 |  | 2020-09-17 09:43 | 44091.4045 | 22 | 44 | 432 |  |  | 2020-09-14 | B70235¦Court #3 judge ¦¦Sep-17-2020 09:42
2020-09-17 09:43 | 44091.4045 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom D |  | 0 | 14.8 | 72.1 | 408 | 19.1 | 62.6 | 436 | No | 2020-09-17 09:43 | 44091.4045 | 19.1 | 62.6 | 436 |  | caution | 2020-09-14 | B20478¦Courtroom D¦¦Sep-17-2020 09:42
2020-09-17 09:43 | 44091.4045 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 3rd floor hallway |  | 0 | 15 | 68 | 421 | 21.6 | 51.1 | 450 | No | 2020-09-17 09:43 | 44091.4045 | 21.6 | 51.1 | 450 |  |  | 2020-09-14 | B20489¦3rd floor hallway ¦¦Sep-17-2020 09:42
2020-09-17 09:43 | 44091.4047 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 204 |  | 1 | 14.1 | 60.7 | 419 | 21.4 | 43.3 | 417 | No | 2020-09-17 09:43 | 44091.4047 | 21.4 | 43.3 | 417 |  |  | 2020-09-14 | B70496¦204¦¦Sep-17-2020 09:42
2020-09-17 09:43 | 44091.4047 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Back stairwell- second floor |  | 1 | 15.8 | 82.9 | 409 | 22.1 | 51 | 405 |  | 2020-09-17 09:43 | 44091.4047 | 22.1 | 51 | 405 |  |  | 2020-09-14 | B20390¦Back stairwell- second floor¦¦Sep-17-2020 09:42
2020-09-17 09:43 | 44091.4049 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 -rear left |  | 2 | 15 | 72 | 367 | 23 | 43 | 397 |  | 2020-09-17 09:43 | 44091.4049 | 23 | 43 | 397 |  |  | 2020-09-14 | B20772¦H12 -rear left ¦¦Sep-17-2020 09:43
2020-09-17 09:43 | 44091.405 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-E wall |  | 0 | 17 | 73 | 440 | 24 | 52 | 610 |  | 2020-09-17 09:43 | 44091.405 | 24 | 52 | 610 |  |  | 2020-09-14 | B25548¦2-E wall¦¦Sep-17-2020 09:43
2020-09-17 09:43 | 44091.405 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown Attorney printer room |  | 1 | 14.5 | 74.7 | 397 | 23.6 | 52 | 469 |  | 2020-09-17 09:43 | 44091.405 | 23.6 | 52 | 469 |  |  | 2020-09-14 | B20494¦Crown Attorney printer room¦¦Sep-17-2020 09:43
2020-09-17 09:43 | 44091.4051 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 403 |  | 2 | 19 | 61.3 | 407 | 23.1 | 47 | 430 | No | 2020-09-17 09:43 | 44091.4051 | 23.1 | 47 | 430 |  |  | 2020-09-14 | B21128¦403¦¦Sep-17-2020 09:43
2020-09-17 09:44 | 44091.4052 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office a |  | 0 | 13.7 | 69.4 | 419 | 21.2 | 45.3 | 452 |  | 2020-09-17 09:44 | 44091.4052 | 21.2 | 45.3 | 452 |  |  | 2020-09-14 | B20367¦Office a¦¦Sep-17-2020 09:43
2020-09-17 09:44 | 44091.4052 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Stairwells |  | 0 | 16.5 | 40.7 | 428 | 21.9 | 47.6 | 510 |  | 2020-09-17 09:44 | 44091.4052 | 21.9 | 47.6 | 510 |  |  | 2020-09-14 | B19890¦Stairwells ¦¦Sep-17-2020 09:43
2020-09-17 09:44 | 44091.4053 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 4 interview room |  | 0 | 15.1 | 71 | 433 | 22.6 | 48.1 | 430 |  | 2020-09-17 09:44 | 44091.4053 | 22.6 | 48.1 | 430 |  |  | 2020-09-14 | B17477¦Level 4 interview room ¦¦Sep-17-2020 09:43
2020-09-17 09:44 | 44091.4053 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 lawyer |  | 0 | 15 | 70 | 412 | 22 | 43 | 430 |  | 2020-09-17 09:44 | 44091.4053 | 22 | 43 | 430 |  |  | 2020-09-14 | B70235¦Court #3 lawyer ¦¦Sep-17-2020 09:43
2020-09-17 09:44 | 44091.4054 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside of door 302 |  | 1 | 16.2 | 60.9 | 385 | 22.5 | 41.8 | 412 |  | 2020-09-17 09:44 | 44091.4054 | 22.5 | 41.8 | 412 |  |  | 2020-09-14 | B70277¦Hallway - outside of door 302¦¦Sep-17-2020 09:43
2020-09-17 09:44 | 44091.4057 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12- middle left |  | 2 | 15 | 72 | 367 | 23 | 43 | 400 |  | 2020-09-17 09:44 | 44091.4057 | 23 | 43 | 400 |  |  | 2020-09-14 | B20772¦H12- middle left ¦¦Sep-17-2020 09:44
2020-09-17 09:44 | 44091.4058 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Between washrooms, second floor |  | 1 | 15.8 | 82.9 | 409 | 22.3 | 52.6 | 407 |  | 2020-09-17 09:44 | 44091.4058 | 22.3 | 52.6 | 407 |  |  | 2020-09-14 | B20390¦Between washrooms, second floor¦¦Sep-17-2020 09:44
2020-09-17 09:44 | 44091.4059 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Main hallway |  | 0 | 16.5 | 40.7 | 428 | 22 | 48.6 | 565 |  | 2020-09-17 09:44 | 44091.4059 | 22 | 48.6 | 565 |  |  | 2020-09-14 | B19890¦Main hallway ¦¦Sep-17-2020 09:44
2020-09-17 09:45 | 44091.4059 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 vestibule |  | 0 | 15 | 70 | 412 | 21 | 47 | 431 |  | 2020-09-17 09:45 | 44091.4059 | 21 | 47 | 431 |  |  | 2020-09-14 | B70235¦Court #3 vestibule ¦¦Sep-17-2020 09:44
2020-09-17 09:45 | 44091.406 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office b |  | 0 | 13.7 | 69.4 | 419 | 21.5 | 46.4 | 443 |  | 2020-09-17 09:45 | 44091.406 | 21.5 | 46.4 | 443 |  |  | 2020-09-14 | B20367¦Office b ¦¦Sep-17-2020 09:44
2020-09-17 09:45 | 44091.406 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Jury room |  | 0 | 15 | 68 | 421 | 22 | 50 | 445 | No | 2020-09-17 09:45 | 44091.406 | 22 | 50 | 445 |  |  | 2020-09-14 | B20489¦Jury room ¦¦Sep-17-2020 09:44
2020-09-17 09:45 | 44091.4061 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 400 |  | 3 | 19 | 61.3 | 407 | 23.3 | 45.1 | 484 | No | 2020-09-17 09:45 | 44091.4061 | 23.3 | 45.1 | 484 |  |  | 2020-09-14 | B21128¦400¦¦Sep-17-2020 09:44
2020-09-17 09:45 | 44091.4062 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 2nd floor hallway |  | 1 | 14.1 | 60.7 | 419 | 21.8 | 44.1 | 442 | No | 2020-09-17 09:45 | 44091.4062 | 21.8 | 44.1 | 442 |  |  | 2020-09-14 | B70496¦2nd floor hallway¦¦Sep-17-2020 09:44
2020-09-17 09:45 | 44091.4064 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | Mediation room |  | 0 | 17 | 73 | 440 | 23 | 51 | 650 |  | 2020-09-17 09:45 | 44091.4064 | 23 | 51 | 650 |  |  | 2020-09-14 | B25548¦Mediation room¦¦Sep-17-2020 09:45
2020-09-17 09:45 | 44091.4064 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom2 2nd door |  | 1 | 13.8 | 71.6 | 478 | 19.9 | 55 | 462 |  | 2020-09-17 09:45 | 44091.4064 | 19.9 | 55 | 462 |  |  | 2020-09-14 | B20474¦Waiting area courtroom2 2nd door¦¦Sep-17-2020 09:45
2020-09-17 09:45 | 44091.4065 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 213 |  | 0 | 11 | 72 | 385 | 23 | 42.6 | 416 | No | 2020-09-17 09:45 | 44091.4065 | 23 | 42.6 | 416 |  |  | 2020-09-14 | B14660¦213¦¦Sep-17-2020 09:45
2020-09-17 09:45 | 44091.4065 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom B |  | 0 | 14.8 | 72.1 | 408 | 19.1 | 60 | 440 | No | 2020-09-17 09:45 | 44091.4065 | 19.1 | 60 | 440 |  | caution | 2020-09-14 | B20478¦Courtroom B¦¦Sep-17-2020 09:45
2020-09-17 09:45 | 44091.4065 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12-middle right |  | 2 | 15 | 72 | 367 | 23 | 43 | 401 |  | 2020-09-17 09:45 | 44091.4065 | 23 | 43 | 401 |  |  | 2020-09-14 | B20772¦H12-middle right ¦¦Sep-17-2020 09:45
2020-09-17 09:45 | 44091.4065 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 4 ramp |  | 0 | 15.1 | 71 | 433 | 22.7 | 48.5 | 440 |  | 2020-09-17 09:45 | 44091.4065 | 22.7 | 48.5 | 440 |  |  | 2020-09-14 | B17477¦Level 4 ramp ¦¦Sep-17-2020 09:45
2020-09-17 09:45 | 44091.4065 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview Room #3 |  | 1 | 15 | 70 | 412 |  |  |  | Occupied, no access | 2020-09-17 09:45 | 44091.4065 | [5 empty] | 2020-09-14 | B70235¦Interview Room #3¦¦Sep-17-2020 09:45
2020-09-17 09:45 | 44091.4066 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside duty council office |  | 1 | 16.2 | 60.9 | 385 | 22.5 | 41.1 | 402 |  | 2020-09-17 09:45 | 44091.4066 | 22.5 | 41.1 | 402 |  |  | 2020-09-14 | B70277¦Hallway - outside duty council office¦¦Sep-17-2020 09:45
2020-09-17 09:46 | 44091.4069 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office c |  | 0 | 13.7 | 69.4 | 419 | 21.7 | 46.2 | 433 |  | 2020-09-17 09:46 | 44091.4069 | 21.7 | 46.2 | 433 |  |  | 2020-09-14 | B20367¦Office c¦¦Sep-17-2020 09:45
2020-09-17 09:46 | 44091.4069 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Front lobby |  | 2 | 16.5 | 40.7 | 428 | 21.8 | 21.9 | 635 |  | 2020-09-17 09:46 | 44091.4069 | 21.8 | 21.9 | 635 |  | low | 2020-09-14 | B19890¦Front lobby¦¦Sep-17-2020 09:46
2020-09-17 09:46 | 44091.407 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12-judge |  | 2 | 15 | 72 | 367 | 23 | 43 | 425 |  | 2020-09-17 09:46 | 44091.407 | 23 | 43 | 425 |  |  | 2020-09-14 | B20772¦H12-judge ¦¦Sep-17-2020 09:46
2020-09-17 09:46 | 44091.407 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney office |  | 2 | 14.5 | 74.7 | 397 | 23.5 | 51.2 | 484 |  | 2020-09-17 09:46 | 44091.407 | 23.5 | 51.2 | 484 |  |  | 2020-09-14 | B20494¦Crown attorney office¦¦Sep-17-2020 09:46
2020-09-17 09:46 | 44091.4071 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Crown attorney waiting area |  | 1 | 15.8 | 82.9 | 409 | 22.6 | 47.8 | 406 |  | 2020-09-17 09:46 | 44091.4071 | 22.6 | 47.8 | 406 |  |  | 2020-09-14 | B20390¦Crown attorney waiting area¦¦Sep-17-2020 09:46
2020-09-17 09:46 | 44091.4071 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 judge |  | 1 | 15 | 70 | 412 |  |  |  | Occupied, no access | 2020-09-17 09:46 | 44091.4071 | [5 empty] | 2020-09-14 | B70235¦Court #2 judge ¦¦Sep-17-2020 09:46
2020-09-17 09:46 | 44091.4073 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 401 |  | 7 | 19 | 61.3 | 407 | 22.7 | 43.4 | 447 | No | 2020-09-17 09:46 | 44091.4073 | 22.7 | 43.4 | 447 |  |  | 2020-09-14 | B21128¦401¦¦Sep-17-2020 09:46
2020-09-17 09:47 | 44091.4074 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 seating area |  | 0 | 15.1 | 71 | 440 | 22.6 | 48.2 | 441 |  | 2020-09-17 09:47 | 44091.4074 | 22.6 | 48.2 | 441 |  |  | 2020-09-14 | B17477¦Level 5 seating area ¦¦Sep-17-2020 09:46
2020-09-17 09:47 | 44091.4074 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - elevator lobby |  | 1 | 16.2 | 60.9 | 385 | 22.5 | 40.1 | 404 |  | 2020-09-17 09:47 | 44091.4074 | 22.5 | 40.1 | 404 |  |  | 2020-09-14 | B70277¦Hallway - elevator lobby¦¦Sep-17-2020 09:46
2020-09-17 09:47 | 44091.4076 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 203 |  | 1 | 14.1 | 60.7 | 419 | 21.2 | 45.6 | 453 | No | 2020-09-17 09:47 | 44091.4076 | 21.2 | 45.6 | 453 |  |  | 2020-09-14 | B70496¦203¦¦Sep-17-2020 09:47
2020-09-17 09:47 | 44091.4077 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 lawyer |  | 1 | 15 | 70 | 412 |  |  |  | Occupied, no access | 2020-09-17 09:47 | 44091.4077 | [5 empty] | 2020-09-14 | B70235¦Court #2 lawyer ¦¦Sep-17-2020 09:47
2020-09-17 09:47 | 44091.4077 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Private room |  | 0 | 15 | 68 | 421 | 22.1 | 49.2 | 430 | No | 2020-09-17 09:47 | 44091.4077 | 22.1 | 49.2 | 430 |  |  | 2020-09-14 | B20489¦Private room ¦¦Sep-17-2020 09:47
2020-09-17 09:47 | 44091.4078 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Courtroom 1 |  | 5 | 16.5 | 40.7 | 428 | 23.2 | 51.1 | 573 |  | 2020-09-17 09:47 | 44091.4078 | 23.2 | 51.1 | 573 |  |  | 2020-09-14 | B19890¦Courtroom 1¦¦Sep-17-2020 09:47
2020-09-17 09:47 | 44091.4078 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 209 |  | 0 | 11 | 72 | 385 | 22.7 | 46.7 | 424 | No | 2020-09-17 09:47 | 44091.4078 | 22.7 | 46.7 | 424 |  |  | 2020-09-14 | B14660¦209¦¦Sep-17-2020 09:47
2020-09-17 09:47 | 44091.4079 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 3 |  | 0 | 13.7 | 69.4 | 419 | 21.7 | 43.7 | 438 |  | 2020-09-17 09:47 | 44091.4079 | 21.7 | 43.7 | 438 |  |  | 2020-09-14 | B20367¦Courtroom 3¦¦Sep-17-2020 09:47
2020-09-17 09:48 | 44091.408 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom2 1st door |  | 1 | 13.8 | 71.6 | 478 | 19.8 | 54.6 | 467 |  | 2020-09-17 09:48 | 44091.408 | 19.8 | 54.6 | 467 |  |  | 2020-09-14 | B20474¦Waiting area courtroom2 1st door¦¦Sep-17-2020 09:47
2020-09-17 09:48 | 44091.4081 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Crown attorneys reception area |  | 1 | 15.8 | 82.9 | 409 | 22.3 | 49.6 | 403 |  | 2020-09-17 09:48 | 44091.4081 | 22.3 | 49.6 | 403 |  |  | 2020-09-14 | B20390¦Crown attorneys reception area¦¦Sep-17-2020 09:47
2020-09-17 09:48 | 44091.4082 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 402 |  | 2 | 19 | 61.3 | 407 | 22.5 | 46.4 | 462 | No | 2020-09-17 09:48 | 44091.4082 | 22.5 | 46.4 | 462 |  |  | 2020-09-14 | B21128¦402¦¦Sep-17-2020 09:47
2020-09-17 09:48 | 44091.4083 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 vestibule |  | 0 | 15 | 70 | 412 | 23 | 47 | 505 |  | 2020-09-17 09:48 | 44091.4083 | 23 | 47 | 505 |  |  | 2020-09-14 | B70235¦Court #2 vestibule ¦¦Sep-17-2020 09:48
2020-09-17 09:48 | 44091.4084 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | 3rd floor stairwell |  | 1 | 16.2 | 60.9 | 385 | 23.1 | 44.1 | 427 |  | 2020-09-17 09:48 | 44091.4084 | 23.1 | 44.1 | 427 |  |  | 2020-09-14 | B70277¦3rd floor stairwell¦¦Sep-17-2020 09:48
2020-09-17 09:48 | 44091.4085 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 2nd floor lobby |  | 1 | 14.1 | 60.7 | 419 | 22 | 44.3 | 452 | No | 2020-09-17 09:48 | 44091.4085 | 22 | 44.3 | 452 |  |  | 2020-09-14 | B70496¦2nd floor lobby¦¦Sep-17-2020 09:48
2020-09-17 09:48 | 44091.4086 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 seating area 2 |  | 0 | 15.1 | 48.6 | 440 | 22.6 | 48.5 | 440 |  | 2020-09-17 09:48 | 44091.4086 | 22.6 | 48.5 | 440 |  |  | 2020-09-14 | B17477¦Level 5 seating area 2 ¦¦Sep-17-2020 09:48
2020-09-17 09:49 | 44091.4087 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 210a |  | 1 | 11 | 72 | 385 | 22.6 | 46.8 | 426 | No | 2020-09-17 09:49 | 44091.4087 | 22.6 | 46.8 | 426 |  |  | 2020-09-14 | B14660¦210a¦¦Sep-17-2020 09:48
2020-09-17 09:49 | 44091.4089 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Crown attorneys office |  | 4 | 19 | 61.3 | 407 | 22.8 | 46.5 | 438 | No | 2020-09-17 09:49 | 44091.4089 | 22.8 | 46.5 | 438 |  |  | 2020-09-14 | B21128¦Crown attorneys office ¦¦Sep-17-2020 09:48
2020-09-17 09:49 | 44091.409 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview room 2 |  | 0 | 15 | 70 | 412 | 22 | 47 | 455 |  | 2020-09-17 09:49 | 44091.409 | 22 | 47 | 455 |  |  | 2020-09-14 | B70235¦Interview room 2¦¦Sep-17-2020 09:48
2020-09-17 09:49 | 44091.409 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Court room 1 judge's desk |  | 1 | 15 | 68 | 421 | 22.1 | 47.8 | 425 | No | 2020-09-17 09:49 | 44091.409 | 22.1 | 47.8 | 425 |  |  | 2020-09-14 | B20489¦Court room 1 judge's desk ¦¦Sep-17-2020 09:48
2020-09-17 09:49 | 44091.409 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 3 |  | 0 | 13.7 | 69.4 | 419 | 22.8 | 44.5 | 469 |  | 2020-09-17 09:49 | 44091.409 | 22.8 | 44.5 | 469 |  |  | 2020-09-14 | B20367¦Waiting room 3¦¦Sep-17-2020 09:48
2020-09-17 09:49 | 44091.4092 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom C |  | 0 | 14.8 | 72.1 | 408 | 20.7 | 56.5 | 449 | No | 2020-09-17 09:49 | 44091.4092 | 20.7 | 56.5 | 449 |  |  | 2020-09-14 | B20478¦Courtroom C¦¦Sep-17-2020 09:49
2020-09-17 09:49 | 44091.4092 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown Attorney library |  | 1 | 14.5 | 74.7 | 397 | 23.2 | 50.9 | 463 |  | 2020-09-17 09:49 | 44091.4092 | 23.2 | 50.9 | 463 |  |  | 2020-09-14 | B20494¦Crown Attorney library ¦¦Sep-17-2020 09:49
2020-09-17 09:49 | 44091.4092 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Front desk |  | 4 | 13.8 | 71.6 | 478 | 19.9 | 57.1 | 491 |  | 2020-09-17 09:49 | 44091.4092 | 19.9 | 57.1 | 491 |  |  | 2020-09-14 | B20474¦Front desk¦¦Sep-17-2020 09:49
2020-09-17 09:50 | 44091.4094 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 201 |  | 1 | 14.1 | 60.7 | 419 | 21.8 | 43 | 445 | No | 2020-09-17 09:50 | 44091.4094 | 21.8 | 43 | 445 |  |  | 2020-09-14 | B70496¦201¦¦Sep-17-2020 09:49
2020-09-17 09:50 | 44091.4095 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Elevator - inside |  | 1 | 16.2 | 60.9 | 385 | 23.5 | 43 | 480 |  | 2020-09-17 09:50 | 44091.4095 | 23.5 | 43 | 480 |  |  | 2020-09-14 | B70277¦Elevator - inside¦¦Sep-17-2020 09:49
2020-09-17 09:50 | 44091.4096 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 4 |  | 1 | 15.8 | 82.9 | 409 | 22.2 | 50.3 | 416 |  | 2020-09-17 09:50 | 44091.4096 | 22.2 | 50.3 | 416 |  |  | 2020-09-14 | B20390¦Outside courtroom 4¦¦Sep-17-2020 09:49
2020-09-17 09:50 | 44091.4097 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Duty Counsel office |  | 0 | 15 | 70 | 412 | 24 | 45 | 497 |  | 2020-09-17 09:50 | 44091.4097 | 24 | 45 | 497 |  |  | 2020-09-14 | B70235¦Duty Counsel office ¦¦Sep-17-2020 09:49
2020-09-17 09:50 | 44091.4099 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Interview room 402a |  | 0 | 13.7 | 69.4 | 419 | 23.5 | 42.8 | 457 |  | 2020-09-17 09:50 | 44091.4099 | 23.5 | 42.8 | 457 |  |  | 2020-09-14 | B20367¦Interview room 402a¦¦Sep-17-2020 09:50
2020-09-17 09:50 | 44091.41 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 206 |  | 0 | 11 | 72 | 385 | 22.5 | 46.5 | 426 | No | 2020-09-17 09:50 | 44091.41 | 22.5 | 46.5 | 426 |  |  | 2020-09-14 | B14660¦206¦¦Sep-17-2020 09:50
2020-09-17 09:51 | 44091.4101 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Manage of operations seating area |  | 0 | 15.1 | 71 | 433 | 22.3 | 49.1 | 435 |  | 2020-09-17 09:51 | 44091.4101 | 22.3 | 49.1 | 435 |  |  | 2020-09-14 | B17477¦Manage of operations seating area ¦¦Sep-17-2020 09:50
2020-09-17 09:51 | 44091.4103 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom A |  | 0 | 14.8 | 72.1 | 408 | 21.5 | 53.9 | 445 | No | 2020-09-17 09:51 | 44091.4103 | 21.5 | 53.9 | 445 |  |  | 2020-09-14 | B20478¦Courtroom A¦¦Sep-17-2020 09:50
2020-09-17 09:51 | 44091.4103 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 judge |  | 1 | 15 | 70 | 412 |  |  |  | Occupied, no access | 2020-09-17 09:51 | 44091.4103 | [5 empty] | 2020-09-14 | B70235¦Court #1 judge ¦¦Sep-17-2020 09:50
2020-09-17 09:51 | 44091.4104 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | 1st Floor - lobby |  | 3 | 16.2 | 60.9 | 385 | 23.5 | 43 | 480 |  | 2020-09-17 09:51 | 44091.4104 | 23.5 | 43 | 480 |  |  | 2020-09-14 | B70277¦1st Floor - lobby¦¦Sep-17-2020 09:50
2020-09-17 09:51 | 44091.4106 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Court room 1 gallery |  | 1 | 15 | 68 | 421 | 22.2 | 47.6 | 429 | No | 2020-09-17 09:51 | 44091.4106 | 22.2 | 47.6 | 429 |  |  | 2020-09-14 | B20489¦Court room 1 gallery ¦¦Sep-17-2020 09:51
2020-09-17 09:51 | 44091.4106 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Interview room 402b |  | 0 | 13.7 | 69.4 | 419 | 23.8 | 41.8 | 448 |  | 2020-09-17 09:51 | 44091.4106 | 23.8 | 41.8 | 448 |  |  | 2020-09-14 | B20367¦Interview room 402b¦¦Sep-17-2020 09:51
2020-09-17 09:51 | 44091.4106 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Front lobby |  | 4 | 20 | 57 | 398 | 21 | 56 | 432 |  | 2020-09-17 09:51 | 44091.4106 | 21 | 56 | 432 |  |  | 2020-09-14 | B19570¦Front lobby ¦¦Sep-17-2020 09:51
2020-09-17 09:52 | 44091.4108 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 5 |  | 1 | 15.8 | 82.9 | 409 | 22.2 | 48.8 | 404 |  | 2020-09-17 09:52 | 44091.4108 | 22.2 | 48.8 | 404 |  |  | 2020-09-14 | B20390¦Outside courtroom 5¦¦Sep-17-2020 09:51
2020-09-17 09:52 | 44091.4108 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area main office |  | 1 | 13.8 | 71.6 | 478 | 20 | 53.9 | 477 |  | 2020-09-17 09:52 | 44091.4108 | 20 | 53.9 | 477 |  |  | 2020-09-14 | B20474¦Waiting area main office¦¦Sep-17-2020 09:51
2020-09-17 09:52 | 44091.411 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 lawyer |  | 1 | 15 | 70 | 412 |  |  |  | Occupied, no access | 2020-09-17 09:52 | 44091.411 | [5 empty] | 2020-09-14 | B70235¦Court #1 lawyer ¦¦Sep-17-2020 09:51
2020-09-17 09:52 | 44091.4111 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 - judge |  | 2 | 15 | 72 | 367 | 23 | 43 | 398 |  | 2020-09-17 09:52 | 44091.4111 | 23 | 43 | 398 |  |  | 2020-09-14 | B20772¦H11 - judge¦¦Sep-17-2020 09:52
2020-09-17 09:52 | 44091.4111 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 201 |  | 1 | 14.1 | 60.7 | 419 | 21.7 | 42.4 | 435 | No | 2020-09-17 09:52 | 44091.4111 | 21.7 | 42.4 | 435 |  |  | 2020-09-14 | B70496¦201¦¦Sep-17-2020 09:52
2020-09-17 09:52 | 44091.4112 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Manage of operations seating area 2 |  | 0 | 15.1 | 71 | 433 | 24 | 47.4 | 434 |  | 2020-09-17 09:52 | 44091.4112 | 24 | 47.4 | 434 |  |  | 2020-09-14 | B17477¦Manage of operations seating area 2 ¦¦Sep-17-2020 09:52
2020-09-17 09:52 | 44091.4113 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | 1st floor - outside service Ontario entrance |  | 2 | 16.2 | 60.9 | 385 | 23 | 44.3 | 534 |  | 2020-09-17 09:52 | 44091.4113 | 23 | 44.3 | 534 |  |  | 2020-09-14 | B70277¦1st floor - outside service Ontario entrance¦¦Sep-17-2020 09:52
2020-09-17 09:53 | 44091.4115 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 vestibule |  | 0 | 15 | 70 | 412 | 23 | 46 | 646 |  | 2020-09-17 09:53 | 44091.4115 | 23 | 46 | 646 |  |  | 2020-09-14 | B70235¦Court #1 vestibule ¦¦Sep-17-2020 09:52
2020-09-17 09:53 | 44091.4117 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Middle left H11 |  | 2 | 15 | 72 | 367 | 23 | 43 | 382 |  | 2020-09-17 09:53 | 44091.4117 | 23 | 43 | 382 |  |  | 2020-09-14 | B20772¦Middle left H11¦¦Sep-17-2020 09:52
2020-09-17 09:53 | 44091.412 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 303 |  | 0 | 11 | 72 | 385 | 22.8 | 43.4 | 434 | No | 2020-09-17 09:53 | 44091.412 | 22.8 | 43.4 | 434 |  |  | 2020-09-14 | B14660¦303¦¦Sep-17-2020 09:53
2020-09-17 09:53 | 44091.412 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 3rd floor hallway south |  | 0 | 15 | 68 | 421 | 22.3 | 47.7 | 462 | No | 2020-09-17 09:53 | 44091.412 | 22.3 | 47.7 | 462 |  |  | 2020-09-14 | B20489¦3rd floor hallway south ¦¦Sep-17-2020 09:53
2020-09-17 09:54 | 44091.4122 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Police Sergeant office |  | 0 | 15 | 70 | 412 | 23 | 45 | 459 |  | 2020-09-17 09:54 | 44091.4122 | 23 | 45 | 459 |  |  | 2020-09-14 | B70235¦Police Sergeant office ¦¦Sep-17-2020 09:53
2020-09-17 09:54 | 44091.4122 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Cell block |  | 1 | 14.5 | 74.7 | 397 | 23.1 | 48.8 | 455 |  | 2020-09-17 09:54 | 44091.4122 | 23.1 | 48.8 | 455 |  |  | 2020-09-14 | B20494¦Cell block¦¦Sep-17-2020 09:53
2020-09-17 09:54 | 44091.4122 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 middle right |  | 2 | 15 | 72 | 367 | 23 | 43 | 385 |  | 2020-09-17 09:54 | 44091.4122 | 23 | 43 | 385 |  |  | 2020-09-14 | B20772¦H11 middle right¦¦Sep-17-2020 09:53
2020-09-17 09:54 | 44091.4124 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Interview room 6 |  | 1 | 15.8 | 82.9 | 409 | 22.3 | 49.1 | 406 |  | 2020-09-17 09:54 | 44091.4124 | 22.3 | 49.1 | 406 |  |  | 2020-09-14 | B20390¦Interview room 6¦¦Sep-17-2020 09:53
2020-09-17 09:54 | 44091.4125 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | Administration office |  | 4 | 14.1 | 60.7 | 419 | 21.7 | 44 | 463 | No | 2020-09-17 09:54 | 44091.4125 | 21.7 | 44 | 463 |  |  | 2020-09-14 | B70496¦Administration office ¦¦Sep-17-2020 09:53
2020-09-17 09:54 | 44091.4126 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Main office |  | 5 | 13.8 | 71.6 | 478 | 20.2 | 53.9 | 477 |  | 2020-09-17 09:54 | 44091.4126 | 20.2 | 53.9 | 477 |  |  | 2020-09-14 | B20474¦Main office¦¦Sep-17-2020 09:54
2020-09-17 09:54 | 44091.4126 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Common are behind Courtroom A |  | 0 | 14.8 | 72.1 | 408 | 21.3 | 53.5 | 442 | No | 2020-09-17 09:54 | 44091.4126 | 21.3 | 53.5 | 442 |  |  | 2020-09-14 | B20478¦Common are behind Courtroom A¦¦Sep-17-2020 09:54
2020-09-17 09:54 | 44091.4128 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 rear right |  | 2 | 15 | 72 | 367 | 23 | 43 | 386 |  | 2020-09-17 09:54 | 44091.4128 | 23 | 43 | 386 |  |  | 2020-09-14 | B20772¦H11 rear right ¦¦Sep-17-2020 09:54
2020-09-17 09:54 | 44091.4128 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Manage of operations seating area 2 |  | 0 | 15.1 | 71 | 433 | 23.8 | 45.2 | 431 | Main scan | 2020-09-17 09:54 | 44091.4128 | 23.8 | 45.2 | 431 |  |  | 2020-09-14 | B17477¦Manage of operations seating area 2 ¦¦Sep-17-2020 09:54
2020-09-17 09:55 | 44091.4129 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court services office |  | 5 | 20 | 57 | 398 | 23 | 48 | 465 |  | 2020-09-17 09:54 | 44091.4129 | 23 | 48 | 465 |  |  | 2020-09-14 | B19570¦Court services office ¦¦Sep-17-2020 09:54
2020-09-17 09:55 | 44091.4129 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 1 |  | 0 | 13.7 | 69.4 | 419 | 22.8 | 46.9 | 472 |  | 2020-09-17 09:55 | 44091.4129 | 22.8 | 46.9 | 472 |  |  | 2020-09-14 | B20367¦Courtroom 1¦¦Sep-17-2020 09:54
2020-09-17 09:55 | 44091.4131 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Front lobby |  | 2 | 18.5 | 41.6 | 450 | 20.5 | 49.8 | 490 |  | 2020-09-17 09:55 | 44091.4131 | 20.5 | 49.8 | 490 |  |  | 2020-09-14 | B25477¦Front lobby¦¦Sep-17-2020 09:54
2020-09-17 09:55 | 44091.4132 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Entrance |  | 0 | 18.1 | 59.8 | 431 | 23.1 | 54.6 | 660 |  | 2020-09-17 09:55 | 44091.4132 | 23.1 | 54.6 | 660 |  |  | 2020-09-14 | B10577¦Main Entrance ¦¦Sep-17-2020 09:55
2020-09-17 09:55 | 44091.4133 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11-rear left |  | 2 | 15 | 72 | 366 | 23 | 43 | 386 |  | 2020-09-17 09:55 | 44091.4133 | 23 | 43 | 386 |  |  | 2020-09-14 | B20772¦H11-rear left¦¦Sep-17-2020 09:55
2020-09-17 09:56 | 44091.4136 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 302 |  | 3 | 11 | 72 | 385 | 23.1 | 42.2 | 467 | No | 2020-09-17 09:56 | 44091.4136 | 23.1 | 42.2 | 467 |  |  | 2020-09-14 | B14660¦302¦¦Sep-17-2020 09:55
2020-09-17 09:56 | 44091.4137 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Trail office |  | 3 | 13.8 | 71.6 | 478 | 20.1 | 53.4 | 476 |  | 2020-09-17 09:56 | 44091.4137 | 20.1 | 53.4 | 476 |  |  | 2020-09-14 | B20474¦Trail office¦¦Sep-17-2020 09:55
2020-09-17 09:56 | 44091.4138 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 1 office |  | 0 | 13.7 | 69.4 | 419 | 22.8 | 49.5 | 464 |  | 2020-09-17 09:56 | 44091.4138 | 22.8 | 49.5 | 464 |  |  | 2020-09-14 | B20367¦Courtroom 1 office ¦¦Sep-17-2020 09:55
2020-09-17 09:56 | 44091.4138 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | HR |  | 3 | 18.5 | 41.6 | 450 | 21 | 48.2 | 535 |  | 2020-09-17 09:56 | 44091.4138 | 21 | 48.2 | 535 |  |  | 2020-09-14 | B25477¦HR¦¦Sep-17-2020 09:55
2020-09-17 09:56 | 44091.4138 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell - third floor |  | 1 | 15.8 | 82.9 | 409 | 22.3 | 50.7 | 424 |  | 2020-09-17 09:56 | 44091.4138 | 22.3 | 50.7 | 424 |  |  | 2020-09-14 | B20390¦Main stairwell - third floor¦¦Sep-17-2020 09:55
2020-09-17 09:56 | 44091.4139 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 hallway |  | 0 | 15.1 | 71 | 437 | 23.7 | 47.6 | 447 |  | 2020-09-17 09:56 | 44091.4139 | 23.7 | 47.6 | 447 |  |  | 2020-09-14 | B17477¦Level 5 hallway ¦¦Sep-17-2020 09:56
2020-09-17 09:56 | 44091.414 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Employee entrance |  | 1 | 20 | 57 | 398 | 23 | 48 | 487 |  | 2020-09-17 09:56 | 44091.414 | 23 | 48 | 487 |  |  | 2020-09-14 | B19570¦Employee entrance ¦¦Sep-17-2020 09:56
2020-09-17 09:57 | 44091.4144 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court admin hall |  | 1 | 20 | 57 | 398 | 23 | 48 | 488 |  | 2020-09-17 09:57 | 44091.4144 | 23 | 48 | 488 |  |  | 2020-09-14 | B19570¦Court admin hall¦¦Sep-17-2020 09:56
2020-09-17 09:57 | 44091.4144 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Lobby South |  | 1 | 18.1 | 59.8 | 431 | 22.3 | 53.5 | 511 |  | 2020-09-17 09:57 | 44091.4144 | 22.3 | 53.5 | 511 |  |  | 2020-09-14 | B10577¦Main Lobby South¦¦Sep-17-2020 09:56
2020-09-17 09:57 | 44091.4145 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | ED office |  | 3 | 18.5 | 41.6 | 450 | 21.3 | 47.4 | 500 |  | 2020-09-17 09:57 | 44091.4145 | 21.3 | 47.4 | 500 |  |  | 2020-09-14 | B25477¦ED office¦¦Sep-17-2020 09:56
2020-09-17 09:57 | 44091.4146 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Third floor waiting area |  | 1 | 15.8 | 82.9 | 409 | 22.3 | 49.7 | 422 |  | 2020-09-17 09:57 | 44091.4146 | 22.3 | 49.7 | 422 |  |  | 2020-09-14 | B20390¦Third floor waiting area¦¦Sep-17-2020 09:56
2020-09-17 09:57 | 44091.4148 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judicial stairwell |  | 0 | 13.7 | 69.4 | 419 | 22.7 | 50 | 491 |  | 2020-09-17 09:57 | 44091.4148 | 22.7 | 50 | 491 |  |  | 2020-09-14 | B20367¦Judicial stairwell ¦¦Sep-17-2020 09:57
2020-09-17 09:58 | 44091.415 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Basement hall w |  | 1 | 20 | 57 | 398 | 22 | 49 | 473 |  | 2020-09-17 09:58 | 44091.415 | 22 | 49 | 473 |  |  | 2020-09-14 | B19570¦Basement hall w¦¦Sep-17-2020 09:57
2020-09-17 09:58 | 44091.415 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 hallway 2 |  | 0 | 15.1 | 71 | 433 | 23.5 | 45.5 | 440 |  | 2020-09-17 09:58 | 44091.415 | 23.5 | 45.5 | 440 |  |  | 2020-09-14 | B17477¦Level 5 hallway 2 ¦¦Sep-17-2020 09:57
2020-09-17 09:58 | 44091.4151 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 301b |  | 0 | 11 | 72 | 385 | 23.1 | 43 | 431 | No | 2020-09-17 09:58 | 44091.4151 | 23.1 | 43 | 431 |  |  | 2020-09-14 | B14660¦301b¦¦Sep-17-2020 09:57
2020-09-17 09:58 | 44091.4153 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Upper landing of stairway |  | 1 | 13.8 | 71.6 | 478 | 20 | 54.6 | 482 |  | 2020-09-17 09:58 | 44091.4153 | 20 | 54.6 | 482 |  |  | 2020-09-14 | B20474¦Upper landing of stairway¦¦Sep-17-2020 09:58
2020-09-17 09:58 | 44091.4156 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Admin office |  | 4 | 18.5 | 41.6 | 450 | 21.7 | 47 | 516 |  | 2020-09-17 09:58 | 44091.4156 | 21.7 | 47 | 516 |  |  | 2020-09-14 | B25477¦Admin office ¦¦Sep-17-2020 09:58
2020-09-17 09:58 | 44091.4156 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Basement hall e |  | 1 | 20 | 57 | 398 | 22 | 50 | 463 |  | 2020-09-17 09:58 | 44091.4156 | 22 | 50 | 463 |  |  | 2020-09-14 | B19570¦Basement hall e ¦¦Sep-17-2020 09:58
2020-09-17 09:59 | 44091.4157 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Law Library |  | 0 | 14.8 | 72.1 | 408 | 22.5 | 50.2 | 476 | No | 2020-09-17 09:59 | 44091.4157 | 22.5 | 50.2 | 476 |  |  | 2020-09-14 | B20478¦Law Library¦¦Sep-17-2020 09:58
2020-09-17 09:59 | 44091.4159 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Court Service Office |  | 2 | 18.1 | 59.8 | 431 | 22.1 | 52.7 | 632 |  | 2020-09-17 09:59 | 44091.4159 | 22.1 | 52.7 | 632 |  |  | 2020-09-14 | B10577¦Court Service Office¦¦Sep-17-2020 09:58
2020-09-17 09:59 | 44091.4159 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 hallway 3 |  | 0 | 15.1 | 71 | 433 | 23.5 | 46 | 436 |  | 2020-09-17 09:59 | 44091.4159 | 23.5 | 46 | 436 |  |  | 2020-09-14 | B17477¦Level 5 hallway 3 ¦¦Sep-17-2020 09:58
2020-09-17 09:59 | 44091.416 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 1 |  | 1 | 15.8 | 82.9 | 409 | 22 | 49 | 409 |  | 2020-09-17 09:59 | 44091.416 | 22 | 49 | 409 |  |  | 2020-09-14 | B20390¦Outside courtroom 1¦¦Sep-17-2020 09:59
2020-09-17 09:59 | 44091.4161 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Interview room 201 |  | 0 | 13.7 | 69.7 | 419 | 22.3 | 44.4 | 458 |  | 2020-09-17 09:59 | 44091.4161 | 22.3 | 44.4 | 458 |  |  | 2020-09-14 | B20367¦Interview room 201¦¦Sep-17-2020 09:59
2020-09-17 09:59 | 44091.4163 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Croqn attorney office |  | 1 | 20 | 57 | 398 | 21 | 49 | 440 |  | 2020-09-17 09:59 | 44091.4163 | 21 | 49 | 440 |  |  | 2020-09-14 | B19570¦Croqn attorney office¦¦Sep-17-2020 09:59
2020-09-17 10:00 | 44091.4167 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom1 |  | 1 | 13.8 | 71.6 | 478 | 20 | 54.1 | 507 |  | 2020-09-17 10:00 | 44091.4167 | 20 | 54.1 | 507 |  |  | 2020-09-14 | B20474¦Waiting area courtroom1¦¦Sep-17-2020 09:59
2020-09-17 10:00 | 44091.4167 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Financial services |  | 2 | 18.5 | 41.6 | 450 | 21.8 | 46.3 | 517 |  | 2020-09-17 10:00 | 44091.4167 | 21.8 | 46.3 | 517 |  |  | 2020-09-14 | B19890¦Financial services ¦¦Sep-17-2020 10:00
2020-09-17 10:00 | 44091.4168 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H14-table |  | 2 | 15 | 72 | 367 | 22 | 44 | 376 |  | 2020-09-17 10:00 | 44091.4168 | 22 | 44 | 376 |  |  | 2020-09-14 | B20772¦H14-table ¦¦Sep-17-2020 10:00
2020-09-17 10:00 | 44091.4169 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 4 bottom |  | 1 | 20 | 57 | 398 | 21 | 53 | 464 |  | 2020-09-17 10:00 | 44091.4169 | 21 | 53 | 464 |  |  | 2020-09-14 | B19570¦Stairwell 4 bottom ¦¦Sep-17-2020 10:00
2020-09-17 10:00 | 44091.417 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 waiting room |  | 0 | 15.1 | 71 | 433 | 23.5 | 46.8 | 432 |  | 2020-09-17 10:00 | 44091.417 | 23.5 | 46.8 | 432 |  |  | 2020-09-14 | B17477¦Level 5 waiting room ¦¦Sep-17-2020 10:00
2020-09-17 10:01 | 44091.4171 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Witness Area |  | 0 | 18.1 | 59.8 | 431 | 22.2 | 53.2 | 659 |  | 2020-09-17 10:01 | 44091.4171 | 22.2 | 53.2 | 659 |  |  | 2020-09-14 | B10577¦Witness Area¦¦Sep-17-2020 10:00
2020-09-17 10:01 | 44091.4172 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside third floor elevator |  | 1 | 15.8 | 82.9 | 409 | 22 | 51.1 | 449 |  | 2020-09-17 10:01 | 44091.4172 | 22 | 51.1 | 449 |  |  | 2020-09-14 | B20390¦Outside third floor elevator¦¦Sep-17-2020 10:00
2020-09-17 10:01 | 44091.4173 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 301a |  | 0 | 11 | 72 | 385 | 22.8 | 43.3 | 413 | No | 2020-09-17 10:01 | 44091.4173 | 22.8 | 43.3 | 413 |  |  | 2020-09-14 | B14660¦301a¦¦Sep-17-2020 10:00
2020-09-17 10:01 | 44091.4174 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | East Stairwell |  | 0 | 14.8 | 72.1 | 408 | 23 | 47.7 | 482 | No | 2020-09-17 10:01 | 44091.4174 | 23 | 47.7 | 482 |  |  | 2020-09-14 | B20478¦East Stairwell ¦¦Sep-17-2020 10:01
2020-09-17 10:01 | 44091.4175 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Administration office |  | 8 | 13.7 | 69.4 | 419 | 22.6 | 48.3 | 980 |  | 2020-09-17 10:01 | 44091.4175 | 22.6 | 48.3 | 980 |  |  | 2020-09-14 | B20367¦Administration office ¦¦Sep-17-2020 10:01
2020-09-17 10:02 | 44091.4177 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 5 bottom |  | 1 | 20 | 57 | 398 | 21 | 52 | 467 |  | 2020-09-17 10:02 | 44091.4177 | 21 | 52 | 467 |  |  | 2020-09-14 | B19570¦Stairwell 5 bottom ¦¦Sep-17-2020 10:01
2020-09-17 10:02 | 44091.4179 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #1 |  | 2 | 13.8 | 71.6 | 478 | 19.7 | 54.4 | 517 |  | 2020-09-17 10:02 | 44091.4179 | 19.7 | 54.4 | 517 |  |  | 2020-09-14 | B20474¦Courtroom #1¦¦Sep-17-2020 10:01
2020-09-17 10:02 | 44091.4179 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 South |  | 0 | 18.1 | 59.8 | 431 | 21.7 | 55.5 | 513 |  | 2020-09-17 10:02 | 44091.4179 | 21.7 | 55.5 | 513 |  |  | 2020-09-14 | B10577¦Courtroom 1 South¦¦Sep-17-2020 10:01
2020-09-17 10:02 | 44091.418 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 waiting room 2 |  | 0 | 15.1 | 71 | 433 | 23.2 | 47.1 | 429 |  | 2020-09-17 10:02 | 44091.418 | 23.2 | 47.1 | 429 |  |  | 2020-09-14 | B17477¦Level 5 waiting room 2¦¦Sep-17-2020 10:01
2020-09-17 10:02 | 44091.4182 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H14- judge |  | 2 | 15 | 72 | 367 | 22 | 44 | 381 |  | 2020-09-17 10:02 | 44091.4182 | 22 | 44 | 381 |  |  | 2020-09-14 | B20772¦H14- judge ¦¦Sep-17-2020 10:02
2020-09-17 10:02 | 44091.4184 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Administration office |  | 9 | 13.7 | 69.4 | 419 | 22.8 | 46.1 | 802 |  | 2020-09-17 10:02 | 44091.4184 | 22.8 | 46.1 | 802 |  |  | 2020-09-14 | B20367¦Administration office ¦¦Sep-17-2020 10:02
2020-09-17 10:03 | 44091.4185 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Courtroom |  | 3 | 18.5 | 41.6 | 450 | 22.3 | 45.5 | 478 |  | 2020-09-17 10:03 | 44091.4185 | 22.3 | 45.5 | 478 |  |  | 2020-09-14 | B25477¦Courtroom ¦¦Sep-17-2020 10:02
2020-09-17 10:03 | 44091.4186 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 1 |  | 0 | 19.6 | 55.5 | 406 | 24.8 | 42 | 412 | No | 2020-09-17 10:03 | 44091.4186 | 24.8 | 42 | 412 |  |  | 2020-09-14 | Pearso¦Lobby 1 ¦¦Sep-17-2020 10:02
2020-09-17 10:03 | 44091.4186 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 East |  | 0 | 18.1 | 59.8 | 431 | 21.8 | 54.9 | 513 |  | 2020-09-17 10:03 | 44091.4186 | 21.8 | 54.9 | 513 |  |  | 2020-09-14 | B10577¦Courtroom 1 East¦¦Sep-17-2020 10:02
2020-09-17 10:04 | 44091.4192 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Mezzanine |  | 0 | 18.5 | 41.6 | 450 | 22.1 | 44.6 | 483 |  | 2020-09-17 10:04 | 44091.4192 | 22.1 | 44.6 | 483 |  |  | 2020-09-14 | B25477¦Mezzanine ¦¦Sep-17-2020 10:03
2020-09-17 10:04 | 44091.4193 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | Crown Attorney |  | 1 | 11 | 72 | 385 | 23.7 | 40.1 | 439 | No | 2020-09-17 10:04 | 44091.4193 | 23.7 | 40.1 | 439 |  |  | 2020-09-14 | B14660¦Crown Attorney¦¦Sep-17-2020 10:03
2020-09-17 10:04 | 44091.4194 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #2 |  | 2 | 13.8 | 71.6 | 478 | 19.3 | 55.5 | 458 |  | 2020-09-17 10:04 | 44091.4194 | 19.3 | 55.5 | 458 |  |  | 2020-09-14 | B20474¦Courtroom #2¦¦Sep-17-2020 10:03
2020-09-17 10:04 | 44091.4194 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 North |  | 2 | 18.1 | 59.8 | 431 | 21.8 | 54.7 | 486 |  | 2020-09-17 10:04 | 44091.4194 | 21.8 | 54.7 | 486 |  |  | 2020-09-14 | B10577¦Courtroom 1 North¦¦Sep-17-2020 10:03
2020-09-17 10:05 | 44091.42 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | 1st Floor Main Common Area |  | 1 | 14.8 | 72.1 | 408 | 22.4 | 48 | 487 | No | 2020-09-17 10:05 | 44091.42 | 22.4 | 48 | 487 |  |  | 2020-09-14 | B20478¦1st Floor Main Common Area¦¦Sep-17-2020 10:04
2020-09-17 10:05 | 44091.42 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 West |  | 0 | 18.1 | 59.8 | 431 | 21.9 | 54.7 | 479 |  | 2020-09-17 10:05 | 44091.42 | 21.9 | 54.7 | 479 |  |  | 2020-09-14 | B10577¦Courtroom 1 West ¦¦Sep-17-2020 10:04
2020-09-17 10:05 | 44091.4201 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Board room |  | 0 | 18.5 | 41.6 | 450 | 22.1 | 43.9 | 445 |  | 2020-09-17 10:05 | 44091.4201 | 22.1 | 43.9 | 445 |  |  | 2020-09-14 | B25477¦Board room ¦¦Sep-17-2020 10:04
2020-09-17 10:05 | 44091.4202 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #3 |  | 2 | 13.8 | 71.6 | 478 | 19.9 | 55 | 458 |  | 2020-09-17 10:05 | 44091.4202 | 19.9 | 55 | 458 |  |  | 2020-09-14 | B20474¦Courtroom #3¦¦Sep-17-2020 10:05
2020-09-17 10:05 | 44091.4204 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom services office |  | 4 | 15.1 | 71 | 462 | 23.3 | 46.1 | 473 |  | 2020-09-17 10:05 | 44091.4204 | 23.3 | 46.1 | 473 |  |  | 2020-09-14 | B17477¦Courtroom services office¦¦Sep-17-2020 10:05
2020-09-17 10:05 | 44091.4205 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 - judge |  | 2 | 15 | 72 | 367 | 22 | 45 | 442 |  | 2020-09-17 10:05 | 44091.4205 | 22 | 45 | 442 |  |  | 2020-09-14 | B20772¦H13 - judge¦¦Sep-17-2020 10:05
2020-09-17 10:06 | 44091.4205 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 Center |  | 0 | 18.1 | 59.8 | 431 | 21.9 | 54.4 | 480 |  | 2020-09-17 10:06 | 44091.4205 | 21.9 | 54.4 | 480 |  |  | 2020-09-14 | B10577¦Courtroom 1 Center¦¦Sep-17-2020 10:05
2020-09-17 10:06 | 44091.4206 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 306 |  | 0 | 11 | 72 | 385 | 23 | 43.1 | 418 | No | 2020-09-17 10:06 | 44091.4206 | 23 | 43.1 | 418 |  |  | 2020-09-14 | B14660¦306¦¦Sep-17-2020 10:05
2020-09-17 10:06 | 44091.4207 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Poa office |  | 6 | 20 | 57 | 398 | 23 | 51 | 535 |  | 2020-09-17 10:06 | 44091.4207 | 23 | 51 | 535 |  |  | 2020-09-14 | B19570¦Poa office ¦¦Sep-17-2020 10:05
2020-09-17 10:06 | 44091.4208 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Library |  | 0 | 18.5 | 41.6 | 450 | 22.1 | 44.2 | 476 |  | 2020-09-17 10:06 | 44091.4208 | 22.1 | 44.2 | 476 |  |  | 2020-09-14 | B25477¦Library ¦¦Sep-17-2020 10:06
2020-09-17 10:06 | 44091.4211 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #4 |  | 2 | 13.8 | 71.6 | 478 | 19.5 | 54.8 | 462 |  | 2020-09-17 10:06 | 44091.4211 | 19.5 | 54.8 | 462 |  |  | 2020-09-14 | B20474¦Courtroom #4¦¦Sep-17-2020 10:06
2020-09-17 10:07 | 44091.4212 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 - prisoner box |  | 2 | 15 | 72 | 367 | 22 | 45 | 395 |  | 2020-09-17 10:07 | 44091.4212 | 22 | 45 | 395 |  |  | 2020-09-14 | B20772¦H13 - prisoner box ¦¦Sep-17-2020 10:06
2020-09-17 10:07 | 44091.4214 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 5 |  | 2 | 20 | 57 | 398 | 22 | 51 | 430 |  | 2020-09-17 10:07 | 44091.4214 | 22 | 51 | 430 |  |  | 2020-09-14 | B19570¦Court 5 ¦¦Sep-17-2020 10:06
2020-09-17 10:07 | 44091.4214 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Admin Office Corridor |  | 0 | 14.8 | 72.1 | 408 | 22.3 | 49.1 | 497 | No | 2020-09-17 10:07 | 44091.4214 | 22.3 | 49.1 | 497 |  |  | 2020-09-14 | B20478¦Admin Office Corridor ¦¦Sep-17-2020 10:06
2020-09-17 10:07 | 44091.4216 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Lobby North |  | 2 | 18.1 | 59.8 | 431 | 22.2 | 53.7 | 653 |  | 2020-09-17 10:07 | 44091.4216 | 22.2 | 53.7 | 653 |  |  | 2020-09-14 | B10577¦Main Lobby North ¦¦Sep-17-2020 10:07
2020-09-17 10:07 | 44091.4216 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 2 |  | 0 | 19.7 | 53.8 | 397 | 19.6 | 47.7 | 411 |  | 2020-09-17 10:07 | 44091.4216 | 19.6 | 47.7 | 411 |  |  | 2020-09-14 | Pearso¦Lobby 2 ¦¦Sep-17-2020 10:07
2020-09-17 10:07 | 44091.4218 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 - witness box |  | 2 | 15 | 72 | 367 | 22 | 45 | 427 |  | 2020-09-17 10:07 | 44091.4218 | 22 | 45 | 427 |  |  | 2020-09-14 | B20772¦H13 - witness box¦¦Sep-17-2020 10:07
2020-09-17 10:08 | 44091.4219 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Case management |  | 5 | 13.7 | 69.4 | 419 | 21.3 | 52.9 | 845 |  | 2020-09-17 10:08 | 44091.4219 | 21.3 | 52.9 | 845 |  |  | 2020-09-14 | B20367¦Case management ¦¦Sep-17-2020 10:07
2020-09-17 10:08 | 44091.4222 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 4 |  | 3 | 20 | 57 | 398 | 22 | 50 | 448 |  | 2020-09-17 10:08 | 44091.4222 | 22 | 50 | 448 |  |  | 2020-09-14 | B19570¦Court 4¦¦Sep-17-2020 10:07
2020-09-17 10:08 | 44091.4222 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Stairwell |  | 0 | 18.1 | 59.8 | 431 | 22.3 | 53.7 | 649 |  | 2020-09-17 10:08 | 44091.4222 | 22.3 | 53.7 | 649 |  |  | 2020-09-14 | B10577¦Main Stairwell¦¦Sep-17-2020 10:08
2020-09-17 10:08 | 44091.4223 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | 2nd Floor common area |  | 0 | 14.8 | 72.1 | 408 | 21.5 | 51.2 | 498 | No | 2020-09-17 10:08 | 44091.4223 | 21.5 | 51.2 | 498 |  |  | 2020-09-14 | B20478¦2nd Floor common area ¦¦Sep-17-2020 10:08
2020-09-17 10:08 | 44091.4225 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 - rear left |  | 2 | 15 | 72 | 367 | 22 | 45 | 390 |  | 2020-09-17 10:08 | 44091.4225 | 22 | 45 | 390 |  |  | 2020-09-14 | B20772¦H13 - rear left ¦¦Sep-17-2020 10:08
2020-09-17 10:09 | 44091.4227 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Kitchen |  | 0 | 17 | 65 | 371 | 20 | 55 | 379 |  | 2020-09-17 10:09 | 44091.4227 | 20 | 55 | 379 |  |  | 2020-09-14 | B20603¦Kitchen¦¦Sep-17-2020 10:08
2020-09-17 10:09 | 44091.4227 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 3 |  | 5 | 20 | 57 | 398 | 21 | 50 | 455 |  | 2020-09-17 10:09 | 44091.4227 | 21 | 50 | 455 |  |  | 2020-09-14 | B19570¦Court 3 ¦¦Sep-17-2020 10:08
2020-09-17 10:09 | 44091.4228 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 3 |  | 0 | 19.7 | 53.8 | 397 | 19.6 | 49.1 | 401 |  | 2020-09-17 10:09 | 44091.4228 | 19.6 | 49.1 | 401 |  |  | 2020-09-14 | Pearso¦Lobby 3¦¦Sep-17-2020 10:08
2020-09-17 10:09 | 44091.423 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Stairwell |  | 0 | 18.1 | 59.6 | 431 | 22.3 | 53.5 | 643 |  | 2020-09-17 10:09 | 44091.423 | 22.3 | 53.5 | 643 |  |  | 2020-09-14 | B10577¦Main Stairwell¦¦Sep-17-2020 10:09
2020-09-17 10:09 | 44091.4232 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 14 judge rm |  | 0 | 19 | 57 | 420 | 22.4 | 47 | 430 |  | 2020-09-17 10:09 | 44091.4232 | 22.4 | 47 | 430 |  |  | 2020-09-14 | B70740¦14 judge rm¦¦Sep-17-2020 10:09
2020-09-17 10:10 | 44091.4233 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 rear right |  | 2 | 15 | 72 | 367 | 22 | 45 | 387 |  | 2020-09-17 10:10 | 44091.4233 | 22 | 45 | 387 |  |  | 2020-09-14 | B20772¦H13 rear right¦¦Sep-17-2020 10:09
2020-09-17 10:10 | 44091.4234 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 1 |  | 2 | 20 | 57 | 398 | 21 | 55 | 457 |  | 2020-09-17 10:10 | 44091.4234 | 21 | 55 | 457 |  |  | 2020-09-14 | B19570¦Court 1¦¦Sep-17-2020 10:09
2020-09-17 10:10 | 44091.4238 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2nd Floor Waiting area North |  | 0 | 18.1 | 59.8 | 431 | 22.5 | 53.1 | 636 |  | 2020-09-17 10:10 | 44091.4238 | 22.5 | 53.1 | 636 |  |  | 2020-09-14 | B10577¦2nd Floor Waiting area North¦¦Sep-17-2020 10:10
2020-09-17 10:10 | 44091.4238 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Mailroom |  | 1 | 17 | 65 | 371 | 21 | 53 | 394 |  | 2020-09-17 10:10 | 44091.4238 | 21 | 53 | 394 |  |  | 2020-09-14 | B20603¦Mailroom¦¦Sep-17-2020 10:10
2020-09-17 10:10 | 44091.4239 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | judgeshallway |  | 0 | 19 | 57 | 420 | 24 | 45 | 480 |  | 2020-09-17 10:10 | 44091.4239 | 24 | 45 | 480 |  |  | 2020-09-14 | B70740¦judgeshallway¦¦Sep-17-2020 10:10
2020-09-17 10:10 | 44091.4239 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 2 |  | 2 | 20 | 57 | 398 | 21 | 53 | 447 |  | 2020-09-17 10:10 | 44091.4239 | 21 | 53 | 447 |  |  | 2020-09-14 | B19570¦Court 2¦¦Sep-17-2020 10:10
2020-09-17 10:10 | 44091.4239 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom a |  | 0 | 19.7 | 53.8 | 397 | 24 | 40.2 | 412 |  | 2020-09-17 10:10 | 44091.4239 | 24 | 40.2 | 412 |  |  | 2020-09-14 | Pearso¦Ballroom a ¦¦Sep-17-2020 10:10
2020-09-17 10:11 | 44091.4242 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Basement Witness protection corridor |  | 0 | 14.8 | 72.1 | 408 | 21.1 | 53.9 | 464 | No | 2020-09-17 10:11 | 44091.4242 | 21.1 | 53.9 | 464 |  |  | 2020-09-14 | B20478¦Basement Witness protection corridor ¦¦Sep-17-2020 10:10
2020-09-17 10:11 | 44091.4244 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2nd floor waiting area center |  | 0 | 18.1 | 59.8 | 431 | 22.5 | 52.5 | 630 |  | 2020-09-17 10:11 | 44091.4244 | 22.5 | 52.5 | 630 |  |  | 2020-09-14 | B10577¦2nd floor waiting area center¦¦Sep-17-2020 10:11
2020-09-17 10:11 | 44091.4245 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Law library hall s |  | 1 | 20 | 57 | 398 | 22 | 53 | 437 |  | 2020-09-17 10:11 | 44091.4245 | 22 | 53 | 437 |  |  | 2020-09-14 | B19570¦Law library hall s ¦¦Sep-17-2020 10:11
2020-09-17 10:12 | 44091.4247 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | rm14 seating area |  | 0 | 19 | 57 | 420 | 22.3 | 46 | 420 |  | 2020-09-17 10:12 | 44091.4247 | 22.3 | 46 | 420 |  |  | 2020-09-14 | B70740¦rm14 seating area¦¦Sep-17-2020 10:11
2020-09-17 10:12 | 44091.4248 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Law library hall n |  | 1 | 20 | 57 | 398 | 22 | 51 | 436 |  | 2020-09-17 10:12 | 44091.4248 | 22 | 51 | 436 |  |  | 2020-09-14 | B19570¦Law library hall n ¦¦Sep-17-2020 10:11
2020-09-17 10:12 | 44091.425 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2nd floor waiting area south |  | 0 | 18.1 | 59.8 | 431 | 22.8 | 52.1 | 600 |  | 2020-09-17 10:12 | 44091.425 | 22.8 | 52.1 | 600 |  |  | 2020-09-14 | B10577¦2nd floor waiting area south¦¦Sep-17-2020 10:12
2020-09-17 10:12 | 44091.4251 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom a 2 |  | 0 | 19.7 | 53.8 | 397 | 23.6 | 40.4 | 412 |  | 2020-09-17 10:12 | 44091.4251 | 23.6 | 40.4 | 412 |  |  | 2020-09-14 | Pearso¦Ballroom a 2 ¦¦Sep-17-2020 10:12
2020-09-17 10:12 | 44091.4253 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Hallway nw |  | 1 | 20 | 57 | 398 | 22 | 51 | 431 |  | 2020-09-17 10:12 | 44091.4253 | 22 | 51 | 431 |  |  | 2020-09-14 | B19570¦Hallway nw ¦¦Sep-17-2020 10:12
2020-09-17 10:12 | 44091.4253 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Basement corridor middle |  | 0 | 14.8 | 72.1 | 408 | 21.1 | 50.6 | 468 | No | 2020-09-17 10:12 | 44091.4253 | 21.1 | 50.6 | 468 |  |  | 2020-09-14 | B20478¦Basement corridor middle¦¦Sep-17-2020 10:12
2020-09-17 10:13 | 44091.4256 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Mediation room c |  | 0 | 17 | 65 | 371 | 21 | 51 | 380 |  | 2020-09-17 10:13 | 44091.4256 | 21 | 51 | 380 |  |  | 2020-09-14 | B20603¦Mediation room c ¦¦Sep-17-2020 10:12
2020-09-17 10:13 | 44091.4257 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 5 top |  | 1 | 20 | 57 | 398 | 22 | 50 | 429 |  | 2020-09-17 10:13 | 44091.4257 | 22 | 50 | 429 |  |  | 2020-09-14 | B19570¦Stairwell 5 top ¦¦Sep-17-2020 10:13
2020-09-17 10:13 | 44091.4258 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom a 3 |  | 0 | 19.7 | 53.8 | 397 | 22.3 | 41 | 411 |  | 2020-09-17 10:13 | 44091.4258 | 22.3 | 41 | 411 |  |  | 2020-09-14 | Pearso¦Ballroom a 3 ¦¦Sep-17-2020 10:13
2020-09-17 10:14 | 44091.4262 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | front HRPS |  | 0 | 19 | 57 | 420 | 22.3 | 42 | 420 |  | 2020-09-17 10:14 | 44091.4262 | 22.3 | 42 | 420 |  |  | 2020-09-14 | B70740¦front HRPS¦¦Sep-17-2020 10:13
2020-09-17 10:14 | 44091.4262 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 259 |  | 1 | 20 | 57 | 398 | 22 | 50 | 427 |  | 2020-09-17 10:14 | 44091.4262 | 22 | 50 | 427 |  |  | 2020-09-14 | B19570¦259¦¦Sep-17-2020 10:13
2020-09-17 10:14 | 44091.4265 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 West |  | 0 | 18.1 | 59.8 | 431 | 23.6 | 52.1 | 549 |  | 2020-09-17 10:14 | 44091.4265 | 23.6 | 52.1 | 549 |  |  | 2020-09-14 | B10577¦Courtroom 2 West¦¦Sep-17-2020 10:14
2020-09-17 10:14 | 44091.4266 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 265 |  | 1 | 20 | 57 | 398 | 22 | 50 | 416 |  | 2020-09-17 10:14 | 44091.4266 | 22 | 50 | 416 |  |  | 2020-09-14 | B19570¦265¦¦Sep-17-2020 10:14
2020-09-17 10:15 | 44091.4269 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | COURT OFFICER |  | 1 | 19 | 57 | 420 | 22.2 | 42 | 420 |  | 2020-09-17 10:15 | 44091.4269 | 22.2 | 42 | 420 |  |  | 2020-09-14 | B70740¦COURT OFFICER¦¦Sep-17-2020 10:14
2020-09-17 10:15 | 44091.427 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 264 |  | 1 | 20 | 57 | 398 | 22 | 50 | 409 |  | 2020-09-17 10:15 | 44091.427 | 22 | 50 | 409 |  |  | 2020-09-14 | B19570¦264¦¦Sep-17-2020 10:14
2020-09-17 10:15 | 44091.4272 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Basement prisoner holding corridor |  | 0 | 14.8 | 72.1 | 408 | 20.8 | 55.5 | 483 | No | 2020-09-17 10:15 | 44091.4272 | 20.8 | 55.5 | 483 |  |  | 2020-09-14 | B20478¦Basement prisoner holding corridor ¦¦Sep-17-2020 10:15
2020-09-17 10:15 | 44091.4273 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Crown office |  | 1 | 13.7 | 69.4 | 419 | 22.4 | 50.4 | 1016 |  | 2020-09-17 10:15 | 44091.4273 | 22.4 | 50.4 | 1016 |  |  | 2020-09-14 | B20367¦Crown office ¦¦Sep-17-2020 10:15
2020-09-17 10:16 | 44091.4275 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 260 |  | 1 | 20 | 57 | 398 | 21 | 49 | 406 |  | 2020-09-17 10:16 | 44091.4275 | 21 | 49 | 406 |  |  | 2020-09-14 | B19570¦260¦¦Sep-17-2020 10:15
2020-09-17 10:16 | 44091.4276 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | COURT ATTORNEY |  | 0 | 19 | 57 | 420 | 22.2 | 37 | 420 |  | 2020-09-17 10:16 | 44091.4276 | 22.2 | 37 | 420 |  | caution | 2020-09-14 | B70740¦COURT ATTORNEY¦¦Sep-17-2020 10:15
2020-09-17 10:16 | 44091.4277 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 South |  | 0 | 18.1 | 59.8 | 431 | 22.2 | 52.3 | 658 |  | 2020-09-17 10:16 | 44091.4277 | 22.2 | 52.3 | 658 |  |  | 2020-09-14 | B10577¦Courtroom 2 South¦¦Sep-17-2020 10:15
2020-09-17 10:16 | 44091.4279 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 261 |  | 1 | 20 | 57 | 398 | 22 | 50 | 409 |  | 2020-09-17 10:16 | 44091.4279 | 22 | 50 | 409 |  |  | 2020-09-14 | B19570¦261¦¦Sep-17-2020 10:16
2020-09-17 10:16 | 44091.428 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ball room a 3 |  | 0 | 19.7 | 53.8 | 397 | 20.7 | 43.8 | 409 |  | 2020-09-17 10:16 | 44091.428 | 20.7 | 43.8 | 409 |  |  | 2020-09-14 | Pearso¦Ball room a 3 ¦¦Sep-17-2020 10:16
2020-09-17 10:17 | 44091.4282 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Crown office 1 |  | 0 | 13.7 | 69.4 | 419 | 22.2 | 50.5 | 713 |  | 2020-09-17 10:17 | 44091.4282 | 22.2 | 50.5 | 713 |  |  | 2020-09-14 | B20367¦Crown office 1¦¦Sep-17-2020 10:16
2020-09-17 10:17 | 44091.4283 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 East |  | 0 | 18.1 | 59.8 | 431 | 22.1 | 52.2 | 648 |  | 2020-09-17 10:17 | 44091.4283 | 22.1 | 52.2 | 648 |  |  | 2020-09-14 | B10577¦Courtroom 1 East¦¦Sep-17-2020 10:16
2020-09-17 10:17 | 44091.4284 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | CROWN ATTORNEY |  | 0 | 19 | 57 | 420 | 22.2 | 37 | 430 |  | 2020-09-17 10:17 | 44091.4284 | 22.2 | 37 | 430 |  | caution | 2020-09-14 | B70740¦CROWN ATTORNEY¦¦Sep-17-2020 10:16
2020-09-17 10:17 | 44091.4285 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 245 |  | 1 | 20 | 57 | 398 | 22 | 49 | 424 |  | 2020-09-17 10:17 | 44091.4285 | 22 | 49 | 424 |  |  | 2020-09-14 | B19570¦245¦¦Sep-17-2020 10:17
2020-09-17 10:18 | 44091.4289 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom b |  | 0 | 19.7 | 53.8 | 397 | 23.5 | 43.1 | 409 |  | 2020-09-17 10:18 | 44091.4289 | 23.5 | 43.1 | 409 |  |  | 2020-09-14 | Pearso¦Ballroom b ¦¦Sep-17-2020 10:17
2020-09-17 10:18 | 44091.4289 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 244 |  | 1 | 20 | 57 | 398 | 22 | 49 | 425 |  | 2020-09-17 10:18 | 44091.4289 | 22 | 49 | 425 |  |  | 2020-09-14 | B19570¦244¦¦Sep-17-2020 10:17
2020-09-17 10:18 | 44091.4292 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | CROWN OFFICE1 |  | 0 | 19 | 57 | 420 | 23 | 44 | 430 |  | 2020-09-17 10:18 | 44091.4292 | 23 | 44 | 430 |  |  | 2020-09-14 | B70740¦CROWN OFFICE1¦¦Sep-17-2020 10:18
2020-09-17 10:18 | 44091.4293 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H17 |  | 2 | 15 | 72 | 367 |  |  |  | The room can not be open with the current keys | 2020-09-17 10:18 | 44091.4293 | [5 empty] | 2020-09-14 | B20772¦H17¦¦Sep-17-2020 10:18
2020-09-17 10:18 | 44091.4293 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Administration office |  | 1 | 13.7 | 69.4 | 419 | 22.3 | 50.9 | 777 |  | 2020-09-17 10:18 | 44091.4293 | 22.3 | 50.9 | 777 |  |  | 2020-09-14 | B90631¦Administration office ¦¦Sep-17-2020 10:18
2020-09-17 10:18 | 44091.4294 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 Outside Enterance |  | 1 | 18.1 | 59.8 | 431 | 22 | 52.2 | 620 |  | 2020-09-17 10:18 | 44091.4294 | 22 | 52.2 | 620 |  |  | 2020-09-14 | B10577¦Courtroom 3 Outside Enterance¦¦Sep-17-2020 10:18
2020-09-17 10:18 | 44091.4294 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 247 |  | 1 | 20 | 57 | 398 | 22 | 50 | 424 |  | 2020-09-17 10:18 | 44091.4294 | 22 | 50 | 424 |  |  | 2020-09-14 | B19570¦247¦¦Sep-17-2020 10:18
2020-09-17 10:18 | 44091.4295 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Mediation room b |  | 0 | 17 | 65 | 371 | 22 | 48 | 382 |  | 2020-09-17 10:18 | 44091.4295 | 22 | 48 | 382 |  |  | 2020-09-14 | B20603¦Mediation room b¦¦Sep-17-2020 10:18
2020-09-17 10:19 | 44091.4297 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | main wshrm corr |  | 0 | 19 | 57 | 420 | 23.2 | 41 | 440 |  | 2020-09-17 10:19 | 44091.4297 | 23.2 | 41 | 440 |  |  | 2020-09-14 | B70740¦main wshrm corr¦¦Sep-17-2020 10:18
2020-09-17 10:19 | 44091.4298 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16- front left |  | 2 | 15 | 72 | 367 | 22 | 45 | 381 |  | 2020-09-17 10:19 | 44091.4298 | 22 | 45 | 381 |  |  | 2020-09-14 | B20772¦H16- front left ¦¦Sep-17-2020 10:18
2020-09-17 10:19 | 44091.4299 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Hallway ne |  | 3 | 20 | 57 | 398 | 22 | 51 | 427 |  | 2020-09-17 10:19 | 44091.4299 | 22 | 51 | 427 |  |  | 2020-09-14 | B19570¦Hallway ne ¦¦Sep-17-2020 10:19
2020-09-17 10:19 | 44091.4301 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Crown office 1 |  | 1 | 13.7 | 69.4 | 419 | 22.4 | 51.1 | 1016 |  | 2020-09-17 10:19 | 44091.4301 | 22.4 | 51.1 | 1016 |  |  | 2020-09-14 | B90631¦Crown office 1¦¦Sep-17-2020 10:19
2020-09-17 10:20 | 44091.4303 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 13 |  | 0 | 19 | 57 | 420 | 23 | 43 | 430 |  | 2020-09-17 10:20 | 44091.4303 | 23 | 43 | 430 |  |  | 2020-09-14 | B70740¦13¦¦Sep-17-2020 10:19
2020-09-17 10:20 | 44091.4303 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 251 |  | 1 | 20 | 57 | 398 | 22 | 51 | 429 |  | 2020-09-17 10:20 | 44091.4303 | 22 | 51 | 429 |  |  | 2020-09-14 | B19570¦251¦¦Sep-17-2020 10:19
2020-09-17 10:20 | 44091.4305 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 Waiting area |  | 0 | 18.1 | 59.8 | 431 | 22.3 | 52.1 | 597 |  | 2020-09-17 10:20 | 44091.4305 | 22.3 | 52.1 | 597 |  |  | 2020-09-14 | B10577¦Courtroom 3 Waiting area¦¦Sep-17-2020 10:19
2020-09-17 10:20 | 44091.4307 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 250 |  | 1 | 20 | 57 | 398 | 22 | 51 | 425 |  | 2020-09-17 10:20 | 44091.4307 | 22 | 51 | 425 |  |  | 2020-09-14 | B19570¦250¦¦Sep-17-2020 10:20
2020-09-17 10:20 | 44091.4307 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Mediation room a |  | 0 | 17 | 65 | 371 | 22 | 47 | 384 |  | 2020-09-17 10:20 | 44091.4307 | 22 | 47 | 384 |  |  | 2020-09-14 | B20603¦Mediation room a¦¦Sep-17-2020 10:20
2020-09-17 10:20 | 44091.4308 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | SEATING 13 |  | 0 | 19 | 57 | 420 | 23 | 43 | 430 |  | 2020-09-17 10:20 | 44091.4308 | 23 | 43 | 430 |  |  | 2020-09-14 | B70740¦SEATING 13¦¦Sep-17-2020 10:20
2020-09-17 10:20 | 44091.4308 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Crown office 2 |  | 0 | 13.7 | 69.4 | 419 | 22.4 | 50.9 | 748 |  | 2020-09-17 10:20 | 44091.4308 | 22.4 | 50.9 | 748 |  |  | 2020-09-14 | B90631¦Crown office 2¦¦Sep-17-2020 10:20
2020-09-17 10:21 | 44091.4312 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 4 top |  | 1 | 20 | 57 | 398 | 21 | 51 | 435 |  | 2020-09-17 10:21 | 44091.4312 | 21 | 51 | 435 |  |  | 2020-09-14 | B19570¦Stairwell 4 top ¦¦Sep-17-2020 10:20
2020-09-17 10:21 | 44091.4312 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom b 1 |  | 0 | 19.7 | 53.8 | 397 | 22.1 | 43.3 | 409 |  | 2020-09-17 10:21 | 44091.4312 | 22.1 | 43.3 | 409 |  |  | 2020-09-14 | Pearso¦Ballroom b 1 ¦¦Sep-17-2020 10:20
2020-09-17 10:21 | 44091.4313 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 front left |  | 2 | 15 | 72 | 367 | 22 | 46 | 404 |  | 2020-09-17 10:21 | 44091.4313 | 22 | 46 | 404 |  |  | 2020-09-14 | B20772¦H16 front left¦¦Sep-17-2020 10:21
2020-09-17 10:21 | 44091.4314 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | SEATING 13 |  | 0 | 19 | 57 | 420 | 23 | 44 | 440 |  | 2020-09-17 10:21 | 44091.4314 | 23 | 44 | 440 |  |  | 2020-09-14 | B70740¦SEATING 13¦¦Sep-17-2020 10:21
2020-09-17 10:22 | 44091.4316 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Interview Room 2 |  | 0 | 18.1 | 59.8 | 431 | 21.9 | 51.9 | 601 |  | 2020-09-17 10:22 | 44091.4316 | 21.9 | 51.9 | 601 |  |  | 2020-09-14 | B10577¦Interview Room 2¦¦Sep-17-2020 10:21
2020-09-17 10:22 | 44091.4317 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Case management |  | 5 | 13.7 | 69.4 | 419 | 22.3 | 48.3 | 846 |  | 2020-09-17 10:22 | 44091.4317 | 22.3 | 48.3 | 846 |  |  | 2020-09-14 | B90631¦Case management ¦¦Sep-17-2020 10:21
2020-09-17 10:22 | 44091.4319 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 12 |  | 0 | 19 | 57 | 440 | 22.5 | 44 | 450 |  | 2020-09-17 10:22 | 44091.4319 | 22.5 | 44 | 450 |  |  | 2020-09-14 | B70740¦12¦¦Sep-17-2020 10:21
2020-09-17 10:22 | 44091.4322 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | North hallway |  | 0 | 17 | 65 | 371 | 22 | 47 | 392 |  | 2020-09-17 10:22 | 44091.4322 | 22 | 47 | 392 |  |  | 2020-09-14 | B20603¦North hallway¦¦Sep-17-2020 10:22
2020-09-17 10:22 | 44091.4322 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 South |  | 0 | 18.1 | 59.8 | 431 | 21.9 | 51.3 | 602 |  | 2020-09-17 10:22 | 44091.4322 | 21.9 | 51.3 | 602 |  |  | 2020-09-14 | B10577¦Courtroom 3 South ¦¦Sep-17-2020 10:22
2020-09-17 10:23 | 44091.4325 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Lunch room |  | 0 | 13.7 | 69.4 | 419 | 21.5 | 50.9 | 580 |  | 2020-09-17 10:23 | 44091.4325 | 21.5 | 50.9 | 580 |  |  | 2020-09-14 | B90631¦Lunch room ¦¦Sep-17-2020 10:22
2020-09-17 10:23 | 44091.4326 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN AREA |  | 2 | 19 | 57 | 420 | 21.8 | 41 | 460 |  | 2020-09-17 10:23 | 44091.4326 | 21.8 | 41 | 460 |  |  | 2020-09-14 | B70740¦MAIN AREA¦¦Sep-17-2020 10:22
2020-09-17 10:23 | 44091.4327 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtrrom 3 East |  | 0 | 18.1 | 59.8 | 431 | 21.8 | 51 | 540 |  | 2020-09-17 10:23 | 44091.4327 | 21.8 | 51 | 540 |  |  | 2020-09-14 | B10577¦Courtrrom 3 East¦¦Sep-17-2020 10:23
2020-09-17 10:24 | 44091.4331 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN OFFICE |  | 2 | 19 | 57 | 440 | 22.1 | 49 | 420 |  | 2020-09-17 10:24 | 44091.4331 | 22.1 | 49 | 420 |  |  | 2020-09-14 | B70740¦MAIN OFFICE¦¦Sep-17-2020 10:23
2020-09-17 10:24 | 44091.4333 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 North |  | 1 | 18.1 | 59.8 | 431 | 21.8 | 52.2 | 474 |  | 2020-09-17 10:24 | 44091.4333 | 21.8 | 52.2 | 474 |  |  | 2020-09-14 | B10577¦Courtroom 1 North¦¦Sep-17-2020 10:24
2020-09-17 10:25 | 44091.4339 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Vwap waiting room |  | 0 | 13.7 | 69.4 | 419 | 21.2 | 51.4 | 497 |  | 2020-09-17 10:25 | 44091.4339 | 21.2 | 51.4 | 497 |  |  | 2020-09-14 | B90631¦Vwap waiting room ¦¦Sep-17-2020 10:24
2020-09-17 10:25 | 44091.434 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Tribunal |  | 2 | 17 | 65 | 371 | 22 | 48 | 413 |  | 2020-09-17 10:25 | 44091.434 | 22 | 48 | 413 |  |  | 2020-09-14 | B20603¦Tribunal¦¦Sep-17-2020 10:24
2020-09-17 10:25 | 44091.4341 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 West |  | 0 | 18.1 | 59.8 | 431 | 21.7 | 51.4 | 494 |  | 2020-09-17 10:25 | 44091.4341 | 21.7 | 51.4 | 494 |  |  | 2020-09-14 | B10577¦Courtroom 3 West¦¦Sep-17-2020 10:25
2020-09-17 10:27 | 44091.4351 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom b 2 |  | 0 | 19.7 | 53.8 | 397 | 21.1 | 47.5 | 408 |  | 2020-09-17 10:26 | 44091.4351 | 21.1 | 47.5 | 408 |  |  | 2020-09-14 | Pearso¦Ballroom b 2 ¦¦Sep-17-2020 10:26
2020-09-17 10:27 | 44091.4353 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Judges chamber |  | 0 | 13.7 | 69.4 | 419 | 21 | 51.6 | 466 |  | 2020-09-17 10:27 | 44091.4353 | 21 | 51.6 | 466 |  |  | 2020-09-14 | B90631¦Judges chamber ¦¦Sep-17-2020 10:26
2020-09-17 10:28 | 44091.4358 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Open space |  | 2 | 17 | 65 | 371 | 22 | 47 | 401 |  | 2020-09-17 10:28 | 44091.4358 | 22 | 47 | 401 |  |  | 2020-09-14 | B20603¦Open space¦¦Sep-17-2020 10:27
2020-09-17 10:28 | 44091.436 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom b 3 |  | 0 | 19.7 | 53.8 | 397 | 20.8 | 49.5 | 408 |  | 2020-09-17 10:28 | 44091.436 | 20.8 | 49.5 | 408 |  |  | 2020-09-14 | Pearso¦Ballroom b 3¦¦Sep-17-2020 10:27
2020-09-17 10:28 | 44091.4363 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom 1 |  | 0 | 13.7 | 69.4 | 419 | 21.6 | 51.6 | 544 |  | 2020-09-17 10:28 | 44091.4363 | 21.6 | 51.6 | 544 |  |  | 2020-09-14 | B90631¦Courtroom 1¦¦Sep-17-2020 10:28
2020-09-17 10:29 | 44091.4365 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H17 back right |  | 2 | 15 | 72 | 367 | 22 | 46 | 406 |  | 2020-09-17 10:29 | 44091.4365 | 22 | 46 | 406 |  |  | 2020-09-14 | B20772¦H17 back right¦¦Sep-17-2020 10:28
2020-09-17 10:29 | 44091.4369 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom c |  | 0 | 19.7 | 53.8 | 397 | 21.2 | 43.9 | 405 |  | 2020-09-17 10:29 | 44091.4369 | 21.2 | 43.9 | 405 |  |  | 2020-09-14 | Pearso¦Ballroom c ¦¦Sep-17-2020 10:29
2020-09-17 10:30 | 44091.4372 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 back left |  | 2 | 15 | 72 | 367 | 22 | 46 | 421 |  | 2020-09-17 10:30 | 44091.4372 | 22 | 46 | 421 |  |  | 2020-09-14 | B20772¦H16 back left ¦¦Sep-17-2020 10:29
2020-09-17 10:31 | 44091.4379 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom 1 waiting room |  | 0 | 13.7 | 69.4 | 419 | 21.2 | 51.8 | 690 |  | 2020-09-17 10:31 | 44091.4379 | 21.2 | 51.8 | 690 |  |  | 2020-09-14 | B90631¦Courtroom 1 waiting room ¦¦Sep-17-2020 10:30
2020-09-17 10:31 | 44091.438 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom c 1 |  | 0 | 19.7 | 53.8 | 397 | 21.3 | 42.6 | 451 |  | 2020-09-17 10:31 | 44091.438 | 21.3 | 42.6 | 451 |  |  | 2020-09-14 | Pearso¦Ballroom c 1 ¦¦Sep-17-2020 10:30
2020-09-17 10:31 | 44091.4381 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Printing room |  | 0 | 17 | 65 | 371 | 22 | 47 | 397 |  | 2020-09-17 10:31 | 44091.4381 | 22 | 47 | 397 |  |  | 2020-09-14 | B20603¦Printing room¦¦Sep-17-2020 10:30
2020-09-17 10:32 | 44091.4389 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Judges lounge |  | 0 | 13.7 | 69.4 | 419 | 21 | 51.7 | 534 |  | 2020-09-17 10:32 | 44091.4389 | 21 | 51.7 | 534 |  |  | 2020-09-14 | B90631¦Judges lounge ¦¦Sep-17-2020 10:32
2020-09-17 10:32 | 44091.4392 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom c 2 |  | 0 | 19.7 | 53.8 | 397 | 19.9 | 42.4 | 458 |  | 2020-09-17 10:32 | 44091.4392 | 19.9 | 42.4 | 458 |  |  | 2020-09-14 | Pearso¦Ballroom c 2¦¦Sep-17-2020 10:32
2020-09-17 10:33 | 44091.4396 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 615 |  | 1 | 17 | 65 | 371 | 23 | 46 | 406 |  | 2020-09-17 10:33 | 44091.4396 | 23 | 46 | 406 |  |  | 2020-09-14 | B20603¦615¦¦Sep-17-2020 10:33
2020-09-17 10:33 | 44091.4398 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom c 3 |  | 0 | 19.7 | 53.8 | 397 | 19.6 | 43.6 | 430 |  | 2020-09-17 10:33 | 44091.4398 | 19.6 | 43.6 | 430 |  |  | 2020-09-14 | Pearso¦Ballroom c 3 ¦¦Sep-17-2020 10:33
2020-09-17 10:35 | 44091.4412 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 616 |  | 0 | 17 | 65 | 371 | 22 | 46 | 393 |  | 2020-09-17 10:35 | 44091.4412 | 22 | 46 | 393 |  |  | 2020-09-14 | B20603¦616¦¦Sep-17-2020 10:35
2020-09-17 10:38 | 44091.4427 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom d |  | 0 | 19.7 | 53.8 | 397 | 20.3 | 43.6 | 406 |  | 2020-09-17 10:38 | 44091.4427 | 20.3 | 43.6 | 406 |  |  | 2020-09-14 | Pearso¦Ballroom d ¦¦Sep-17-2020 10:37
2020-09-17 10:39 | 44091.4436 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom d 1 |  | 0 | 19.7 | 53.8 | 397 | 20.1 | 42.9 | 406 |  | 2020-09-17 10:39 | 44091.4436 | 20.1 | 42.9 | 406 |  |  | 2020-09-14 | Pearso¦Ballroom d 1¦¦Sep-17-2020 10:38
2020-09-17 10:40 | 44091.4443 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 626 |  | 0 | 17 | 65 | 371 | 22 | 46 | 384 |  | 2020-09-17 10:40 | 44091.4443 | 22 | 46 | 384 |  |  | 2020-09-14 | B20603¦626¦¦Sep-17-2020 10:39
2020-09-17 10:42 | 44091.4456 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 612 |  | 0 | 17 | 65 | 371 | 23 | 46 | 385 |  | 2020-09-17 10:42 | 44091.4456 | 23 | 46 | 385 |  |  | 2020-09-14 | B20603¦612¦¦Sep-17-2020 10:41
2020-09-17 10:42 | 44091.4458 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom d 2 |  | 0 | 19.7 | 53.8 | 397 | 20.1 | 42.9 | 406 |  | 2020-09-17 10:42 | 44091.4458 | 20.1 | 42.9 | 406 |  |  | 2020-09-14 | Pearso¦Ballroom d 2¦¦Sep-17-2020 10:41
2020-09-17 10:42 | 44091.4462 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 0 | 14 | 53 | 411 | 15.6 | 62.3 | 477 |  | 2020-09-17 10:42 | 44091.4462 | 15.6 | 62.3 | 477 |  | caution | 2020-09-14 | B16187¦Court 3¦¦Sep-17-2020 10:42
2020-09-17 10:43 | 44091.4466 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 0 | 14 | 53 | 411 | 16.3 | 61 | 527 |  | 2020-09-17 10:43 | 44091.4466 | 16.3 | 61 | 527 |  | caution | 2020-09-14 | B16187¦Court 3¦¦Sep-17-2020 10:43
2020-09-17 10:43 | 44091.4468 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Administrative office |  | 4 | 16 | 60 | 399 | 20.7 | 51.7 | 478 |  | 2020-09-17 10:43 | 44091.4468 | 20.7 | 51.7 | 478 |  |  | 2020-09-14 | B90558¦Administrative office¦¦Sep-17-2020 10:43
2020-09-17 10:43 | 44091.4468 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | 2nd floor Crown Attorney office |  | 0 | 14.8 | 72.1 | 408 | 21.3 | 53.5 | 442 | No | 2020-09-17 10:43 | 44091.4468 | 21.3 | 53.5 | 442 |  |  | 2020-09-14 | B20478¦2nd floor Crown Attorney office ¦¦Sep-17-2020 10:43
2020-09-17 10:44 | 44091.4471 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 0 | 14 | 53 | 411 | 18 | 55.6 | 531 |  | 2020-09-17 10:44 | 44091.4471 | 18 | 55.6 | 531 |  |  | 2020-09-14 | B16187¦Court 3¦¦Sep-17-2020 10:43
2020-09-17 10:44 | 44091.4474 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Entrance |  | 0 | 14 | 53 | 411 | 13.2 | 67.2 | 404 |  | 2020-09-17 10:44 | 44091.4474 | 13.2 | 67.2 | 404 |  | high | 2020-09-14 | B16187¦Entrance ¦¦Sep-17-2020 10:44
2020-09-17 10:44 | 44091.4475 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Open space 2 |  | 1 | 17 | 65 | 371 | 23 | 46 | 406 |  | 2020-09-17 10:44 | 44091.4475 | 23 | 46 | 406 |  |  | 2020-09-14 | B20603¦Open space 2¦¦Sep-17-2020 10:44
2020-09-17 10:45 | 44091.4477 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom d 3 |  | 0 | 19.7 | 53.8 | 397 | 20.1 | 45.1 | 406 |  | 2020-09-17 10:45 | 44091.4477 | 20.1 | 45.1 | 406 |  |  | 2020-09-14 | Pearso¦Ballroom d 3 ¦¦Sep-17-2020 10:44
2020-09-17 10:45 | 44091.4478 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 4 |  | 0 | 14 | 53 | 411 | 19.3 | 49.2 | 480 |  | 2020-09-17 10:45 | 44091.4478 | 19.3 | 49.2 | 480 |  |  | 2020-09-14 | B16187¦Court 4¦¦Sep-17-2020 10:44
2020-09-17 10:45 | 44091.4482 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 14 | 53 | 411 | 20.8 | 45.2 | 445 |  | 2020-09-17 10:45 | 44091.4482 | 20.8 | 45.2 | 445 |  |  | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 10:45
2020-09-17 10:45 | 44091.4482 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Waiting area near h11 entrance |  | 2 | 15 | 72 | 367 | 22 | 45 | 390 |  | 2020-09-17 10:45 | 44091.4482 | 22 | 45 | 390 |  |  | 2020-09-14 | B20772¦Waiting area near h11 entrance¦¦Sep-17-2020 10:45
2020-09-17 10:46 | 44091.4486 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 14 | 53 | 411 | 20.6 | 42.1 | 515 |  | 2020-09-17 10:46 | 44091.4486 | 20.6 | 42.1 | 515 |  |  | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 10:45
2020-09-17 10:46 | 44091.4488 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Waiting area opposite side of h11 |  | 2 | 15 | 72 | 367 | 22 | 45 | 381 |  | 2020-09-17 10:46 | 44091.4488 | 22 | 45 | 381 |  |  | 2020-09-14 | B20772¦Waiting area opposite side of h11 ¦¦Sep-17-2020 10:46
2020-09-17 10:46 | 44091.4489 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 14 | 53 | 411 | 20.8 | 42.7 | 514 |  | 2020-09-17 10:46 | 44091.4489 | 20.8 | 42.7 | 514 |  |  | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 10:46
2020-09-17 10:47 | 44091.449 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom e |  | 0 | 19.7 | 53.8 | 397 | 19.1 | 45.1 | 400 |  | 2020-09-17 10:47 | 44091.449 | 19.1 | 45.1 | 400 |  |  | 2020-09-14 | Pearso¦Ballroom e¦¦Sep-17-2020 10:46
2020-09-17 10:47 | 44091.4493 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Interview room |  | 2 | 15 | 72 | 367 | 22 | 45 | 384 |  | 2020-09-17 10:47 | 44091.4493 | 22 | 45 | 384 |  |  | 2020-09-14 | B20772¦Interview room¦¦Sep-17-2020 10:47
2020-09-17 10:47 | 44091.4493 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 14 | 53 | 411 | 20.4 | 42.4 | 450 |  | 2020-09-17 10:47 | 44091.4493 | 20.4 | 42.4 | 450 |  |  | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 10:47
2020-09-17 10:47 | 44091.4494 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Hallway room b |  | 0 | 17 | 65 | 371 | 23 | 45 | 394 |  | 2020-09-17 10:47 | 44091.4494 | 23 | 45 | 394 |  |  | 2020-09-14 | B20603¦Hallway room b¦¦Sep-17-2020 10:47
2020-09-17 10:48 | 44091.4497 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom e 1 |  | 0 | 19.7 | 53.8 | 397 | 18.8 | 48.7 | 411 |  | 2020-09-17 10:48 | 44091.4497 | 18.8 | 48.7 | 411 |  |  | 2020-09-14 | Pearso¦Ballroom e 1¦¦Sep-17-2020 10:47
2020-09-17 10:48 | 44091.4498 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Waiting area 2 floor |  | 0 | 16 | 60 | 399 | 20.7 | 50.1 | 440 |  | 2020-09-17 10:48 | 44091.4498 | 20.7 | 50.1 | 440 |  |  | 2020-09-14 | B90558¦Waiting area 2 floor¦¦Sep-17-2020 10:47
2020-09-17 10:48 | 44091.4499 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 1 |  | 0 | 14 | 53 | 411 | 20.5 | 38.5 | 444 |  | 2020-09-17 10:48 | 44091.4499 | 20.5 | 38.5 | 444 |  | caution | 2020-09-14 | B16187¦Court 1¦¦Sep-17-2020 10:47
2020-09-17 10:49 | 44091.4504 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 14 | 53 | 411 | 20.8 | 40.8 | 434 |  | 2020-09-17 10:49 | 44091.4504 | 20.8 | 40.8 | 434 |  |  | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 10:48
2020-09-17 10:49 | 44091.4509 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Opp office |  | 0 | 14 | 53 | 411 | 20.8 | 40.3 | 446 |  | 2020-09-17 10:49 | 44091.4509 | 20.8 | 40.3 | 446 |  |  | 2020-09-14 | B16187¦Opp office¦¦Sep-17-2020 10:49
2020-09-17 10:50 | 44091.4511 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom b |  | 0 | 17 | 65 | 371 | 23 | 45 | 380 |  | 2020-09-17 10:50 | 44091.4511 | 23 | 45 | 380 |  |  | 2020-09-14 | B20603¦Courtroom b¦¦Sep-17-2020 10:49
2020-09-17 10:50 | 44091.4513 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Opp office |  | 0 | 14 | 53 | 411 | 20.9 | 40.2 | 452 |  | 2020-09-17 10:50 | 44091.4513 | 20.9 | 40.2 | 452 |  |  | 2020-09-14 | B16187¦Opp office ¦¦Sep-17-2020 10:49
2020-09-17 10:50 | 44091.4516 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom e 2 |  | 0 | 19.7 | 53.8 | 397 | 18.2 | 47.7 | 410 |  | 2020-09-17 10:50 | 44091.4516 | 18.2 | 47.7 | 410 |  |  | 2020-09-14 | Pearso¦Ballroom e 2¦¦Sep-17-2020 10:50
2020-09-17 10:50 | 44091.4517 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Cell block |  | 1 | 14.5 | 74.7 | 397 | 23.1 | 48.8 | 455 |  | 2020-09-17 10:50 | 44091.4517 | 23.1 | 48.8 | 455 |  |  | 2020-09-14 | B20494¦Cell block¦¦Sep-17-2020 10:50
2020-09-17 10:51 | 44091.4518 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Crown attorney |  | 0 | 14 | 53 | 411 | 21.3 | 39.2 | 460 |  | 2020-09-17 10:51 | 44091.4518 | 21.3 | 39.2 | 460 |  | caution | 2020-09-14 | B16187¦Crown attorney ¦¦Sep-17-2020 10:50
2020-09-17 10:51 | 44091.4522 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 2 |  | 0 | 14 | 53 | 411 | 21.1 | 37.8 | 461 |  | 2020-09-17 10:51 | 44091.4522 | 21.1 | 37.8 | 461 |  | caution | 2020-09-14 | B16187¦Court 2¦¦Sep-17-2020 10:51
2020-09-17 10:51 | 44091.4523 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 1 |  | 1 | 15.2 | 70 | 377 | 23.4 | 43.1 | 396 |  | 2020-09-17 10:51 | 44091.4523 | 23.4 | 43.1 | 396 |  |  | 2020-09-14 | B20494¦Courtroom 1¦¦Sep-17-2020 10:51
2020-09-17 10:51 | 44091.4523 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 3 gallery |  | 0 | 15 | 68 | 421 | 21.4 | 46.4 | 470 | No | 2020-09-17 10:51 | 44091.4523 | 21.4 | 46.4 | 470 |  |  | 2020-09-14 | B20151¦Court room 3 gallery ¦¦Sep-17-2020 10:51
2020-09-17 10:52 | 44091.4525 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 2 |  | 0 | 14 | 53 | 411 | 21.5 | 37.6 | 453 |  | 2020-09-17 10:52 | 44091.4525 | 21.5 | 37.6 | 453 |  | caution | 2020-09-14 | B16187¦Court 2¦¦Sep-17-2020 10:51
2020-09-17 10:52 | 44091.4526 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom#1 |  | 2 | 16 | 60 | 399 | 21.5 | 48.5 | 433 |  | 2020-09-17 10:52 | 44091.4526 | 21.5 | 48.5 | 433 |  |  | 2020-09-14 | B90558¦Courtroom#1¦¦Sep-17-2020 10:51
2020-09-17 10:52 | 44091.4527 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom a |  | 0 | 17 | 65 | 371 | 23 | 44 | 378 |  | 2020-09-17 10:52 | 44091.4527 | 23 | 44 | 378 |  |  | 2020-09-14 | B20603¦Courtroom a¦¦Sep-17-2020 10:51
2020-09-17 10:52 | 44091.4528 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Front lobby |  | 3 | 17.8 | 47 | 390 | 20 | 57.4 | 469 |  | 2020-09-17 10:52 | 44091.4528 | 20 | 57.4 | 469 |  |  | 2020-09-14 | B11228¦Front lobby¦¦Sep-17-2020 10:52
2020-09-17 10:52 | 44091.4529 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 14 | 53 | 411 | 21.1 | 40 | 453 |  | 2020-09-17 10:52 | 44091.4529 | 21.1 | 40 | 453 |  | caution | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 10:52
2020-09-17 10:52 | 44091.4529 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom e 3 |  | 0 | 19.7 | 53.8 | 397 | 18.6 | 47.8 | 403 |  | 2020-09-17 10:52 | 44091.4529 | 18.6 | 47.8 | 403 |  |  | 2020-09-14 | Pearso¦Ballroom e 3¦¦Sep-17-2020 10:52
2020-09-17 10:53 | 44091.4532 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 3 |  | 1 | 15.2 | 70 | 377 | 23 | 48.8 | 466 |  | 2020-09-17 10:53 | 44091.4532 | 23 | 48.8 | 466 |  |  | 2020-09-14 | B20494¦Courtroom 3¦¦Sep-17-2020 10:52
2020-09-17 10:53 | 44091.4532 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 3 judge |  | 0 | 15 | 68 | 421 | 21.7 | 45.5 | 476 | No | 2020-09-17 10:53 | 44091.4532 | 21.7 | 45.5 | 476 |  |  | 2020-09-14 | B20151¦Court room 3 judge ¦¦Sep-17-2020 10:52
2020-09-17 10:53 | 44091.4533 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 14 | 53 | 411 | 21.5 | 39.7 | 457 |  | 2020-09-17 10:53 | 44091.4533 | 21.5 | 39.7 | 457 |  | caution | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 10:52
2020-09-17 10:53 | 44091.4534 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 306 |  | 0 | 11 | 72 | 385 | 23 | 43.1 | 418 | No | 2020-09-17 10:53 | 44091.4534 | 23 | 43.1 | 418 |  |  | 2020-09-14 | B14660¦306¦¦Sep-17-2020 10:52
2020-09-17 10:53 | 44091.4538 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 14 | 53 | 411 | 21.2 | 40 | 454 |  | 2020-09-17 10:53 | 44091.4538 | 21.2 | 40 | 454 |  | caution | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 10:53
2020-09-17 10:53 | 44091.4538 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Front stairs |  | 1 | 17.9 | 49 | 390 | 20.3 | 56 | 500 |  | 2020-09-17 10:53 | 44091.4538 | 20.3 | 56 | 500 |  |  | 2020-09-14 | B11228¦Front stairs¦¦Sep-17-2020 10:53
2020-09-17 10:54 | 44091.454 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom f |  | 0 | 19.7 | 53.8 | 397 | 19.4 | 57.4 | 398 |  | 2020-09-17 10:54 | 44091.454 | 19.4 | 57.4 | 398 |  |  | 2020-09-14 | Pearso¦Ballroom f¦¦Sep-17-2020 10:53
2020-09-17 10:54 | 44091.4541 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 14 | 53 | 411 | 21.8 | 38.1 | 462 |  | 2020-09-17 10:54 | 44091.4541 | 21.8 | 38.1 | 462 |  | caution | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 10:53
2020-09-17 10:54 | 44091.4543 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | South hallway |  | 0 | 17 | 65 | 371 | 23 | 45 | 395 |  | 2020-09-17 10:54 | 44091.4543 | 23 | 45 | 395 |  |  | 2020-09-14 | B20603¦South hallway¦¦Sep-17-2020 10:54
2020-09-17 10:54 | 44091.4544 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 2nd floor SE hall |  | 1 | 14.5 | 74.7 | 397 | 23 | 47.7 | 532 |  | 2020-09-17 10:54 | 44091.4544 | 23 | 47.7 | 532 |  |  | 2020-09-14 | B20494¦2nd floor SE hall¦¦Sep-17-2020 10:54
2020-09-17 10:54 | 44091.4545 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Upper courtroom |  | 1 | 17.9 | 49 | 390 | 21.8 | 54.7 | 434 |  | 2020-09-17 10:54 | 44091.4545 | 21.8 | 54.7 | 434 |  |  | 2020-09-14 | B11228¦Upper courtroom¦¦Sep-17-2020 10:54
2020-09-17 10:55 | 44091.4546 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 14 | 53 | 411 | 22 | 38.4 | 438 |  | 2020-09-17 10:55 | 44091.4546 | 22 | 38.4 | 438 |  | caution | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 10:54
2020-09-17 10:55 | 44091.4547 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom f 1 |  | 0 | 19.7 | 53.8 | 397 | 19.8 | 53.9 | 402 |  | 2020-09-17 10:55 | 44091.4547 | 19.8 | 53.9 | 402 |  |  | 2020-09-14 | Pearso¦Ballroom f 1 ¦¦Sep-17-2020 10:54
2020-09-17 10:55 | 44091.4549 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | TC office |  | 0 | 16 | 60 | 399 | 23.2 | 48.6 | 430 |  | 2020-09-17 10:55 | 44091.4549 | 23.2 | 48.6 | 430 |  |  | 2020-09-14 | B90558¦TC office¦¦Sep-17-2020 10:54
2020-09-17 10:55 | 44091.4549 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Crown attorneys office |  | 4 | 19 | 61.3 | 407 | 22.8 | 46.5 | 438 | No | 2020-09-17 10:55 | 44091.4549 | 22.8 | 46.5 | 438 |  |  | 2020-09-14 | B21128¦Crown attorneys office ¦¦Sep-17-2020 10:55
2020-09-17 10:55 | 44091.455 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 14 | 53 | 411 | 22.4 | 38 | 445 |  | 2020-09-17 10:55 | 44091.455 | 22.4 | 38 | 445 |  | caution | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 10:55
2020-09-17 10:55 | 44091.4551 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Second floor hallway nw |  | 1 | 15.2 | 70 | 377 | 22.2 | 49 | 496 |  | 2020-09-17 10:55 | 44091.4551 | 22.2 | 49 | 496 |  |  | 2020-09-14 | B20494¦Second floor hallway nw¦¦Sep-17-2020 10:55
2020-09-17 10:56 | 44091.4553 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Upper office |  | 1 | 17.9 | 49 | 390 | 22.4 | 52.2 | 433 |  | 2020-09-17 10:56 | 44091.4553 | 22.4 | 52.2 | 433 |  |  | 2020-09-14 | B11228¦Upper office¦¦Sep-17-2020 10:55
2020-09-17 10:56 | 44091.4553 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom f 2 |  | 0 | 19.7 | 53.8 | 397 | 20.1 | 55.3 | 402 |  | 2020-09-17 10:56 | 44091.4553 | 20.1 | 55.3 | 402 |  |  | 2020-09-14 | Pearso¦Ballroom f 2 ¦¦Sep-17-2020 10:55
2020-09-17 10:56 | 44091.4554 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Cell waiting area |  | 0 | 14 | 53 | 411 | 21.6 | 40.2 | 480 |  | 2020-09-17 10:56 | 44091.4554 | 21.6 | 40.2 | 480 |  |  | 2020-09-14 | B16187¦Cell waiting area¦¦Sep-17-2020 10:55
2020-09-17 10:56 | 44091.4554 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 1 |  | 0 | 15 | 68 | 421 | 21.9 | 41.4 | 423 | No | 2020-09-17 10:56 | 44091.4554 | 21.9 | 41.4 | 423 |  |  | 2020-09-14 | B20151¦Court room 1¦¦Sep-17-2020 10:55
2020-09-17 10:56 | 44091.4557 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 14 | 53 | 411 | 21.4 | 40.3 | 436 |  | 2020-09-17 10:56 | 44091.4557 | 21.4 | 40.3 | 436 |  |  | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 10:56
2020-09-17 10:57 | 44091.456 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Criminal justice office |  | 2 | 14.5 | 74.7 | 397 | 23.1 | 47.2 | 541 |  | 2020-09-17 10:57 | 44091.456 | 23.1 | 47.2 | 541 |  |  | 2020-09-14 | B20494¦Criminal justice office¦¦Sep-17-2020 10:56
2020-09-17 10:57 | 44091.4561 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 128 |  | 0 | 14 | 54 | 378 | 17 | 61.2 | 393 | No | 2020-09-17 10:57 | 44091.4561 | 17 | 61.2 | 393 |  | caution | 2020-09-14 | B14660¦128¦¦Sep-17-2020 10:56
2020-09-17 10:57 | 44091.4561 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Upper hall |  | 1 | 17.9 | 49 | 390 | 22.4 | 52 | 439 |  | 2020-09-17 10:57 | 44091.4561 | 22.4 | 52 | 439 |  |  | 2020-09-14 | B11228¦Upper hall¦¦Sep-17-2020 10:56
2020-09-17 10:57 | 44091.4561 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Basement hallway |  | 0 | 14 | 53 | 411 | 21.8 | 44 | 481 |  | 2020-09-17 10:57 | 44091.4561 | 21.8 | 44 | 481 |  |  | 2020-09-14 | B16187¦Basement hallway¦¦Sep-17-2020 10:56
2020-09-17 10:57 | 44091.4562 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice O'Brien office |  | 0 | 16 | 60 | 399 | 20.5 | 48.5 | 436 | Dehumidifier running set at 17 | 2020-09-17 10:57 | 44091.4562 | 20.5 | 48.5 | 436 |  |  | 2020-09-14 | B90558¦Justice O'Brien office¦¦Sep-17-2020 10:56
2020-09-17 10:58 | 44091.4567 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom f 3 |  | 0 | 19.7 | 53.8 | 397 | 20.2 | 54 | 403 |  | 2020-09-17 10:58 | 44091.4567 | 20.2 | 54 | 403 |  |  | 2020-09-14 | Pearso¦Ballroom f 3 ¦¦Sep-17-2020 10:57
2020-09-17 10:58 | 44091.4568 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family justice waiting room |  | 1 | 15.2 | 70 | 377 | 22.3 | 49.6 | 492 |  | 2020-09-17 10:58 | 44091.4568 | 22.3 | 49.6 | 492 |  |  | 2020-09-14 | B20494¦Family justice waiting room¦¦Sep-17-2020 10:57
2020-09-17 10:58 | 44091.4568 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Back stairs |  | 1 | 17.9 | 49 | 390 | 23 | 51.2 | 473 |  | 2020-09-17 10:58 | 44091.4568 | 23 | 51.2 | 473 |  |  | 2020-09-14 | B11228¦Back stairs¦¦Sep-17-2020 10:57
2020-09-17 10:59 | 44091.4574 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Policeroom 1 |  | 0 | 19.7 | 53.8 | 397 | 20.3 | 47.3 | 400 |  | 2020-09-17 10:59 | 44091.4574 | 20.3 | 47.3 | 400 |  |  | 2020-09-14 | Pearso¦Policeroom 1 ¦¦Sep-17-2020 10:58
2020-09-17 10:59 | 44091.4575 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin office |  | 2 | 15 | 68 | 421 | 22 | 48 | 657 | No | 2020-09-17 10:59 | 44091.4575 | 22 | 48 | 657 |  |  | 2020-09-14 | B20151¦Admin office ¦¦Sep-17-2020 10:58
2020-09-17 10:59 | 44091.4577 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Lower courtroom lobby |  | 1 | 17.9 | 49 | 390 | 22.7 | 50.8 | 468 |  | 2020-09-17 10:59 | 44091.4577 | 22.7 | 50.8 | 468 |  |  | 2020-09-14 | B11228¦Lower courtroom lobby¦¦Sep-17-2020 10:59
2020-09-17 10:59 | 44091.4577 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice Wheeler office |  | 0 | 16 | 60 | 399 | 20.3 | 51.4 | 444 |  | 2020-09-17 10:59 | 44091.4577 | 20.3 | 51.4 | 444 |  |  | 2020-09-14 | B90558¦Justice Wheeler office¦¦Sep-17-2020 10:59
2020-09-17 10:59 | 44091.4577 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 2 |  | 2 | 14.5 | 74.7 | 397 | 23 | 45 | 442 |  | 2020-09-17 10:59 | 44091.4577 | 23 | 45 | 442 |  |  | 2020-09-14 | B20494¦Courtroom 2¦¦Sep-17-2020 10:59
2020-09-17 10:59 | 44091.4577 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice Wheeler office |  | 0 | 16 | 60 | 399 | 20.3 | 51.4 | 444 |  | 2020-09-17 10:59 | 44091.4577 | 20.3 | 51.4 | 444 |  |  | 2020-09-14 | B90558¦Justice Wheeler office¦¦Sep-17-2020 10:59
2020-09-17 10:59 | 44091.4578 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Front door entrance |  | 10 | 21.4 | 42.5 | 404 | 23.4 | 45.8 | 517 | No | 2020-09-17 10:59 | 44091.4578 | 23.4 | 45.8 | 517 |  |  | 2020-09-14 | B21128¦Front door entrance ¦¦Sep-17-2020 10:59
2020-09-17 10:59 | 44091.4578 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 001 |  | 0 | 15 | 54 | 378 | 19.2 | 52.2 | 403 | No | 2020-09-17 10:59 | 44091.4578 | 19.2 | 52.2 | 403 |  |  | 2020-09-14 | B14660¦001¦¦Sep-17-2020 10:59
2020-09-17 11:00 | 44091.4583 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Policeroom 2 |  | 0 | 19.7 | 53.8 | 397 | 20.2 | 47.1 | 399 |  | 2020-09-17 11:00 | 44091.4583 | 20.2 | 47.1 | 399 |  |  | 2020-09-14 | Pearso¦Policeroom 2 ¦¦Sep-17-2020 10:59
2020-09-17 11:00 | 44091.4583 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family court office |  | 3 | 15.2 | 70 | 377 | 22.9 | 47.6 | 508 |  | 2020-09-17 11:00 | 44091.4583 | 22.9 | 47.6 | 508 |  |  | 2020-09-14 | B20494¦Family court office ¦¦Sep-17-2020 11:00
2020-09-17 11:00 | 44091.4584 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Lower courtroom |  | 1 | 17.9 | 49 | 390 | 21.8 | 51 | 413 |  | 2020-09-17 11:00 | 44091.4584 | 21.8 | 51 | 413 |  |  | 2020-09-14 | B11228¦Lower courtroom¦¦Sep-17-2020 11:00
2020-09-17 11:00 | 44091.4585 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin supervisor |  | 0 | 15 | 68 | 421 | 22.1 | 48 | 661 | No | 2020-09-17 11:00 | 44091.4585 | 22.1 | 48 | 661 |  |  | 2020-09-14 | B20151¦Admin supervisor ¦¦Sep-17-2020 11:00
2020-09-17 11:01 | 44091.4588 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 403 |  | 10 | 21.4 | 42.5 | 404 | 23.5 | 42.2 | 544 | No | 2020-09-17 11:01 | 44091.4588 | 23.5 | 42.2 | 544 |  |  | 2020-09-14 | B21128¦403¦¦Sep-17-2020 11:00
2020-09-17 11:01 | 44091.4591 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE CORKERY |  | 1 | 17 | 59 | 450 | 20 | 55 | 493 | YES | 2020-09-17 11:01 | 44091.4591 | 20 | 55 | 493 |  |  | 2020-09-14 | B20022¦JUDGE CORKERY¦¦Sep-17-2020 11:01
2020-09-17 11:01 | 44091.4591 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 028 |  | 0 | 14 | 54 | 378 | 20.6 | 47.8 | 417 | No | 2020-09-17 11:01 | 44091.4591 | 20.6 | 47.8 | 417 |  |  | 2020-09-14 | B14660¦028¦¦Sep-17-2020 11:01
2020-09-17 11:02 | 44091.4595 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Policeroom 3 |  | 0 | 19.7 | 53.8 | 397 | 19.9 | 46.8 | 399 |  | 2020-09-17 11:02 | 44091.4595 | 19.9 | 46.8 | 399 |  |  | 2020-09-14 | Pearso¦Policeroom 3¦¦Sep-17-2020 11:01
2020-09-17 11:02 | 44091.4595 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Office lobby |  | 2 | 17.9 | 49 | 390 | 22.2 | 52 | 508 |  | 2020-09-17 11:02 | 44091.4595 | 22.2 | 52 | 508 |  |  | 2020-09-14 | B11228¦Office lobby¦¦Sep-17-2020 11:01
2020-09-17 11:02 | 44091.4595 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin file |  | 1 | 15 | 68 | 421 | 22.2 | 46.6 | 614 | No | 2020-09-17 11:02 | 44091.4595 | 22.2 | 46.6 | 614 |  |  | 2020-09-14 | B20151¦Admin file ¦¦Sep-17-2020 11:01
2020-09-17 11:02 | 44091.4597 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family court inner office |  | 1 | 15.2 | 70 | 377 | 23.1 | 44.2 | 530 |  | 2020-09-17 11:02 | 44091.4597 | 23.1 | 44.2 | 530 |  |  | 2020-09-14 | B20494¦Family court inner office ¦¦Sep-17-2020 11:02
2020-09-17 11:02 | 44091.4598 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE STAFF ROOM |  | 1 | 17 | 59 | 450 | 20 | 55.3 | 463 | YES | 2020-09-17 11:02 | 44091.4598 | 20 | 55.3 | 463 |  |  | 2020-09-14 | B20022¦JUDGE STAFF ROOM¦¦Sep-17-2020 11:02
2020-09-17 11:03 | 44091.4601 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Office |  | 2 | 17.9 | 49 | 390 | 22.1 | 54 | 514 |  | 2020-09-17 11:03 | 44091.4601 | 22.1 | 54 | 514 |  |  | 2020-09-14 | B11228¦Office¦¦Sep-17-2020 11:02
2020-09-17 11:03 | 44091.4601 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Policeroom 4 |  | 0 | 19.7 | 53.8 | 397 | 20.1 | 47.2 | 409 |  | 2020-09-17 11:03 | 44091.4601 | 20.1 | 47.2 | 409 |  |  | 2020-09-14 | Pearso¦Policeroom 4¦¦Sep-17-2020 11:02
2020-09-17 11:03 | 44091.4604 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Entryway |  | 3 | 18.1 | 74.2 | 413 | 19.3 | 64.5 | 590 |  | 2020-09-17 11:03 | 44091.4604 | 19.3 | 64.5 | 590 |  | caution | 2020-09-14 | B20390¦Entryway¦¦Sep-17-2020 11:02
2020-09-17 11:03 | 44091.4605 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 019 |  | 0 | 14 | 54 | 378 | 21.5 | 46 | 414 | No | 2020-09-17 11:03 | 44091.4605 | 21.5 | 46 | 414 |  |  | 2020-09-14 | B14660¦019¦¦Sep-17-2020 11:03
2020-09-17 11:03 | 44091.4605 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | VISITING JUDGE |  | 1 | 17 | 59 | 450 | 20.4 | 56.6 | 463 | YES | 2020-09-17 11:03 | 44091.4605 | 20.4 | 56.6 | 463 |  |  | 2020-09-14 | B20022¦VISITING JUDGE¦¦Sep-17-2020 11:03
2020-09-17 11:04 | 44091.4608 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 2nd floor NE hall |  | 1 | 14.5 | 74.7 | 397 | 22.9 | 48.1 | 513 |  | 2020-09-17 11:04 | 44091.4608 | 22.9 | 48.1 | 513 |  |  | 2020-09-14 | B20494¦2nd floor NE hall¦¦Sep-17-2020 11:03
2020-09-17 11:04 | 44091.4609 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin waiting area |  | 0 | 15 | 68 | 421 | 21.9 | 43.8 | 503 | No | 2020-09-17 11:04 | 44091.4609 | 21.9 | 43.8 | 503 |  |  | 2020-09-14 | B20151¦Admin waiting area ¦¦Sep-17-2020 11:03
2020-09-17 11:04 | 44091.461 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE INGRAM |  | 1 | 17 | 59 | 450 | 21.2 | 55.1 | 473 | YES | 2020-09-17 11:04 | 44091.461 | 21.2 | 55.1 | 473 |  |  | 2020-09-14 | B20022¦JUDGE INGRAM¦¦Sep-17-2020 11:03
2020-09-17 11:04 | 44091.4614 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 011 |  | 0 | 14 | 54 | 374 | 21.8 | 44.7 | 413 | No | 2020-09-17 11:04 | 44091.4614 | 21.8 | 44.7 | 413 |  |  | 2020-09-14 | B14660¦011¦¦Sep-17-2020 11:04
2020-09-17 11:05 | 44091.4615 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE MCLEOD |  | 1 | 17 | 59 | 450 | 21 | 57.6 | 476 | YES | 2020-09-17 11:05 | 44091.4615 | 21 | 57.6 | 476 |  |  | 2020-09-14 | B20022¦JUDGE MCLEOD¦¦Sep-17-2020 11:04
2020-09-17 11:05 | 44091.4616 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Criminal office |  | 2 | 15.2 | 70 | 377 | 23.3 | 45.4 | 521 |  | 2020-09-17 11:05 | 44091.4616 | 23.3 | 45.4 | 521 |  |  | 2020-09-14 | B20494¦Criminal office¦¦Sep-17-2020 11:04
2020-09-17 11:05 | 44091.4616 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | N.W entrance |  | 2 | 21.4 | 42.5 | 404 | 23.5 | 41.7 | 540 | No | 2020-09-17 11:05 | 44091.4616 | 23.5 | 41.7 | 540 |  |  | 2020-09-14 | B21128¦N.W entrance ¦¦Sep-17-2020 11:04
2020-09-17 11:05 | 44091.4617 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main waiting area |  | 6 | 18.1 | 74.2 | 413 | 20.3 | 60.1 | 504 |  | 2020-09-17 11:05 | 44091.4617 | 20.3 | 60.1 | 504 |  | caution | 2020-09-14 | B20390¦Main waiting area¦¦Sep-17-2020 11:04
2020-09-17 11:05 | 44091.4617 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Main entry |  | 3 | 14.5 | 74.7 | 397 | 23 | 48.8 | 518 |  | 2020-09-17 11:05 | 44091.4617 | 23 | 48.8 | 518 |  |  | 2020-09-14 | B20494¦Main entry¦¦Sep-17-2020 11:04
2020-09-17 11:06 | 44091.4623 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 JUDGE |  | 2 | 17 | 59 | 450 | 21 | 51.2 | 479 | NO | 2020-09-17 11:06 | 44091.4623 | 21 | 51.2 | 479 |  |  | 2020-09-14 | B20022¦COURT 3 JUDGE¦¦Sep-17-2020 11:05
2020-09-17 11:06 | 44091.4623 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | OPP OFFICE |  | 1 | 19 | 49 | 395 | 23 | 44 | 535 |  | 2020-09-17 11:06 | 44091.4623 | 23 | 44 | 535 |  |  | 2020-09-14 | B70235¦OPP OFFICE ¦¦Sep-17-2020 11:05
2020-09-17 11:06 | 44091.4624 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 waiting area |  | 0 | 15 | 68 | 421 | 21.9 | 44 | 487 | No | 2020-09-17 11:06 | 44091.4624 | 21.9 | 44 | 487 |  |  | 2020-09-14 | B20151¦Court room 2 waiting area ¦¦Sep-17-2020 11:05
2020-09-17 11:06 | 44091.4628 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 LAWYER |  | 2 | 17 | 59 | 450 | 20.8 | 51.3 | 458 |  | 2020-09-17 11:06 | 44091.4628 | 20.8 | 51.3 | 458 |  |  | 2020-09-14 | B20022¦COURT 3 LAWYER¦¦Sep-17-2020 11:06
2020-09-17 11:06 | 44091.4628 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 118 |  | 0 | 14 | 54 | 374 | 22.5 | 43.3 | 411 | No | 2020-09-17 11:06 | 44091.4628 | 22.5 | 43.3 | 411 |  |  | 2020-09-14 | B14660¦118¦¦Sep-17-2020 11:06
2020-09-17 11:07 | 44091.4629 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 405 |  | 5 | 21.4 | 42.5 | 404 | 23 | 43.2 | 487 | No | 2020-09-17 11:07 | 44091.4629 | 23 | 43.2 | 487 |  |  | 2020-09-14 | B21128¦405¦¦Sep-17-2020 11:06
2020-09-17 11:07 | 44091.4631 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office E |  | 3 | 19 | 49 | 395 | 23 | 44 | 525 |  | 2020-09-17 11:07 | 44091.4631 | 23 | 44 | 525 |  |  | 2020-09-14 | B70235¦Main office E ¦¦Sep-17-2020 11:06
2020-09-17 11:07 | 44091.4632 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 3 |  | 2 | 18.1 | 74.2 | 413 | 20.7 | 58.4 | 492 |  | 2020-09-17 11:07 | 44091.4632 | 20.7 | 58.4 | 492 |  |  | 2020-09-14 | B20390¦Outside courtroom 3¦¦Sep-17-2020 11:06
2020-09-17 11:07 | 44091.4633 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | ADVICE COUNSEL |  | 2 | 17 | 59 | 450 | 20.4 | 45.6 | 444 |  | 2020-09-17 11:07 | 44091.4633 | 20.4 | 45.6 | 444 |  |  | 2020-09-14 | B20022¦ADVICE COUNSEL¦¦Sep-17-2020 11:07
2020-09-17 11:08 | 44091.4639 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 115 |  | 0 | 14 | 54 | 374 | 22.7 | 40.4 | 410 | No | 2020-09-17 11:08 | 44091.4639 | 22.7 | 40.4 | 410 |  |  | 2020-09-14 | B14660¦115¦¦Sep-17-2020 11:07
2020-09-17 11:08 | 44091.4639 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 gallery |  | 2 | 15 | 68 | 421 | 22.1 | 45 | 539 | No | 2020-09-17 11:08 | 44091.4639 | 22.1 | 45 | 539 |  |  | 2020-09-14 | B20151¦Court room 2 gallery ¦¦Sep-17-2020 11:08
2020-09-17 11:08 | 44091.4639 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 WAITING AREA |  | 1 | 17 | 59 | 450 | 20.1 | 48.9 | 442 |  | 2020-09-17 11:08 | 44091.4639 | 20.1 | 48.9 | 442 |  |  | 2020-09-14 | B20022¦COURT 3 WAITING AREA¦¦Sep-17-2020 11:08
2020-09-17 11:08 | 44091.464 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 5 |  | 1 | 15.2 | 70 | 377 | 22.3 | 47 | 438 |  | 2020-09-17 11:08 | 44091.464 | 22.3 | 47 | 438 |  |  | 2020-09-14 | B20494¦Courtroom 5¦¦Sep-17-2020 11:08
2020-09-17 11:08 | 44091.4642 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Interview room 1 |  | 1 | 14.5 | 74.7 | 397 | 22.9 | 47.8 | 496 |  | 2020-09-17 11:08 | 44091.4642 | 22.9 | 47.8 | 496 |  |  | 2020-09-14 | B20494¦Interview room 1¦¦Sep-17-2020 11:08
2020-09-17 11:08 | 44091.4642 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office C |  | 3 | 19 | 49 | 395 | 23 | 45 | 524 |  | 2020-09-17 11:08 | 44091.4642 | 23 | 45 | 524 |  |  | 2020-09-14 | B70235¦Main office C ¦¦Sep-17-2020 11:08
2020-09-17 11:09 | 44091.4642 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 2 |  | 3 | 18.1 | 74.2 | 413 | 20.8 | 58.5 | 508 |  | 2020-09-17 11:08 | 44091.4642 | 20.8 | 58.5 | 508 |  |  | 2020-09-14 | B20390¦Outside courtroom 2¦¦Sep-17-2020 11:08
2020-09-17 11:09 | 44091.4646 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT OFFICE LOBBY |  | 3 | 17 | 59 | 450 | 21.7 | 52.3 | 547 |  | 2020-09-17 11:09 | 44091.4646 | 21.7 | 52.3 | 547 |  |  | 2020-09-14 | B20022¦COURT OFFICE LOBBY¦¦Sep-17-2020 11:09
2020-09-17 11:09 | 44091.4646 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 406 |  | 6 | 21.4 | 42.5 | 404 | 23.1 | 40.3 | 497 | No | 2020-09-17 11:09 | 44091.4646 | 23.1 | 40.3 | 497 |  |  | 2020-09-14 | B21128¦406¦¦Sep-17-2020 11:09
2020-09-17 11:10 | 44091.4653 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT OFFICE |  | 2 | 17 | 59 | 450 | 21.5 | 49.3 | 520 |  | 2020-09-17 11:10 | 44091.4653 | 21.5 | 49.3 | 520 |  |  | 2020-09-14 | B20022¦COURT OFFICE¦¦Sep-17-2020 11:09
2020-09-17 11:10 | 44091.4653 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Front entrance |  | 0 | 23 | 41.5 | 420 | 22.7 | 41.3 | 441 |  | 2020-09-17 11:10 | 44091.4653 | 22.7 | 41.3 | 441 |  |  | 2020-09-14 | B17477¦Front entrance ¦¦Sep-17-2020 11:10
2020-09-17 11:10 | 44091.4655 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway ne |  | 2 | 15.2 | 70 | 377 | 22.7 | 49.4 | 476 |  | 2020-09-17 11:10 | 44091.4655 | 22.7 | 49.4 | 476 |  |  | 2020-09-14 | B20494¦Third floor hallway ne¦¦Sep-17-2020 11:10
2020-09-17 11:10 | 44091.4655 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NW Hall |  | 0 | 18 | 70 | 440 | 23 | 54 | 580 |  | 2020-09-17 11:10 | 44091.4655 | 23 | 54 | 580 |  |  | 2020-09-14 | B25548¦NW Hall¦¦Sep-17-2020 11:10
2020-09-17 11:10 | 44091.4656 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | First floor vending machines |  | 1 | 18.1 | 74.2 | 413 | 21.6 | 55.7 | 480 |  | 2020-09-17 11:10 | 44091.4656 | 21.6 | 55.7 | 480 |  |  | 2020-09-14 | B20390¦First floor vending machines ¦¦Sep-17-2020 11:10
2020-09-17 11:10 | 44091.4656 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office W |  | 3 | 19 | 49 | 395 | 23 | 45 | 530 |  | 2020-09-17 11:10 | 44091.4656 | 23 | 45 | 530 |  |  | 2020-09-14 | B70235¦Main office W¦¦Sep-17-2020 11:10
2020-09-17 11:11 | 44091.4657 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | MEDIATION ROOM |  | 2 | 17 | 59 | 450 | 20.8 | 52.7 | 517 |  | 2020-09-17 11:11 | 44091.4657 | 20.8 | 52.7 | 517 |  |  | 2020-09-14 | B20022¦MEDIATION ROOM¦¦Sep-17-2020 11:10
2020-09-17 11:11 | 44091.4662 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 judge desk |  | 2 | 15 | 68 | 421 | 22.1 | 44.7 | 604 | No | 2020-09-17 11:11 | 44091.4662 | 22.1 | 44.7 | 604 |  |  | 2020-09-14 | B20151¦Court room 2 judge desk ¦¦Sep-17-2020 11:11
2020-09-17 11:11 | 44091.4662 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 107 |  | 2 | 14 | 54 | 374 | 19.7 | 45 | 430 | No | 2020-09-17 11:11 | 44091.4662 | 19.7 | 45 | 430 |  |  | 2020-09-14 | B14660¦107¦¦Sep-17-2020 11:11
2020-09-17 11:11 | 44091.4662 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 407 |  | 2 | 21.4 | 42.5 | 404 | 23.1 | 43.4 | 428 | No | 2020-09-17 11:11 | 44091.4662 | 23.1 | 43.4 | 428 |  |  | 2020-09-14 | B21128¦407¦¦Sep-17-2020 11:11
2020-09-17 11:12 | 44091.4664 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | 1st floor - outside service Ontario entrance |  | 2 | 16.2 | 60.9 | 385 | 23 | 44.3 | 534 |  | 2020-09-17 11:12 | 44091.4664 | 23 | 44.3 | 534 |  |  | 2020-09-14 | B70277¦1st floor - outside service Ontario entrance¦¦Sep-17-2020 11:11
2020-09-17 11:12 | 44091.4665 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | OFFICER ROOM |  | 2 | 17 | 59 | 450 | 20.9 | 57.3 | 519 |  | 2020-09-17 11:12 | 44091.4665 | 20.9 | 57.3 | 519 |  |  | 2020-09-14 | B20022¦OFFICER ROOM¦¦Sep-17-2020 11:11
2020-09-17 11:12 | 44091.4666 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NE hall |  | 0 | 18 | 70 | 440 | 23 | 53 | 580 |  | 2020-09-17 11:12 | 44091.4666 | 23 | 53 | 580 |  |  | 2020-09-14 | B25548¦NE hall¦¦Sep-17-2020 11:11
2020-09-17 11:12 | 44091.4667 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Interview room 2 |  | 1 | 14.5 | 74.7 | 397 | 22.6 | 47.2 | 528 |  | 2020-09-17 11:12 | 44091.4667 | 22.6 | 47.2 | 528 |  |  | 2020-09-14 | B20494¦Interview room 2¦¦Sep-17-2020 11:12
2020-09-17 11:12 | 44091.4668 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Security |  | 1 | 23 | 41.5 | 420 | 21.7 | 47.8 | 586 |  | 2020-09-17 11:12 | 44091.4668 | 21.7 | 47.8 | 586 |  |  | 2020-09-14 | B17477¦Security ¦¦Sep-17-2020 11:12
2020-09-17 11:12 | 44091.4669 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Trial office |  | 0 | 19 | 49 | 395 | 23 | 44 | 480 |  | 2020-09-17 11:12 | 44091.4669 | 23 | 44 | 480 |  |  | 2020-09-14 | B70235¦Trial office ¦¦Sep-17-2020 11:12
2020-09-17 11:12 | 44091.467 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 1 FLOOR LOBBY |  | 4 | 17 | 59 | 450 | 19 | 60.1 | 574 |  | 2020-09-17 11:12 | 44091.467 | 19 | 60.1 | 574 |  | caution | 2020-09-14 | B20022¦1 FLOOR LOBBY¦¦Sep-17-2020 11:12
2020-09-17 11:13 | 44091.4673 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell - first floor |  | 1 | 18.1 | 74.2 | 413 | 21.8 | 53.9 | 438 |  | 2020-09-17 11:13 | 44091.4673 | 21.8 | 53.9 | 438 |  |  | 2020-09-14 | B20390¦Main stairwell - first floor¦¦Sep-17-2020 11:12
2020-09-17 11:13 | 44091.4675 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway se |  | 2 | 15.2 | 70 | 377 | 25.2 | 45.2 | 498 |  | 2020-09-17 11:13 | 44091.4675 | 25.2 | 45.2 | 498 |  |  | 2020-09-14 | B20494¦Third floor hallway se¦¦Sep-17-2020 11:13
2020-09-17 11:13 | 44091.4676 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | E hall |  | 0 | 18 | 70 | 440 | 23 | 53 | 580 |  | 2020-09-17 11:13 | 44091.4676 | 23 | 53 | 580 |  |  | 2020-09-14 | B25548¦E hall¦¦Sep-17-2020 11:13
2020-09-17 11:13 | 44091.4676 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR LUNCH ROOM |  | 2 | 17 | 59 | 450 | 21.2 | 50.7 | 505 |  | 2020-09-17 11:13 | 44091.4676 | 21.2 | 50.7 | 505 |  |  | 2020-09-14 | B20022¦2 FLOOR LUNCH ROOM¦¦Sep-17-2020 11:13
2020-09-17 11:13 | 44091.4676 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 113 |  | 1 | 14 | 54 | 374 | 21.3 | 42.7 | 415 | No | 2020-09-17 11:13 | 44091.4676 | 21.3 | 42.7 | 415 |  |  | 2020-09-14 | B14660¦113¦¦Sep-17-2020 11:13
2020-09-17 11:14 | 44091.4678 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 1 seating area |  | 0 | 23 | 41.5 | 420 | 22.2 | 47.2 | 444 |  | 2020-09-17 11:14 | 44091.4678 | 22.2 | 47.2 | 444 |  |  | 2020-09-14 | B17477¦Level 1 seating area ¦¦Sep-17-2020 11:13
2020-09-17 11:14 | 44091.468 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Public seating area |  | 0 | 21 | 29.9 | 429 | 23.5 | 41 | 578 |  | 2020-09-17 11:14 | 44091.468 | 23.5 | 41 | 578 |  |  | 2020-09-14 | B19890¦Public seating area ¦¦Sep-17-2020 11:13
2020-09-17 11:14 | 44091.4681 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jennifer Broderick office |  | 0 | 19 | 49 | 395 | 23 | 44 | 474 |  | 2020-09-17 11:14 | 44091.4681 | 23 | 44 | 474 |  |  | 2020-09-14 | B70235¦Jennifer Broderick office ¦¦Sep-17-2020 11:14
2020-09-17 11:14 | 44091.4683 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 2 JUDGE |  | 2 | 17 | 59 | 450 | 21.3 | 50.6 | 465 |  | 2020-09-17 11:14 | 44091.4683 | 21.3 | 50.6 | 465 |  |  | 2020-09-14 | B20022¦COURT 2 JUDGE¦¦Sep-17-2020 11:14
2020-09-17 11:15 | 44091.4685 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 1 seating area 2 |  | 0 | 23 | 41.5 | 420 | 22.7 | 46.4 | 438 |  | 2020-09-17 11:15 | 44091.4685 | 22.7 | 46.4 | 438 |  |  | 2020-09-14 | B17477¦Level 1 seating area 2¦¦Sep-17-2020 11:14
2020-09-17 11:15 | 44091.4686 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell, second floor |  | 1 | 18.1 | 74.2 | 413 | 22 | 52.9 | 436 |  | 2020-09-17 11:15 | 44091.4686 | 22 | 52.9 | 436 |  |  | 2020-09-14 | B20390¦Main stairwell, second floor¦¦Sep-17-2020 11:14
2020-09-17 11:15 | 44091.4686 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 4 |  | 4 | 14.5 | 74.7 | 397 | 22.6 | 48.7 | 511 |  | 2020-09-17 11:15 | 44091.4686 | 22.6 | 48.7 | 511 |  |  | 2020-09-14 | B20494¦Courtroom 4¦¦Sep-17-2020 11:14
2020-09-17 11:15 | 44091.4688 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NE hall |  | 0 | 18 | 70 | 440 | 23 | 53 | 580 |  | 2020-09-17 11:15 | 44091.4688 | 23 | 53 | 580 |  |  | 2020-09-14 | B25548¦NE hall¦¦Sep-17-2020 11:15
2020-09-17 11:15 | 44091.4688 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 2 LAWYER |  | 2 | 21 | 59 | 450 | 21 | 50.7 | 454 |  | 2020-09-17 11:15 | 44091.4688 | 21 | 50.7 | 454 |  |  | 2020-09-14 | B20022¦COURT 2 LAWYER¦¦Sep-17-2020 11:15
2020-09-17 11:15 | 44091.4689 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 408 |  | 2 | 21.4 | 42.5 | 404 | 25.2 | 41.9 | 512 | No | 2020-09-17 11:15 | 44091.4689 | 25.2 | 41.9 | 512 |  |  | 2020-09-14 | B21128¦408¦¦Sep-17-2020 11:15
2020-09-17 11:15 | 44091.4689 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Maintenance |  | 0 | 21 | 29.9 | 429 | 24.2 | 42 | 597 |  | 2020-09-17 11:15 | 44091.4689 | 24.2 | 42 | 597 |  |  | 2020-09-14 | B19890¦Maintenance ¦¦Sep-17-2020 11:15
2020-09-17 11:15 | 44091.469 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 114 |  | 0 | 14 | 54 | 374 | 21.8 | 45.2 | 406 | No | 2020-09-17 11:15 | 44091.469 | 21.8 | 45.2 | 406 |  |  | 2020-09-14 | B14660¦114¦¦Sep-17-2020 11:15
2020-09-17 11:16 | 44091.4691 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Robert Beninger office |  | 0 | 19 | 49 | 395 | 22 | 44 | 481 |  | 2020-09-17 11:16 | 44091.4691 | 22 | 44 | 481 |  |  | 2020-09-14 | B70235¦Robert Beninger office ¦¦Sep-17-2020 11:15
2020-09-17 11:16 | 44091.4693 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 JUDGE |  | 2 | 17 | 59 | 450 | 20.8 | 52.1 | 482 |  | 2020-09-17 11:16 | 44091.4693 | 20.8 | 52.1 | 482 |  |  | 2020-09-14 | B20022¦COURT 1 JUDGE¦¦Sep-17-2020 11:15
2020-09-17 11:16 | 44091.4694 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Second floor waiting area |  | 1 | 18.1 | 74.2 | 413 | 22.3 | 51 | 430 |  | 2020-09-17 11:16 | 44091.4694 | 22.3 | 51 | 430 |  |  | 2020-09-14 | B20390¦Second floor waiting area¦¦Sep-17-2020 11:15
2020-09-17 11:17 | 44091.4698 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 RIGHT SIDE |  | 2 | 17 | 59 | 450 | 21.3 | 50 | 557 |  | 2020-09-17 11:17 | 44091.4698 | 21.3 | 50 | 557 |  |  | 2020-09-14 | B20022¦COURT 1 RIGHT SIDE¦¦Sep-17-2020 11:16
2020-09-17 11:17 | 44091.4698 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Crown office |  | 2 | 21 | 29.9 | 429 | 24 | 42 | 543 |  | 2020-09-17 11:17 | 44091.4698 | 24 | 42 | 543 |  |  | 2020-09-14 | B19890¦Crown office¦¦Sep-17-2020 11:16
2020-09-17 11:17 | 44091.4701 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Stuart Konyer office |  | 0 | 19 | 49 | 395 | 22 | 44 | 481 |  | 2020-09-17 11:17 | 44091.4701 | 22 | 44 | 481 |  |  | 2020-09-14 | B70235¦Stuart Konyer office ¦¦Sep-17-2020 11:16
2020-09-17 11:17 | 44091.4702 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom #1 |  | 4 | 18.8 | 46.2 | 405 | 21.3 | 45.9 | 533 |  | 2020-09-17 11:17 | 44091.4702 | 21.3 | 45.9 | 533 |  |  | 2020-09-14 | B21554¦Courtroom #1¦¦Sep-17-2020 11:17
2020-09-17 11:17 | 44091.4703 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway nw |  | 1 | 15.2 | 70 | 377 | 22.8 | 48.7 | 448 |  | 2020-09-17 11:17 | 44091.4703 | 22.8 | 48.7 | 448 |  |  | 2020-09-14 | B20494¦Third floor hallway nw¦¦Sep-17-2020 11:17
2020-09-17 11:17 | 44091.4704 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 LEFT SIDE |  | 2 | 17 | 59 | 450 | 21.4 | 50.2 | 483 |  | 2020-09-17 11:17 | 44091.4704 | 21.4 | 50.2 | 483 |  |  | 2020-09-14 | B20022¦COURT 1 LEFT SIDE¦¦Sep-17-2020 11:17
2020-09-17 11:17 | 44091.4704 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside second floor elevator |  | 1 | 18.1 | 74.2 | 413 | 22.6 | 49.8 | 426 |  | 2020-09-17 11:17 | 44091.4704 | 22.6 | 49.8 | 426 |  |  | 2020-09-14 | B20390¦Outside second floor elevator¦¦Sep-17-2020 11:17
2020-09-17 11:18 | 44091.4706 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 seating area |  | 0 | 23 | 41.5 | 420 | 23 | 45.8 | 428 |  | 2020-09-17 11:18 | 44091.4706 | 23 | 45.8 | 428 |  |  | 2020-09-14 | B17477¦Courtroom 100 seating area ¦¦Sep-17-2020 11:17
2020-09-17 11:18 | 44091.4707 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 101 |  | 0 | 14 | 54 | 374 | 21.6 | 41 | 436 | No | 2020-09-17 11:18 | 44091.4707 | 21.6 | 41 | 436 |  |  | 2020-09-14 | B14660¦101¦¦Sep-17-2020 11:17
2020-09-17 11:18 | 44091.4707 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 414 |  | 2 | 21.5 | 42.5 | 404 | 24.1 | 42.8 | 465 | No | 2020-09-17 11:18 | 44091.4707 | 24.1 | 42.8 | 465 |  |  | 2020-09-14 | B21128¦414¦¦Sep-17-2020 11:17
2020-09-17 11:18 | 44091.4708 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Library |  | 0 | 16 | 60 | 399 | 20.8 | 51 | 426 |  | 2020-09-17 11:18 | 44091.4708 | 20.8 | 51 | 426 |  |  | 2020-09-14 | B90558¦Library¦¦Sep-17-2020 11:17
2020-09-17 11:18 | 44091.4709 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JURY ROOM |  | 2 | 17 | 59 | 450 | 21.4 | 50.2 | 483 |  | 2020-09-17 11:18 | 44091.4709 | 21.4 | 50.2 | 483 |  |  | 2020-09-14 | B20022¦JURY ROOM¦¦Sep-17-2020 11:18
2020-09-17 11:18 | 44091.471 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Lunch room |  | 0 | 19 | 49 | 395 | 21 | 46 | 481 |  | 2020-09-17 11:18 | 44091.471 | 21 | 46 | 481 |  |  | 2020-09-14 | B70235¦Lunch room ¦¦Sep-17-2020 11:18
2020-09-17 11:18 | 44091.471 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NW hall |  | 0 | 18 | 70 | 440 | 24 | 52 | 600 |  | 2020-09-17 11:18 | 44091.471 | 24 | 52 | 600 |  |  | 2020-09-14 | B25548¦NW hall¦¦Sep-17-2020 11:18
2020-09-17 11:19 | 44091.4713 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Public seating area 2 |  | 0 | 21 | 29.9 | 429 | 23.1 | 42.3 | 525 |  | 2020-09-17 11:19 | 44091.4713 | 23.1 | 42.3 | 525 |  |  | 2020-09-14 | B19890¦Public seating area 2¦¦Sep-17-2020 11:18
2020-09-17 11:19 | 44091.4715 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR LEFT MEETING |  | 2 | 17 | 59 | 450 | 21.5 | 50 | 489 |  | 2020-09-17 11:19 | 44091.4715 | 21.5 | 50 | 489 |  |  | 2020-09-14 | B20022¦2 FLOOR LEFT MEETING¦¦Sep-17-2020 11:18
2020-09-17 11:19 | 44091.4715 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 seating area 2 |  | 0 | 23 | 41.5 | 420 | 22.7 | 46.2 | 430 |  | 2020-09-17 11:19 | 44091.4715 | 22.7 | 46.2 | 430 |  |  | 2020-09-14 | B17477¦Courtroom 100 seating area 2¦¦Sep-17-2020 11:18
2020-09-17 11:19 | 44091.4718 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family services |  | 1 | 14.5 | 74.7 | 397 | 22.8 | 54.2 | 478 |  | 2020-09-17 11:19 | 44091.4718 | 22.8 | 54.2 | 478 |  |  | 2020-09-14 | B20494¦Family services¦¦Sep-17-2020 11:19
2020-09-17 11:19 | 44091.4719 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 101 |  | 0 | 14 | 54 | 374 | 20.5 | 50.4 | 416 | No | 2020-09-17 11:20 | 44091.4719 | 20.5 | 50.4 | 416 |  |  | 2020-09-14 | B14660¦101¦¦Sep-17-2020 11:19
2020-09-17 11:20 | 44091.4719 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court support office |  | 0 | 19 | 49 | 395 | 22 | 46 | 492 |  | 2020-09-17 11:20 | 44091.4719 | 22 | 46 | 492 |  |  | 2020-09-14 | B70235¦Court support office ¦¦Sep-17-2020 11:19
2020-09-17 11:20 | 44091.4719 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom#2 |  | 3 | 18.8 | 46.2 | 405 | 21.3 | 37.1 | 507 |  | 2020-09-17 11:20 | 44091.4719 | 21.3 | 37.1 | 507 |  | caution | 2020-09-14 | B21554¦Courtroom#2¦¦Sep-17-2020 11:19
2020-09-17 11:20 | 44091.4722 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside museum |  | 1 | 18.1 | 74.2 | 413 | 22.6 | 50.4 | 422 |  | 2020-09-17 11:20 | 44091.4722 | 22.6 | 50.4 | 422 |  |  | 2020-09-14 | B20390¦Outside museum¦¦Sep-17-2020 11:19
2020-09-17 11:20 | 44091.4722 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR RIGHT MEETING |  | 2 | 17 | 59 | 450 | 21.6 | 51 | 490 |  | 2020-09-17 11:20 | 44091.4722 | 21.6 | 51 | 490 |  |  | 2020-09-14 | B20022¦2 FLOOR RIGHT MEETING¦¦Sep-17-2020 11:20
2020-09-17 11:20 | 44091.4723 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 413 |  | 2 | 21.5 | 42.5 | 404 | 24.2 | 44.2 | 577 | No | 2020-09-17 11:20 | 44091.4723 | 24.2 | 44.2 | 577 |  |  | 2020-09-14 | B21128¦413¦¦Sep-17-2020 11:20
2020-09-17 11:20 | 44091.4723 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway sw |  | 1 | 15.2 | 70 | 377 | 24.3 | 44.8 | 448 |  | 2020-09-17 11:20 | 44091.4723 | 24.3 | 44.8 | 448 |  |  | 2020-09-14 | B20494¦Third floor hallway sw¦¦Sep-17-2020 11:20
2020-09-17 11:20 | 44091.4724 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Courtroom 2 |  | 0 | 21 | 29.9 | 429 | 23.2 | 39.1 | 455 |  | 2020-09-17 11:20 | 44091.4724 | 23.2 | 39.1 | 455 |  | caution | 2020-09-14 | B19890¦Courtroom 2¦¦Sep-17-2020 11:20
2020-09-17 11:21 | 44091.4729 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 1 FLOOR MAIN HALL |  | 2 | 17 | 59 | 450 | 21.8 | 48 | 517 |  | 2020-09-17 11:21 | 44091.4729 | 21.8 | 48 | 517 |  |  | 2020-09-14 | B20022¦1 FLOOR MAIN HALL¦¦Sep-17-2020 11:20
2020-09-17 11:21 | 44091.4729 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Crown staff office |  | 1 | 19 | 49 | 395 | 22 | 46 | 507 |  | 2020-09-17 11:21 | 44091.4729 | 22 | 46 | 507 |  |  | 2020-09-14 | B70235¦Crown staff office ¦¦Sep-17-2020 11:21
2020-09-17 11:21 | 44091.473 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Interview room |  | 2 | 15 | 72 | 367 | 22 | 45 | 384 |  | 2020-09-17 11:21 | 44091.473 | 22 | 45 | 384 |  |  | 2020-09-14 | B20772¦Interview room¦¦Sep-17-2020 11:21
2020-09-17 11:21 | 44091.4731 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Museum |  | 1 | 18.1 | 74.2 | 413 | 22 | 51.3 | 420 |  | 2020-09-17 11:21 | 44091.4731 | 22 | 51.3 | 420 |  |  | 2020-09-14 | B20390¦Museum¦¦Sep-17-2020 11:21
2020-09-17 11:21 | 44091.4731 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom #3 |  | 4 | 18.8 | 46.2 | 405 | 21.1 | 39.1 | 570 |  | 2020-09-17 11:21 | 44091.4731 | 21.1 | 39.1 | 570 |  | caution | 2020-09-14 | B21554¦Courtroom #3¦¦Sep-17-2020 11:21
2020-09-17 11:21 | 44091.4731 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 134 |  | 0 | 14 | 54 | 374 | 20.1 | 46.1 | 422 | No | 2020-09-17 11:21 | 44091.4731 | 20.1 | 46.1 | 422 |  |  | 2020-09-14 | B14660¦134¦¦Sep-17-2020 11:21
2020-09-17 11:22 | 44091.4733 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Courtroom 1 |  | 0 | 21 | 29.9 | 429 | 23.7 | 38.4 | 444 |  | 2020-09-17 11:22 | 44091.4733 | 23.7 | 38.4 | 444 |  | caution | 2020-09-14 | B19890¦Courtroom 1¦¦Sep-17-2020 11:21
2020-09-17 11:22 | 44091.4735 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room waiting room/entrance |  | 1 | 20.2 | 41.3 | 366 | 23 | 39.1 | 406 |  | 2020-09-17 11:22 | 44091.4735 | 23 | 39.1 | 406 |  | caution | 2020-09-14 | B70277¦Court room waiting room/entrance¦¦Sep-17-2020 11:21
2020-09-17 11:22 | 44091.4738 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | SOUTH WING ENTRANCE |  | 2 | 17 | 59 | 450 | 22 | 48 | 509 | FOR EARLIER "YES" THIS WAS AN ERROR - I ACCESSED ALL ROOMS. | 2020-09-17 11:22 | 44091.4738 | 22 | 48 | 509 |  |  | 2020-09-14 | B20022¦SOUTH WING ENTRANCE¦¦Sep-17-2020 11:22
2020-09-17 11:22 | 44091.4738 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 412 |  | 2 | 21.4 | 42.5 | 404 | 23.3 | 43.3 | 572 | No | 2020-09-17 11:22 | 44091.4738 | 23.3 | 43.3 | 572 |  |  | 2020-09-14 | B21128¦412¦¦Sep-17-2020 11:22
2020-09-17 11:23 | 44091.474 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | Center hall |  | 0 | 18 | 70 | 440 | 23 | 52 | 605 |  | 2020-09-17 11:23 | 44091.474 | 23 | 52 | 605 |  |  | 2020-09-14 | B25548¦Center hall¦¦Sep-17-2020 11:22
2020-09-17 11:23 | 44091.4741 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 136 |  | 5 | 14 | 54 | 374 | 21.7 | 43.1 | 440 | No | 2020-09-17 11:23 | 44091.4741 | 21.7 | 43.1 | 440 |  |  | 2020-09-14 | B14660¦136¦¦Sep-17-2020 11:22
2020-09-17 11:23 | 44091.4741 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 doors |  | 0 | 23 | 41.5 | 430 | 22.3 | 48 | 418 |  | 2020-09-17 11:23 | 44091.4741 | 22.3 | 48 | 418 |  |  | 2020-09-14 | B17477¦Courtroom 100 doors ¦¦Sep-17-2020 11:22
2020-09-17 11:23 | 44091.4741 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Fire pump |  | 1 | 14.5 | 74.7 | 397 | 23.5 | 49.6 | 465 |  | 2020-09-17 11:23 | 44091.4741 | 23.5 | 49.6 | 465 |  |  | 2020-09-14 | B20494¦Fire pump ¦¦Sep-17-2020 11:22
2020-09-17 11:23 | 44091.4744 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Stairwells |  | 0 | 21 | 29.9 | 429 | 22.2 | 43.5 | 540 |  | 2020-09-17 11:23 | 44091.4744 | 22.2 | 43.5 | 540 |  |  | 2020-09-14 | B19890¦Stairwells ¦¦Sep-17-2020 11:23
2020-09-17 11:23 | 44091.4744 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom#2 |  | 0 | 16 | 60 | 399 | 20.7 | 49.2 | 452 | Unable to access courtroom #3 court in session no access to justice Letourneau office | 2020-09-17 11:23 | 44091.4744 | 20.7 | 49.2 | 452 |  |  | 2020-09-14 | B90558¦Courtroom#2¦¦Sep-17-2020 11:23
2020-09-17 11:23 | 44091.4745 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Peterborough Police |  | 1 | 19 | 49 | 395 | 22 | 46 | 553 |  | 2020-09-17 11:23 | 44091.4745 | 22 | 46 | 553 |  |  | 2020-09-14 | B70235¦Peterborough Police ¦¦Sep-17-2020 11:23
2020-09-17 11:23 | 44091.4746 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Waiting area outside courtroom3 |  | 1 | 18.8 | 46.2 | 405 | 21.7 | 41.7 | 551 |  | 2020-09-17 11:23 | 44091.4746 | 21.7 | 41.7 | 551 |  |  | 2020-09-14 | B21554¦Waiting area outside courtroom3¦¦Sep-17-2020 11:23
2020-09-17 11:23 | 44091.4746 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 6 |  | 1 | 18.1 | 74.2 | 413 | 21.9 | 52.7 | 418 |  | 2020-09-17 11:23 | 44091.4746 | 21.9 | 52.7 | 418 |  |  | 2020-09-14 | B20390¦Outside courtroom 6¦¦Sep-17-2020 11:23
2020-09-17 11:24 | 44091.4748 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room waiting room/entrance - left side |  | 1 | 20.2 | 41.3 | 366 | 23.1 | 38.7 | 418 |  | 2020-09-17 11:24 | 44091.4748 | 23.1 | 38.7 | 418 |  | caution | 2020-09-14 | B70277¦Court room waiting room/entrance - left side¦¦Sep-17-2020 11:23
2020-09-17 11:24 | 44091.4748 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 bench |  | 0 | 23 | 41.5 | 420 | 21.8 | 49.4 | 414 |  | 2020-09-17 11:24 | 44091.4748 | 21.8 | 49.4 | 414 |  |  | 2020-09-14 | B17477¦Courtroom 100 bench ¦¦Sep-17-2020 11:23
2020-09-17 11:24 | 44091.475 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Main hallway |  | 0 | 21 | 29.9 | 429 | 22.6 | 45.2 | 577 |  | 2020-09-17 11:24 | 44091.475 | 22.6 | 45.2 | 577 |  |  | 2020-09-14 | B19890¦Main hallway ¦¦Sep-17-2020 11:23
2020-09-17 11:24 | 44091.4751 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 144 |  | 0 | 14 | 54 | 374 | 22.3 | 41.1 | 423 | No | 2020-09-17 11:24 | 44091.4751 | 22.3 | 41.1 | 423 |  |  | 2020-09-14 | B14660¦144¦¦Sep-17-2020 11:24
2020-09-17 11:24 | 44091.4751 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 411 |  | 6 | 21.4 | 42.5 | 404 | 22.1 | 42.1 | 475 | No | 2020-09-17 11:24 | 44091.4751 | 22.1 | 42.1 | 475 |  |  | 2020-09-14 | B21128¦411¦¦Sep-17-2020 11:24
2020-09-17 11:25 | 44091.4755 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-E wall |  | 0 | 18 | 70 | 440 | 23 | 52 | 660 |  | 2020-09-17 11:25 | 44091.4755 | 23 | 52 | 660 |  |  | 2020-09-14 | B25548¦1-E wall¦¦Sep-17-2020 11:24
2020-09-17 11:25 | 44091.4755 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Jury room waiting area |  | 1 | 18.1 | 74.2 | 413 | 23.1 | 50.1 | 412 |  | 2020-09-17 11:25 | 44091.4755 | 23.1 | 50.1 | 412 |  |  | 2020-09-14 | B20390¦Jury room waiting area¦¦Sep-17-2020 11:24
2020-09-17 11:25 | 44091.4758 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 1 ramp |  | 0 | 23 | 41.5 | 420 | 22 | 49.3 | 426 |  | 2020-09-17 11:25 | 44091.4758 | 22 | 49.3 | 426 |  |  | 2020-09-14 | B17477¦Level 1 ramp ¦¦Sep-17-2020 11:25
2020-09-17 11:25 | 44091.4759 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Basement corridor washroom area |  | 1 | 18.8 | 46.2 | 405 | 21.8 | 41.3 | 565 |  | 2020-09-17 11:25 | 44091.4759 | 21.8 | 41.3 | 565 |  |  | 2020-09-14 | B21554¦Basement corridor washroom area¦¦Sep-17-2020 11:25
2020-09-17 11:26 | 44091.4762 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 122 |  | 0 | 14 | 54 | 374 | 22.6 | 40.7 | 444 | No | 2020-09-17 11:26 | 44091.4762 | 22.6 | 40.7 | 444 |  |  | 2020-09-14 | B14660¦122¦¦Sep-17-2020 11:25
2020-09-17 11:26 | 44091.4762 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 410 |  | 2 | 21.4 | 42.5 | 404 | 22.3 | 47 | 444 | No | 2020-09-17 11:26 | 44091.4762 | 22.3 | 47 | 444 |  |  | 2020-09-14 | B21128¦410¦¦Sep-17-2020 11:25
2020-09-17 11:26 | 44091.4765 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Staff area |  | 4 | 21 | 29.9 | 429 | 23 | 44.5 | 575 |  | 2020-09-17 11:26 | 44091.4765 | 23 | 44.5 | 575 |  |  | 2020-09-14 | B25477¦Staff area ¦¦Sep-17-2020 11:26
2020-09-17 11:26 | 44091.4765 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Back stairwell, second floor |  | 1 | 18.1 | 74.2 | 413 | 22.5 | 50.4 | 416 |  | 2020-09-17 11:26 | 44091.4765 | 22.5 | 50.4 | 416 |  |  | 2020-09-14 | B20390¦Back stairwell, second floor¦¦Sep-17-2020 11:26
2020-09-17 11:26 | 44091.4765 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 2 sitting area |  | 0 | 23 | 41.5 | 420 | 22.4 | 48.6 | 431 |  | 2020-09-17 11:26 | 44091.4765 | 22.4 | 48.6 | 431 |  |  | 2020-09-14 | B17477¦Level 2 sitting area ¦¦Sep-17-2020 11:26
2020-09-17 11:26 | 44091.4766 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - back right, facing judge |  | 2 | 20.2 | 41.3 | 366 | 23 | 37.6 | 406 |  | 2020-09-17 11:26 | 44091.4766 | 23 | 37.6 | 406 |  | caution | 2020-09-14 | B70277¦Court room - back right, facing judge¦¦Sep-17-2020 11:26
2020-09-17 11:27 | 44091.4768 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview room 4 |  | 0 | 19 | 49 | 395 | 23 | 45 | 539 |  | 2020-09-17 11:27 | 44091.4768 | 23 | 45 | 539 |  |  | 2020-09-14 | B70235¦Interview room 4¦¦Sep-17-2020 11:26
2020-09-17 11:27 | 44091.4768 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- E wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 615 |  | 2020-09-17 11:27 | 44091.4768 | 24 | 51 | 615 |  |  | 2020-09-14 | B25548¦1- E wall¦¦Sep-17-2020 11:26
2020-09-17 11:27 | 44091.4772 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 409 |  | 9 | 21.4 | 42.5 | 404 | 22.7 | 47.7 | 470 | No | 2020-09-17 11:27 | 44091.4772 | 22.7 | 47.7 | 470 |  |  | 2020-09-14 | B21128¦409¦¦Sep-17-2020 11:27
2020-09-17 11:27 | 44091.4772 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 105 |  | 0 | 14 | 54 | 374 | 22.1 | 39.7 | 440 | No | 2020-09-17 11:27 | 44091.4772 | 22.1 | 39.7 | 440 |  | caution | 2020-09-14 | B14660¦105¦¦Sep-17-2020 11:27
2020-09-17 11:27 | 44091.4774 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Front lobby |  | 2 | 21 | 29.9 | 429 | 22.8 | 45 | 593 |  | 2020-09-17 11:27 | 44091.4774 | 22.8 | 45 | 593 |  |  | 2020-09-14 | B25477¦Front lobby ¦¦Sep-17-2020 11:27
2020-09-17 11:27 | 44091.4774 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Basement corridor at exit door |  | 1 | 18.8 | 46.2 | 405 | 22.3 | 41.5 | 586 |  | 2020-09-17 11:27 | 44091.4774 | 22.3 | 41.5 | 586 |  |  | 2020-09-14 | B21554¦Basement corridor at exit door¦¦Sep-17-2020 11:27
2020-09-17 11:28 | 44091.4775 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Between second floor washrooms |  | 1 | 18.1 | 74.2 | 413 | 22.3 | 51.2 | 416 |  | 2020-09-17 11:28 | 44091.4775 | 22.3 | 51.2 | 416 |  |  | 2020-09-14 | B20390¦Between second floor washrooms¦¦Sep-17-2020 11:27
2020-09-17 11:28 | 44091.4776 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - Back left facing judge |  | 2 | 20.2 | 41.3 | 366 | 22.7 | 38.7 | 397 |  | 2020-09-17 11:28 | 44091.4776 | 22.7 | 38.7 | 397 |  | caution | 2020-09-14 | B70277¦Court room - Back left facing judge¦¦Sep-17-2020 11:27
2020-09-17 11:28 | 44091.4777 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 2 ramp |  | 0 | 23 | 41.5 | 420 | 22.7 | 47.5 | 431 |  | 2020-09-17 11:28 | 44091.4777 | 22.7 | 47.5 | 431 |  |  | 2020-09-14 | B17477¦Level 2 ramp ¦¦Sep-17-2020 11:27
2020-09-17 11:28 | 44091.4778 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 1st floor hall by elevator |  | 1 | 14.5 | 74.7 | 397 | 23.7 | 47.5 | 469 |  | 2020-09-17 11:28 | 44091.4778 | 23.7 | 47.5 | 469 |  |  | 2020-09-14 | B20494¦1st floor hall by elevator¦¦Sep-17-2020 11:27
2020-09-17 11:28 | 44091.478 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 106 |  | 0 | 14 | 54 | 374 | 22.7 | 39.4 | 428 | No | 2020-09-17 11:28 | 44091.478 | 22.7 | 39.4 | 428 |  | caution | 2020-09-14 | B14660¦106¦¦Sep-17-2020 11:28
2020-09-17 11:28 | 44091.4781 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 402 |  | 3 | 21.4 | 42.5 | 404 | 23 | 46.2 | 494 | No | 2020-09-17 11:28 | 44091.4781 | 23 | 46.2 | 494 |  |  | 2020-09-14 | B21128¦402¦¦Sep-17-2020 11:28
2020-09-17 11:28 | 44091.4781 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-E wall |  | 0 | 18 | 70 | 440 | 23 | 51 | 600 |  | 2020-09-17 11:28 | 44091.4781 | 23 | 51 | 600 |  |  | 2020-09-14 | B25548¦1-E wall¦¦Sep-17-2020 11:28
2020-09-17 11:29 | 44091.4782 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 1 |  | 3 | 15.2 | 70 | 377 | 23.6 | 39.3 | 398 |  | 2020-09-17 11:29 | 44091.4782 | 23.6 | 39.3 | 398 |  | caution | 2020-09-14 | B20494¦Courtroom 1¦¦Sep-17-2020 11:28
2020-09-17 11:29 | 44091.4783 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 vestibule |  | 0 | 19 | 49 | 395 | 23 | 46 | 560 |  | 2020-09-17 11:29 | 44091.4783 | 23 | 46 | 560 |  |  | 2020-09-14 | B70235¦Court #4 vestibule ¦¦Sep-17-2020 11:28
2020-09-17 11:29 | 44091.4785 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 3 seating area |  | 0 | 23 | 41.5 | 420 | 22.6 | 47.8 | 440 |  | 2020-09-17 11:29 | 44091.4785 | 22.6 | 47.8 | 440 |  |  | 2020-09-14 | B17477¦Level 3 seating area ¦¦Sep-17-2020 11:29
2020-09-17 11:29 | 44091.4788 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - Middle left, facing judge |  | 2 | 20.2 | 41.3 | 366 | 22.5 | 39 | 397 |  | 2020-09-17 11:29 | 44091.4788 | 22.5 | 39 | 397 |  | caution | 2020-09-14 | B70277¦Court room - Middle left, facing judge¦¦Sep-17-2020 11:29
2020-09-17 11:30 | 44091.4788 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Stairway landing |  | 1 | 18.8 | 46.2 | 576 | 22.6 | 42.2 | 576 |  | 2020-09-17 11:30 | 44091.4788 | 22.6 | 42.2 | 576 |  |  | 2020-09-14 | B21554¦Stairway landing¦¦Sep-17-2020 11:29
2020-09-17 11:30 | 44091.4789 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Crown attorneys waiting area |  | 1 | 18.1 | 74.2 | 413 | 22.5 | 48.5 | 408 |  | 2020-09-17 11:30 | 44091.4789 | 22.5 | 48.5 | 408 |  |  | 2020-09-14 | B20390¦Crown attorneys waiting area¦¦Sep-17-2020 11:29
2020-09-17 11:30 | 44091.479 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 401 |  | 3 | 21.4 | 42.5 | 404 | 23 | 43.3 | 491 | No | 2020-09-17 11:30 | 44091.479 | 23 | 43.3 | 491 |  |  | 2020-09-14 | B21128¦401¦¦Sep-17-2020 11:29
2020-09-17 11:30 | 44091.4791 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 111 |  | 0 | 14 | 54 | 374 | 22.7 | 41.9 | 433 | No | 2020-09-17 11:30 | 44091.4791 | 22.7 | 41.9 | 433 |  |  | 2020-09-14 | B14660¦111¦¦Sep-17-2020 11:29
2020-09-17 11:31 | 44091.4795 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- S wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 610 |  | 2020-09-17 11:31 | 44091.4795 | 24 | 51 | 610 |  |  | 2020-09-14 | B25548¦1- S wall¦¦Sep-17-2020 11:30
2020-09-17 11:31 | 44091.4796 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview Room 3 |  | 0 | 19 | 49 | 395 | 23 | 45 | 534 |  | 2020-09-17 11:31 | 44091.4796 | 23 | 45 | 534 |  |  | 2020-09-14 | B70235¦Interview Room 3¦¦Sep-17-2020 11:30
2020-09-17 11:31 | 44091.4797 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Crown attorneys reception area |  | 1 | 18.1 | 74.2 | 413 | 2.5 | 49.5 | 404 |  | 2020-09-17 11:31 | 44091.4797 | 2.5 | 49.5 | 404 |  |  | 2020-09-14 | B20390¦Crown attorneys reception area¦¦Sep-17-2020 11:30
2020-09-17 11:31 | 44091.4798 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - Middle right, facing judge |  | 2 | 20.2 | 41.3 | 366 | 22.5 | 39.2 | 396 |  | 2020-09-17 11:31 | 44091.4798 | 22.5 | 39.2 | 396 |  | caution | 2020-09-14 | B70277¦Court room - Middle right, facing judge¦¦Sep-17-2020 11:30
2020-09-17 11:31 | 44091.4798 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 400 |  | 4 | 21.4 | 42.5 | 404 | 23 | 44.1 | 475 | No | 2020-09-17 11:31 | 44091.4798 | 23 | 44.1 | 475 |  |  | 2020-09-14 | B21128¦400¦¦Sep-17-2020 11:30
2020-09-17 11:31 | 44091.4798 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 1 |  | 3 | 15.2 | 70 | 377 | 23.2 | 42.1 | 392 |  | 2020-09-17 11:31 | 44091.4798 | 23.2 | 42.1 | 392 |  |  | 2020-09-14 | B20494¦Courtroom 1¦¦Sep-17-2020 11:30
2020-09-17 11:31 | 44091.4799 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 3 seating area 2 |  | 0 | 23 | 41.5 | 420 | 22.7 | 47.6 | 439 |  | 2020-09-17 11:31 | 44091.4799 | 22.7 | 47.6 | 439 |  |  | 2020-09-14 | B17477¦Level 3 seating area 2 ¦¦Sep-17-2020 11:31
2020-09-17 11:31 | 44091.48 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney library |  | 1 | 14.5 | 74.7 | 397 | 23.3 | 50.2 | 495 |  | 2020-09-17 11:31 | 44091.48 | 23.3 | 50.2 | 495 |  |  | 2020-09-14 | B20494¦Crown attorney library ¦¦Sep-17-2020 11:31
2020-09-17 11:32 | 44091.4806 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 203 |  | 0 | 14 | 54 | 374 | 22.3 | 45.2 | 522 | Np | 2020-09-17 11:32 | 44091.4806 | 22.3 | 45.2 | 522 |  |  | 2020-09-14 | B14660¦203¦¦Sep-17-2020 11:32
2020-09-17 11:32 | 44091.4806 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Crown attorneys office |  | 2 | 21.4 | 42.5 | 404 | 23.1 | 43.7 | 462 | No | 2020-09-17 11:32 | 44091.4806 | 23.1 | 43.7 | 462 |  |  | 2020-09-14 | B21128¦Crown attorneys office ¦¦Sep-17-2020 11:32
2020-09-17 11:32 | 44091.4807 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 seating area |  | 0 | 23 | 41.5 | 420 | 22.8 | 47.1 | 428 |  | 2020-09-17 11:32 | 44091.4807 | 22.8 | 47.1 | 428 |  |  | 2020-09-14 | B17477¦Courtroom 300 seating area ¦¦Sep-17-2020 11:32
2020-09-17 11:32 | 44091.4807 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 vestibule |  | 0 | 19 | 49 | 395 | 22 | 45 | 468 |  | 2020-09-17 11:32 | 44091.4807 | 22 | 45 | 468 |  |  | 2020-09-14 | B70235¦Court #3 vestibule ¦¦Sep-17-2020 11:32
2020-09-17 11:32 | 44091.4807 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - Judges desk, left side |  | 2 | 20.2 | 41.3 | 366 | 22.5 | 39.4 | 393 |  | 2020-09-17 11:32 | 44091.4807 | 22.5 | 39.4 | 393 |  | caution | 2020-09-14 | B70277¦Court room - Judges desk, left side¦¦Sep-17-2020 11:32
2020-09-17 11:32 | 44091.4807 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 4 |  | 1 | 18.1 | 74.2 | 413 | 22.1 | 49.8 | 412 |  | 2020-09-17 11:32 | 44091.4807 | 22.1 | 49.8 | 412 |  |  | 2020-09-14 | B20390¦Outside courtroom 4¦¦Sep-17-2020 11:32
2020-09-17 11:33 | 44091.481 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Legal aid office corridor |  | 1 | 18.8 | 46.2 | 405 | 22.2 | 42.2 | 576 |  | 2020-09-17 11:33 | 44091.481 | 22.2 | 42.2 | 576 |  |  | 2020-09-14 | B21554¦Legal aid office corridor¦¦Sep-17-2020 11:32
2020-09-17 11:33 | 44091.4812 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- S wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 590 |  | 2020-09-17 11:33 | 44091.4812 | 24 | 51 | 590 |  |  | 2020-09-14 | B25548¦1- S wall¦¦Sep-17-2020 11:32
2020-09-17 11:33 | 44091.4814 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom B |  | 0 | 17.8 | 53.7 | 411 | 20.3 | 58.8 | 510 | No access to Courtroom C & D due to trial proceedings | 2020-09-17 11:33 | 44091.4814 | 20.3 | 58.8 | 510 |  |  | 2020-09-14 | B20478¦Courtroom B¦¦Sep-17-2020 11:33
2020-09-17 11:34 | 44091.4817 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview Room 2 |  | 0 | 19 | 49 | 395 | 23 | 45 | 523 |  | 2020-09-17 11:34 | 44091.4817 | 23 | 45 | 523 |  |  | 2020-09-14 | B70235¦Interview Room 2¦¦Sep-17-2020 11:33
2020-09-17 11:34 | 44091.4817 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 seating area 2 |  | 0 | 23 | 41.5 | 420 | 23 | 46.6 | 419 |  | 2020-09-17 11:34 | 44091.4817 | 23 | 46.6 | 419 |  |  | 2020-09-14 | B17477¦Courtroom 300 seating area 2 ¦¦Sep-17-2020 11:33
2020-09-17 11:34 | 44091.4818 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney office |  | 2 | 14.5 | 74.7 | 397 | 23.1 | 50.2 | 507 |  | 2020-09-17 11:34 | 44091.4818 | 23.1 | 50.2 | 507 |  |  | 2020-09-14 | B20494¦Crown attorney office¦¦Sep-17-2020 11:33
2020-09-17 11:34 | 44091.4818 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 213 |  | 0 | 14 | 54 | 374 | 22.6 | 44.8 | 432 | No | 2020-09-17 11:34 | 44091.4818 | 22.6 | 44.8 | 432 |  |  | 2020-09-14 | B14660¦213¦¦Sep-17-2020 11:33
2020-09-17 11:34 | 44091.4819 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - Judges desk, right side |  | 2 | 20.2 | 41.3 | 366 | 22.6 | 39.3 | 394 |  | 2020-09-17 11:34 | 44091.4819 | 22.6 | 39.3 | 394 |  | caution | 2020-09-14 | B70277¦Court room - Judges desk, right side¦¦Sep-17-2020 11:33
2020-09-17 11:34 | 44091.4821 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 5 |  | 1 | 18.1 | 74.2 | 413 | 22 | 49.5 | 415 |  | 2020-09-17 11:34 | 44091.4821 | 22 | 49.5 | 415 |  |  | 2020-09-14 | B20390¦Outside courtroom 5¦¦Sep-17-2020 11:34
2020-09-17 11:34 | 44091.4822 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom A |  | 0 | 17.8 | 53.7 | 411 | 22.2 | 53.2 | 500 | No access to Courtroom C & D due to trial proceedings | 2020-09-17 11:34 | 44091.4822 | 22.2 | 53.2 | 500 |  |  | 2020-09-14 | B20478¦Courtroom A¦¦Sep-17-2020 11:34
2020-09-17 11:34 | 44091.4823 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Main waiting area |  | 2 | 18.8 | 46.2 | 405 | 21.8 | 42.9 | 537 |  | 2020-09-17 11:34 | 44091.4823 | 21.8 | 42.9 | 537 |  |  | 2020-09-14 | B21554¦Main waiting area ¦¦Sep-17-2020 11:34
2020-09-17 11:35 | 44091.4827 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 vestibule |  | 0 | 19 | 49 | 395 | 23 | 44 | 507 |  | 2020-09-17 11:35 | 44091.4827 | 23 | 44 | 507 |  |  | 2020-09-14 | B70235¦Court #2 vestibule ¦¦Sep-17-2020 11:35
2020-09-17 11:35 | 44091.4829 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- S wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 640 |  | 2020-09-17 11:35 | 44091.4829 | 24 | 51 | 640 |  |  | 2020-09-14 | B25548¦1- S wall¦¦Sep-17-2020 11:35
2020-09-17 11:35 | 44091.4829 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Front lobby |  | 4 | 21.1 | 35.6 | 453 | 21.2 | 46 | 537 |  | 2020-09-17 11:35 | 44091.4829 | 21.2 | 46 | 537 |  |  | 2020-09-14 | B25477¦Front lobby ¦¦Sep-17-2020 11:35
2020-09-17 11:35 | 44091.4829 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - Witness stand |  | 2 | 20.2 | 41.3 | 366 | 22.7 | 39 | 394 |  | 2020-09-17 11:35 | 44091.4829 | 22.7 | 39 | 394 |  | caution | 2020-09-14 | B70277¦Court room - Witness stand¦¦Sep-17-2020 11:35
2020-09-17 11:36 | 44091.483 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 209 |  | 1 | 14 | 54 | 374 | 22.7 | 46.2 | 465 | No | 2020-09-17 11:36 | 44091.483 | 22.7 | 46.2 | 465 |  |  | 2020-09-14 | B14660¦209¦¦Sep-17-2020 11:35
2020-09-17 11:36 | 44091.4833 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Front deask |  | 6 | 18.8 | 46.2 | 405 | 21.6 | 45.5 | 593 |  | 2020-09-17 11:36 | 44091.4833 | 21.6 | 45.5 | 593 |  |  | 2020-09-14 | B21554¦Front deask¦¦Sep-17-2020 11:36
2020-09-17 11:36 | 44091.4835 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Common Area behind Courtroom A |  | 0 | 17.8 | 53.7 | 411 | 22.8 | 53.2 | 500 | No access to Courtroom C & D due to trial proceedings | 2020-09-17 11:36 | 44091.4835 | 22.8 | 53.2 | 500 |  |  | 2020-09-14 | B20478¦Common Area behind Courtroom A¦¦Sep-17-2020 11:36
2020-09-17 11:36 | 44091.4835 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | HR |  | 2 | 21.1 | 35.6 | 453 | 21.7 | 45 | 553 |  | 2020-09-17 11:36 | 44091.4835 | 21.7 | 45 | 553 |  |  | 2020-09-14 | B25477¦HR¦¦Sep-17-2020 11:36
2020-09-17 11:36 | 44091.4837 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Court services |  | 0 | 23 | 41.5 | 420 | 23.1 | 46.51 | 426 |  | 2020-09-17 11:36 | 44091.4837 | 23.1 | 46.51 | 426 |  |  | 2020-09-14 | B17477¦Court services ¦¦Sep-17-2020 11:36
2020-09-17 11:37 | 44091.4837 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Interview room 6 |  | 1 | 18.1 | 74.2 | 413 | 21.9 | 50.3 | 413 |  | 2020-09-17 11:37 | 44091.4837 | 21.9 | 50.3 | 413 |  |  | 2020-09-14 | B20390¦Interview room 6¦¦Sep-17-2020 11:36
2020-09-17 11:37 | 44091.4839 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Duty Counsel room |  | 0 | 19 | 49 | 395 | 23 | 43 | 526 |  | 2020-09-17 11:37 | 44091.4839 | 23 | 43 | 526 |  |  | 2020-09-14 | B70235¦Duty Counsel room ¦¦Sep-17-2020 11:36
2020-09-17 11:37 | 44091.4839 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- S wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 640 |  | 2020-09-17 11:37 | 44091.4839 | 24 | 51 | 640 |  |  | 2020-09-14 | B25548¦1- S wall¦¦Sep-17-2020 11:36
2020-09-17 11:37 | 44091.484 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney printer room |  | 1 | 14.5 | 74.7 | 397 | 23.1 | 52.5 | 509 |  | 2020-09-17 11:37 | 44091.484 | 23.1 | 52.5 | 509 |  |  | 2020-09-14 | B20494¦Crown attorney printer room ¦¦Sep-17-2020 11:36
2020-09-17 11:37 | 44091.4842 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 210 |  | 2 | 14 | 54 | 374 | 22.7 | 46.2 | 454 | Np | 2020-09-17 11:37 | 44091.4842 | 22.7 | 46.2 | 454 |  |  | 2020-09-14 | B14660¦210¦¦Sep-17-2020 11:37
2020-09-17 11:37 | 44091.4843 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Main office |  | 3 | 18.8 | 46.2 | 405 | 21.8 | 44.9 | 661 |  | 2020-09-17 11:37 | 44091.4843 | 21.8 | 44.9 | 661 |  |  | 2020-09-14 | B21554¦Main office¦¦Sep-17-2020 11:37
2020-09-17 11:38 | 44091.4845 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | ED office |  | 2 | 21.1 | 35.6 | 453 | 22 | 44 | 538 |  | 2020-09-17 11:38 | 44091.4845 | 22 | 44 | 538 |  |  | 2020-09-14 | B25477¦ED office ¦¦Sep-17-2020 11:37
2020-09-17 11:38 | 44091.4845 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Law library |  | 0 | 17.8 | 53.7 | 411 | 23 | 50.8 | 473 | No access to Courtroom C & D due to trial proceedings | 2020-09-17 11:38 | 44091.4845 | 23 | 50.8 | 473 |  |  | 2020-09-14 | B20478¦Law library ¦¦Sep-17-2020 11:37
2020-09-17 11:38 | 44091.4847 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Judges chamber - front desk area |  | 1 | 20.2 | 41.3 | 366 | 22.8 | 39.9 | 395 |  | 2020-09-17 11:38 | 44091.4847 | 22.8 | 39.9 | 395 |  | caution | 2020-09-14 | B70277¦Judges chamber - front desk area¦¦Sep-17-2020 11:37
2020-09-17 11:38 | 44091.4847 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 doors |  | 0 | 23 | 41.5 | 420 | 23.1 | 46.5 | 415 |  | 2020-09-17 11:38 | 44091.4847 | 23.1 | 46.5 | 415 |  |  | 2020-09-14 | B17477¦Courtroom 300 doors ¦¦Sep-17-2020 11:37
2020-09-17 11:38 | 44091.4848 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Interview room 8 |  | 1 | 18.1 | 74.2 | 413 | 21.9 | 49.6 | 412 |  | 2020-09-17 11:38 | 44091.4848 | 21.9 | 49.6 | 412 |  |  | 2020-09-14 | B20390¦Interview room 8¦¦Sep-17-2020 11:38
2020-09-17 11:39 | 44091.4852 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 206 |  | 0 | 14 | 54 | 374 | 22.5 | 44.8 | 447 | No | 2020-09-17 11:39 | 44091.4852 | 22.5 | 44.8 | 447 |  |  | 2020-09-14 | B14660¦206¦¦Sep-17-2020 11:38
2020-09-17 11:39 | 44091.4855 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 bench |  | 0 | 23 | 41.5 | 420 | 23.1 | 46.7 | 413 |  | 2020-09-17 11:39 | 44091.4855 | 23.1 | 46.7 | 413 |  |  | 2020-09-14 | B17477¦Courtroom 300 bench ¦¦Sep-17-2020 11:39
2020-09-17 11:39 | 44091.4855 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | East Stairwell |  | 0 | 17.8 | 53.7 | 411 | 23.5 | 46.5 | 567 | No access to Courtroom C & D due to trial proceedings | 2020-09-17 11:39 | 44091.4855 | 23.5 | 46.5 | 567 |  |  | 2020-09-14 | B20478¦East Stairwell ¦¦Sep-17-2020 11:39
2020-09-17 11:39 | 44091.4856 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Admin office |  | 2 | 21.1 | 35.6 | 453 | 22.3 | 43 | 524 |  | 2020-09-17 11:39 | 44091.4856 | 22.3 | 43 | 524 |  |  | 2020-09-14 | B25477¦Admin office ¦¦Sep-17-2020 11:39
2020-09-17 11:39 | 44091.4856 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 vestibule |  | 0 | 19 | 49 | 395 | 23 | 45 | 782 |  | 2020-09-17 11:39 | 44091.4856 | 23 | 45 | 782 |  |  | 2020-09-14 | B70235¦Court #1 vestibule ¦¦Sep-17-2020 11:39
2020-09-17 11:39 | 44091.4857 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Judges chamber - behind desk, beside back door |  | 1 | 20.2 | 41.3 | 366 | 23 | 40.1 | 399 |  | 2020-09-17 11:39 | 44091.4857 | 23 | 40.1 | 399 |  |  | 2020-09-14 | B70277¦Judges chamber - behind desk, beside back door¦¦Sep-17-2020 11:39
2020-09-17 11:40 | 44091.4859 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 judge |  | 1 | 26 | 37 | 365 | 24 | 40 | 382 |  | 2020-09-17 11:40 | 44091.4859 | 24 | 40 | 382 |  | caution | 2020-09-14 | B20772¦H9 judge ¦¦Sep-17-2020 11:39
2020-09-17 11:40 | 44091.486 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell, third floor |  | 1 | 18.1 | 74.2 | 413 | 22.6 | 50.7 | 417 |  | 2020-09-17 11:40 | 44091.486 | 22.6 | 50.7 | 417 |  |  | 2020-09-14 | B20390¦Main stairwell, third floor¦¦Sep-17-2020 11:39
2020-09-17 11:40 | 44091.4862 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney waiting room |  | 1 | 14.5 | 74.7 | 397 | 22.9 | 51.3 | 525 |  | 2020-09-17 11:40 | 44091.4862 | 22.9 | 51.3 | 525 |  |  | 2020-09-14 | B20494¦Crown attorney waiting room ¦¦Sep-17-2020 11:40
2020-09-17 11:40 | 44091.4862 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 590 |  | 2020-09-17 11:40 | 44091.4862 | 24 | 51 | 590 |  |  | 2020-09-14 | B25548¦1-S wall¦¦Sep-17-2020 11:40
2020-09-17 11:41 | 44091.4865 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 middle |  | 1 | 26 | 37 | 365 | 24 | 40 | 382 |  | 2020-09-17 11:41 | 44091.4865 | 24 | 40 | 382 |  | caution | 2020-09-14 | B20772¦H9 middle¦¦Sep-17-2020 11:40
2020-09-17 11:41 | 44091.4866 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Financial services |  | 4 | 21.1 | 35.6 | 453 | 22.4 | 43.4 | 531 |  | 2020-09-17 11:41 | 44091.4866 | 22.4 | 43.4 | 531 |  |  | 2020-09-14 | B25477¦Financial services ¦¦Sep-17-2020 11:40
2020-09-17 11:41 | 44091.4867 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Third floor waiting area |  | 1 | 18.1 | 74.2 | 413 | 22.6 | 49.3 | 416 |  | 2020-09-17 11:41 | 44091.4867 | 22.6 | 49.3 | 416 |  |  | 2020-09-14 | B20390¦Third floor waiting area¦¦Sep-17-2020 11:40
2020-09-17 11:41 | 44091.4868 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Main floor common area |  | 2 | 17.8 | 53.7 | 411 | 22.7 | 46.1 | 516 | No access to Courtroom C & D due to trial proceedings | 2020-09-17 11:41 | 44091.4868 | 22.7 | 46.1 | 516 |  |  | 2020-09-14 | B20478¦Main floor common area¦¦Sep-17-2020 11:40
2020-09-17 11:41 | 44091.4868 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Front Lobby |  | 2 | 19 | 54.1 | 393 | 20.3 | 53.9 | 436 | Unable to access courtroom #1and#2for the first round of readings Court was in session | 2020-09-17 11:41 | 44091.4868 | 20.3 | 53.9 | 436 |  |  | 2020-09-14 | B20550¦Front Lobby¦¦Sep-17-2020 11:41
2020-09-17 11:41 | 44091.4868 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 3 ramp |  | 0 | 23 | 41.5 | 420 | 22.8 | 46.9 | 435 |  | 2020-09-17 11:41 | 44091.4868 | 22.8 | 46.9 | 435 |  |  | 2020-09-14 | B17477¦Level 3 ramp ¦¦Sep-17-2020 11:41
2020-09-17 11:41 | 44091.487 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation office - desk area |  | 2 | 20.2 | 41.3 | 366 | 23.1 | 39 | 403 |  | 2020-09-17 11:41 | 44091.487 | 23.1 | 39 | 403 |  | caution | 2020-09-14 | B70277¦Mediation office - desk area¦¦Sep-17-2020 11:41
2020-09-17 11:41 | 44091.487 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 - box |  | 1 | 26 | 37 | 365 | 23 | 42 | 383 |  | 2020-09-17 11:41 | 44091.487 | 23 | 42 | 383 |  |  | 2020-09-14 | B20772¦H9 - box ¦¦Sep-17-2020 11:41
2020-09-17 11:42 | 44091.4877 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 left |  | 1 | 26 | 37 | 365 | 23 | 42 | 386 |  | 2020-09-17 11:42 | 44091.4877 | 23 | 42 | 386 |  |  | 2020-09-14 | B20772¦H9 left ¦¦Sep-17-2020 11:42
2020-09-17 11:42 | 44091.4877 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 1 |  | 1 | 18.1 | 74.2 | 413 | 22.1 | 49.8 | 405 |  | 2020-09-17 11:42 | 44091.4877 | 22.1 | 49.8 | 405 |  |  | 2020-09-14 | B20390¦Outside courtroom 1¦¦Sep-17-2020 11:42
2020-09-17 11:42 | 44091.4878 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation office - printer area |  | 2 | 20.2 | 41.3 | 366 | 23.1 | 39.3 | 466 |  | 2020-09-17 11:42 | 44091.4878 | 23.1 | 39.3 | 466 |  | caution | 2020-09-14 | B70277¦Mediation office - printer area¦¦Sep-17-2020 11:42
2020-09-17 11:42 | 44091.4878 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Courtroom |  | 6 | 21.1 | 35.6 | 453 | 22.4 | 43.8 | 499 |  | 2020-09-17 11:42 | 44091.4878 | 22.4 | 43.8 | 499 |  |  | 2020-09-14 | B25477¦Courtroom ¦¦Sep-17-2020 11:42
2020-09-17 11:42 | 44091.4878 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 4 seating area |  | 0 | 23 | 41.5 | 420 | 22.9 | 45.9 | 445 |  | 2020-09-17 11:42 | 44091.4878 | 22.9 | 45.9 | 445 |  |  | 2020-09-14 | B17477¦Level 4 seating area ¦¦Sep-17-2020 11:42
2020-09-17 11:43 | 44091.4881 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- S wall |  | 0 | 18 | 70 | 440 | 24 | 49 | 590 |  | 2020-09-17 11:43 | 44091.4881 | 24 | 49 | 590 |  |  | 2020-09-14 | B25548¦1- S wall¦¦Sep-17-2020 11:42
2020-09-17 11:43 | 44091.4881 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 right |  | 1 | 26 | 37 | 365 | 23 | 42 | 382 |  | 2020-09-17 11:43 | 44091.4881 | 23 | 42 | 382 |  |  | 2020-09-14 | B20772¦H9 right¦¦Sep-17-2020 11:42
2020-09-17 11:43 | 44091.4882 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 303 |  | 1 | 14 | 54 | 374 | 22.6 | 42.5 | 450 | No | 2020-09-17 11:43 | 44091.4882 | 22.6 | 42.5 | 450 |  |  | 2020-09-14 | B14660¦303¦¦Sep-17-2020 11:43
2020-09-17 11:43 | 44091.4883 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Corridor outside of Admin office |  | 0 | 17.8 | 53.7 | 411 | 23.2 | 45.1 | 517 | No access to Courtroom C & D due to trial proceedings | 2020-09-17 11:43 | 44091.4883 | 23.2 | 45.1 | 517 |  |  | 2020-09-14 | B20478¦Corridor outside of Admin office ¦¦Sep-17-2020 11:43
2020-09-17 11:43 | 44091.4884 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Cell block |  | 1 | 14.5 | 74.7 | 397 | 22.5 | 50.3 | 469 |  | 2020-09-17 11:43 | 44091.4884 | 22.5 | 50.3 | 469 |  |  | 2020-09-14 | B20494¦Cell block ¦¦Sep-17-2020 11:43
2020-09-17 11:44 | 44091.4885 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 4 seating area 2 |  | 0 | 23 | 41.5 | 420 | 22.9 | 45.5 | 430 |  | 2020-09-17 11:44 | 44091.4885 | 22.9 | 45.5 | 430 |  |  | 2020-09-14 | B17477¦Level 4 seating area 2¦¦Sep-17-2020 11:43
2020-09-17 11:44 | 44091.4888 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Mezzanine |  | 0 | 21.1 | 35.6 | 453 | 22.3 | 43.1 | 510 |  | 2020-09-17 11:44 | 44091.4888 | 22.3 | 43.1 | 510 |  |  | 2020-09-14 | B25477¦Mezzanine ¦¦Sep-17-2020 11:43
2020-09-17 11:44 | 44091.489 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Kitchen/lunch room - counter area |  | 1 | 20.2 | 41.3 | 366 | 23 | 39.1 | 440 |  | 2020-09-17 11:44 | 44091.489 | 23 | 39.1 | 440 |  | caution | 2020-09-14 | B70277¦Kitchen/lunch room - counter area¦¦Sep-17-2020 11:44
2020-09-17 11:44 | 44091.4891 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Main entrance |  | 0 | 19.4 | 55 | 422 | 21.2 | 50.2 | 435 |  | 2020-09-17 11:44 | 44091.4891 | 21.2 | 50.2 | 435 |  |  | 2020-09-14 | B25039¦Main entrance¦¦Sep-17-2020 11:44
2020-09-17 11:45 | 44091.4892 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 waiting area |  | 1 | 26 | 37 | 365 | 23 | 42 | 385 |  | 2020-09-17 11:45 | 44091.4892 | 23 | 42 | 385 |  |  | 2020-09-14 | B20772¦H9 waiting area¦¦Sep-17-2020 11:44
2020-09-17 11:45 | 44091.4893 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-W wall |  | 0 | 18 | 70 | 440 | 24 | 50 | 590 |  | 2020-09-17 11:45 | 44091.4893 | 24 | 50 | 590 |  |  | 2020-09-14 | B25548¦1-W wall¦¦Sep-17-2020 11:44
2020-09-17 11:45 | 44091.4893 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 302 |  | 4 | 14 | 54 | 374 | 23.1 | 39.5 | 445 | No | 2020-09-17 11:45 | 44091.4893 | 23.1 | 39.5 | 445 |  | caution | 2020-09-14 | B14660¦302¦¦Sep-17-2020 11:44
2020-09-17 11:45 | 44091.4895 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Courtroom#2 |  | 0 | 19 | 54.1 | 393 | 24 | 41.8 | 447 |  | 2020-09-17 11:45 | 44091.4895 | 24 | 41.8 | 447 |  |  | 2020-09-14 | B20550¦Courtroom#2¦¦Sep-17-2020 11:44
2020-09-17 11:45 | 44091.4895 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | 2nd floor common area |  | 1 | 17.8 | 53.7 | 411 | 22.7 | 48.6 | 553 | No access to Courtroom C & D due to trial proceedings | 2020-09-17 11:45 | 44091.4895 | 22.7 | 48.6 | 553 |  |  | 2020-09-14 | B20478¦2nd floor common area ¦¦Sep-17-2020 11:44
2020-09-17 11:45 | 44091.4896 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside third floor elevator |  | 1 | 18.1 | 74.2 | 413 | 22 | 50.1 | 438 |  | 2020-09-17 11:45 | 44091.4896 | 22 | 50.1 | 438 |  |  | 2020-09-14 | B20390¦Outside third floor elevator¦¦Sep-17-2020 11:44
2020-09-17 11:45 | 44091.4896 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 seating area |  | 0 | 23 | 41.5 | 429 | 23 | 45.6 | 424 |  | 2020-09-17 11:45 | 44091.4896 | 23 | 45.6 | 424 |  |  | 2020-09-14 | B17477¦Courtroom 400 seating area ¦¦Sep-17-2020 11:45
2020-09-17 11:45 | 44091.4897 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Board room |  | 0 | 21.1 | 35.6 | 453 | 22.3 | 42.4 | 463 |  | 2020-09-17 11:45 | 44091.4897 | 22.3 | 42.4 | 463 |  |  | 2020-09-14 | B25477¦Board room ¦¦Sep-17-2020 11:45
2020-09-17 11:45 | 44091.4897 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Police Sergeant office |  | 2 | 19 | 49 | 395 |  |  |  | Occupied, no a | 2020-09-17 11:45 | 44091.4897 | [5 empty] | 2020-09-14 | B70235¦Police Sergeant office ¦¦Sep-17-2020 11:45
2020-09-17 11:46 | 44091.4902 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Lunch room |  | 0 | 19.4 | 55 | 422 | 21.6 | 53.7 | 513 |  | 2020-09-17 11:46 | 44091.4902 | 21.6 | 53.7 | 513 |  |  | 2020-09-14 | B25039¦Lunch room¦¦Sep-17-2020 11:45
2020-09-17 11:46 | 44091.4903 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - kitchen entrance |  | 1 | 20.2 | 41.3 | 366 | 23 | 39.2 | 415 |  | 2020-09-17 11:46 | 44091.4903 | 23 | 39.2 | 415 |  | caution | 2020-09-14 | B70277¦Mediation room - kitchen entrance¦¦Sep-17-2020 11:46
2020-09-17 11:46 | 44091.4905 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Library |  | 0 | 21.1 | 35.6 | 453 | 22.4 | 42.7 | 470 |  | 2020-09-17 11:46 | 44091.4905 | 22.4 | 42.7 | 470 |  |  | 2020-09-14 | B25477¦Library ¦¦Sep-17-2020 11:46
2020-09-17 11:46 | 44091.4906 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jennifer Munby office |  | 1 | 19 | 49 | 395 |  |  |  | Occupied, no access | 2020-09-17 11:46 | 44091.4906 | [5 empty] | 2020-09-14 | B70235¦Jennifer Munby office ¦¦Sep-17-2020 11:46
2020-09-17 11:47 | 44091.4906 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Courtroom$1 |  | 0 | 19 | 54.1 | 393 | 23.9 | 41.6 | 438 |  | 2020-09-17 11:47 | 44091.4906 | 23.9 | 41.6 | 438 |  |  | 2020-09-14 | B20550¦Courtroom$1¦¦Sep-17-2020 11:46
2020-09-17 11:47 | 44091.4907 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 seating area 2 |  | 0 | 23 | 41.5 | 420 | 22.8 | 45.8 | 427 |  | 2020-09-17 11:47 | 44091.4907 | 22.8 | 45.8 | 427 |  |  | 2020-09-14 | B17477¦Courtroom 400 seating area 2 ¦¦Sep-17-2020 11:46
2020-09-17 11:47 | 44091.4908 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-W wall |  | 0 | 18 | 70 | 440 | 24 | 50 | 590 |  | 2020-09-17 11:47 | 44091.4908 | 24 | 50 | 590 |  |  | 2020-09-14 | B25548¦1-W wall¦¦Sep-17-2020 11:46
2020-09-17 11:47 | 44091.4909 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | 2nd floor Crown Attorney corridor |  | 0 | 17.8 | 53.7 | 411 | 22.5 | 49.8 | 481 | No access to Courtroom C & D due to trial proceedings | 2020-09-17 11:47 | 44091.4909 | 22.5 | 49.8 | 481 |  |  | 2020-09-14 | B20478¦2nd floor Crown Attorney corridor ¦¦Sep-17-2020 11:46
2020-09-17 11:47 | 44091.491 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - centre table |  | 1 | 20.2 | 41.3 | 366 | 23.1 | 38.8 | 414 |  | 2020-09-17 11:47 | 44091.491 | 23.1 | 38.8 | 414 |  | caution | 2020-09-14 | B70277¦Mediation room - centre table¦¦Sep-17-2020 11:46
2020-09-17 11:47 | 44091.4912 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Lunch room hall |  | 0 | 19.4 | 55 | 422 | 22.1 | 52.3 | 515 |  | 2020-09-17 11:47 | 44091.4912 | 22.1 | 52.3 | 515 |  |  | 2020-09-14 | B25039¦Lunch room hall¦¦Sep-17-2020 11:47
2020-09-17 11:47 | 44091.4913 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jason Mariasine office |  | 1 | 19 | 49 | 395 |  |  |  | Occupied, no access | 2020-09-17 11:47 | 44091.4913 | [5 empty] | 2020-09-14 | B70235¦Jason Mariasine office ¦¦Sep-17-2020 11:47
2020-09-17 11:48 | 44091.4916 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 301b |  | 0 | 14 | 54 | 374 | 23.1 | 41.3 | 424 | No | 2020-09-17 11:48 | 44091.4916 | 23.1 | 41.3 | 424 |  |  | 2020-09-14 | B14660¦301b¦¦Sep-17-2020 11:47
2020-09-17 11:48 | 44091.4919 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - near hallway entrance |  | 1 | 20.2 | 41.3 | 366 | 23.1 | 38.9 | 414 |  | 2020-09-17 11:48 | 44091.4919 | 23.1 | 38.9 | 414 |  | caution | 2020-09-14 | B70277¦Mediation room - near hallway entrance¦¦Sep-17-2020 11:48
2020-09-17 11:48 | 44091.492 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Judicial office corridor |  | 0 | 17.8 | 53.7 | 411 | 22.3 | 50.5 | 477 | No access to Courtroom C & D due to trial proceedings | 2020-09-17 11:48 | 44091.492 | 22.3 | 50.5 | 477 |  |  | 2020-09-14 | B20478¦Judicial office corridor ¦¦Sep-17-2020 11:48
2020-09-17 11:49 | 44091.492 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Service Ontario |  | 3 | 19.4 | 55 | 422 | 22.6 | 51.8 | 535 |  | 2020-09-17 11:49 | 44091.492 | 22.6 | 51.8 | 535 |  |  | 2020-09-14 | B25039¦Service Ontario¦¦Sep-17-2020 11:48
2020-09-17 11:49 | 44091.4921 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Peterborough Police |  | 1 | 19 | 49 | 395 | 22 | 46 | 553 |  | 2020-09-17 11:49 | 44091.4921 | 22 | 46 | 553 |  |  | 2020-09-14 | B70235¦Peterborough Police ¦¦Sep-17-2020 11:48
2020-09-17 11:49 | 44091.4921 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 doors |  | 3 | 23 | 41.5 | 420 | 23 | 46 | 426 |  | 2020-09-17 11:49 | 44091.4921 | 23 | 46 | 426 |  |  | 2020-09-14 | B17477¦Courtroom 400 doors¦¦Sep-17-2020 11:48
2020-09-17 11:49 | 44091.4923 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Waiting area small |  | 0 | 19 | 54.1 | 393 | 24.6 | 41 | 441 |  | 2020-09-17 11:49 | 44091.4923 | 24.6 | 41 | 441 |  |  | 2020-09-14 | B20550¦Waiting area small¦¦Sep-17-2020 11:48
2020-09-17 11:49 | 44091.4924 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-W wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 600 |  | 2020-09-17 11:49 | 44091.4924 | 24 | 51 | 600 |  |  | 2020-09-14 | B25548¦1-W wall¦¦Sep-17-2020 11:49
2020-09-17 11:49 | 44091.4926 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 judge |  | 1 | 19 | 49 | 395 |  |  |  | Occupied, no access | 2020-09-17 11:49 | 44091.4926 | [5 empty] | 2020-09-14 | B70235¦Court #4 judge ¦¦Sep-17-2020 11:49
2020-09-17 11:50 | 44091.4929 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Duty council office - desk area |  | 1 | 20.2 | 41.3 | 366 | 23.1 | 38.5 | 410 |  | 2020-09-17 11:50 | 44091.4929 | 23.1 | 38.5 | 410 |  | caution | 2020-09-14 | B70277¦Duty council office - desk area¦¦Sep-17-2020 11:49
2020-09-17 11:50 | 44091.493 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Water fountain |  | 0 | 19.4 | 55 | 422 | 22.1 | 51 | 528 |  | 2020-09-17 11:50 | 44091.493 | 22.1 | 51 | 528 |  |  | 2020-09-14 | B25039¦Water fountain¦¦Sep-17-2020 11:49
2020-09-17 11:50 | 44091.4932 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 lawyer |  | 1 | 19 | 49 | 395 |  |  |  | Occupied, no access | 2020-09-17 11:50 | 44091.4932 | [5 empty] | 2020-09-14 | B70235¦Court #4 lawyer ¦¦Sep-17-2020 11:50
2020-09-17 11:50 | 44091.4934 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 bench |  | 3 | 23 | 41.5 | 420 | 22.7 | 45.9 | 420 |  | 2020-09-17 11:50 | 44091.4934 | 22.7 | 45.9 | 420 |  |  | 2020-09-14 | B17477¦Courtroom 400 bench ¦¦Sep-17-2020 11:50
2020-09-17 11:51 | 44091.4935 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Waiting area big |  | 0 | 19 | 54.1 | 393 | 24.6 | 39.7 | 443 |  | 2020-09-17 11:51 | 44091.4935 | 24.6 | 39.7 | 443 |  | caution | 2020-09-14 | B20550¦Waiting area big¦¦Sep-17-2020 11:50
2020-09-17 11:51 | 44091.4938 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Crown attorney office |  | 2 | 15 | 68 | 421 | 21.1 | 52.7 | 534 | No | 2020-09-17 11:51 | 44091.4938 | 21.1 | 52.7 | 534 |  |  | 2020-09-14 | B20489¦Crown attorney office ¦¦Sep-17-2020 11:51
2020-09-17 11:51 | 44091.4939 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 judge |  | 1 | 19 | 49 | 395 |  |  |  | Occupied, no access | 2020-09-17 11:51 | 44091.4939 | [5 empty] | 2020-09-14 | B70235¦Court #3 judge ¦¦Sep-17-2020 11:51
2020-09-17 11:51 | 44091.4939 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Meditation room |  | 0 | 19.4 | 55 | 422 | 22.6 | 51.4 | 521 |  | 2020-09-17 11:51 | 44091.4939 | 22.6 | 51.4 | 521 |  |  | 2020-09-14 | B25039¦Meditation room¦¦Sep-17-2020 11:51
2020-09-17 11:51 | 44091.4939 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Duty council office - back right seating |  | 1 | 20.2 | 41.3 | 366 | 23.2 | 38.3 | 409 |  | 2020-09-17 11:51 | 44091.4939 | 23.2 | 38.3 | 409 |  | caution | 2020-09-14 | B70277¦Duty council office - back right seating¦¦Sep-17-2020 11:51
2020-09-17 11:52 | 44091.4944 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 lawyer |  | 1 | 19 | 49 | 395 |  |  |  | Occupied, no access | 2020-09-17 11:52 | 44091.4944 | [5 empty] | 2020-09-14 | B70235¦Court #3 lawyer ¦¦Sep-17-2020 11:51
2020-09-17 11:52 | 44091.4945 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Security desk |  | 0 | 19 | 54.1 | 393 | 24 | 41 | 439 |  | 2020-09-17 11:52 | 44091.4945 | 24 | 41 | 439 |  |  | 2020-09-14 | B20550¦Security desk¦¦Sep-17-2020 11:52
2020-09-17 11:52 | 44091.4946 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | S foyer |  | 0 | 18 | 70 | 440 | 24 | 50 | 625 |  | 2020-09-17 11:52 | 44091.4946 | 24 | 50 | 625 |  |  | 2020-09-14 | B25548¦S foyer¦¦Sep-17-2020 11:52
2020-09-17 11:52 | 44091.4947 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Basement corridor middle |  | 0 | 17.8 | 53.7 | 411 | 21.8 | 56 | 518 | No access to Courtroom C & D due to trial proceedings | 2020-09-17 11:52 | 44091.4947 | 21.8 | 56 | 518 |  |  | 2020-09-14 | B20478¦Basement corridor middle ¦¦Sep-17-2020 11:52
2020-09-17 11:53 | 44091.4949 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Fire extinguisher |  | 0 | 19.4 | 55 | 422 | 22.6 | 51.4 | 541 |  | 2020-09-17 11:53 | 44091.4949 | 22.6 | 51.4 | 541 |  |  | 2020-09-14 | B25039¦Fire extinguisher¦¦Sep-17-2020 11:52
2020-09-17 11:53 | 44091.495 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 4 ramp |  | 0 | 23 | 41.5 | 420 | 22.9 | 46.6 | 424 |  | 2020-09-17 11:53 | 44091.495 | 22.9 | 46.6 | 424 |  |  | 2020-09-14 | B17477¦Level 4 ramp ¦¦Sep-17-2020 11:52
2020-09-17 11:53 | 44091.495 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 judge |  | 1 | 26 | 37 | 365 | 22 | 43 | 377 |  | 2020-09-17 11:53 | 44091.495 | 22 | 43 | 377 |  |  | 2020-09-14 | B20772¦H15 judge¦¦Sep-17-2020 11:52
2020-09-17 11:53 | 44091.495 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 judge |  | 1 | 19 | 49 | 395 |  |  |  | Occupied, no access | 2020-09-17 11:53 | 44091.495 | [5 empty] | 2020-09-14 | B70235¦Court #2 judge ¦¦Sep-17-2020 11:52
2020-09-17 11:53 | 44091.4951 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Crown attorney waiting area |  | 0 | 15 | 68 | 421 | 21.5 | 51.8 | 553 | No | 2020-09-17 11:53 | 44091.4951 | 21.5 | 51.8 | 553 |  |  | 2020-09-14 | B20489¦Crown attorney waiting area ¦¦Sep-17-2020 11:52
2020-09-17 11:53 | 44091.4954 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Administration office east |  | 1 | 18 | 61 | 422 | 23 | 43 | 576 |  | 2020-09-17 11:53 | 44091.4954 | 23 | 43 | 576 |  |  | 2020-09-14 | B25479¦Administration office east ¦¦Sep-17-2020 11:53
2020-09-17 11:53 | 44091.4955 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 301a |  | 0 | 14 | 54 | 374 | 23.5 | 39.8 | 420 | No | 2020-09-17 11:53 | 44091.4955 | 23.5 | 39.8 | 420 |  | caution | 2020-09-14 | B14660¦301a¦¦Sep-17-2020 11:53
2020-09-17 11:54 | 44091.4957 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 lawyer |  | 1 | 19 | 49 | 395 |  |  |  | Occupied, no access | 2020-09-17 11:54 | 44091.4957 | [5 empty] | 2020-09-14 | B70235¦Court #2 lawyer ¦¦Sep-17-2020 11:53
2020-09-17 11:54 | 44091.4958 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Administration office west |  | 2 | 18 | 61 | 422 | 23 | 44 | 591 |  | 2020-09-17 11:54 | 44091.4958 | 23 | 44 | 591 |  |  | 2020-09-14 | B25479¦Administration office west ¦¦Sep-17-2020 11:54
2020-09-17 11:54 | 44091.4959 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside of door “302” at the end |  | 1 | 20.2 | 41.3 | 466 | 22.3 | 38.8 | 418 |  | 2020-09-17 11:54 | 44091.4959 | 22.3 | 38.8 | 418 |  | caution | 2020-09-14 | B70277¦Hallway - outside of door “302” at the end¦¦Sep-17-2020 11:54
2020-09-17 11:54 | 44091.4959 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Handicapped washroom |  | 0 | 19.4 | 55 | 422 | 22.6 | 51.2 | 524 |  | 2020-09-17 11:54 | 44091.4959 | 22.6 | 51.2 | 524 |  |  | 2020-09-14 | B25039¦Handicapped washroom¦¦Sep-17-2020 11:54
2020-09-17 11:54 | 44091.4959 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 plaintiff |  | 1 | 26 | 37 | 365 | 22 | 43 | 387 |  | 2020-09-17 11:54 | 44091.4959 | 22 | 43 | 387 |  |  | 2020-09-14 | B20772¦H15 plaintiff¦¦Sep-17-2020 11:54
2020-09-17 11:54 | 44091.496 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | N foyer |  | 0 | 18 | 70 | 440 | 24 | 50 | 585 |  | 2020-09-17 11:54 | 44091.496 | 24 | 50 | 585 |  |  | 2020-09-14 | B25548¦N foyer¦¦Sep-17-2020 11:54
2020-09-17 11:54 | 44091.496 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 seating area |  | 0 | 23 | 41.5 | 420 | 22.8 | 46.9 | 418 |  | 2020-09-17 11:54 | 44091.496 | 22.8 | 46.9 | 418 |  |  | 2020-09-14 | B17477¦Level 5 seating area ¦¦Sep-17-2020 11:54
2020-09-17 11:54 | 44091.496 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Administrative office |  | 2 | 19 | 54.1 | 393 | 24 | 41.1 | 447 |  | 2020-09-17 11:54 | 44091.496 | 24 | 41.1 | 447 |  |  | 2020-09-14 | B20550¦Administrative office¦¦Sep-17-2020 11:54
2020-09-17 11:55 | 44091.4962 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Basement prisoner holding corridor |  | 0 | 17.8 | 53.7 | 411 | 21.2 | 50.5 | 477 | No access to Courtroom C & D due to trial proceedings | 2020-09-17 11:54 | 44091.4962 | 21.2 | 50.5 | 477 |  |  | 2020-09-14 | B20478¦Basement prisoner holding corridor ¦¦Sep-17-2020 11:54
2020-09-17 11:55 | 44091.4963 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 2nd floor hallway |  | 0 | 15 | 68 | 421 | 21.7 | 50.4 | 466 | No | 2020-09-17 11:55 | 44091.4963 | 21.7 | 50.4 | 466 |  |  | 2020-09-14 | B20489¦2nd floor hallway ¦¦Sep-17-2020 11:54
2020-09-17 11:55 | 44091.4963 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 judge |  | 1 | 19 | 49 | 395 |  |  |  | Occupied, no access | 2020-09-17 11:55 | 44091.4963 | [5 empty] | 2020-09-14 | B70235¦Court #1 judge ¦¦Sep-17-2020 11:54
2020-09-17 11:55 | 44091.4964 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Intake office |  | 0 | 18 | 61 | 422 | 23 | 38 | 600 |  | 2020-09-17 11:55 | 44091.4964 | 23 | 38 | 600 |  | caution | 2020-09-14 | B25479¦Intake office ¦¦Sep-17-2020 11:54
2020-09-17 11:55 | 44091.4968 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 defense |  | 1 | 26 | 37 | 365 | 22 | 44 | 385 |  | 2020-09-17 11:55 | 44091.4968 | 22 | 44 | 385 |  |  | 2020-09-14 | B20772¦H15 defense ¦¦Sep-17-2020 11:55
2020-09-17 11:56 | 44091.4969 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside of duty council office entrance |  | 1 | 20.2 | 41.3 | 366 | 22.2 | 39.3 | 420 |  | 2020-09-17 11:56 | 44091.4969 | 22.2 | 39.3 | 420 |  | caution | 2020-09-14 | B70277¦Hallway - outside of duty council office entrance¦¦Sep-17-2020 11:55
2020-09-17 11:56 | 44091.4969 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Rear hall |  | 0 | 19.4 | 55 | 422 | 22.7 | 51 | 527 |  | 2020-09-17 11:56 | 44091.4969 | 22.7 | 51 | 527 |  |  | 2020-09-14 | B25039¦Rear hall¦¦Sep-17-2020 11:55
2020-09-17 11:56 | 44091.4969 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 lawyer |  | 1 | 19 | 49 | 395 |  |  |  | Occupied, no access | 2020-09-17 11:56 | 44091.4969 | [5 empty] | 2020-09-14 | B70235¦Court #1 lawyer ¦¦Sep-17-2020 11:55
2020-09-17 11:56 | 44091.4971 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Lunchroom |  | 0 | 18 | 61 | 422 | 23 | 39 | 593 |  | 2020-09-17 11:56 | 44091.4971 | 23 | 39 | 593 |  | caution | 2020-09-14 | B25479¦Lunchroom ¦¦Sep-17-2020 11:55
2020-09-17 11:56 | 44091.4971 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 seating area 2 |  | 0 | 23 | 41.5 | 420 | 22.3 | 47.2 | 420 |  | 2020-09-17 11:56 | 44091.4971 | 22.3 | 47.2 | 420 |  |  | 2020-09-14 | B17477¦Level 5 seating area 2 ¦¦Sep-17-2020 11:55
2020-09-17 11:56 | 44091.4972 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 18 | 70 | 440 | 24 | 50 | 600 |  | 2020-09-17 11:56 | 44091.4972 | 24 | 50 | 600 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-17-2020 11:55
2020-09-17 11:56 | 44091.4976 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main lobby |  | 6 | 19 | 49 | 395 | 23 | 43 | 568 |  | 2020-09-17 11:56 | 44091.4976 | 23 | 43 | 568 |  |  | 2020-09-14 | B70235¦Main lobby ¦¦Sep-17-2020 11:56
2020-09-17 11:57 | 44091.4976 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 2 |  | 0 | 18 | 61 | 422 | 22 | 43 | 552 | Couldn't get into courtroom 1,3,4 and 5 | 2020-09-17 11:57 | 44091.4976 | 22 | 43 | 552 |  |  | 2020-09-14 | B25479¦Courtroom 2¦¦Sep-17-2020 11:56
2020-09-17 11:57 | 44091.4978 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | 911 entrance |  | 0 | 19.4 | 55 | 422 | 22.7 | 51.1 | 527 |  | 2020-09-17 11:57 | 44091.4978 | 22.7 | 51.1 | 527 |  |  | 2020-09-14 | B25039¦911 entrance¦¦Sep-17-2020 11:56
2020-09-17 11:57 | 44091.4979 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 3rd floor hallway |  | 0 | 15 | 68 | 421 | 22 | 49.7 | 424 | No | 2020-09-17 11:57 | 44091.4979 | 22 | 49.7 | 424 |  |  | 2020-09-14 | B20489¦3rd floor hallway ¦¦Sep-17-2020 11:56
2020-09-17 11:57 | 44091.4981 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Manage of operations seating area |  | 0 | 23 | 41.5 | 420 | 22.7 | 46.7 | 425 |  | 2020-09-17 11:57 | 44091.4981 | 22.7 | 46.7 | 425 |  |  | 2020-09-14 | B17477¦Manage of operations seating area ¦¦Sep-17-2020 11:57
2020-09-17 11:58 | 44091.4984 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Library |  | 0 | 18 | 61 | 422 | 23 | 43 | 536 |  | 2020-09-17 11:58 | 44091.4984 | 23 | 43 | 536 |  |  | 2020-09-14 | B25479¦Library ¦¦Sep-17-2020 11:57
2020-09-17 11:58 | 44091.4985 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 18 | 70 | 440 | 23 | 50 | 585 |  | 2020-09-17 11:58 | 44091.4985 | 23 | 50 | 585 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-17-2020 11:57
2020-09-17 11:58 | 44091.4986 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - elevator lobby |  | 1 | 20.2 | 41.3 | 366 | 22.3 | 38.4 | 452 |  | 2020-09-17 11:58 | 44091.4986 | 22.3 | 38.4 | 452 |  | caution | 2020-09-14 | B70277¦Hallway - elevator lobby¦¦Sep-17-2020 11:57
2020-09-17 11:58 | 44091.4987 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | Court Attorney |  | 1 | 14 | 54 | 374 | 22.9 | 40.3 | 443 | No | 2020-09-17 11:58 | 44091.4987 | 22.9 | 40.3 | 443 |  |  | 2020-09-14 | B14660¦Court Attorney¦¦Sep-17-2020 11:58
2020-09-17 11:58 | 44091.4988 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | TC office |  | 2 | 18 | 61 | 422 | 23 | 42 | 560 |  | 2020-09-17 11:58 | 44091.4988 | 23 | 42 | 560 |  |  | 2020-09-14 | B25479¦TC office ¦¦Sep-17-2020 11:58
2020-09-17 11:58 | 44091.4988 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Office 1 |  | 0 | 19.4 | 55 | 422 | 22.6 | 50.8 | 532 |  | 2020-09-17 11:58 | 44091.4988 | 22.6 | 50.8 | 532 |  |  | 2020-09-14 | B25039¦Office 1¦¦Sep-17-2020 11:58
2020-09-17 11:58 | 44091.4988 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Manage of operations seating area 2 |  | 0 | 23 | 41.5 | 420 | 22.6 | 46.7 | 425 |  | 2020-09-17 11:58 | 44091.4988 | 22.6 | 46.7 | 425 |  |  | 2020-09-14 | B17477¦Manage of operations seating area 2 ¦¦Sep-17-2020 11:58
2020-09-17 11:59 | 44091.4991 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Jury room |  | 0 | 15 | 68 | 421 | 22.5 | 48 | 421 | No | 2020-09-17 11:59 | 44091.4991 | 22.5 | 48 | 421 |  |  | 2020-09-14 | B20489¦Jury room ¦¦Sep-17-2020 11:58
2020-09-17 11:59 | 44091.4992 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | JP lobby |  | 0 | 18 | 61 | 422 | 24 | 39 | 560 |  | 2020-09-17 11:59 | 44091.4992 | 24 | 39 | 560 |  | caution | 2020-09-14 | B25479¦JP lobby ¦¦Sep-17-2020 11:58
2020-09-17 11:59 | 44091.4993 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 rear right |  | 1 | 26 | 37 | 365 | 22 | 44 | 384 |  | 2020-09-17 11:59 | 44091.4993 | 22 | 44 | 384 |  |  | 2020-09-14 | B20772¦H15 rear right¦¦Sep-17-2020 11:58
2020-09-17 11:59 | 44091.4994 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | 3rd floor stairwell |  | 1 | 20.2 | 41.3 | 366 | 23 | 40.8 | 457 |  | 2020-09-17 11:59 | 44091.4994 | 23 | 40.8 | 457 |  |  | 2020-09-14 | B70277¦3rd floor stairwell ¦¦Sep-17-2020 11:59
2020-09-17 11:59 | 44091.4996 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Copier room |  | 0 | 19.4 | 55 | 422 | 22.5 | 51.3 | 528 |  | 2020-09-17 11:59 | 44091.4996 | 22.5 | 51.3 | 528 |  |  | 2020-09-14 | B25039¦Copier room¦¦Sep-17-2020 11:59
2020-09-17 12:00 | 44091.4997 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 hallway |  | 0 | 23 | 41.5 | 420 | 22.6 | 47 | 422 |  | 2020-09-17 12:00 | 44091.4997 | 22.6 | 47 | 422 |  |  | 2020-09-14 | B17477¦Level 5 hallway ¦¦Sep-17-2020 11:59
2020-09-17 12:00 | 44091.4998 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 306 |  | 0 | 14 | 54 | 374 | 22.8 | 43.9 | 429 | No | 2020-09-17 12:00 | 44091.4998 | 22.8 | 43.9 | 429 |  |  | 2020-09-14 | B14660¦306¦¦Sep-17-2020 11:59
2020-09-17 12:00 | 44091.5 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 rear left |  | 1 | 26 | 37 | 365 | 22 | 45 | 385 |  | 2020-09-17 12:00 | 44091.5 | 22 | 45 | 385 |  |  | 2020-09-14 | B20772¦H15 rear left¦¦Sep-17-2020 11:59
2020-09-17 12:00 | 44091.5003 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Main lobby south |  | 3 | 18 | 61 | 422 | 23 | 40 | 568 |  | 2020-09-17 12:00 | 44091.5003 | 23 | 40 | 568 |  | caution | 2020-09-14 | B25479¦Main lobby south ¦¦Sep-17-2020 12:00
2020-09-17 12:01 | 44091.5004 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 18 | 70 | 440 | 23 | 50 | 585 |  | 2020-09-17 12:01 | 44091.5004 | 23 | 50 | 585 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-17-2020 12:00
2020-09-17 12:01 | 44091.5004 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 West |  | 0 | 18.1 | 59.8 | 431 | 21.7 | 51.4 | 494 |  | 2020-09-17 12:01 | 44091.5004 | 21.7 | 51.4 | 494 |  |  | 2020-09-14 | B10577¦Courtroom 3 West¦¦Sep-17-2020 12:00
2020-09-17 12:01 | 44091.5005 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 hallway 2 |  | 0 | 23 | 41.5 | 420 | 22.3 | 47.9 | 423 |  | 2020-09-17 12:01 | 44091.5005 | 22.3 | 47.9 | 423 |  |  | 2020-09-14 | B17477¦Level 5 hallway 2¦¦Sep-17-2020 12:00
2020-09-17 12:01 | 44091.5006 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Office 2 |  | 0 | 19.4 | 55 | 422 | 21.7 | 53.5 | 549 |  | 2020-09-17 12:01 | 44091.5006 | 21.7 | 53.5 | 549 |  |  | 2020-09-14 | B25039¦Office 2¦¦Sep-17-2020 12:00
2020-09-17 12:01 | 44091.5008 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Main lobby north |  | 0 | 18 | 61 | 422 | 23 | 41 | 585 | Couldn't get into supervisors office | 2020-09-17 12:01 | 44091.5008 | 23 | 41 | 585 |  |  | 2020-09-14 | B25479¦Main lobby north ¦¦Sep-17-2020 12:01
2020-09-17 12:01 | 44091.5008 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Private room |  | 0 | 15 | 68 | 421 | 22.3 | 47.7 | 421 | No | 2020-09-17 12:01 | 44091.5008 | 22.3 | 47.7 | 421 |  |  | 2020-09-14 | B20489¦Private room ¦¦Sep-17-2020 12:01
2020-09-17 12:01 | 44091.501 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Inside elevator on 3rd floor |  | 1 | 20.2 | 41.3 | 366 | 23 | 41 | 470 |  | 2020-09-17 12:01 | 44091.501 | 23 | 41 | 470 |  |  | 2020-09-14 | B70277¦Inside elevator on 3rd floor¦¦Sep-17-2020 12:01
2020-09-17 12:02 | 44091.5011 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 waiting room |  | 1 | 26 | 37 | 365 | 22 | 46 | 384 |  | 2020-09-17 12:02 | 44091.5011 | 22 | 46 | 384 |  |  | 2020-09-14 | B20772¦H15 waiting room ¦¦Sep-17-2020 12:01
2020-09-17 12:02 | 44091.5013 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 hallway |  | 0 | 23 | 41.5 | 420 | 22.1 | 48.5 | 423 |  | 2020-09-17 12:02 | 44091.5013 | 22.1 | 48.5 | 423 |  |  | 2020-09-14 | B17477¦Level 5 hallway ¦¦Sep-17-2020 12:01
2020-09-17 12:02 | 44091.5014 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Judges panel |  | 0 | 19.4 | 55 | 422 | 21.6 | 54.2 | 554 |  | 2020-09-17 12:02 | 44091.5014 | 21.6 | 54.2 | 554 |  |  | 2020-09-14 | B25039¦Judges panel¦¦Sep-17-2020 12:02
2020-09-17 12:02 | 44091.5017 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 600 |  | 2020-09-17 12:02 | 44091.5017 | 24 | 51 | 600 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-17-2020 12:02
2020-09-17 12:03 | 44091.502 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Entrance |  | 0 | 22.3 | 48.6 | 399 | 24.1 | 47.2 | 470 |  | 2020-09-17 12:03 | 44091.502 | 24.1 | 47.2 | 470 |  |  | 2020-09-14 | B10577¦Main Entrance ¦¦Sep-17-2020 12:02
2020-09-17 12:03 | 44091.5021 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside of washrooms |  | 1 | 20.2 | 41.3 | 366 | 23.1 | 35.2 | 435 |  | 2020-09-17 12:03 | 44091.5021 | 23.1 | 35.2 | 435 |  | caution | 2020-09-14 | B70277¦Hallway - outside of washrooms¦¦Sep-17-2020 12:02
2020-09-17 12:03 | 44091.5021 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Court room 1 judge's desk |  | 1 | 15 | 68 | 421 | 22.6 | 47.1 | 429 | No | 2020-09-17 12:03 | 44091.5021 | 22.6 | 47.1 | 429 |  |  | 2020-09-14 | B20489¦Court room 1 judge's desk ¦¦Sep-17-2020 12:03
2020-09-17 12:03 | 44091.5022 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 hallway 3 |  | 0 | 23 | 41.5 | 420 | 22.2 | 48.5 | 427 |  | 2020-09-17 12:03 | 44091.5022 | 22.2 | 48.5 | 427 |  |  | 2020-09-14 | B17477¦Level 5 hallway 3 ¦¦Sep-17-2020 12:03
2020-09-17 12:04 | 44091.5028 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main lobby south |  | 0 | 22.3 | 48.6 | 399 | 23.6 | 43.8 | 687 |  | 2020-09-17 12:04 | 44091.5028 | 23.6 | 43.8 | 687 |  |  | 2020-09-14 | B10577¦Main lobby south¦¦Sep-17-2020 12:04
2020-09-17 12:04 | 44091.5031 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 waiting room |  | 0 | 23 | 22.1 | 427 | 22.2 | 48.1 | 423 |  | 2020-09-17 12:04 | 44091.5031 | 22.2 | 48.1 | 423 |  |  | 2020-09-14 | B17477¦Level 5 waiting room ¦¦Sep-17-2020 12:04
2020-09-17 12:04 | 44091.5031 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Courtroom front east |  | 0 | 19.4 | 55 | 422 | 21.5 | 54.4 | 550 |  | 2020-09-17 12:05 | 44091.5031 | 21.5 | 54.4 | 550 |  |  | 2020-09-14 | B25039¦Courtroom front east¦¦Sep-17-2020 12:04
2020-09-17 12:05 | 44091.5035 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Court Service Office |  | 2 | 22.3 | 48.6 | 399 | 24.1 | 43.1 | 800 |  | 2020-09-17 12:05 | 44091.5035 | 24.1 | 43.1 | 800 |  |  | 2020-09-14 | B10577¦Court Service Office¦¦Sep-17-2020 12:05
2020-09-17 12:05 | 44091.5035 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Court room 1 gallery |  | 1 | 15 | 68 | 421 | 22.6 | 46.2 | 429 | No | 2020-09-17 12:05 | 44091.5035 | 22.6 | 46.2 | 429 |  |  | 2020-09-14 | B20489¦Court room 1 gallery ¦¦Sep-17-2020 12:05
2020-09-17 12:05 | 44091.5037 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- N wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 580 |  | 2020-09-17 12:05 | 44091.5037 | 24 | 51 | 580 |  |  | 2020-09-14 | B25548¦1- N wall¦¦Sep-17-2020 12:05
2020-09-17 12:06 | 44091.5039 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #1 |  | 2 | 19 | 40.2 | 407 | 20.6 | 49.1 | 548 |  | 2020-09-17 12:06 | 44091.5039 | 20.6 | 49.1 | 548 |  |  | 2020-09-14 | B20474¦Courtroom #1¦¦Sep-17-2020 12:05
2020-09-17 12:06 | 44091.5041 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Courtroom front west |  | 0 | 19.4 | 55 | 422 | 21.3 | 54.8 | 548 |  | 2020-09-17 12:06 | 44091.5041 | 21.3 | 54.8 | 548 |  |  | 2020-09-14 | B25039¦Courtroom front west¦¦Sep-17-2020 12:05
2020-09-17 12:06 | 44091.5041 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Witness Area |  | 0 | 22.3 | 48.6 | 399 | 24.1 | 43.6 | 826 |  | 2020-09-17 12:06 | 44091.5041 | 24.1 | 43.6 | 826 |  |  | 2020-09-14 | B10577¦Witness Area¦¦Sep-17-2020 12:05
2020-09-17 12:06 | 44091.5044 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 waiting room 2 |  | 0 | 23 | 41.5 | 420 | 22.2 | 48.5 | 421 |  | 2020-09-17 12:06 | 44091.5044 | 22.2 | 48.5 | 421 |  |  | 2020-09-14 | B17477¦Level 5 waiting room 2¦¦Sep-17-2020 12:06
2020-09-17 12:07 | 44091.5048 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 18 | 70 | 440 | 24 | 50 | 590 |  | 2020-09-17 12:07 | 44091.5048 | 24 | 50 | 590 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-17-2020 12:06
2020-09-17 12:07 | 44091.5051 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Courtroom rear east |  | 0 | 19.4 | 55 | 422 | 21.3 | 54.9 | 544 |  | 2020-09-17 12:07 | 44091.5051 | 21.3 | 54.9 | 544 |  |  | 2020-09-14 | B25039¦Courtroom rear east¦¦Sep-17-2020 12:07
2020-09-17 12:08 | 44091.5052 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #3 |  | 2 | 19 | 40.2 | 407 | 20.1 | 51.6 | 497 |  | 2020-09-17 12:08 | 44091.5052 | 20.1 | 51.6 | 497 |  |  | 2020-09-14 | B20474¦Courtroom #3¦¦Sep-17-2020 12:07
2020-09-17 12:08 | 44091.5055 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 3rd floor hallway south |  | 0 | 15 | 68 | 421 | 22.3 | 48.2 | 451 | No | 2020-09-17 12:08 | 44091.5055 | 22.3 | 48.2 | 451 |  |  | 2020-09-14 | B20489¦3rd floor hallway south ¦¦Sep-17-2020 12:07
2020-09-17 12:08 | 44091.5056 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | 1st Floor - front door lobby |  | 3 | 20.2 | 41.3 | 366 | 23.5 | 41 | 560 |  | 2020-09-17 12:08 | 44091.5056 | 23.5 | 41 | 560 |  |  | 2020-09-14 | B70277¦1st Floor - front door lobby¦¦Sep-17-2020 12:08
2020-09-17 12:08 | 44091.5056 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Foyers |  | 1 | 15.9 | 47.9 | 408 | 17.8 | 55.7 | 504 |  | 2020-09-17 12:08 | 44091.5056 | 17.8 | 55.7 | 504 |  |  | 2020-09-14 | B20367¦Foyers ¦¦Sep-17-2020 12:08
2020-09-17 12:08 | 44091.5056 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Front lobby |  | 3 | 21 | 45 | 400 | 21 | 50 | 428 |  | 2020-09-17 12:08 | 44091.5056 | 21 | 50 | 428 |  |  | 2020-09-14 | B19570¦Front lobby¦¦Sep-17-2020 12:08
2020-09-17 12:09 | 44091.506 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Kitchen |  | 0 | 18 | 57 | 373 | 21 | 50 | 378 |  | 2020-09-17 12:09 | 44091.506 | 21 | 50 | 378 |  |  | 2020-09-14 | B20603¦Kitchen¦¦Sep-17-2020 12:08
2020-09-17 12:09 | 44091.5062 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Courtroom rear west |  | 0 | 19.4 | 55 | 422 | 21.3 | 55 | 545 |  | 2020-09-17 12:09 | 44091.5062 | 21.3 | 55 | 545 |  |  | 2020-09-14 | B25039¦Courtroom rear west¦¦Sep-17-2020 12:08
2020-09-17 12:09 | 44091.5064 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 courtroom office |  | 3 | 23 | 41.5 | 420 | 22.2 | 50.2 | 493 |  | 2020-09-17 12:09 | 44091.5064 | 22.2 | 50.2 | 493 |  |  | 2020-09-14 | B17477¦Level 5 courtroom office ¦¦Sep-17-2020 12:09
2020-09-17 12:09 | 44091.5064 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- S wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 610 |  | 2020-09-17 12:09 | 44091.5064 | 24 | 51 | 610 |  |  | 2020-09-14 | B25548¦2- S wall¦¦Sep-17-2020 12:09
2020-09-17 12:09 | 44091.5064 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Robing corridor |  | 1 | 19 | 40.2 | 407 | 20.2 | 51.4 | 525 |  | 2020-09-17 12:09 | 44091.5064 | 20.2 | 51.4 | 525 |  |  | 2020-09-14 | B20474¦Robing corridor¦¦Sep-17-2020 12:09
2020-09-17 12:10 | 44091.5071 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Waiting room |  | 0 | 19.4 | 55 | 422 | 21.6 | 55.3 | 536 |  | 2020-09-17 12:10 | 44091.5071 | 21.6 | 55.3 | 536 |  |  | 2020-09-14 | B25039¦Waiting room¦¦Sep-17-2020 12:10
2020-09-17 12:11 | 44091.5073 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Mailroom |  | 0 | 18 | 57 | 373 | 21 | 49 | 391 |  | 2020-09-17 12:11 | 44091.5073 | 21 | 49 | 391 |  |  | 2020-09-14 | B20603¦Mailroom¦¦Sep-17-2020 12:10
2020-09-17 12:11 | 44091.5073 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Hallway nw |  | 1 | 21 | 45 | 400 | 22 | 47 | 411 |  | 2020-09-17 12:11 | 44091.5073 | 22 | 47 | 411 |  |  | 2020-09-14 | B19570¦Hallway nw¦¦Sep-17-2020 12:10
2020-09-17 12:11 | 44091.5077 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Administration office |  | 7 | 15.9 | 55.4 | 408 | 20.4 | 54.2 | 895 |  | 2020-09-17 12:11 | 44091.5077 | 20.4 | 54.2 | 895 |  |  | 2020-09-14 | B20367¦Administration office ¦¦Sep-17-2020 12:11
2020-09-17 12:11 | 44091.5077 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 650 |  | 2020-09-17 12:11 | 44091.5077 | 24 | 51 | 650 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-17-2020 12:11
2020-09-17 12:11 | 44091.5077 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Lobby north |  | 0 | 22.3 | 48.6 | 399 | 23.5 | 45.6 | 830 |  | 2020-09-17 12:11 | 44091.5077 | 23.5 | 45.6 | 830 |  |  | 2020-09-14 | B10577¦Main Lobby north¦¦Sep-17-2020 12:11
2020-09-17 12:11 | 44091.5078 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Law library hall s |  | 1 | 21 | 45 | 400 | 22 | 47 | 406 |  | 2020-09-17 12:11 | 44091.5078 | 22 | 47 | 406 |  |  | 2020-09-14 | B19570¦Law library hall s¦¦Sep-17-2020 12:11
2020-09-17 12:11 | 44091.5078 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 4 interview room. |  | 0 | 23 | 41.5 | 420 | 22.2 | 47.6 | 428 |  | 2020-09-17 12:11 | 44091.5078 | 22.2 | 47.6 | 428 |  |  | 2020-09-14 | B17477¦Level 4 interview room. ¦¦Sep-17-2020 12:11
2020-09-17 12:11 | 44091.508 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Mediation room 2 |  | 0 | 19.4 | 55 | 422 | 21.7 | 54.9 | 524 |  | 2020-09-17 12:11 | 44091.508 | 21.7 | 54.9 | 524 |  |  | 2020-09-14 | B25039¦Mediation room 2¦¦Sep-17-2020 12:11
2020-09-17 12:12 | 44091.508 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area at mens washroom |  | 1 | 19 | 40.2 | 407 | 20.3 | 51.5 | 529 |  | 2020-09-17 12:12 | 44091.508 | 20.3 | 51.5 | 529 |  |  | 2020-09-14 | B20474¦Basement waiting area at mens washroom¦¦Sep-17-2020 12:11
2020-09-17 12:12 | 44091.5082 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Law library hall n |  | 1 | 21 | 45 | 400 | 22 | 47 | 404 |  | 2020-09-17 12:12 | 44091.5082 | 22 | 47 | 404 |  |  | 2020-09-14 | B19570¦Law library hall n¦¦Sep-17-2020 12:11
2020-09-17 12:12 | 44091.5084 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Stairwell |  | 0 | 22.3 | 48.6 | 399 | 23.6 | 45.8 | 833 |  | 2020-09-17 12:12 | 44091.5084 | 23.6 | 45.8 | 833 |  |  | 2020-09-14 | B10577¦Main Stairwell¦¦Sep-17-2020 12:12
2020-09-17 12:12 | 44091.5086 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Mediation room c |  | 0 | 18 | 57 | 373 | 22 | 48 | 382 |  | 2020-09-17 12:12 | 44091.5086 | 22 | 48 | 382 |  |  | 2020-09-14 | B20603¦Mediation room c¦¦Sep-17-2020 12:12
2020-09-17 12:12 | 44091.5087 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 judge |  | 1 | 26 | 37 | 365 | 24 | 41 | 381 |  | 2020-09-17 12:12 | 44091.5087 | 24 | 41 | 381 |  |  | 2020-09-14 | B20772¦H12 judge¦¦Sep-17-2020 12:12
2020-09-17 12:13 | 44091.5087 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Administration office |  | 8 | 15.9 | 47.9 | 408 | 22.2 | 46.2 | 710 |  | 2020-09-17 12:13 | 44091.5087 | 22.2 | 46.2 | 710 |  |  | 2020-09-14 | B20367¦Administration office ¦¦Sep-17-2020 12:12
2020-09-17 12:13 | 44091.5088 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court admin hall |  | 1 | 21 | 45 | 400 | 22 | 48 | 409 |  | 2020-09-17 12:13 | 44091.5088 | 22 | 48 | 409 |  |  | 2020-09-14 | B19570¦Court admin hall ¦¦Sep-17-2020 12:12
2020-09-17 12:13 | 44091.5088 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Mediation room 1 |  | 0 | 19.4 | 55 | 422 | 21.8 | 54.4 | 518 |  | 2020-09-17 12:13 | 44091.5088 | 21.8 | 54.4 | 518 |  |  | 2020-09-14 | B25039¦Mediation room 1¦¦Sep-17-2020 12:12
2020-09-17 12:14 | 44091.5096 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 17 | 70 | 440 | 24 | 50 | 595 |  | 2020-09-17 12:14 | 44091.5096 | 24 | 50 | 595 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-17-2020 12:13
2020-09-17 12:14 | 44091.5097 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Washroom |  | 0 | 19.4 | 55 | 422 | 21.8 | 54.9 | 531 |  | 2020-09-17 12:14 | 44091.5097 | 21.8 | 54.9 | 531 |  |  | 2020-09-14 | B25039¦Washroom¦¦Sep-17-2020 12:14
2020-09-17 12:14 | 44091.51 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Poa office |  | 6 | 21 | 45 | 400 | 22 | 51 | 505 |  | 2020-09-17 12:14 | 44091.51 | 22 | 51 | 505 |  |  | 2020-09-14 | B19570¦Poa office ¦¦Sep-17-2020 12:14
2020-09-17 12:15 | 44091.5103 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Court operations |  | 1 | 16.1 | 47.9 | 408 | 21.2 | 46 | 489 |  | 2020-09-17 12:15 | 44091.5103 | 21.2 | 46 | 489 |  |  | 2020-09-14 | B20367¦Court operations ¦¦Sep-17-2020 12:14
2020-09-17 12:15 | 44091.5104 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 5 |  | 2 | 21 | 45 | 400 | 22 | 51 | 478 |  | 2020-09-17 12:15 | 44091.5104 | 22 | 51 | 478 |  |  | 2020-09-14 | B19570¦Court 5¦¦Sep-17-2020 12:14
2020-09-17 12:15 | 44091.5104 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Mediation room b |  | 0 | 18 | 57 | 373 | 22 | 49 | 379 |  | 2020-09-17 12:15 | 44091.5104 | 22 | 49 | 379 |  |  | 2020-09-14 | B20603¦Mediation room b¦¦Sep-17-2020 12:15
2020-09-17 12:15 | 44091.5105 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2nd floor wait are North |  | 0 | 22.3 | 48.6 | 399 | 23.1 | 45.5 | 800 |  | 2020-09-17 12:15 | 44091.5105 | 23.1 | 45.5 | 800 |  |  | 2020-09-14 | B10577¦2nd floor wait are North¦¦Sep-17-2020 12:15
2020-09-17 12:15 | 44091.5106 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- S wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 590 |  | 2020-09-17 12:15 | 44091.5106 | 24 | 51 | 590 |  |  | 2020-09-14 | B25548¦2- S wall¦¦Sep-17-2020 12:15
2020-09-17 12:15 | 44091.5107 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Main hall |  | 0 | 19.4 | 55 | 422 | 22 | 53.8 | 556 |  | 2020-09-17 12:15 | 44091.5107 | 22 | 53.8 | 556 |  |  | 2020-09-14 | B25039¦Main hall¦¦Sep-17-2020 12:15
2020-09-17 12:16 | 44091.5113 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2 floor wait area center |  | 0 | 22.3 | 48.6 | 399 | 23.3 | 47.3 | 780 |  | 2020-09-17 12:16 | 44091.5113 | 23.3 | 47.3 | 780 |  |  | 2020-09-14 | B10577¦2 floor wait area center¦¦Sep-17-2020 12:16
2020-09-17 12:16 | 44091.5113 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area at mens washroom |  | 1 | 19 | 40.2 | 407 | 20.3 | 51.5 | 529 |  | 2020-09-17 12:16 | 44091.5113 | 20.3 | 51.5 | 529 |  |  | 2020-09-14 | B20474¦Basement waiting area at mens washroom¦¦Sep-17-2020 12:16
2020-09-17 12:16 | 44091.5113 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 4 |  | 3 | 21 | 45 | 400 | 21 | 49 | 475 |  | 2020-09-17 12:16 | 44091.5113 | 21 | 49 | 475 |  |  | 2020-09-14 | B19570¦Court 4¦¦Sep-17-2020 12:16
2020-09-17 12:16 | 44091.5114 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 1 |  | 0 | 15.9 | 47.9 | 408 | 21.4 | 43.1 | 492 |  | 2020-09-17 12:16 | 44091.5114 | 21.4 | 43.1 | 492 |  |  | 2020-09-14 | B20367¦Waiting room 1¦¦Sep-17-2020 12:16
2020-09-17 12:16 | 44091.5114 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- S wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 620 |  | 2020-09-17 12:16 | 44091.5114 | 24 | 51 | 620 |  |  | 2020-09-14 | B25548¦2- S wall¦¦Sep-17-2020 12:16
2020-09-17 12:17 | 44091.5116 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Emergency exit |  | 0 | 19.4 | 55 | 422 | 22.1 | 53 | 558 |  | 2020-09-17 12:17 | 44091.5116 | 22.1 | 53 | 558 |  |  | 2020-09-14 | B25039¦Emergency exit¦¦Sep-17-2020 12:16
2020-09-17 12:17 | 44091.5117 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 3 |  | 2 | 21 | 45 | 400 | 21 | 49 | 451 |  | 2020-09-17 12:17 | 44091.5117 | 21 | 49 | 451 |  |  | 2020-09-14 | B19570¦Court 3¦¦Sep-17-2020 12:16
2020-09-17 12:17 | 44091.512 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 plaintiff |  | 1 | 26 | 37 | 365 | 24 | 42 | 380 |  | 2020-09-17 12:17 | 44091.512 | 24 | 42 | 380 |  |  | 2020-09-14 | B20772¦H12 plaintiff¦¦Sep-17-2020 12:17
2020-09-17 12:17 | 44091.512 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Mediation room a |  | 0 | 18 | 57 | 373 | 22 | 45 | 380 |  | 2020-09-17 12:17 | 44091.512 | 22 | 45 | 380 |  |  | 2020-09-14 | B20603¦Mediation room a¦¦Sep-17-2020 12:17
2020-09-17 12:17 | 44091.5121 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2 floor waiting area south |  | 0 | 22.3 | 48.6 | 399 | 23.2 | 47.4 | 786 |  | 2020-09-17 12:17 | 44091.5121 | 23.2 | 47.4 | 786 |  |  | 2020-09-14 | B10577¦2 floor waiting area south¦¦Sep-17-2020 12:17
2020-09-17 12:17 | 44091.5121 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judges chamber foyers |  | 0 | 15.9 | 47.9 | 408 | 21.7 | 46.6 | 488 |  | 2020-09-17 12:18 | 44091.5121 | 21.7 | 46.6 | 488 |  |  | 2020-09-14 | B20367¦Judges chamber foyers ¦¦Sep-17-2020 12:17
2020-09-17 12:18 | 44091.5123 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- S wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 620 |  | 2020-09-17 12:18 | 44091.5123 | 24 | 51 | 620 |  |  | 2020-09-14 | B25548¦2- S wall¦¦Sep-17-2020 12:17
2020-09-17 12:18 | 44091.5124 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 1 |  | 3 | 21 | 45 | 400 | 21 | 54 | 444 |  | 2020-09-17 12:18 | 44091.5124 | 21 | 54 | 444 |  |  | 2020-09-14 | B19570¦Court 1¦¦Sep-17-2020 12:17
2020-09-17 12:18 | 44091.5124 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Common room |  | 2 | 19.4 | 55 | 422 | 22.3 | 52.7 | 567 |  | 2020-09-17 12:18 | 44091.5124 | 22.3 | 52.7 | 567 |  |  | 2020-09-14 | B25039¦Common room¦¦Sep-17-2020 12:17
2020-09-17 12:18 | 44091.5125 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 defendant |  | 1 | 26 | 37 | 365 | 24 | 42 | 381 |  | 2020-09-17 12:18 | 44091.5125 | 24 | 42 | 381 |  |  | 2020-09-14 | B20772¦H12 defendant¦¦Sep-17-2020 12:18
2020-09-17 12:18 | 44091.5128 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 West |  | 0 | 23.1 | 48.6 | 399 | 23.5 | 47 | 655 |  | 2020-09-17 12:18 | 44091.5128 | 23.5 | 47 | 655 |  |  | 2020-09-14 | B10577¦Courtroom 2 West¦¦Sep-17-2020 12:18
2020-09-17 12:19 | 44091.5129 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area courtroom3 |  | 1 | 19 | 40.2 | 407 | 20.3 | 51.5 | 562 |  | 2020-09-17 12:19 | 44091.5129 | 20.3 | 51.5 | 562 |  |  | 2020-09-14 | B20474¦Basement waiting area courtroom3¦¦Sep-17-2020 12:18
2020-09-17 12:19 | 44091.513 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judges chamber foyers |  | 0 | 15.9 | 47.9 | 408 | 21.9 | 46.2 | 492 |  | 2020-09-17 12:19 | 44091.513 | 21.9 | 46.2 | 492 |  |  | 2020-09-14 | B20367¦Judges chamber foyers ¦¦Sep-17-2020 12:18
2020-09-17 12:19 | 44091.5131 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 2 |  | 2 | 21 | 45 | 400 | 22 | 49 | 432 |  | 2020-09-17 12:19 | 44091.5131 | 22 | 49 | 432 |  |  | 2020-09-14 | B19570¦Court 2¦¦Sep-17-2020 12:18
2020-09-17 12:19 | 44091.5132 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 rear right |  | 1 | 26 | 37 | 365 | 24 | 42 | 384 |  | 2020-09-17 12:19 | 44091.5132 | 24 | 42 | 384 |  |  | 2020-09-14 | B20772¦H12 rear right¦¦Sep-17-2020 12:19
2020-09-17 12:19 | 44091.5133 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | North hallway |  | 0 | 18 | 57 | 373 | 22 | 45 | 381 |  | 2020-09-17 12:19 | 44091.5133 | 22 | 45 | 381 |  |  | 2020-09-14 | B20603¦North hallway¦¦Sep-17-2020 12:19
2020-09-17 12:20 | 44091.5135 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 259 |  | 1 | 21 | 45 | 400 | 22 | 48 | 404 |  | 2020-09-17 12:20 | 44091.5135 | 22 | 48 | 404 |  |  | 2020-09-14 | B19570¦259¦¦Sep-17-2020 12:19
2020-09-17 12:20 | 44091.5139 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 rear left |  | 1 | 26 | 37 | 365 | 24 | 42 | 386 |  | 2020-09-17 12:20 | 44091.5139 | 24 | 42 | 386 |  |  | 2020-09-14 | B20772¦H12 rear left ¦¦Sep-17-2020 12:19
2020-09-17 12:20 | 44091.514 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 South |  | 0 | 22.3 | 48.6 | 399 | 23.6 | 46.8 | 639 |  | 2020-09-17 12:20 | 44091.514 | 23.6 | 46.8 | 639 |  |  | 2020-09-14 | B10577¦Courtroom 2 South¦¦Sep-17-2020 12:20
2020-09-17 12:20 | 44091.5141 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judicial stairwell |  | 0 | 15.9 | 47.9 | 408 | 21.8 | 49.8 | 485 |  | 2020-09-17 12:20 | 44091.5141 | 21.8 | 49.8 | 485 |  |  | 2020-09-14 | B20367¦Judicial stairwell ¦¦Sep-17-2020 12:20
2020-09-17 12:21 | 44091.5144 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 265 |  | 1 | 21 | 45 | 400 | 23 | 46 | 408 |  | 2020-09-17 12:21 | 44091.5144 | 23 | 46 | 408 |  |  | 2020-09-14 | B19570¦265¦¦Sep-17-2020 12:20
2020-09-17 12:21 | 44091.5146 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- W wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 600 |  | 2020-09-17 12:21 | 44091.5146 | 24 | 51 | 600 |  |  | 2020-09-14 | B25548¦2- W wall¦¦Sep-17-2020 12:21
2020-09-17 12:21 | 44091.5147 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basementwaiting area inside dble doors |  | 1 | 19 | 40.2 | 407 | 20.2 | 51.8 | 575 |  | 2020-09-17 12:21 | 44091.5147 | 20.2 | 51.8 | 575 |  |  | 2020-09-14 | B20474¦Basementwaiting area inside dble doors¦¦Sep-17-2020 12:21
2020-09-17 12:21 | 44091.5147 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 East |  | 0 | 22.3 | 48.6 | 399 | 23.3 | 47.3 | 648 |  | 2020-09-17 12:21 | 44091.5147 | 23.3 | 47.3 | 648 |  |  | 2020-09-14 | B10577¦Courtroom 2 East¦¦Sep-17-2020 12:21
2020-09-17 12:21 | 44091.5149 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 1 |  | 0 | 15.9 | 47.9 | 408 | 22 | 47.1 | 478 |  | 2020-09-17 12:21 | 44091.5149 | 22 | 47.1 | 478 |  |  | 2020-09-14 | B20367¦Courtroom 1¦¦Sep-17-2020 12:21
2020-09-17 12:22 | 44091.5151 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 264 |  | 1 | 21 | 45 | 400 | 23 | 46 | 404 |  | 2020-09-17 12:22 | 44091.5151 | 23 | 46 | 404 |  |  | 2020-09-14 | B19570¦264¦¦Sep-17-2020 12:21
2020-09-17 12:22 | 44091.5153 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 retiring room |  | 1 | 26 | 37 | 365 | 24 | 41 | 383 |  | 2020-09-17 12:22 | 44091.5153 | 24 | 41 | 383 |  |  | 2020-09-14 | B20772¦H12 retiring room¦¦Sep-17-2020 12:22
2020-09-17 12:22 | 44091.5155 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 North |  | 0 | 22.3 | 48.6 | 399 | 23.8 | 46.5 | 627 |  | 2020-09-17 12:22 | 44091.5155 | 23.8 | 46.5 | 627 |  |  | 2020-09-14 | B10577¦Courtroom 2 North¦¦Sep-17-2020 12:22
2020-09-17 12:22 | 44091.5155 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Tribunal |  | 1 | 18 | 57 | 373 | 22 | 45 | 409 |  | 2020-09-17 12:22 | 44091.5155 | 22 | 45 | 409 |  |  | 2020-09-14 | B20603¦Tribunal¦¦Sep-17-2020 12:22
2020-09-17 12:22 | 44091.5155 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 261 |  | 1 | 21 | 45 | 400 | 22 | 46 | 410 |  | 2020-09-17 12:22 | 44091.5155 | 22 | 46 | 410 |  |  | 2020-09-14 | B19570¦261¦¦Sep-17-2020 12:22
2020-09-17 12:22 | 44091.5156 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- W wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 610 |  | 2020-09-17 12:22 | 44091.5156 | 24 | 51 | 610 |  |  | 2020-09-14 | B25548¦2- W wall¦¦Sep-17-2020 12:22
2020-09-17 12:23 | 44091.5157 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 1 judges chamber |  | 0 | 15.9 | 47.9 | 408 | 22 | 50 | 472 |  | 2020-09-17 12:23 | 44091.5157 | 22 | 50 | 472 |  |  | 2020-09-14 | B20367¦Courtroom 1 judges chamber ¦¦Sep-17-2020 12:22
2020-09-17 12:23 | 44091.5158 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Bottom stairs foyer |  | 1 | 19 | 40.2 | 407 | 19.9 | 52.5 | 589 |  | 2020-09-17 12:23 | 44091.5158 | 19.9 | 52.5 | 589 |  |  | 2020-09-14 | B20474¦Bottom stairs foyer¦¦Sep-17-2020 12:22
2020-09-17 12:23 | 44091.516 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 260 |  | 1 | 21 | 45 | 400 | 22 | 46 | 405 |  | 2020-09-17 12:23 | 44091.516 | 22 | 46 | 405 |  |  | 2020-09-14 | B19570¦260¦¦Sep-17-2020 12:23
2020-09-17 12:24 | 44091.5164 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 outside |  | 0 | 22.3 | 48.6 | 399 | 22.8 | 49.1 | 648 |  | 2020-09-17 12:24 | 44091.5164 | 22.8 | 49.1 | 648 |  |  | 2020-09-14 | B10577¦Courtroom 3 outside¦¦Sep-17-2020 12:23
2020-09-17 12:24 | 44091.5164 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 5 top |  | 1 | 21 | 45 | 400 | 22 | 46 | 405 |  | 2020-09-17 12:24 | 44091.5164 | 22 | 46 | 405 |  |  | 2020-09-14 | B19570¦Stairwell 5 top¦¦Sep-17-2020 12:23
2020-09-17 12:24 | 44091.5168 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- W wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 620 |  | 2020-09-17 12:24 | 44091.5168 | 24 | 51 | 620 |  |  | 2020-09-14 | B25548¦2- W wall¦¦Sep-17-2020 12:24
2020-09-17 12:24 | 44091.517 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 5 bottom |  | 1 | 21 | 45 | 400 | 22 | 47 | 408 |  | 2020-09-17 12:24 | 44091.517 | 22 | 47 | 408 |  |  | 2020-09-14 | B19570¦Stairwell 5 bottom ¦¦Sep-17-2020 12:24
2020-09-17 12:25 | 44091.5173 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Reception room |  | 1 | 18 | 57 | 373 | 23 | 45 | 399 |  | 2020-09-17 12:25 | 44091.5173 | 23 | 45 | 399 |  |  | 2020-09-14 | B20603¦Reception room¦¦Sep-17-2020 12:24
2020-09-17 12:25 | 44091.5174 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Basement hall w |  | 1 | 21 | 45 | 400 | 22 | 48 | 428 |  | 2020-09-17 12:25 | 44091.5174 | 22 | 48 | 428 |  |  | 2020-09-14 | B19570¦Basement hall w¦¦Sep-17-2020 12:25
2020-09-17 12:25 | 44091.5174 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Lower landing of stairs |  | 1 | 19 | 40.2 | 407 | 19.8 | 52.4 | 584 |  | 2020-09-17 12:25 | 44091.5174 | 19.8 | 52.4 | 584 |  |  | 2020-09-14 | B20474¦Lower landing of stairs¦¦Sep-17-2020 12:25
2020-09-17 12:25 | 44091.5174 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 waiting area |  | 0 | 22.3 | 48.6 | 399 | 22.7 | 48.5 | 500 |  | 2020-09-17 12:25 | 44091.5174 | 22.7 | 48.5 | 500 |  |  | 2020-09-14 | B10577¦Courtroom 3 waiting area¦¦Sep-17-2020 12:25
2020-09-17 12:26 | 44091.5179 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- N wall |  | 0 | 18 | 70 | 440 | 24 | 52 | 710 |  | 2020-09-17 12:26 | 44091.5179 | 24 | 52 | 710 |  |  | 2020-09-14 | B25548¦2- N wall¦¦Sep-17-2020 12:25
2020-09-17 12:26 | 44091.518 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 2 |  | 0 | 15.9 | 47.9 | 408 | 21.2 | 41.1 | 486 |  | 2020-09-17 12:26 | 44091.518 | 21.2 | 41.1 | 486 |  |  | 2020-09-14 | B20367¦Waiting room 2¦¦Sep-17-2020 12:25
2020-09-17 12:26 | 44091.518 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Employee entrance |  | 1 | 21 | 45 | 400 | 22 | 49 | 425 |  | 2020-09-17 12:26 | 44091.518 | 22 | 49 | 425 |  |  | 2020-09-14 | B19570¦Employee entrance ¦¦Sep-17-2020 12:25
2020-09-17 12:26 | 44091.5181 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 South |  | 0 | 22.3 | 48.6 | 399 | 22.6 | 48.7 | 483 |  | 2020-09-17 12:26 | 44091.5181 | 22.6 | 48.7 | 483 |  |  | 2020-09-14 | B10577¦Courtroom 3 South¦¦Sep-17-2020 12:26
2020-09-17 12:26 | 44091.5182 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 judge |  | 1 | 26 | 37 | 365 | 23 | 41 | 373 |  | 2020-09-17 12:26 | 44091.5182 | 23 | 41 | 373 |  |  | 2020-09-14 | B20772¦H11 judge ¦¦Sep-17-2020 12:26
2020-09-17 12:27 | 44091.5184 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Basement hall e |  | 1 | 21 | 45 | 400 | 21 | 48 | 427 |  | 2020-09-17 12:27 | 44091.5184 | 21 | 48 | 427 |  |  | 2020-09-14 | B19570¦Basement hall e ¦¦Sep-17-2020 12:26
2020-09-17 12:27 | 44091.5187 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Open space |  | 2 | 18 | 57 | 373 | 22 | 45 | 394 |  | 2020-09-17 12:27 | 44091.5187 | 22 | 45 | 394 |  |  | 2020-09-14 | B20603¦Open space¦¦Sep-17-2020 12:26
2020-09-17 12:27 | 44091.5187 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 East |  | 0 | 22.3 | 48.6 | 399 | 22.8 | 48.6 | 485 |  | 2020-09-17 12:27 | 44091.5187 | 22.8 | 48.6 | 485 |  |  | 2020-09-14 | B10577¦Courtroom 3 East¦¦Sep-17-2020 12:26
2020-09-17 12:27 | 44091.5189 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 2 |  | 0 | 15.9 | 47.9 | 408 | 21.3 | 42.4 | 449 |  | 2020-09-17 12:27 | 44091.5189 | 21.3 | 42.4 | 449 |  |  | 2020-09-14 | B20367¦Courtroom 2¦¦Sep-17-2020 12:27
2020-09-17 12:27 | 44091.519 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Main floor at stairway |  | 1 | 19 | 40.2 | 407 | 19.8 | 52.1 | 583 |  | 2020-09-17 12:27 | 44091.519 | 19.8 | 52.1 | 583 |  |  | 2020-09-14 | B20474¦Main floor at stairway¦¦Sep-17-2020 12:27
2020-09-17 12:27 | 44091.5191 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Ceiwn attorney office |  | 1 | 21 | 45 | 400 | 20 | 49 | 427 |  | 2020-09-17 12:27 | 44091.5191 | 20 | 49 | 427 |  |  | 2020-09-14 | B19570¦Ceiwn attorney office¦¦Sep-17-2020 12:27
2020-09-17 12:27 | 44091.5191 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 plaintiff |  | 1 | 26 | 37 | 365 | 23 | 41 | 374 |  | 2020-09-17 12:27 | 44091.5191 | 23 | 41 | 374 |  |  | 2020-09-14 | B20772¦H11 plaintiff¦¦Sep-17-2020 12:27
2020-09-17 12:28 | 44091.5192 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 18 | 70 | 440 | 24 | 50 | 630 |  | 2020-09-17 12:28 | 44091.5192 | 24 | 50 | 630 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-17-2020 12:27
2020-09-17 12:28 | 44091.5194 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 North |  | 1 | 22.3 | 48.6 | 399 | 22.7 | 48.8 | 486 |  | 2020-09-17 12:28 | 44091.5194 | 22.7 | 48.8 | 486 |  |  | 2020-09-14 | B10577¦Courtroom 3 North ¦¦Sep-17-2020 12:27
2020-09-17 12:28 | 44091.5194 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 4 bottom |  | 1 | 21 | 45 | 400 | 21 | 50 | 429 |  | 2020-09-17 12:28 | 44091.5194 | 21 | 50 | 429 |  |  | 2020-09-14 | B19570¦Stairwell 4 bottom¦¦Sep-17-2020 12:28
2020-09-17 12:28 | 44091.5198 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office a |  | 0 | 15.9 | 47.9 | 408 | 21.6 | 43.2 | 448 |  | 2020-09-17 12:28 | 44091.5198 | 21.6 | 43.2 | 448 |  |  | 2020-09-14 | B20367¦Office a¦¦Sep-17-2020 12:28
2020-09-17 12:29 | 44091.5199 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 4 top |  | 1 | 21 | 45 | 400 | 21 | 50 | 433 |  | 2020-09-17 12:29 | 44091.5199 | 21 | 50 | 433 |  |  | 2020-09-14 | B19570¦Stairwell 4 top¦¦Sep-17-2020 12:28
2020-09-17 12:29 | 44091.5199 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 616 |  | 1 | 18 | 57 | 373 | 23 | 45 | 418 |  | 2020-09-17 12:29 | 44091.5199 | 23 | 45 | 418 |  |  | 2020-09-14 | B20603¦616¦¦Sep-17-2020 12:28
2020-09-17 12:29 | 44091.5201 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 West |  | 0 | 22.3 | 48.6 | 399 | 22.7 | 49.4 | 486 |  | 2020-09-17 12:29 | 44091.5201 | 22.7 | 49.4 | 486 |  |  | 2020-09-14 | B10577¦Courtroom 3 West¦¦Sep-17-2020 12:28
2020-09-17 12:29 | 44091.5204 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 245 |  | 1 | 21 | 45 | 400 | 21 | 49 | 423 |  | 2020-09-17 12:29 | 44091.5204 | 21 | 49 | 423 |  |  | 2020-09-14 | B19570¦245¦¦Sep-17-2020 12:29
2020-09-17 12:29 | 44091.5205 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 defendant |  | 1 | 26 | 37 | 365 | 23 | 41 | 380 |  | 2020-09-17 12:29 | 44091.5205 | 23 | 41 | 380 |  |  | 2020-09-14 | B20772¦H11 defendant¦¦Sep-17-2020 12:29
2020-09-17 12:30 | 44091.5206 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office b |  | 0 | 15.9 | 47.9 | 408 | 21.7 | 41.8 | 444 |  | 2020-09-17 12:30 | 44091.5206 | 21.7 | 41.8 | 444 |  |  | 2020-09-14 | B20367¦Office b¦¦Sep-17-2020 12:29
2020-09-17 12:30 | 44091.5208 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 635 |  | 2020-09-17 12:30 | 44091.5208 | 24 | 51 | 635 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-17-2020 12:29
2020-09-17 12:30 | 44091.5211 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 rear right |  | 1 | 26 | 37 | 365 | 23 | 41 | 379 |  | 2020-09-17 12:30 | 44091.5211 | 23 | 41 | 379 |  |  | 2020-09-14 | B20772¦H11 rear right¦¦Sep-17-2020 12:30
2020-09-17 12:31 | 44091.5213 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 250 |  | 1 | 21 | 45 | 400 | 22 | 48 | 401 |  | 2020-09-17 12:31 | 44091.5213 | 22 | 48 | 401 |  |  | 2020-09-14 | B19570¦250¦¦Sep-17-2020 12:30
2020-09-17 12:31 | 44091.5214 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 615 |  | 0 | 18 | 57 | 373 | 22 | 45 | 401 |  | 2020-09-17 12:31 | 44091.5214 | 22 | 45 | 401 |  |  | 2020-09-14 | B20603¦615¦¦Sep-17-2020 12:30
2020-09-17 12:31 | 44091.5215 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office c |  | 0 | 15.9 | 47.9 | 408 | 21.6 | 41.9 | 445 |  | 2020-09-17 12:31 | 44091.5215 | 21.6 | 41.9 | 445 |  |  | 2020-09-14 | B20367¦Office c¦¦Sep-17-2020 12:31
2020-09-17 12:31 | 44091.5218 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom4 corridor |  | 1 | 19 | 40.2 | 407 | 19.8 | 53.1 | 511 |  | 2020-09-17 12:31 | 44091.5218 | 19.8 | 53.1 | 511 |  |  | 2020-09-14 | B20474¦Courtroom4 corridor¦¦Sep-17-2020 12:31
2020-09-17 12:31 | 44091.5218 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Hallway ne |  | 1 | 21 | 45 | 400 | 22 | 49 | 402 |  | 2020-09-17 12:31 | 44091.5218 | 22 | 49 | 402 |  |  | 2020-09-14 | B19570¦Hallway ne ¦¦Sep-17-2020 12:31
2020-09-17 12:32 | 44091.5221 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 251 |  | 1 | 21 | 45 | 400 | 22 | 48 | 402 |  | 2020-09-17 12:32 | 44091.5221 | 22 | 48 | 402 |  |  | 2020-09-14 | B19570¦251¦¦Sep-17-2020 12:31
2020-09-17 12:32 | 44091.5222 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 620 |  | 2020-09-17 12:32 | 44091.5222 | 24 | 51 | 620 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-17-2020 12:31
2020-09-17 12:32 | 44091.5222 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 rear left |  | 1 | 26 | 37 | 365 | 23 | 41 | 380 |  | 2020-09-17 12:32 | 44091.5222 | 23 | 41 | 380 |  |  | 2020-09-14 | B20772¦H11 rear left¦¦Sep-17-2020 12:32
2020-09-17 12:32 | 44091.5224 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 244 |  | 1 | 21 | 45 | 400 | 22 | 47 | 403 |  | 2020-09-17 12:32 | 44091.5224 | 22 | 47 | 403 |  |  | 2020-09-14 | B19570¦244¦¦Sep-17-2020 12:32
2020-09-17 12:32 | 44091.5225 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 3 |  | 0 | 15.9 | 47.9 | 408 | 22.1 | 45 | 466 |  | 2020-09-17 12:32 | 44091.5225 | 22.1 | 45 | 466 |  |  | 2020-09-14 | B20367¦Courtroom 3¦¦Sep-17-2020 12:32
2020-09-17 12:33 | 44091.5228 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 247 |  | 1 | 21 | 45 | 400 | 22 | 48 | 402 |  | 2020-09-17 12:33 | 44091.5228 | 22 | 48 | 402 |  |  | 2020-09-14 | B19570¦247¦¦Sep-17-2020 12:32
2020-09-17 12:33 | 44091.523 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 630 |  | 2020-09-17 12:33 | 44091.523 | 24 | 51 | 630 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-17-2020 12:33
2020-09-17 12:33 | 44091.5232 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Printing room |  | 0 | 18 | 57 | 373 | 22 | 45 | 411 |  | 2020-09-17 12:33 | 44091.5232 | 22 | 45 | 411 |  |  | 2020-09-14 | B20603¦Printing room¦¦Sep-17-2020 12:33
2020-09-17 12:34 | 44091.5236 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom2 2nd door |  | 1 | 19 | 40.2 | 407 | 19.6 | 53 | 477 |  | 2020-09-17 12:34 | 44091.5236 | 19.6 | 53 | 477 |  |  | 2020-09-14 | B20474¦Waiting area courtroom2 2nd door¦¦Sep-17-2020 12:33
2020-09-17 12:34 | 44091.5237 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 3 |  | 2 | 15.9 | 47.9 | 408 | 22.6 | 41.4 | 508 |  | 2020-09-17 12:34 | 44091.5237 | 22.6 | 41.4 | 508 |  |  | 2020-09-14 | B20367¦Waiting room 3¦¦Sep-17-2020 12:34
2020-09-17 12:34 | 44091.5238 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 640 |  | 2020-09-17 12:34 | 44091.5238 | 24 | 51 | 640 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-17-2020 12:34
2020-09-17 12:34 | 44091.5238 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 retiring room |  | 1 | 26 | 37 | 365 | 23 | 42 | 388 |  | 2020-09-17 12:34 | 44091.5238 | 23 | 42 | 388 |  |  | 2020-09-14 | B20772¦H11 retiring room ¦¦Sep-17-2020 12:34
2020-09-17 12:35 | 44091.5245 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-E wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 620 |  | 2020-09-17 12:35 | 44091.5245 | 24 | 51 | 620 |  |  | 2020-09-14 | B25548¦2-E wall¦¦Sep-17-2020 12:35
2020-09-17 12:35 | 44091.5247 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 626 |  | 0 | 18 | 57 | 373 | 22 | 45 | 400 |  | 2020-09-17 12:36 | 44091.5247 | 22 | 45 | 400 |  |  | 2020-09-14 | B20603¦626¦¦Sep-17-2020 12:35
2020-09-17 12:36 | 44091.5248 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Jurors room |  | 0 | 15.9 | 47.9 | 408 | 22.5 | 47.5 | 490 |  | 2020-09-17 12:36 | 44091.5248 | 22.5 | 47.5 | 490 |  |  | 2020-09-14 | B20367¦Jurors room ¦¦Sep-17-2020 12:35
2020-09-17 12:37 | 44091.5255 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- E wall |  | 0 | 18 | 70 | 440 | 24 | 51 | 670 |  | 2020-09-17 12:37 | 44091.5255 | 24 | 51 | 670 |  |  | 2020-09-14 | B25548¦2- E wall¦¦Sep-17-2020 12:36
2020-09-17 12:37 | 44091.5256 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom 2 1st door |  | 1 | 19 | 40.2 | 407 | 19.7 | 53.2 | 521 |  | 2020-09-17 12:37 | 44091.5256 | 19.7 | 53.2 | 521 |  |  | 2020-09-14 | B20474¦Waiting area courtroom 2 1st door¦¦Sep-17-2020 12:36
2020-09-17 12:37 | 44091.526 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H14 - Near exit entrance |  | 1 | 26 | 37 | 365 | 23 | 42 | 373 |  | 2020-09-17 12:37 | 44091.526 | 23 | 42 | 373 |  |  | 2020-09-14 | B20772¦H14 - Near exit entrance¦¦Sep-17-2020 12:37
2020-09-17 12:38 | 44091.5262 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 612 |  | 0 | 18 | 57 | 373 | 23 | 45 | 403 |  | 2020-09-17 12:38 | 44091.5262 | 23 | 45 | 403 |  |  | 2020-09-14 | B20603¦612¦¦Sep-17-2020 12:37
2020-09-17 12:38 | 44091.5266 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H14 judge table |  | 1 | 26 | 37 | 365 | 23 | 42 | 374 |  | 2020-09-17 12:38 | 44091.5266 | 23 | 42 | 374 |  |  | 2020-09-14 | B20772¦H14 judge table¦¦Sep-17-2020 12:38
2020-09-17 12:39 | 44091.5268 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-E wall |  | 0 | 18 | 70 | 440 | 24 | 50 | 630 |  | 2020-09-17 12:39 | 44091.5268 | 24 | 50 | 630 |  |  | 2020-09-14 | B25548¦2-E wall¦¦Sep-17-2020 12:38
2020-09-17 12:39 | 44091.527 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Front desk |  | 2 | 19 | 40.2 | 407 | 19.9 | 52.4 | 544 |  | 2020-09-17 12:39 | 44091.527 | 19.9 | 52.4 | 544 |  |  | 2020-09-14 | B20474¦Front desk¦¦Sep-17-2020 12:38
2020-09-17 12:39 | 44091.5272 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Hallway |  | 0 | 15.9 | 47.9 | 408 | 21.8 | 43.3 | 513 |  | 2020-09-17 12:39 | 44091.5272 | 21.8 | 43.3 | 513 |  |  | 2020-09-14 | B20367¦Hallway ¦¦Sep-17-2020 12:39
2020-09-17 12:40 | 44091.528 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Open space 2 |  | 1 | 18 | 57 | 373 | 23 | 45 | 414 |  | 2020-09-17 12:40 | 44091.528 | 23 | 45 | 414 |  |  | 2020-09-14 | B20603¦Open space 2¦¦Sep-17-2020 12:40
2020-09-17 12:41 | 44091.5282 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Lunch room |  | 1 | 15.9 | 47.9 | 408 | 20.4 | 54 | 600 |  | 2020-09-17 12:41 | 44091.5282 | 20.4 | 54 | 600 |  |  | 2020-09-14 | B90631¦Lunch room ¦¦Sep-17-2020 12:40
2020-09-17 12:41 | 44091.5286 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area main office |  | 1 | 19 | 40.2 | 407 | 20 | 52.2 | 489 |  | 2020-09-17 12:41 | 44091.5286 | 20 | 52.2 | 489 |  |  | 2020-09-14 | B20474¦Waiting area main office¦¦Sep-17-2020 12:41
2020-09-17 12:41 | 44091.5288 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | Mediation room |  | 0 | 18 | 70 | 440 | 24 | 51 | 610 |  | 2020-09-17 12:41 | 44091.5288 | 24 | 51 | 610 |  |  | 2020-09-14 | B25548¦Mediation room¦¦Sep-17-2020 12:41
2020-09-17 12:42 | 44091.529 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 judge |  | 1 | 26 | 37 | 365 | 23 | 42 | 373 |  | 2020-09-17 12:42 | 44091.529 | 23 | 42 | 373 |  |  | 2020-09-14 | B20772¦H13 judge¦¦Sep-17-2020 12:41
2020-09-17 12:42 | 44091.5293 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Case management |  | 5 | 15.9 | 47.9 | 408 | 21.1 | 52.8 | 882 |  | 2020-09-17 12:42 | 44091.5293 | 21.1 | 52.8 | 882 |  |  | 2020-09-14 | B90631¦Case management ¦¦Sep-17-2020 12:42
2020-09-17 12:42 | 44091.5294 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 plaintiff |  | 1 | 26 | 37 | 365 | 23 | 42 | 372 |  | 2020-09-17 12:42 | 44091.5294 | 23 | 42 | 372 |  |  | 2020-09-14 | B20772¦H13 plaintiff¦¦Sep-17-2020 12:42
2020-09-17 12:43 | 44091.5301 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 dependant |  | 1 | 26 | 37 | 365 | 23 | 42 | 373 |  | 2020-09-17 12:43 | 44091.5301 | 23 | 42 | 373 |  |  | 2020-09-14 | B20772¦H13 dependant¦¦Sep-17-2020 12:43
2020-09-17 12:44 | 44091.5307 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 rear right |  | 1 | 26 | 37 | 365 | 23 | 42 | 373 |  | 2020-09-17 12:44 | 44091.5307 | 23 | 42 | 373 |  |  | 2020-09-14 | B20772¦H13 rear right¦¦Sep-17-2020 12:44
2020-09-17 12:44 | 44091.5308 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 1 |  | 0 | 20.3 | 46.1 | 420 | 25.3 | 34.2 | 409 |  | 2020-09-17 12:44 | 44091.5308 | 25.3 | 34.2 | 409 |  | low | 2020-09-14 | Pearso¦Lobby 1¦¦Sep-17-2020 12:44
2020-09-17 12:45 | 44091.5315 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Crown office 1 |  | 0 | 15.9 | 47.9 | 408 | 21.9 | 51.7 | 749 |  | 2020-09-17 12:45 | 44091.5315 | 21.9 | 51.7 | 749 |  |  | 2020-09-14 | B90631¦Crown office 1¦¦Sep-17-2020 12:45
2020-09-17 12:46 | 44091.5316 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Hallway room b |  | 0 | 18 | 57 | 373 | 23 | 44 | 391 |  | 2020-09-17 12:46 | 44091.5316 | 23 | 44 | 391 |  |  | 2020-09-14 | B20603¦Hallway room b¦¦Sep-17-2020 12:45
2020-09-17 12:46 | 44091.5319 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Main office |  | 4 | 19 | 40.2 | 407 | 20.6 | 51.6 | 517 |  | 2020-09-17 12:46 | 44091.5319 | 20.6 | 51.6 | 517 |  |  | 2020-09-14 | B20474¦Main office¦¦Sep-17-2020 12:45
2020-09-17 12:46 | 44091.5319 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 2 |  | 0 | 20.3 | 46.1 | 420 | 22.7 | 37.6 | 405 |  | 2020-09-17 12:46 | 44091.5319 | 22.7 | 37.6 | 405 |  | caution | 2020-09-14 | Pearso¦Lobby 2 ¦¦Sep-17-2020 12:45
2020-09-17 12:46 | 44091.5321 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 rear left |  | 1 | 26 | 37 | 365 | 23 | 42 | 377 |  | 2020-09-17 12:46 | 44091.5321 | 23 | 42 | 377 |  |  | 2020-09-14 | B20772¦H13 rear left ¦¦Sep-17-2020 12:46
2020-09-17 12:47 | 44091.5325 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Administration |  | 1 | 15.9 | 47.9 | 408 | 22.3 | 50.1 | 897 |  | 2020-09-17 12:47 | 44091.5325 | 22.3 | 50.1 | 897 |  |  | 2020-09-14 | B90631¦Administration ¦¦Sep-17-2020 12:46
2020-09-17 12:47 | 44091.5326 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 3 |  | 0 | 20.3 | 46.1 | 420 | 21.7 | 43.4 | 402 |  | 2020-09-17 12:47 | 44091.5326 | 21.7 | 43.4 | 402 |  |  | 2020-09-14 | Pearso¦Lobby 3 ¦¦Sep-17-2020 12:47
2020-09-17 12:48 | 44091.5332 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Trial office |  | 2 | 19 | 40.2 | 407 | 20.7 | 49.8 | 491 |  | 2020-09-17 12:48 | 44091.5332 | 20.7 | 49.8 | 491 |  |  | 2020-09-14 | B20474¦Trial office¦¦Sep-17-2020 12:47
2020-09-17 12:48 | 44091.5333 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Crown office 2 |  | 1 | 15.9 | 47.9 | 408 | 22.2 | 50.1 | 906 |  | 2020-09-17 12:48 | 44091.5333 | 22.2 | 50.1 | 906 |  |  | 2020-09-14 | B90631¦Crown office 2¦¦Sep-17-2020 12:47
2020-09-17 12:48 | 44091.5336 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Policeroom 1 |  | 0 | 20.3 | 46.1 | 420 | 21.8 | 43.1 | 404 |  | 2020-09-17 12:48 | 44091.5336 | 21.8 | 43.1 | 404 |  |  | 2020-09-14 | Pearso¦Policeroom 1¦¦Sep-17-2020 12:48
2020-09-17 12:49 | 44091.5339 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom b |  | 0 | 18 | 57 | 373 | 22 | 45 | 395 |  | 2020-09-17 12:49 | 44091.5339 | 22 | 45 | 395 |  |  | 2020-09-14 | B20603¦Courtroom b¦¦Sep-17-2020 12:48
2020-09-17 12:50 | 44091.5345 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Policeroom 2 |  | 0 | 20.3 | 46.1 | 420 | 21.7 | 43.6 | 402 |  | 2020-09-17 12:50 | 44091.5345 | 21.7 | 43.6 | 402 |  |  | 2020-09-14 | Pearso¦Policeroom 2 ¦¦Sep-17-2020 12:49
2020-09-17 12:50 | 44091.5349 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Vwap waiting room |  | 0 | 15.7 | 47.9 | 408 | 21.2 | 51.3 | 565 |  | 2020-09-17 12:50 | 44091.5349 | 21.2 | 51.3 | 565 |  |  | 2020-09-14 | B90631¦Vwap waiting room ¦¦Sep-17-2020 12:50
2020-09-17 12:50 | 44091.5349 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | judge rm14 |  | 1 | 21 | 46 | 420 | 21.6 | 44 | 440 | Rm 11 | 2020-09-17 12:50 | 44091.5349 | 21.6 | 44 | 440 |  |  | 2020-09-14 | B70740¦judge rm14¦¦Sep-17-2020 12:50
2020-09-17 12:51 | 44091.5355 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | rm14 |  | 0 | 21 | 46 | 420 | 22 | 48 | 430 |  | 2020-09-17 12:51 | 44091.5355 | 22 | 48 | 430 |  |  | 2020-09-14 | B70740¦rm14¦¦Sep-17-2020 12:51
2020-09-17 12:51 | 44091.5357 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Judges chamber foyers |  | 0 | 15.9 | 47.9 | 408 | 21.5 | 51.4 | 562 |  | 2020-09-17 12:51 | 44091.5357 | 21.5 | 51.4 | 562 |  |  | 2020-09-14 | B90631¦Judges chamber foyers ¦¦Sep-17-2020 12:51
2020-09-17 12:52 | 44091.5358 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #2 |  | 4 | 19 | 40.2 | 407 | 20.1 | 51.2 | 488 | courtroom #4 was in session | 2020-09-17 12:52 | 44091.5358 | 20.1 | 51.2 | 488 |  |  | 2020-09-14 | B20474¦Courtroom #2¦¦Sep-17-2020 12:51
2020-09-17 12:52 | 44091.536 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom a |  | 0 | 18 | 57 | 373 | 23 | 44 | 388 |  | 2020-09-17 12:52 | 44091.536 | 23 | 44 | 388 |  |  | 2020-09-14 | B20603¦Courtroom a¦¦Sep-17-2020 12:51
2020-09-17 12:52 | 44091.536 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 judge |  | 1 | 26 | 37 | 365 | 22 | 42 | 373 |  | 2020-09-17 12:52 | 44091.536 | 22 | 42 | 373 |  |  | 2020-09-14 | B20772¦H16 judge¦¦Sep-17-2020 12:51
2020-09-17 12:52 | 44091.5362 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | rm14 seating |  | 0 | 21 | 46 | 420 | 22 | 47 | 420 |  | 2020-09-17 12:52 | 44091.5362 | 22 | 47 | 420 |  |  | 2020-09-14 | B70740¦rm14 seating¦¦Sep-17-2020 12:52
2020-09-17 12:52 | 44091.5364 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Judges chamber |  | 0 | 15.9 | 47.9 | 408 | 22.5 | 51.3 | 514 |  | 2020-09-17 12:52 | 44091.5364 | 22.5 | 51.3 | 514 |  |  | 2020-09-14 | B90631¦Judges chamber ¦¦Sep-17-2020 12:52
2020-09-17 12:53 | 44091.5365 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Policeroom 3 |  | 0 | 20.3 | 46.1 | 420 | 21.6 | 43.2 | 399 |  | 2020-09-17 12:53 | 44091.5365 | 21.6 | 43.2 | 399 |  |  | 2020-09-14 | Pearso¦Policeroom 3 ¦¦Sep-17-2020 12:52
2020-09-17 12:53 | 44091.5366 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 Typer |  | 1 | 26 | 37 | 365 | 22 | 42 | 384 |  | 2020-09-17 12:53 | 44091.5366 | 22 | 42 | 384 |  |  | 2020-09-14 | B20772¦H16 Typer¦¦Sep-17-2020 12:52
2020-09-17 12:53 | 44091.5368 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | judge baldwin |  | 0 | 21 | 46 | 420 | 22.3 | 46 | 460 |  | 2020-09-17 12:53 | 44091.5368 | 22.3 | 46 | 460 |  |  | 2020-09-14 | B70740¦judge baldwin¦¦Sep-17-2020 12:52
2020-09-17 12:54 | 44091.5374 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | front HRPS |  | 0 | 21 | 46 | 420 | 22.2 | 42 | 420 |  | 2020-09-17 12:54 | 44091.5374 | 22.2 | 42 | 420 |  |  | 2020-09-14 | B70740¦front HRPS¦¦Sep-17-2020 12:53
2020-09-17 12:54 | 44091.5375 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom 1 |  | 0 | 15.9 | 47.9 | 408 | 21.9 | 50.6 | 622 |  | 2020-09-17 12:54 | 44091.5375 | 21.9 | 50.6 | 622 |  |  | 2020-09-14 | B90631¦Courtroom 1¦¦Sep-17-2020 12:53
2020-09-17 12:54 | 44091.5375 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom a |  | 0 | 21.4 | 44.2 | 396 | 21.1 | 45.1 | 409 |  | 2020-09-17 12:54 | 44091.5375 | 21.1 | 45.1 | 409 |  |  | 2020-09-14 | Pearso¦Ballroom a ¦¦Sep-17-2020 12:54
2020-09-17 12:54 | 44091.5375 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 1 |  | 3 | 15.2 | 70 | 377 | 23.2 | 42.1 | 392 |  | 2020-09-17 12:54 | 44091.5375 | 23.2 | 42.1 | 392 |  |  | 2020-09-14 | B20494¦Courtroom 1¦¦Sep-17-2020 12:54
2020-09-17 12:55 | 44091.538 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Upper landing stairway |  | 1 | 19 | 40.2 | 407 | 19.8 | 52.6 | 542 |  | 2020-09-17 12:55 | 44091.538 | 19.8 | 52.6 | 542 |  |  | 2020-09-14 | B20474¦Upper landing stairway¦¦Sep-17-2020 12:54
2020-09-17 12:55 | 44091.538 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 plaintiff |  | 1 | 26 | 37 | 365 | 22 | 42 | 380 |  | 2020-09-17 12:55 | 44091.538 | 22 | 42 | 380 |  |  | 2020-09-14 | B20772¦H16 plaintiff¦¦Sep-17-2020 12:54
2020-09-17 12:55 | 44091.5381 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | court officer |  | 0 | 21 | 46 | 420 | 21.6 | 37 | 460 |  | 2020-09-17 12:55 | 44091.5381 | 21.6 | 37 | 460 |  | caution | 2020-09-14 | B70740¦court officer¦¦Sep-17-2020 12:54
2020-09-17 12:55 | 44091.5382 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | South hallway |  | 0 | 18 | 57 | 373 | 23 | 44 | 390 |  | 2020-09-17 12:55 | 44091.5382 | 23 | 44 | 390 |  |  | 2020-09-14 | B20603¦South hallway¦¦Sep-17-2020 12:55
2020-09-17 12:55 | 44091.5383 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom waiting room |  | 0 | 15.9 | 47.9 | 408 | 21.6 | 50.1 | 726 |  | 2020-09-17 12:55 | 44091.5383 | 21.6 | 50.1 | 726 |  |  | 2020-09-14 | B90631¦Courtroom waiting room ¦¦Sep-17-2020 12:55
2020-09-17 12:56 | 44091.5388 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | judge brown |  | 0 | 21 | 46 | 420 | 22.6 | 47 | 460 |  | 2020-09-17 12:56 | 44091.5388 | 22.6 | 47 | 460 |  |  | 2020-09-14 | B70740¦judge brown¦¦Sep-17-2020 12:55
2020-09-17 12:56 | 44091.5389 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 3 |  | 1 | 15.2 | 70 | 477 | 22.8 | 48.5 | 472 |  | 2020-09-17 12:56 | 44091.5389 | 22.8 | 48.5 | 472 |  |  | 2020-09-14 | B20494¦Courtroom 3¦¦Sep-17-2020 12:56
2020-09-17 12:56 | 44091.5391 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom a 1 |  | 0 | 20.3 | 46.1 | 420 | 20.5 | 47.1 | 408 |  | 2020-09-17 12:56 | 44091.5391 | 20.5 | 47.1 | 408 |  |  | 2020-09-14 | Pearso¦Ballroom a 1¦¦Sep-17-2020 12:56
2020-09-17 12:56 | 44091.5392 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 defendant |  | 1 | 26 | 37 | 365 | 22 | 42 | 377 |  | 2020-09-17 12:56 | 44091.5392 | 22 | 42 | 377 |  |  | 2020-09-14 | B20772¦H16 defendant¦¦Sep-17-2020 12:56
2020-09-17 12:57 | 44091.5393 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | CROWN OFFICE 1 |  | 0 | 21 | 46 | 420 | 22.7 | 45 | 430 |  | 2020-09-17 12:57 | 44091.5393 | 22.7 | 45 | 430 |  |  | 2020-09-14 | B70740¦CROWN OFFICE 1¦¦Sep-17-2020 12:56
2020-09-17 12:57 | 44091.5396 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom #1 |  | 1 | 19 | 40.2 | 407 | 19.9 | 52.6 | 566 |  | 2020-09-17 12:57 | 44091.5396 | 19.9 | 52.6 | 566 |  |  | 2020-09-14 | B20474¦Waiting area courtroom #1¦¦Sep-17-2020 12:57
2020-09-17 12:57 | 44091.5398 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney printer room |  | 1 | 14.5 | 74.7 | 397 | 23.1 | 49.2 | 513 |  | 2020-09-17 12:57 | 44091.5398 | 23.1 | 49.2 | 513 |  |  | 2020-09-14 | B20494¦Crown attorney printer room¦¦Sep-17-2020 12:57
2020-09-17 12:57 | 44091.5399 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 printer area |  | 1 | 26 | 37 | 365 | 22 | 43 | 377 |  | 2020-09-17 12:57 | 44091.5399 | 22 | 43 | 377 |  |  | 2020-09-14 | B20772¦H16 printer area¦¦Sep-17-2020 12:57
2020-09-17 12:57 | 44091.5399 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN WR CORR |  | 0 | 21 | 46 | 420 | 22.5 | 43 | 425 |  | 2020-09-17 12:57 | 44091.5399 | 22.5 | 43 | 425 |  |  | 2020-09-14 | B70740¦MAIN WR CORR¦¦Sep-17-2020 12:57
2020-09-17 12:58 | 44091.5405 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 13 |  | 0 | 21 | 46 | 420 | 23 | 44 | 430 |  | 2020-09-17 12:58 | 44091.5405 | 23 | 44 | 430 |  |  | 2020-09-14 | B70740¦13¦¦Sep-17-2020 12:58
2020-09-17 12:59 | 44091.5407 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom a 2 |  | 0 | 20.3 | 46.1 | 420 | 20.6 | 47.6 | 407 |  | 2020-09-17 12:59 | 44091.5407 | 20.6 | 47.6 | 407 |  |  | 2020-09-14 | Pearso¦Ballroom a 2¦¦Sep-17-2020 12:58
2020-09-17 12:59 | 44091.5408 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Second floor hallway nw |  | 1 | 15.2 | 70 | 377 | 22.8 | 46.6 | 488 |  | 2020-09-17 12:59 | 44091.5408 | 22.8 | 46.6 | 488 |  |  | 2020-09-14 | B20494¦Second floor hallway nw¦¦Sep-17-2020 12:58
2020-09-17 12:59 | 44091.5411 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | SEATING 13 |  | 0 | 21 | 46 | 420 | 23 | 43 | 430 |  | 2020-09-17 12:59 | 44091.5411 | 23 | 43 | 430 |  |  | 2020-09-14 | B70740¦SEATING 13¦¦Sep-17-2020 12:59
2020-09-17 13:00 | 44091.5417 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Creation attorney library |  | 1 | 14.5 | 74.7 | 397 | 23.1 | 48.8 | 512 |  | 2020-09-17 13:00 | 44091.5417 | 23.1 | 48.8 | 512 |  |  | 2020-09-14 | B20494¦Creation attorney library¦¦Sep-17-2020 13:00
2020-09-17 13:00 | 44091.5417 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | SEATING 12 |  | 0 | 21 | 46 | 420 | 23 | 44 | 430 |  | 2020-09-17 13:00 | 44091.5417 | 23 | 44 | 430 |  |  | 2020-09-14 | B70740¦SEATING 12¦¦Sep-17-2020 13:00
2020-09-17 13:01 | 44091.5421 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 12 |  | 0 | 21 | 46 | 420 | 22.8 | 45 | 450 |  | 2020-09-17 13:01 | 44091.5421 | 22.8 | 45 | 450 |  |  | 2020-09-14 | B70740¦12¦¦Sep-17-2020 13:00
2020-09-17 13:01 | 44091.5423 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Second floor hallway sw |  | 1 | 15.2 | 70 | 387 | 22.6 | 48.3 | 480 |  | 2020-09-17 13:01 | 44091.5423 | 22.6 | 48.3 | 480 |  |  | 2020-09-14 | B20494¦Second floor hallway sw¦¦Sep-17-2020 13:00
2020-09-17 13:01 | 44091.5423 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom a 3 |  | 0 | 20.3 | 46.1 | 420 | 20.7 | 46.9 | 407 |  | 2020-09-17 13:01 | 44091.5423 | 20.7 | 46.9 | 407 |  |  | 2020-09-14 | Pearso¦Ballroom a 3 ¦¦Sep-17-2020 13:00
2020-09-17 13:01 | 44091.5426 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN AREA |  | 4 | 21 | 46 | 420 | 22.3 | 45 | 450 |  | 2020-09-17 13:01 | 44091.5426 | 22.3 | 45 | 450 |  |  | 2020-09-14 | B70740¦MAIN AREA¦¦Sep-17-2020 13:01
2020-09-17 13:01 | 44091.5426 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 3 gallery |  | 1 | 15 | 68 | 421 | 22.6 | 39.2 | 439 | No | 2020-09-17 13:01 | 44091.5426 | 22.6 | 39.2 | 439 |  | caution | 2020-09-14 | B20151¦Court room 3 gallery ¦¦Sep-17-2020 13:01
2020-09-17 13:02 | 44091.5427 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area |  | 1 | 26 | 37 | 365 | 23 | 42 | 378 |  | 2020-09-17 13:02 | 44091.5427 | 23 | 42 | 378 |  |  | 2020-09-14 | B20772¦Courtroom waiting area¦¦Sep-17-2020 13:01
2020-09-17 13:02 | 44091.5429 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st floor main lobby |  | 3 | 13.8 | 57.3 | 394 | 18.1 | 55.1 | 571 | no | 2020-09-17 13:02 | 44091.5429 | 18.1 | 55.1 | 571 |  |  | 2020-09-14 | B70496¦1st floor main lobby¦¦Sep-17-2020 13:01
2020-09-17 13:02 | 44091.5431 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN OFFICE |  | 2 | 21 | 46 | 420 | 22.5 | 47 | 470 |  | 2020-09-17 13:02 | 44091.5431 | 22.5 | 47 | 470 |  |  | 2020-09-14 | B70740¦MAIN OFFICE¦¦Sep-17-2020 13:02
2020-09-17 13:03 | 44091.5435 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area part b |  | 1 | 26 | 37 | 365 | 23 | 42 | 372 |  | 2020-09-17 13:03 | 44091.5435 | 23 | 42 | 372 |  |  | 2020-09-14 | B20772¦Courtroom waiting area part b ¦¦Sep-17-2020 13:02
2020-09-17 13:03 | 44091.5436 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney office |  | 3 | 14.5 | 74.7 | 397 | 23.2 | 50.1 | 548 |  | 2020-09-17 13:03 | 44091.5436 | 23.2 | 50.1 | 548 |  |  | 2020-09-14 | B20494¦Crown attorney office¦¦Sep-17-2020 13:02
2020-09-17 13:03 | 44091.5438 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 3 judge's desk |  | 1 | 15 | 68 | 421 | 22.6 | 39.4 | 447 | No | 2020-09-17 13:03 | 44091.5438 | 22.6 | 39.4 | 447 |  | caution | 2020-09-14 | B20151¦Court room 3 judge's desk ¦¦Sep-17-2020 13:03
2020-09-17 13:03 | 44091.5439 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family court waiting room |  | 1 | 15.2 | 70 | 377 | 23 | 48.5 | 497 |  | 2020-09-17 13:03 | 44091.5439 | 23 | 48.5 | 497 |  |  | 2020-09-14 | B20494¦Family court waiting room¦¦Sep-17-2020 13:03
2020-09-17 13:04 | 44091.5441 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st floor hallway |  | 1 | 13.8 | 57.3 | 394 | 20.3 | 49.1 | 497 | no | 2020-09-17 13:04 | 44091.5441 | 20.3 | 49.1 | 497 |  |  | 2020-09-14 | B70496¦1st floor hallway¦¦Sep-17-2020 13:03
2020-09-17 13:04 | 44091.5444 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Administrative office |  | 3 | 17 | 52.3 | 402 | 21.4 | 47.3 | 483 |  | 2020-09-17 13:04 | 44091.5444 | 21.4 | 47.3 | 483 |  |  | 2020-09-14 | B90558¦Administrative office¦¦Sep-17-2020 13:04
2020-09-17 13:04 | 44091.5448 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st floor seating area |  | 1 | 13.8 | 57.3 | 394 | 20.6 | 46.8 | 442 | no | 2020-09-17 13:04 | 44091.5448 | 20.6 | 46.8 | 442 |  |  | 2020-09-14 | B70496¦1st floor seating area¦¦Sep-17-2020 13:04
2020-09-17 13:05 | 44091.5455 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 101 |  | 3 | 13.8 | 57.3 | 394 | 21.8 | 42.7 | 456 | no | 2020-09-17 13:05 | 44091.5455 | 21.8 | 42.7 | 456 |  |  | 2020-09-14 | B70496¦101¦¦Sep-17-2020 13:05
2020-09-17 13:06 | 44091.5455 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | entryway |  | 2 | 18.6 | 70.9 | 418 | 19.9 | 61.3 | 554 |  | 2020-09-17 13:06 | 44091.5455 | 19.9 | 61.3 | 554 |  | caution | 2020-09-14 | B20390¦entryway¦¦Sep-17-2020 13:05
2020-09-17 13:06 | 44091.5457 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 1 |  | 0 | 15 | 68 | 421 | 22.5 | 37 | 393 | No | 2020-09-17 13:06 | 44091.5457 | 22.5 | 37 | 393 |  | caution | 2020-09-14 | B20151¦Court room 1¦¦Sep-17-2020 13:05
2020-09-17 13:07 | 44091.5463 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 102 |  | 2 | 13.8 | 57.3 | 394 | 22.2 | 39.4 | 446 | no | 2020-09-17 13:07 | 44091.5463 | 22.2 | 39.4 | 446 |  | caution | 2020-09-14 | B70496¦102¦¦Sep-17-2020 13:06
2020-09-17 13:07 | 44091.5465 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main floor waiting area |  | 4 | 18.6 | 70.9 | 418 | 20.5 | 58.2 | 481 |  | 2020-09-17 13:07 | 44091.5465 | 20.5 | 58.2 | 481 |  |  | 2020-09-14 | B20390¦Main floor waiting area¦¦Sep-17-2020 13:07
2020-09-17 13:07 | 44091.5468 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom#1 |  | 1 | 17 | 52.3 | 402 | 21.7 | 45.3 | 442 |  | 2020-09-17 13:07 | 44091.5468 | 21.7 | 45.3 | 442 |  |  | 2020-09-14 | B90558¦Courtroom#1¦¦Sep-17-2020 13:07
2020-09-17 13:07 | 44091.5468 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family court office |  | 2 | 15.2 | 70 | 377 | 22.8 | 47.1 | 510 |  | 2020-09-17 13:07 | 44091.5468 | 22.8 | 47.1 | 510 |  |  | 2020-09-14 | B20494¦Family court office ¦¦Sep-17-2020 13:07
2020-09-17 13:08 | 44091.5471 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom b |  | 0 | 20.3 | 46.1 | 420 | 22.8 | 42 | 405 |  | 2020-09-17 13:08 | 44091.5471 | 22.8 | 42 | 405 |  |  | 2020-09-14 | Pearso¦Ballroom b ¦¦Sep-17-2020 13:07
2020-09-17 13:08 | 44091.5474 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 102 |  | 2 | 13.8 | 57.3 | 394 | 22.4 | 39.2 | 440 | no | 2020-09-17 13:08 | 44091.5474 | 22.4 | 39.2 | 440 |  | caution | 2020-09-14 | B70496¦102¦¦Sep-17-2020 13:08
2020-09-17 13:08 | 44091.5475 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 2 |  | 2 | 18.6 | 70.9 | 418 | 20.8 | 57 | 502 |  | 2020-09-17 13:08 | 44091.5475 | 20.8 | 57 | 502 |  |  | 2020-09-14 | B20390¦Outside courtroom 2¦¦Sep-17-2020 13:08
2020-09-17 13:09 | 44091.5477 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom b 1 |  | 0 | 20.3 | 46.1 | 420 | 22.3 | 42.7 | 407 |  | 2020-09-17 13:09 | 44091.5477 | 22.3 | 42.7 | 407 |  |  | 2020-09-14 | Pearso¦Ballroom b 1 ¦¦Sep-17-2020 13:08
2020-09-17 13:09 | 44091.5479 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family court vestibule |  | 2 | 15.2 | 70 | 377 | 22.8 | 43.4 | 504 |  | 2020-09-17 13:09 | 44091.5479 | 22.8 | 43.4 | 504 |  |  | 2020-09-14 | B20494¦Family court vestibule ¦¦Sep-17-2020 13:08
2020-09-17 13:09 | 44091.548 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | stairwell |  | 1 | 13.8 | 57.3 | 394 | 22.3 | 43.4 | 576 | no | 2020-09-17 13:09 | 44091.548 | 22.3 | 43.4 | 576 |  |  | 2020-09-14 | B70496¦stairwell¦¦Sep-17-2020 13:09
2020-09-17 13:09 | 44091.5482 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney waiting room |  | 1 | 14.5 | 74.7 | 397 | 23.2 | 51 | 555 |  | 2020-09-17 13:09 | 44091.5482 | 23.2 | 51 | 555 |  |  | 2020-09-14 | B20494¦Crown attorney waiting room¦¦Sep-17-2020 13:09
2020-09-17 13:10 | 44091.5483 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | OPP office |  | 2 | 18 | 50 | 404 | 23 | 45 | 578 |  | 2020-09-17 13:10 | 44091.5483 | 23 | 45 | 578 |  |  | 2020-09-14 | B70235¦OPP office ¦¦Sep-17-2020 13:09
2020-09-17 13:10 | 44091.5487 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 2nd floor elevator lobby |  | 1 | 13.8 | 57.3 | 394 | 22.5 | 43.5 | 520 | no | 2020-09-17 13:10 | 44091.5487 | 22.5 | 43.5 | 520 |  |  | 2020-09-14 | B70496¦2nd floor elevator lobby¦¦Sep-17-2020 13:10
2020-09-17 13:10 | 44091.5488 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 3 |  | 2 | 18.6 | 70.9 | 418 | 20.9 | 56.2 | 471 |  | 2020-09-17 13:10 | 44091.5488 | 20.9 | 56.2 | 471 |  |  | 2020-09-14 | B20390¦Outside courtroom 3¦¦Sep-17-2020 13:10
2020-09-17 13:10 | 44091.5489 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 1st floor hall by elevator |  | 2 | 14.5 | 74.7 | 397 | 23.8 | 45.3 | 485 |  | 2020-09-17 13:10 | 44091.5489 | 23.8 | 45.3 | 485 |  |  | 2020-09-14 | B20494¦1st floor hall by elevator¦¦Sep-17-2020 13:10
2020-09-17 13:11 | 44091.549 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom#2 |  | 3 | 17 | 52.3 | 402 | 21.5 | 45.2 | 446 |  | 2020-09-17 13:11 | 44091.549 | 21.5 | 45.2 | 446 |  |  | 2020-09-14 | B90558¦Courtroom#2¦¦Sep-17-2020 13:10
2020-09-17 13:11 | 44091.5494 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family court office |  | 2 | 15.2 | 70 | 377 | 22.9 | 45.5 | 500 |  | 2020-09-17 13:11 | 44091.5494 | 22.9 | 45.5 | 500 |  |  | 2020-09-14 | B20494¦Family court office ¦¦Sep-17-2020 13:11
2020-09-17 13:11 | 44091.5494 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 204 |  | 1 | 13.8 | 57.3 | 394 | 22 | 40.2 | 450 | no | 2020-09-17 13:11 | 44091.5494 | 22 | 40.2 | 450 |  |  | 2020-09-14 | B70496¦204¦¦Sep-17-2020 13:11
2020-09-17 13:11 | 44091.5496 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 South |  | 0 | 22.3 | 48.6 | 399 | 23.1 | 48.1 | 708 |  | 2020-09-17 13:11 | 44091.5496 | 23.1 | 48.1 | 708 |  |  | 2020-09-14 | B10577¦Courtroom 1 South¦¦Sep-17-2020 13:11
2020-09-17 13:12 | 44091.5497 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | First floor vending machines |  | 1 | 18.6 | 70.9 | 418 | 21.5 | 56.4 | 464 |  | 2020-09-17 13:12 | 44091.5497 | 21.5 | 56.4 | 464 |  |  | 2020-09-14 | B20390¦First floor vending machines¦¦Sep-17-2020 13:11
2020-09-17 13:12 | 44091.5498 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom b 3 |  | 0 | 20.3 | 46.1 | 420 | 22 | 44 | 404 |  | 2020-09-17 13:12 | 44091.5498 | 22 | 44 | 404 |  |  | 2020-09-14 | Pearso¦Ballroom b 3 ¦¦Sep-17-2020 13:11
2020-09-17 13:12 | 44091.5498 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office E |  | 2 | 18 | 50 | 404 | 23 | 43 | 521 |  | 2020-09-17 13:12 | 44091.5498 | 23 | 43 | 521 |  |  | 2020-09-14 | B70235¦Main office E ¦¦Sep-17-2020 13:11
2020-09-17 13:12 | 44091.5502 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 East |  | 0 | 22.3 | 48.6 | 399 | 23.5 | 47.9 | 687 |  | 2020-09-17 13:12 | 44091.5502 | 23.5 | 47.9 | 687 |  |  | 2020-09-14 | B10577¦Courtroom 1 East¦¦Sep-17-2020 13:12
2020-09-17 13:12 | 44091.5502 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 204 |  | 1 | 13.8 | 57.3 | 394 | 21.8 | 40.5 | 426 | no | 2020-09-17 13:12 | 44091.5502 | 21.8 | 40.5 | 426 |  |  | 2020-09-14 | B70496¦204¦¦Sep-17-2020 13:12
2020-09-17 13:13 | 44091.5505 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom c |  | 0 | 20.3 | 46.1 | 420 | 22.2 | 41.8 | 402 |  | 2020-09-17 13:13 | 44091.5505 | 22.2 | 41.8 | 402 |  |  | 2020-09-14 | Pearso¦Ballroom c ¦¦Sep-17-2020 13:12
2020-09-17 13:13 | 44091.5505 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office C |  | 2 | 18 | 50 | 404 | 23 | 43 | 516 |  | 2020-09-17 13:13 | 44091.5505 | 23 | 43 | 516 |  |  | 2020-09-14 | B70235¦Main office C ¦¦Sep-17-2020 13:12
2020-09-17 13:13 | 44091.5505 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 gallery |  | 2 | 15 | 68 | 421 | 22.8 | 42 | 520 | No | 2020-09-17 13:13 | 44091.5505 | 22.8 | 42 | 520 |  |  | 2020-09-14 | B20151¦Court room 2 gallery ¦¦Sep-17-2020 13:12
2020-09-17 13:13 | 44091.5509 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 North |  | 0 | 22.3 | 48.6 | 399 | 23.4 | 48 | 674 |  | 2020-09-17 13:13 | 44091.5509 | 23.4 | 48 | 674 |  |  | 2020-09-14 | B10577¦Courtroom 1 North¦¦Sep-17-2020 13:13
2020-09-17 13:13 | 44091.551 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 2nd floor hallway |  | 1 | 13.8 | 57.3 | 394 | 22.3 | 41.4 | 455 | no | 2020-09-17 13:13 | 44091.551 | 22.3 | 41.4 | 455 |  |  | 2020-09-14 | B70496¦2nd floor hallway¦¦Sep-17-2020 13:13
2020-09-17 13:13 | 44091.551 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell, first floor |  | 1 | 18.6 | 70.9 | 418 | 21.8 | 54.1 | 443 |  | 2020-09-17 13:13 | 44091.551 | 21.8 | 54.1 | 443 |  |  | 2020-09-14 | B20390¦Main stairwell, first floor ¦¦Sep-17-2020 13:13
2020-09-17 13:14 | 44091.5511 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Cell block |  | 1 | 14.5 | 74.7 | 397 | 23.3 | 46.7 | 482 |  | 2020-09-17 13:14 | 44091.5511 | 23.3 | 46.7 | 482 |  |  | 2020-09-14 | B20494¦Cell block¦¦Sep-17-2020 13:13
2020-09-17 13:14 | 44091.5511 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom c 1 |  | 0 | 20.3 | 46.1 | 420 | 22.1 | 41.3 | 401 |  | 2020-09-17 13:14 | 44091.5511 | 22.1 | 41.3 | 401 |  |  | 2020-09-14 | Pearso¦Ballroom c 1 ¦¦Sep-17-2020 13:13
2020-09-17 13:14 | 44091.5512 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom#3 |  | 4 | 17 | 52.3 | 402 | 21.7 | 45 | 436 |  | 2020-09-17 13:14 | 44091.5512 | 21.7 | 45 | 436 |  |  | 2020-09-14 | B90558¦Courtroom#3¦¦Sep-17-2020 13:13
2020-09-17 13:14 | 44091.5514 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 West |  | 0 | 22.3 | 48.6 | 399 | 23.5 | 48.2 | 666 |  | 2020-09-17 13:14 | 44091.5514 | 23.5 | 48.2 | 666 |  |  | 2020-09-14 | B10577¦Courtroom 1 West¦¦Sep-17-2020 13:14
2020-09-17 13:15 | 44091.5518 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 Center |  | 0 | 22.3 | 48.6 | 399 | 23.3 | 48.7 | 665 |  | 2020-09-17 13:15 | 44091.5518 | 23.3 | 48.7 | 665 |  |  | 2020-09-14 | B10577¦Courtroom 1 Center¦¦Sep-17-2020 13:14
2020-09-17 13:15 | 44091.5518 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 5 |  | 1 | 15.2 | 70 | 377 | 22.3 | 46.6 | 441 |  | 2020-09-17 13:15 | 44091.5518 | 22.3 | 46.6 | 441 |  |  | 2020-09-14 | B20494¦Courtroom 5¦¦Sep-17-2020 13:14
2020-09-17 13:15 | 44091.5519 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom c 2 |  | 0 | 20.3 | 46.1 | 420 | 21.7 | 42.2 | 400 |  | 2020-09-17 13:15 | 44091.5519 | 21.7 | 42.2 | 400 |  |  | 2020-09-14 | Pearso¦Ballroom c 2¦¦Sep-17-2020 13:14
2020-09-17 13:15 | 44091.5522 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office W |  | 2 | 18 | 50 | 404 | 23 | 43 | 510 |  | 2020-09-17 13:15 | 44091.5522 | 23 | 43 | 510 |  |  | 2020-09-14 | B70235¦Main office W ¦¦Sep-17-2020 13:15
2020-09-17 13:15 | 44091.5523 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice Letourneau office |  | 0 | 17 | 52.3 | 402 | 22 | 45.8 | 439 |  | 2020-09-17 13:15 | 44091.5523 | 22 | 45.8 | 439 |  |  | 2020-09-14 | B90558¦Justice Letourneau office¦¦Sep-17-2020 13:15
2020-09-17 13:15 | 44091.5523 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 judge's desk |  | 2 | 15 | 68 | 421 | 21.8 | 41.1 | 546 | No | 2020-09-17 13:15 | 44091.5523 | 21.8 | 41.1 | 546 |  |  | 2020-09-14 | B20151¦Court room 2 judge's desk ¦¦Sep-17-2020 13:15
2020-09-17 13:15 | 44091.5524 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell, second floor |  | 1 | 18.6 | 70.9 | 418 | 22.1 | 52.9 | 440 |  | 2020-09-17 13:15 | 44091.5524 | 22.1 | 52.9 | 440 |  |  | 2020-09-14 | B20390¦Main stairwell, second floor¦¦Sep-17-2020 13:15
2020-09-17 13:16 | 44091.5531 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Second floor waiting area |  | 1 | 18.6 | 70.9 | 418 | 22.3 | 50.5 | 432 |  | 2020-09-17 13:16 | 44091.5531 | 22.3 | 50.5 | 432 |  |  | 2020-09-14 | B20390¦Second floor waiting area ¦¦Sep-17-2020 13:16
2020-09-17 13:17 | 44091.5534 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway ne |  | 1 | 15.2 | 70 | 377 | 22.6 | 47.3 | 473 |  | 2020-09-17 13:17 | 44091.5534 | 22.6 | 47.3 | 473 |  |  | 2020-09-14 | B20494¦Third floor hallway ne¦¦Sep-17-2020 13:16
2020-09-17 13:17 | 44091.5535 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice Wheeler office |  | 0 | 17 | 52.3 | 402 | 21.6 | 46 | 429 |  | 2020-09-17 13:17 | 44091.5535 | 21.6 | 46 | 429 |  |  | 2020-09-14 | B90558¦Justice Wheeler office¦¦Sep-17-2020 13:17
2020-09-17 13:17 | 44091.5535 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 |  | 2 | 15 | 68 | 421 | 22.8 | 34.5 | 559 | No | 2020-09-17 13:17 | 44091.5535 | 22.8 | 34.5 | 559 |  | low | 2020-09-14 | B20151¦Court room 2¦¦Sep-17-2020 13:17
2020-09-17 13:18 | 44091.5538 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Front lobby |  | 1 | 17.7 | 46.2 | 435 | 19.4 | 53.6 | 535 |  | 2020-09-17 13:18 | 44091.5538 | 19.4 | 53.6 | 535 |  |  | 2020-09-14 | B19890¦Front lobby¦¦Sep-17-2020 13:17
2020-09-17 13:18 | 44091.554 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside museum |  | 1 | 18.6 | 70.9 | 418 | 22.5 | 51.1 | 430 |  | 2020-09-17 13:18 | 44091.554 | 22.5 | 51.1 | 430 |  |  | 2020-09-14 | B20390¦Outside museum¦¦Sep-17-2020 13:17
2020-09-17 13:18 | 44091.5541 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family services |  | 1 | 14.5 | 74.7 | 397 | 22.4 | 47.8 | 482 |  | 2020-09-17 13:18 | 44091.5541 | 22.4 | 47.8 | 482 |  |  | 2020-09-14 | B20494¦Family services ¦¦Sep-17-2020 13:17
2020-09-17 13:18 | 44091.5545 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Public seating area |  | 0 | 17.7 | 46.2 | 435 | 20.3 | 54 | 582 |  | 2020-09-17 13:18 | 44091.5545 | 20.3 | 54 | 582 |  |  | 2020-09-14 | B19890¦Public seating area ¦¦Sep-17-2020 13:18
2020-09-17 13:19 | 44091.5546 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway se |  | 3 | 15.2 | 70 | 377 | 23.7 | 46.3 | 486 |  | 2020-09-17 13:19 | 44091.5546 | 23.7 | 46.3 | 486 |  |  | 2020-09-14 | B20494¦Third floor hallway se¦¦Sep-17-2020 13:18
2020-09-17 13:19 | 44091.5547 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Museum |  | 1 | 18.6 | 70.9 | 418 | 22.1 | 51.9 | 436 |  | 2020-09-17 13:19 | 44091.5547 | 22.1 | 51.9 | 436 |  |  | 2020-09-14 | B20390¦Museum ¦¦Sep-17-2020 13:18
2020-09-17 13:19 | 44091.5547 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice O'Brien office |  | 0 | 17 | 52.3 | 402 | 19.9 | 42.8 | 441 | Dehumidifier running set at 17 | 2020-09-17 13:19 | 44091.5547 | 19.9 | 42.8 | 441 |  |  | 2020-09-14 | B90558¦Justice O'Brien office¦¦Sep-17-2020 13:18
2020-09-17 13:19 | 44091.555 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 waiting |  | 0 | 15 | 68 | 421 | 22.8 | 39 | 501 |  | 2020-09-17 13:19 | 44091.555 | 22.8 | 39 | 501 |  | caution | 2020-09-14 | B20151¦Court room 2 waiting ¦¦Sep-17-2020 13:19
2020-09-17 13:20 | 44091.5553 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Trial office |  | 2 | 18 | 50 | 403 | 23 | 42 | 479 |  | 2020-09-17 13:20 | 44091.5553 | 23 | 42 | 479 |  |  | 2020-09-14 | B70235¦Trial office ¦¦Sep-17-2020 13:19
2020-09-17 13:20 | 44091.5554 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Main entrance |  | 0 | 17.7 | 46.2 | 435 | 21.4 | 51.2 | 590 |  | 2020-09-17 13:20 | 44091.5554 | 21.4 | 51.2 | 590 |  |  | 2020-09-14 | B19890¦Main entrance ¦¦Sep-17-2020 13:19
2020-09-17 13:21 | 44091.5559 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jennifer Mumby office |  | 0 | 18 | 50 | 404 | 22 | 41 | 496 |  | 2020-09-17 13:21 | 44091.5559 | 22 | 41 | 496 |  |  | 2020-09-14 | B70235¦Jennifer Mumby office ¦¦Sep-17-2020 13:20
2020-09-17 13:21 | 44091.556 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Library |  | 0 | 17 | 52.3 | 402 | 19.9 | 50 | 436 |  | 2020-09-17 13:21 | 44091.556 | 19.9 | 50 | 436 |  |  | 2020-09-14 | B90558¦Library¦¦Sep-17-2020 13:20
2020-09-17 13:21 | 44091.556 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 203 |  | 1 | 13.8 | 57.3 | 394 | 21.3 | 43.5 | 468 | no | 2020-09-17 13:21 | 44091.556 | 21.3 | 43.5 | 468 |  |  | 2020-09-14 | B70496¦203¦¦Sep-17-2020 13:20
2020-09-17 13:21 | 44091.5565 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway nw |  | 1 | 15.2 | 70 | 377 | 23.2 | 47.6 | 457 |  | 2020-09-17 13:21 | 44091.5565 | 23.2 | 47.6 | 457 |  |  | 2020-09-14 | B20494¦Third floor hallway nw¦¦Sep-17-2020 13:21
2020-09-17 13:21 | 44091.5565 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Robert Beninger office |  | 0 | 18 | 50 | 404 | 22 | 42 | 491 |  | 2020-09-17 13:21 | 44091.5565 | 22 | 42 | 491 |  |  | 2020-09-14 | B70235¦Robert Beninger office ¦¦Sep-17-2020 13:21
2020-09-17 13:21 | 44091.5565 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Staff area |  | 4 | 17.7 | 46.2 | 435 | 22.3 | 45.4 | 596 |  | 2020-09-17 13:21 | 44091.5565 | 22.3 | 45.4 | 596 |  |  | 2020-09-14 | B19890¦Staff area ¦¦Sep-17-2020 13:21
2020-09-17 13:22 | 44091.5567 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin waiting area |  | 0 | 15 | 68 | 421 | 22.2 | 37.2 | 474 |  | 2020-09-17 13:22 | 44091.5567 | 22.2 | 37.2 | 474 |  | caution | 2020-09-14 | B20151¦Admin waiting area ¦¦Sep-17-2020 13:21
2020-09-17 13:22 | 44091.5568 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Fire pump |  | 1 | 14.5 | 74.7 | 397 | 23.6 | 48 | 476 |  | 2020-09-17 13:22 | 44091.5568 | 23.6 | 48 | 476 |  |  | 2020-09-14 | B20494¦Fire pump¦¦Sep-17-2020 13:21
2020-09-17 13:22 | 44091.5569 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Jury room waiting area |  | 1 | 18.6 | 70.9 | 418 | 22.3 | 51.6 | 414 |  | 2020-09-17 13:22 | 44091.5569 | 22.3 | 51.6 | 414 |  |  | 2020-09-14 | B20390¦Jury room waiting area¦¦Sep-17-2020 13:21
2020-09-17 13:22 | 44091.5571 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 202 |  | 3 | 13.8 | 57.3 | 394 | 22 | 40.6 | 490 | no | 2020-09-17 13:22 | 44091.5571 | 22 | 40.6 | 490 |  |  | 2020-09-14 | B70496¦202¦¦Sep-17-2020 13:22
2020-09-17 13:23 | 44091.5575 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | TC office |  | 0 | 17 | 52.3 | 402 | 21 | 47.4 | 429 |  | 2020-09-17 13:23 | 44091.5575 | 21 | 47.4 | 429 |  |  | 2020-09-14 | B90558¦TC office¦¦Sep-17-2020 13:22
2020-09-17 13:23 | 44091.5575 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Crown òffice |  | 2 | 17.7 | 46.2 | 435 | 22.7 | 45.9 | 569 |  | 2020-09-17 13:23 | 44091.5575 | 22.7 | 45.9 | 569 |  |  | 2020-09-14 | B19890¦Crown òffice¦¦Sep-17-2020 13:22
2020-09-17 13:23 | 44091.5576 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom c 3 |  | 0 | 20.3 | 46.1 | 420 | 21.5 | 42.6 | 400 |  | 2020-09-17 13:23 | 44091.5576 | 21.5 | 42.6 | 400 |  |  | 2020-09-14 | Pearso¦Ballroom c 3¦¦Sep-17-2020 13:23
2020-09-17 13:23 | 44091.5577 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Stuart Konyer |  | 0 | 18 | 50 | 404 | 22 | 45 | 481 |  | 2020-09-17 13:23 | 44091.5577 | 22 | 45 | 481 |  |  | 2020-09-14 | B70235¦Stuart Konyer ¦¦Sep-17-2020 13:23
2020-09-17 13:23 | 44091.5578 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 201 |  | 1 | 13.8 | 57.3 | 394 | 21.8 | 41.6 | 460 | no | 2020-09-17 13:23 | 44091.5578 | 21.8 | 41.6 | 460 |  |  | 2020-09-14 | B70496¦201¦¦Sep-17-2020 13:23
2020-09-17 13:23 | 44091.5578 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin office |  | 3 | 15 | 68 | 421 | 22.7 | 42.7 | 569 | No | 2020-09-17 13:23 | 44091.5578 | 22.7 | 42.7 | 569 |  |  | 2020-09-14 | B20151¦Admin office ¦¦Sep-17-2020 13:23
2020-09-17 13:24 | 44091.5583 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway sw |  | 1 | 15.2 | 70 | 377 | 24.1 | 44.7 | 457 |  | 2020-09-17 13:24 | 44091.5583 | 24.1 | 44.7 | 457 |  |  | 2020-09-14 | B20494¦Third floor hallway sw¦¦Sep-17-2020 13:24
2020-09-17 13:24 | 44091.5584 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | Administration Office |  | 3 | 13.8 | 57.3 | 394 | 21.8 | 41.7 | 480 | no | 2020-09-17 13:24 | 44091.5584 | 21.8 | 41.7 | 480 |  |  | 2020-09-14 | B70496¦Administration Office¦¦Sep-17-2020 13:24
2020-09-17 13:24 | 44091.5585 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 4 |  | 2 | 14.5 | 74.7 | 397 | 23.1 | 45.8 | 503 |  | 2020-09-17 13:24 | 44091.5585 | 23.1 | 45.8 | 503 |  |  | 2020-09-14 | B20494¦Courtroom 4¦¦Sep-17-2020 13:24
2020-09-17 13:25 | 44091.5589 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Lunch room |  | 0 | 18 | 50 | 404 | 22 | 46 | 501 |  | 2020-09-17 13:25 | 44091.5589 | 22 | 46 | 501 |  |  | 2020-09-14 | B70235¦Lunch room ¦¦Sep-17-2020 13:24
2020-09-17 13:25 | 44091.5591 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin supervisor |  | 1 | 15 | 68 | 421 | 22.8 | 43.7 | 725 | No | 2020-09-17 13:25 | 44091.5591 | 22.8 | 43.7 | 725 |  |  | 2020-09-14 | B20151¦Admin supervisor ¦¦Sep-17-2020 13:25
2020-09-17 13:25 | 44091.5591 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Waiting area 2 floor |  | 0 | 17 | 52.3 | 402 | 20.7 | 48.1 | 430 |  | 2020-09-17 13:25 | 44091.5591 | 20.7 | 48.1 | 430 |  |  | 2020-09-14 | B90558¦Waiting area 2 floor¦¦Sep-17-2020 13:25
2020-09-17 13:25 | 44091.5591 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | Outside Customer Service Entrance |  | 1 | 13.8 | 57.3 | 394 | 15.2 | 51.5 | 405 | no | 2020-09-17 13:25 | 44091.5591 | 15.2 | 51.5 | 405 |  |  | 2020-09-14 | B70496¦Outside Customer Service Entrance¦¦Sep-17-2020 13:25
2020-09-17 13:25 | 44091.5592 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 6 |  | 1 | 18.6 | 70.9 | 418 | 22.6 | 50.1 | 417 |  | 2020-09-17 13:25 | 44091.5592 | 22.6 | 50.1 | 417 |  |  | 2020-09-14 | B20390¦Outside courtroom 6¦¦Sep-17-2020 13:25
2020-09-17 13:25 | 44091.5593 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Public seating area 2 |  | 0 | 17.7 | 46.2 | 435 | 22.4 |  | 498 |  | 2020-09-17 13:25 | 44091.5593 | 22.4 |  | 498 |  |  | 2020-09-14 | B19890¦Public seating area 2¦¦Sep-17-2020 13:25
2020-09-17 13:26 | 44091.5599 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 1 |  | 1 | 15.2 | 70 | 377 |  |  |  | Doors locked; no access available | 2020-09-17 13:26 | 44091.5599 | [5 empty] | 2020-09-14 | B20494¦Courtroom 1¦¦Sep-17-2020 13:26
2020-09-17 13:26 | 44091.5599 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court support office |  | 0 | 18 | 50 | 404 | 22 | 45 | 495 |  | 2020-09-17 13:26 | 44091.5599 | 22 | 45 | 495 |  |  | 2020-09-14 | B70235¦Court support office ¦¦Sep-17-2020 13:26
2020-09-17 13:27 | 44091.5602 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Back stairwell, second floor |  | 1 | 18.6 | 70.9 | 418 | 22.4 | 51.2 | 415 |  | 2020-09-17 13:27 | 44091.5602 | 22.4 | 51.2 | 415 |  |  | 2020-09-14 | B20390¦Back stairwell, second floor¦¦Sep-17-2020 13:26
2020-09-17 13:27 | 44091.5604 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin file room |  | 0 | 15 | 68 | 421 | 22.8 | 40 | 498 | No | 2020-09-17 13:27 | 44091.5604 | 22.8 | 40 | 498 |  | caution | 2020-09-14 | B20151¦Admin file room ¦¦Sep-17-2020 13:26
2020-09-17 13:27 | 44091.5604 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Courtroom 2 |  | 0 | 17.7 | 46.2 | 435 | 22.5 | 41.2 | 456 |  | 2020-09-17 13:27 | 44091.5604 | 22.5 | 41.2 | 456 |  |  | 2020-09-14 | B19890¦Courtroom 2¦¦Sep-17-2020 13:26
2020-09-17 13:27 | 44091.5605 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Interview room 2 |  | 1 | 14.5 | 74.7 | 397 | 22.9 | 46.2 | 496 |  | 2020-09-17 13:27 | 44091.5605 | 22.9 | 46.2 | 496 |  |  | 2020-09-14 | B20494¦Interview room 2¦¦Sep-17-2020 13:27
2020-09-17 13:28 | 44091.5612 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Crown staff office |  | 2 | 18 | 50 | 404 | 22 | 46 | 571 |  | 2020-09-17 13:28 | 44091.5612 | 22 | 46 | 571 |  |  | 2020-09-14 | B70235¦Crown staff office ¦¦Sep-17-2020 13:28
2020-09-17 13:28 | 44091.5613 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Between second floor washrooms |  | 1 | 18.6 | 70.9 | 418 | 22.5 | 51.3 | 427 |  | 2020-09-17 13:28 | 44091.5613 | 22.5 | 51.3 | 427 |  |  | 2020-09-14 | B20390¦Between second floor washrooms¦¦Sep-17-2020 13:28
2020-09-17 13:28 | 44091.5613 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Courtroom 1 |  | 0 | 17.7 | 46.2 | 435 | 22.3 | 40.9 | 476 |  | 2020-09-17 13:28 | 44091.5613 | 22.3 | 40.9 | 476 |  |  | 2020-09-14 | B19890¦Courtroom 1¦¦Sep-17-2020 13:28
2020-09-17 13:29 | 44091.5617 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom d |  | 0 | 20.3 | 46.1 | 420 | 21 | 44.5 | 400 |  | 2020-09-17 13:29 | 44091.5617 | 21 | 44.5 | 400 |  |  | 2020-09-14 | Pearso¦Ballroom d ¦¦Sep-17-2020 13:28
2020-09-17 13:29 | 44091.562 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Interview room 1 |  | 1 | 14.5 | 74.7 | 397 | 22.7 | 46.3 | 502 |  | 2020-09-17 13:29 | 44091.562 | 22.7 | 46.3 | 502 |  |  | 2020-09-14 | B20494¦Interview room 1¦¦Sep-17-2020 13:29
2020-09-17 13:30 | 44091.5622 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Stairwells |  | 0 | 17.7 | 46.2 | 435 | 22.2 | 45.8 | 561 |  | 2020-09-17 13:30 | 44091.5622 | 22.2 | 45.8 | 561 |  |  | 2020-09-14 | B19890¦Stairwells ¦¦Sep-17-2020 13:29
2020-09-17 13:30 | 44091.5622 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Peterborough Police |  | 3 | 18 | 50 | 404 | 22 | 45 | 599 |  | 2020-09-17 13:30 | 44091.5622 | 22 | 45 | 599 |  |  | 2020-09-14 | B70235¦Peterborough Police ¦¦Sep-17-2020 13:29
2020-09-17 13:30 | 44091.5625 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | in front of second floor elevator |  | 1 | 18.6 | 70.9 | 418 | 22.8 | 48.6 | 429 |  | 2020-09-17 13:30 | 44091.5625 | 22.8 | 48.6 | 429 |  |  | 2020-09-14 | B20390¦in front of second floor elevator¦¦Sep-17-2020 13:30
2020-09-17 13:30 | 44091.5627 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom d 1 |  | 0 | 20.3 | 46.1 | 420 | 21.2 | 44.4 | 399 |  | 2020-09-17 13:30 | 44091.5627 | 21.2 | 44.4 | 399 |  |  | 2020-09-14 | Pearso¦Ballroom d 1¦¦Sep-17-2020 13:30
2020-09-17 13:30 | 44091.5628 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Main hallway |  | 0 | 17.7 | 46.2 | 435 | 22.4 | 46.8 | 589 |  | 2020-09-17 13:30 | 44091.5628 | 22.4 | 46.8 | 589 |  |  | 2020-09-14 | B19890¦Main hallway ¦¦Sep-17-2020 13:30
2020-09-17 13:31 | 44091.5629 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Main entry |  | 3 | 14.5 | 74.7 | 397 | 22.8 | 47.9 | 512 |  | 2020-09-17 13:31 | 44091.5629 | 22.8 | 47.9 | 512 |  |  | 2020-09-14 | B20494¦Main entry¦¦Sep-17-2020 13:30
2020-09-17 13:31 | 44091.5633 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Crown attorneys waiting area |  | 1 | 18.6 | 70.9 | 418 | 22.8 | 48 | 415 |  | 2020-09-17 13:31 | 44091.5633 | 22.8 | 48 | 415 |  |  | 2020-09-14 | B20390¦Crown attorneys waiting area¦¦Sep-17-2020 13:31
2020-09-17 13:31 | 44091.5634 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #1 |  | 2 | 21.2 | 34.1 | 399 | 21.5 | 39 | 468 |  | 2020-09-17 13:31 | 44091.5634 | 21.5 | 39 | 468 |  | caution | 2020-09-14 | B20474¦Courtroom #1¦¦Sep-17-2020 13:31
2020-09-17 13:31 | 44091.5635 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom d 2 |  | 0 | 20.3 | 46.1 | 420 | 21 | 43.9 | 398 |  | 2020-09-17 13:31 | 44091.5635 | 21 | 43.9 | 398 |  |  | 2020-09-14 | Pearso¦Ballroom d 2¦¦Sep-17-2020 13:31
2020-09-17 13:32 | 44091.5637 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview room 4 |  | 0 | 18 | 50 | 404 | 22 | 44 | 544 |  | 2020-09-17 13:32 | 44091.5637 | 22 | 44 | 544 |  |  | 2020-09-14 | B70235¦Interview room 4 ¦¦Sep-17-2020 13:31
2020-09-17 13:32 | 44091.5641 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Crown attorneys reception area |  | 1 | 18.6 | 70.9 | 418 | 22.5 | 49.5 | 414 |  | 2020-09-17 13:32 | 44091.5641 | 22.5 | 49.5 | 414 |  |  | 2020-09-14 | B20390¦Crown attorneys reception area¦¦Sep-17-2020 13:32
2020-09-17 13:32 | 44091.5642 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom d 3 |  | 0 | 20.3 | 46.1 | 420 | 21.2 | 44 | 398 |  | 2020-09-17 13:32 | 44091.5642 | 21.2 | 44 | 398 |  |  | 2020-09-14 | Pearso¦Ballroom d 3 ¦¦Sep-17-2020 13:32
2020-09-17 13:33 | 44091.5645 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Criminal justice office |  | 3 | 14.5 | 74.7 | 397 | 22.9 | 45.3 | 533 |  | 2020-09-17 13:33 | 44091.5645 | 22.9 | 45.3 | 533 |  |  | 2020-09-14 | B20494¦Criminal justice office¦¦Sep-17-2020 13:32
2020-09-17 13:33 | 44091.5648 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 vestibule |  | 0 | 18 | 50 | 404 | 23 | 44 | 525 |  | 2020-09-17 13:33 | 44091.5648 | 23 | 44 | 525 |  |  | 2020-09-14 | B70235¦Court #4 vestibule ¦¦Sep-17-2020 13:33
2020-09-17 13:34 | 44091.5653 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 5 |  | 1 | 18.6 | 70.9 | 418 | 22.6 | 48.5 | 418 |  | 2020-09-17 13:34 | 44091.5653 | 22.6 | 48.5 | 418 |  |  | 2020-09-14 | B20390¦Outside courtroom 5¦¦Sep-17-2020 13:34
2020-09-17 13:34 | 44091.5655 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 2nd floor SE hall |  | 1 | 14.5 | 74.7 | 397 | 22.7 | 45.4 | 545 |  | 2020-09-17 13:34 | 44091.5655 | 22.7 | 45.4 | 545 |  |  | 2020-09-14 | B20494¦2nd floor SE hall¦¦Sep-17-2020 13:34
2020-09-17 13:35 | 44091.566 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 306 |  | 0 | 14 | 54 | 374 | 22.8 | 43.9 | 429 | No | 2020-09-17 13:35 | 44091.566 | 22.8 | 43.9 | 429 |  |  | 2020-09-14 | B14660¦306¦¦Sep-17-2020 13:35
2020-09-17 13:35 | 44091.5661 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 vestibule |  | 0 | 18 | 50 | 404 | 22 | 45 | 460 |  | 2020-09-17 13:35 | 44091.5661 | 22 | 45 | 460 |  |  | 2020-09-14 | B70235¦Court #3 vestibule ¦¦Sep-17-2020 13:35
2020-09-17 13:36 | 44091.5664 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 4 |  | 1 | 18.6 | 70.9 | 418 | 22.3 | 49.1 | 418 |  | 2020-09-17 13:36 | 44091.5664 | 22.3 | 49.1 | 418 |  |  | 2020-09-14 | B20390¦Outside courtroom 4¦¦Sep-17-2020 13:35
2020-09-17 13:36 | 44091.5667 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom #2 |  | 2 | 21.2 | 34.1 | 399 | 20.7 | 33.5 | 450 |  | 2020-09-17 13:36 | 44091.5667 | 20.7 | 33.5 | 450 |  | low | 2020-09-14 | B21554¦Courtroom #2¦¦Sep-17-2020 13:36
2020-09-17 13:37 | 44091.5671 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview Room 2 |  | 0 | 18 | 50 | 404 | 23 | 44 | 548 |  | 2020-09-17 13:37 | 44091.5671 | 23 | 44 | 548 |  |  | 2020-09-14 | B70235¦Interview Room 2 ¦¦Sep-17-2020 13:36
2020-09-17 13:37 | 44091.5673 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Interview room 6 |  | 1 | 18.6 | 70.9 | 418 | 22.2 | 49.5 | 416 |  | 2020-09-17 13:37 | 44091.5673 | 22.2 | 49.5 | 416 |  |  | 2020-09-14 | B20390¦Interview room 6¦¦Sep-17-2020 13:36
2020-09-17 13:37 | 44091.5674 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 2 |  | 2 | 14.5 | 74.7 | 397 | 22.4 | 45.6 | 449 |  | 2020-09-17 13:37 | 44091.5674 | 22.4 | 45.6 | 449 |  |  | 2020-09-14 | B20494¦Courtroom 2¦¦Sep-17-2020 13:37
2020-09-17 13:37 | 44091.5675 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom e |  | 0 | 20.3 | 46.1 | 420 | 20.8 | 46.2 | 398 |  | 2020-09-17 13:37 | 44091.5675 | 20.8 | 46.2 | 398 |  |  | 2020-09-14 | Pearso¦Ballroom e¦¦Sep-17-2020 13:37
2020-09-17 13:38 | 44091.5679 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 vestibule |  | 0 | 18 | 50 | 404 | 23 | 42 | 504 |  | 2020-09-17 13:38 | 44091.5679 | 23 | 42 | 504 |  |  | 2020-09-14 | B70235¦Court #2 vestibule ¦¦Sep-17-2020 13:37
2020-09-17 13:38 | 44091.568 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom #3 |  | 4 | 21.2 | 34.1 | 399 | 21.4 | 42.5 | 623 |  | 2020-09-17 13:38 | 44091.568 | 21.4 | 42.5 | 623 |  |  | 2020-09-14 | B21554¦Courtroom #3¦¦Sep-17-2020 13:37
2020-09-17 13:38 | 44091.5681 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom e 1 |  | 0 | 20.3 | 46.1 | 420 | 21 | 46 | 397 |  | 2020-09-17 13:38 | 44091.5681 | 21 | 46 | 397 |  |  | 2020-09-14 | Pearso¦Ballroom e 1 ¦¦Sep-17-2020 13:38
2020-09-17 13:38 | 44091.5682 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom D |  | 0 | 18.6 | 45.2 | 404 | 21.2 | 53.5 | 476 | No access to Courtroom C due to trial proceedings | 2020-09-17 13:38 | 44091.5682 | 21.2 | 53.5 | 476 |  |  | 2020-09-14 | B20478¦Courtroom D¦¦Sep-17-2020 13:38
2020-09-17 13:38 | 44091.5683 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Interview room 8 |  | 1 | 18.6 | 70.9 | 418 | 22.1 | 49.5 | 416 |  | 2020-09-17 13:38 | 44091.5683 | 22.1 | 49.5 | 416 |  |  | 2020-09-14 | B20390¦Interview room 8¦¦Sep-17-2020 13:38
2020-09-17 13:39 | 44091.5686 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom e2 |  | 0 | 20.3 | 46.1 | 420 | 20.7 | 47 | 398 |  | 2020-09-17 13:39 | 44091.5686 | 20.7 | 47 | 398 |  |  | 2020-09-14 | Pearso¦Ballroom e2 ¦¦Sep-17-2020 13:38
2020-09-17 13:39 | 44091.5691 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 2nd floor NE hall |  | 2 | 14.5 | 74.7 | 397 | 22.5 | 48.8 | 537 |  | 2020-09-17 13:39 | 44091.5691 | 22.5 | 48.8 | 537 |  |  | 2020-09-14 | B20494¦2nd floor NE hall ¦¦Sep-17-2020 13:39
2020-09-17 13:39 | 44091.5691 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 128 |  | 0 | 25 | 24 | 370 | 23.7 | 35.6 | 392 | No | 2020-09-17 13:39 | 44091.5691 | 23.7 | 35.6 | 392 |  | caution | 2020-09-14 | B14660¦128¦¦Sep-17-2020 13:39
2020-09-17 13:39 | 44091.5691 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Duty Counsel room |  | 0 | 18 | 50 | 404 | 23 | 42 | 534 |  | 2020-09-17 13:39 | 44091.5691 | 23 | 42 | 534 |  |  | 2020-09-14 | B70235¦Duty Counsel room ¦¦Sep-17-2020 13:39
2020-09-17 13:40 | 44091.5694 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom B |  | 0 | 18.6 | 45.2 | 404 | 21.5 | 53.6 | 493 | No access to Courtroom C due to trial proceedings | 2020-09-17 13:40 | 44091.5694 | 21.5 | 53.6 | 493 |  |  | 2020-09-14 | B20478¦Courtroom B¦¦Sep-17-2020 13:39
2020-09-17 13:40 | 44091.5698 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Waiting area outside courtroom3 |  | 1 | 21.2 | 34.1 | 399 | 21.7 | 36.2 | 548 |  | 2020-09-17 13:40 | 44091.5698 | 21.7 | 36.2 | 548 |  | caution | 2020-09-14 | B21554¦Waiting area outside courtroom3¦¦Sep-17-2020 13:40
2020-09-17 13:41 | 44091.5702 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom e 3 |  | 0 | 20.3 | 46.1 | 420 | 20.6 | 47.3 | 398 |  | 2020-09-17 13:41 | 44091.5702 | 20.6 | 47.3 | 398 |  |  | 2020-09-14 | Pearso¦Ballroom e 3 ¦¦Sep-17-2020 13:41
2020-09-17 13:42 | 44091.5705 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom A |  | 0 | 18.6 | 45.2 | 404 | 23.3 | 49.4 | 514 | No access to Courtroom C due to trial proceedings | 2020-09-17 13:42 | 44091.5705 | 23.3 | 49.4 | 514 |  |  | 2020-09-14 | B20478¦Courtroom A¦¦Sep-17-2020 13:41
2020-09-17 13:42 | 44091.5706 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell, third floor |  | 1 | 18.6 | 70.9 | 418 | 23.8 | 47.6 | 422 |  | 2020-09-17 13:42 | 44091.5706 | 23.8 | 47.6 | 422 |  |  | 2020-09-14 | B20390¦Main stairwell, third floor¦¦Sep-17-2020 13:41
2020-09-17 13:42 | 44091.5707 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 11 |  | 2 | 19 | 57 | 420 | 21.6 | 50 | 430 |  | 2020-09-17 13:42 | 44091.5707 | 21.6 | 50 | 430 |  |  | 2020-09-14 | B70740¦11¦¦Sep-17-2020 13:41
2020-09-17 13:42 | 44091.5709 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 001 |  | 0 | 25 | 24 | 370 | 21.8 | 37.6 | 400 | No | 2020-09-17 13:42 | 44091.5709 | 21.8 | 37.6 | 400 |  | caution | 2020-09-14 | B14660¦001¦¦Sep-17-2020 13:42
2020-09-17 13:43 | 44091.5712 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 vestibule |  | 0 | 18 | 50 | 404 | 23 | 43 | 650 |  | 2020-09-17 13:43 | 44091.5712 | 23 | 43 | 650 |  |  | 2020-09-14 | B70235¦Court #1 vestibule ¦¦Sep-17-2020 13:42
2020-09-17 13:43 | 44091.5712 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Third floor waiting area |  | 1 | 18.6 | 70.9 | 418 | 23.6 | 46.4 | 421 |  | 2020-09-17 13:43 | 44091.5712 | 23.6 | 46.4 | 421 |  |  | 2020-09-14 | B20390¦Third floor waiting area¦¦Sep-17-2020 13:42
2020-09-17 13:43 | 44091.5713 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE STAFF ROOM |  | 1 | 17 | 54 | 502 | 21 | 49 | 502 |  | 2020-09-17 13:43 | 44091.5713 | 21 | 49 | 502 |  |  | 2020-09-14 | B20022¦JUDGE STAFF ROOM¦¦Sep-17-2020 13:42
2020-09-17 13:43 | 44091.5714 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Basement corridor at washrooms |  | 1 | 21.2 | 34.1 | 399 | 21.7 | 37 | 533 |  | 2020-09-17 13:43 | 44091.5714 | 21.7 | 37 | 533 |  | caution | 2020-09-14 | B21554¦Basement corridor at washrooms¦¦Sep-17-2020 13:42
2020-09-17 13:43 | 44091.5718 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom f |  | 0 | 20.3 | 46.1 | 420 | 20.8 | 48.5 | 395 |  | 2020-09-17 13:43 | 44091.5718 | 20.8 | 48.5 | 395 |  |  | 2020-09-14 | Pearso¦Ballroom f ¦¦Sep-17-2020 13:43
2020-09-17 13:43 | 44091.5718 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE CORKERY |  | 1 | 17 | 54 | 502 | 21.8 | 49 | 457 |  | 2020-09-17 13:43 | 44091.5718 | 21.8 | 49 | 457 |  |  | 2020-09-14 | B20022¦JUDGE CORKERY¦¦Sep-17-2020 13:43
2020-09-17 13:44 | 44091.5719 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Common area beside Courtroom A |  | 0 | 18.6 | 45.2 | 404 | 24.1 | 47.4 | 491 | No access to Courtroom C due to trial proceedings | 2020-09-17 13:44 | 44091.5719 | 24.1 | 47.4 | 491 |  |  | 2020-09-14 | B20478¦Common area beside Courtroom A¦¦Sep-17-2020 13:43
2020-09-17 13:44 | 44091.5721 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 1 |  | 1 | 18.6 | 70.9 | 418 | 22.7 | 47.8 | 420 |  | 2020-09-17 13:44 | 44091.5721 | 22.7 | 47.8 | 420 |  |  | 2020-09-14 | B20390¦Outside courtroom 1 ¦¦Sep-17-2020 13:43
2020-09-17 13:44 | 44091.5723 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | VISITING JUDGE |  | 1 | 17 | 54 | 502 | 21.9 | 51.9 | 459 |  | 2020-09-17 13:44 | 44091.5723 | 21.9 | 51.9 | 459 |  |  | 2020-09-14 | B20022¦VISITING JUDGE¦¦Sep-17-2020 13:44
2020-09-17 13:45 | 44091.5727 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main lobby |  | 5 | 18 | 50 | 404 | 23 | 42 | 550 |  | 2020-09-17 13:45 | 44091.5727 | 23 | 42 | 550 |  |  | 2020-09-14 | B70235¦Main lobby ¦¦Sep-17-2020 13:44
2020-09-17 13:45 | 44091.5728 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Law library |  | 0 | 18.6 | 45.2 | 404 | 24.2 | 49.4 | 491 | No access to Courtroom C due to trial proceedings | 2020-09-17 13:45 | 44091.5728 | 24.2 | 49.4 | 491 |  |  | 2020-09-14 | B20478¦Law library ¦¦Sep-17-2020 13:44
2020-09-17 13:45 | 44091.5729 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | VISITING JUDGE |  | 1 | 17 | 54 | 502 | 21.9 | 51.9 | 459 |  | 2020-09-17 13:45 | 44091.5729 | 21.9 | 51.9 | 459 |  |  | 2020-09-14 | B20022¦VISITING JUDGE¦¦Sep-17-2020 13:45
2020-09-17 13:45 | 44091.573 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside third floor elevator |  | 1 | 18.6 | 70.9 | 418 | 22.2 | 50.2 | 433 |  | 2020-09-17 13:45 | 44091.573 | 22.2 | 50.2 | 433 |  |  | 2020-09-14 | B20390¦Outside third floor elevator¦¦Sep-17-2020 13:45
2020-09-17 13:45 | 44091.573 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Basement corridor at exit door |  | 1 | 21.2 | 34.1 | 399 | 22 | 37 | 510 |  | 2020-09-17 13:45 | 44091.573 | 22 | 37 | 510 |  | caution | 2020-09-14 | B21554¦Basement corridor at exit door¦¦Sep-17-2020 13:45
2020-09-17 13:45 | 44091.573 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 028 |  | 0 | 25 | 24 | 370 | 22.5 | 37.6 | 424 | No | 2020-09-17 13:45 | 44091.573 | 22.5 | 37.6 | 424 |  | caution | 2020-09-14 | B14660¦028¦¦Sep-17-2020 13:45
2020-09-17 13:46 | 44091.5736 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE INGRAM |  | 1 | 17 | 54 | 502 | 21.8 | 51 | 463 |  | 2020-09-17 13:46 | 44091.5736 | 21.8 | 51 | 463 |  |  | 2020-09-14 | B20022¦JUDGE INGRAM¦¦Sep-17-2020 13:46
2020-09-17 13:46 | 44091.5737 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Front Lobby |  | 2 | 21.8 | 43.8 | 390 | 23.3 | 39.6 | 434 |  | 2020-09-17 13:46 | 44091.5737 | 23.3 | 39.6 | 434 |  | caution | 2020-09-14 | B20550¦Front Lobby¦¦Sep-17-2020 13:46
2020-09-17 13:47 | 44091.574 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | East Stairwell |  | 0 | 18.6 | 45.2 | 404 | 24.5 | 41.6 | 531 | No access to Courtroom C due to trial proceedings | 2020-09-17 13:47 | 44091.574 | 24.5 | 41.6 | 531 |  |  | 2020-09-14 | B20478¦East Stairwell ¦¦Sep-17-2020 13:46
2020-09-17 13:47 | 44091.5742 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 019 |  | 0 | 25 | 24 | 370 | 22.8 | 38.4 | 412 | No | 2020-09-17 13:47 | 44091.5742 | 22.8 | 38.4 | 412 |  | caution | 2020-09-14 | B14660¦019¦¦Sep-17-2020 13:46
2020-09-17 13:47 | 44091.5742 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE INGRAM |  | 2 | 17 | 54 | 502 | 21.8 | 51 | 463 |  | 2020-09-17 13:47 | 44091.5742 | 21.8 | 51 | 463 |  |  | 2020-09-14 | B20022¦JUDGE INGRAM¦¦Sep-17-2020 13:46
2020-09-17 13:47 | 44091.5743 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Strairway landing |  | 1 | 21.2 | 34.1 | 399 | 22.2 | 39.6 | 493 |  | 2020-09-17 13:47 | 44091.5743 | 22.2 | 39.6 | 493 |  | caution | 2020-09-14 | B21554¦Strairway landing¦¦Sep-17-2020 13:47
2020-09-17 13:48 | 44091.5747 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 019 |  | 0 | 25 | 24 | 370 | 22.8 | 38.4 | 412 | No | 2020-09-17 13:48 | 44091.5747 | 22.8 | 38.4 | 412 |  | caution | 2020-09-14 | B14660¦019¦¦Sep-17-2020 13:47
2020-09-17 13:48 | 44091.5748 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Front lobby |  | 2 | 20.8 | 41 | 437 | 22.4 | 43.6 | 522 |  | 2020-09-17 13:48 | 44091.5748 | 22.4 | 43.6 | 522 |  |  | 2020-09-14 | B25477¦Front lobby¦¦Sep-17-2020 13:47
2020-09-17 13:48 | 44091.5749 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE MCLEOD |  | 1 | 17 | 54 | 502 | 21.6 | 54 | 469 |  | 2020-09-17 13:48 | 44091.5749 | 21.6 | 54 | 469 |  |  | 2020-09-14 | B20022¦JUDGE MCLEOD¦¦Sep-17-2020 13:47
2020-09-17 13:48 | 44091.5751 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Main floor common area |  | 3 | 18.6 | 45.2 | 404 | 23.5 | 44.3 | 532 | No access to Courtroom C due to trial proceedings | 2020-09-17 13:48 | 44091.5751 | 23.5 | 44.3 | 532 |  |  | 2020-09-14 | B20478¦Main floor common area ¦¦Sep-17-2020 13:48
2020-09-17 13:49 | 44091.5754 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Main waiting area |  | 1 | 21.2 | 34.1 | 399 | 22.1 | 36.1 | 483 |  | 2020-09-17 13:49 | 44091.5754 | 22.1 | 36.1 | 483 |  | caution | 2020-09-14 | B21554¦Main waiting area¦¦Sep-17-2020 13:48
2020-09-17 13:49 | 44091.5755 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 JUDGE |  | 2 | 17 | 54 | 502 | 21.7 | 49 | 482 |  | 2020-09-17 13:49 | 44091.5755 | 21.7 | 49 | 482 |  |  | 2020-09-14 | B20022¦COURT 3 JUDGE¦¦Sep-17-2020 13:48
2020-09-17 13:49 | 44091.5755 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | HR |  | 4 | 20.8 | 41 | 437 | 22.4 | 44.5 | 555 |  | 2020-09-17 13:49 | 44091.5755 | 22.4 | 44.5 | 555 |  |  | 2020-09-14 | B25477¦HR¦¦Sep-17-2020 13:48
2020-09-17 13:49 | 44091.5759 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Courtroom#1 |  | 1 | 21.8 | 43.8 | 490 | 24.3 | 37.8 | 422 |  | 2020-09-17 13:49 | 44091.5759 | 24.3 | 37.8 | 422 |  | caution | 2020-09-14 | B20550¦Courtroom#1¦¦Sep-17-2020 13:49
2020-09-17 13:50 | 44091.5761 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | ED office |  | 2 | 20.8 | 41 | 437 | 22.4 | 43 | 516 |  | 2020-09-17 13:50 | 44091.5761 | 22.4 | 43 | 516 |  |  | 2020-09-14 | B25477¦ED office ¦¦Sep-17-2020 13:49
2020-09-17 13:50 | 44091.5762 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 011 |  | 0 | 25 | 24 | 370 | 22.9 | 37.5 | 418 | No | 2020-09-17 13:50 | 44091.5762 | 22.9 | 37.5 | 418 |  | caution | 2020-09-14 | B14660¦011¦¦Sep-17-2020 13:49
2020-09-17 13:50 | 44091.5762 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 LAWYER |  | 2 | 17 | 54 | 502 | 21.3 | 49 | 467 |  | 2020-09-17 13:50 | 44091.5762 | 21.3 | 49 | 467 |  |  | 2020-09-14 | B20022¦COURT 3 LAWYER¦¦Sep-17-2020 13:49
2020-09-17 13:50 | 44091.5762 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Corridor outside Admin office |  | 0 | 18.6 | 45.2 | 404 | 24.1 | 43.6 | 514 | No access to Courtroom C due to trial proceedings | 2020-09-17 13:50 | 44091.5762 | 24.1 | 43.6 | 514 |  |  | 2020-09-14 | B20478¦Corridor outside Admin office ¦¦Sep-17-2020 13:49
2020-09-17 13:50 | 44091.5764 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Crown attorneys office |  | 2 | 21.4 | 42.5 | 404 | 23.1 | 43.7 | 462 | No | 2020-09-17 13:50 | 44091.5764 | 23.1 | 43.7 | 462 |  |  | 2020-09-14 | B21128¦Crown attorneys office ¦¦Sep-17-2020 13:50
2020-09-17 13:50 | 44091.5765 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jason Mariasine office |  | 1 | 18 | 50 | 404 |  |  |  | Occupied, no access | 2020-09-17 13:50 | 44091.5765 | [5 empty] | 2020-09-14 | B70235¦Jason Mariasine office ¦¦Sep-17-2020 13:50
2020-09-17 13:51 | 44091.5767 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | ADVICE COUNSEL |  | 2 | 17 | 54 | 502 | 20.6 | 45 | 448 |  | 2020-09-17 13:50 | 44091.5767 | 20.6 | 45 | 448 |  |  | 2020-09-14 | B20022¦ADVICE COUNSEL¦¦Sep-17-2020 13:50
2020-09-17 13:51 | 44091.5768 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Legal aid office corridor |  | 1 | 21.2 | 34.1 | 399 | 21.8 | 39.5 | 483 |  | 2020-09-17 13:51 | 44091.5768 | 21.8 | 39.5 | 483 |  | caution | 2020-09-14 | B21554¦Legal aid office corridor¦¦Sep-17-2020 13:50
2020-09-17 13:51 | 44091.577 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Admim office |  | 2 | 20.8 | 41 | 437 | 22.5 | 44.5 | 523 |  | 2020-09-17 13:51 | 44091.577 | 22.5 | 44.5 | 523 |  |  | 2020-09-14 | B25477¦Admim office ¦¦Sep-17-2020 13:50
2020-09-17 13:51 | 44091.577 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jennifer Broderick office |  | 1 | 18 | 60 | 404 |  |  |  |  | 2020-09-17 13:51 | 44091.577 | [5 empty] | 2020-09-14 | B70235¦Jennifer Broderick office ¦¦Sep-17-2020 13:50
2020-09-17 13:51 | 44091.5771 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area part b |  | 1 | 26 | 37 | 365 | 23 | 42 | 372 |  | 2020-09-17 13:51 | 44091.5771 | 23 | 42 | 372 |  |  | 2020-09-14 | B20772¦Courtroom waiting area part b ¦¦Sep-17-2020 13:51
2020-09-17 13:51 | 44091.5772 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | 2nd floor common area |  | 0 | 18.6 | 45.2 | 404 | 23.5 | 45.8 | 570 | No access to Courtroom C due to trial proceedings | 2020-09-17 13:51 | 44091.5772 | 23.5 | 45.8 | 570 |  |  | 2020-09-14 | B20478¦2nd floor common area ¦¦Sep-17-2020 13:51
2020-09-17 13:51 | 44091.5773 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Courtroom#2 |  | 0 | 21.8 | 43.8 | 390 | 24.5 | 36.3 | 412 |  | 2020-09-17 13:51 | 44091.5773 | 24.5 | 36.3 | 412 |  | caution | 2020-09-14 | B20550¦Courtroom#2¦¦Sep-17-2020 13:51
2020-09-17 13:51 | 44091.5773 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Kitchen |  | 1 | 19 | 53 | 381 | 21 | 52 | 419 |  | 2020-09-17 13:51 | 44091.5773 | 21 | 52 | 419 |  |  | 2020-09-14 | B20603¦Kitchen¦¦Sep-17-2020 13:51
2020-09-17 13:51 | 44091.5774 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 WAITING AREA |  | 2 | 17 | 54 | 502 | 20 | 48.6 | 440 |  | 2020-09-17 13:51 | 44091.5774 | 20 | 48.6 | 440 |  |  | 2020-09-14 | B20022¦COURT 3 WAITING AREA¦¦Sep-17-2020 13:51
2020-09-17 13:52 | 44091.5777 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 118 |  | 0 | 25 | 24 | 370 | 22.8 | 37.9 | 405 | No | 2020-09-17 13:52 | 44091.5777 | 22.8 | 37.9 | 405 |  | caution | 2020-09-14 | B14660¦118¦¦Sep-17-2020 13:51
2020-09-17 13:52 | 44091.5779 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Financial services |  | 4 | 20.8 | 44.2 | 530 | 22.4 | 44.4 | 530 |  | 2020-09-17 13:52 | 44091.5779 | 22.4 | 44.4 | 530 |  |  | 2020-09-14 | B25477¦Financial services ¦¦Sep-17-2020 13:52
2020-09-17 13:52 | 44091.5779 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT OFFICE LOBBY |  | 2 | 17 | 54 | 502 | 21 | 52 | 574 |  | 2020-09-17 13:52 | 44091.5779 | 21 | 52 | 574 |  |  | 2020-09-14 | B20022¦COURT OFFICE LOBBY¦¦Sep-17-2020 13:52
2020-09-17 13:52 | 44091.578 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 judge |  | 1 | 18 | 60 | 404 |  |  |  | Occupied, no access | 2020-09-17 13:52 | 44091.578 | [5 empty] | 2020-09-14 | B70235¦Court #4 judge ¦¦Sep-17-2020 13:52
2020-09-17 13:53 | 44091.5782 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | 2nd floor Crown Attorney corridor |  | 0 | 18.6 | 45.2 | 404 | 23.3 | 46.1 | 460 | No access to Courtroom C due to trial proceedings | 2020-09-17 13:53 | 44091.5782 | 23.3 | 46.1 | 460 |  |  | 2020-09-14 | B20478¦2nd floor Crown Attorney corridor ¦¦Sep-17-2020 13:52
2020-09-17 13:53 | 44091.5785 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT OFFICE |  | 2 | 17 | 54 | 502 | 21.8 | 52 | 684 |  | 2020-09-17 13:53 | 44091.5785 | 21.8 | 52 | 684 |  |  | 2020-09-14 | B20022¦COURT OFFICE¦¦Sep-17-2020 13:52
2020-09-17 13:53 | 44091.5785 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Waiting area small |  | 0 | 21.8 | 43.8 | 390 | 24.8 | 34.6 | 403 |  | 2020-09-17 13:53 | 44091.5785 | 24.8 | 34.6 | 403 |  | low | 2020-09-14 | B20550¦Waiting area small¦¦Sep-17-2020 13:53
2020-09-17 13:53 | 44091.5786 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 lawyer |  | 1 | 18 | 50 | 404 |  |  |  | Occupied, no access | 2020-09-17 13:53 | 44091.5786 | [5 empty] | 2020-09-14 | B70235¦Court #4 lawyer ¦¦Sep-17-2020 13:53
2020-09-17 13:53 | 44091.5787 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Front entrance hall way |  | 7 | 21.1 | 45.6 | 426 | 22.8 | 44.4 | 464 | No | 2020-09-17 13:53 | 44091.5787 | 22.8 | 44.4 | 464 |  |  | 2020-09-14 | B21128¦Front entrance hall way¦¦Sep-17-2020 13:53
2020-09-17 13:54 | 44091.5789 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Mailroom |  | 1 | 19 | 53 | 381 | 21 | 50 | 424 |  | 2020-09-17 13:54 | 44091.5789 | 21 | 50 | 424 |  |  | 2020-09-14 | B20603¦Mailroom¦¦Sep-17-2020 13:53
2020-09-17 13:54 | 44091.5789 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 115 |  | 0 | 25 | 24 | 370 | 23 | 35.4 | 412 | No | 2020-09-17 13:54 | 44091.5789 | 23 | 35.4 | 412 |  | caution | 2020-09-14 | B14660¦115¦¦Sep-17-2020 13:53
2020-09-17 13:54 | 44091.5789 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Courtroom |  | 4 | 20.8 | 41 | 437 | 22.3 | 43.8 | 477 |  | 2020-09-17 13:54 | 44091.5789 | 22.3 | 43.8 | 477 |  |  | 2020-09-14 | B25477¦Courtroom ¦¦Sep-17-2020 13:53
2020-09-17 13:54 | 44091.579 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Main office |  | 3 | 21.2 | 34.1 | 399 | 23.6 | 44.5 | 803 |  | 2020-09-17 13:54 | 44091.579 | 23.6 | 44.5 | 803 |  |  | 2020-09-14 | B21554¦Main office¦¦Sep-17-2020 13:53
2020-09-17 13:54 | 44091.5791 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 judge |  | 1 | 18 | 50 | 404 |  |  |  | Occupied, no access | 2020-09-17 13:54 | 44091.5791 | [5 empty] | 2020-09-14 | B70235¦Court #3 judge ¦¦Sep-17-2020 13:53
2020-09-17 13:54 | 44091.5791 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | MEDIATION ROOM |  | 1 | 17 | 54 | 502 | 21.8 | 48 | 586 |  | 2020-09-17 13:54 | 44091.5791 | 21.8 | 48 | 586 |  |  | 2020-09-14 | B20022¦MEDIATION ROOM¦¦Sep-17-2020 13:53
2020-09-17 13:55 | 44091.5796 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | OFFICER ROOM |  | 2 | 17 | 54 | 502 | 21.6 | 57 | 650 |  | 2020-09-17 13:55 | 44091.5796 | 21.6 | 57 | 650 |  |  | 2020-09-14 | B20022¦OFFICER ROOM¦¦Sep-17-2020 13:54
2020-09-17 13:55 | 44091.5796 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Mezzanine |  | 1 | 20.8 | 41 | 437 | 22.2 | 43.8 | 556 |  | 2020-09-17 13:55 | 44091.5796 | 22.2 | 43.8 | 556 |  |  | 2020-09-14 | B25477¦Mezzanine ¦¦Sep-17-2020 13:54
2020-09-17 13:55 | 44091.5797 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 lawyer |  | 1 | 18 | 50 | 404 |  |  |  | Occupied, no access | 2020-09-17 13:55 | 44091.5797 | [5 empty] | 2020-09-14 | B70235¦Court #3 lawyer ¦¦Sep-17-2020 13:54
2020-09-17 13:55 | 44091.5797 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 403 |  | 2 | 21.1 | 45.6 | 426 | 23.3 | 42.9 | 552 | No | 2020-09-17 13:55 | 44091.5797 | 23.3 | 42.9 | 552 |  |  | 2020-09-14 | B21128¦403¦¦Sep-17-2020 13:54
2020-09-17 13:55 | 44091.5798 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Basement witness protection corridor |  | 0 | 18.6 | 45.2 | 404 | 22.5 | 51 | 506 | No access to Courtroom C due to trial proceedings | 2020-09-17 13:55 | 44091.5798 | 22.5 | 51 | 506 |  |  | 2020-09-14 | B20478¦Basement witness protection corridor ¦¦Sep-17-2020 13:54
2020-09-17 13:55 | 44091.5801 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Waiting area big |  | 0 | 21.8 | 43.8 | 390 | 24.4 | 36.3 | 406 |  | 2020-09-17 13:55 | 44091.5801 | 24.4 | 36.3 | 406 |  | caution | 2020-09-14 | B20550¦Waiting area big¦¦Sep-17-2020 13:55
2020-09-17 13:55 | 44091.5802 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | 1st Floor - Front Lobby |  | 3 | 20.7 | 33.8 | 383 | 22.6 | 39.9 | 590 |  | 2020-09-17 13:55 | 44091.5802 | 22.6 | 39.9 | 590 |  | caution | 2020-09-14 | B70277¦1st Floor - Front Lobby¦¦Sep-17-2020 13:55
2020-09-17 13:55 | 44091.5802 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 1 FLOOR LOBBY |  | 5 | 17 | 54 | 502 | 21.4 | 51.2 | 568 |  | 2020-09-17 13:55 | 44091.5802 | 21.4 | 51.2 | 568 |  |  | 2020-09-14 | B20022¦1 FLOOR LOBBY¦¦Sep-17-2020 13:55
2020-09-17 13:56 | 44091.5803 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Board room |  | 0 | 20.8 | 41 | 437 | 22.4 | 43 | 473 |  | 2020-09-17 13:56 | 44091.5803 | 22.4 | 43 | 473 |  |  | 2020-09-14 | B25477¦Board room¦¦Sep-17-2020 13:55
2020-09-17 13:56 | 44091.5805 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 judge |  | 1 | 18 | 50 | 404 |  |  |  | Occupied, no access | 2020-09-17 13:56 | 44091.5805 | [5 empty] | 2020-09-14 | B70235¦Court #2 judge ¦¦Sep-17-2020 13:55
2020-09-17 13:56 | 44091.5807 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Mediation room c |  | 0 | 19 | 53 | 381 | 22 | 49 | 404 |  | 2020-09-17 13:56 | 44091.5807 | 22 | 49 | 404 |  |  | 2020-09-14 | B20603¦Mediation room c¦¦Sep-17-2020 13:56
2020-09-17 13:56 | 44091.5809 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR LUNCH ROOM |  | 2 | 17 | 54 | 502 | 21.8 | 45.6 | 492 |  | 2020-09-17 13:56 | 44091.5809 | 21.8 | 45.6 | 492 |  |  | 2020-09-14 | B20022¦2 FLOOR LUNCH ROOM¦¦Sep-17-2020 13:56
2020-09-17 13:56 | 44091.5809 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 107 |  | 3 | 25 | 24 | 370 | 22.7 | 35.4 | 433 | No | 2020-09-17 13:56 | 44091.5809 | 22.7 | 35.4 | 433 |  | caution | 2020-09-14 | B14660¦107¦¦Sep-17-2020 13:56
2020-09-17 13:57 | 44091.5809 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Library |  | 1 | 20.8 | 41 | 437 | 22.8 | 43.9 | 464 |  | 2020-09-17 13:57 | 44091.5809 | 22.8 | 43.9 | 464 |  |  | 2020-09-14 | B25477¦Library ¦¦Sep-17-2020 13:56
2020-09-17 13:57 | 44091.581 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Basement corridor middle |  | 0 | 18.6 | 45.2 | 404 | 22.2 | 49.3 | 507 | No access to Courtroom C due to trial proceedings | 2020-09-17 13:57 | 44091.581 | 22.2 | 49.3 | 507 |  |  | 2020-09-14 | B20478¦Basement corridor middle ¦¦Sep-17-2020 13:56
2020-09-17 13:57 | 44091.581 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview Room 3 |  | 1 | 18 | 50 | 404 |  |  |  | Occupied, no access | 2020-09-17 13:57 | 44091.581 | [5 empty] | 2020-09-14 | B70235¦Interview Room 3 ¦¦Sep-17-2020 13:56
2020-09-17 13:57 | 44091.5811 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | N.W hallway entrance |  | 2 | 21.1 | 45.6 | 426 | 23.4 | 43.5 | 445 | No | 2020-09-17 13:57 | 44091.5811 | 23.4 | 43.5 | 445 |  |  | 2020-09-14 | B21128¦N.W hallway entrance ¦¦Sep-17-2020 13:56
2020-09-17 13:57 | 44091.5815 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 2 JUDGE |  | 2 | 17 | 54 | 502 | 21.5 | 46 | 465 |  | 2020-09-17 13:57 | 44091.5815 | 21.5 | 46 | 465 |  |  | 2020-09-14 | B20022¦COURT 2 JUDGE¦¦Sep-17-2020 13:57
2020-09-17 13:57 | 44091.5816 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Security desk |  | 0 | 21.8 | 43.8 | 390 | 24 | 37.6 | 416 |  | 2020-09-17 13:57 | 44091.5816 | 24 | 37.6 | 416 |  | caution | 2020-09-14 | B20550¦Security desk¦¦Sep-17-2020 13:57
2020-09-17 13:58 | 44091.5818 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 lawyer |  | 1 | 18 | 50 | 404 |  |  |  | Occupied, no access | 2020-09-17 13:58 | 44091.5818 | [5 empty] | 2020-09-14 | B70235¦Court #2 lawyer ¦¦Sep-17-2020 13:57
2020-09-17 13:58 | 44091.5818 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 113 |  | 0 | 25 | 24 | 370 | 22.2 | 37.4 | 411 | No | 2020-09-17 13:58 | 44091.5818 | 22.2 | 37.4 | 411 |  | caution | 2020-09-14 | B14660¦113¦¦Sep-17-2020 13:57
2020-09-17 13:58 | 44091.5819 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 2 LAWYER |  | 2 | 17 | 54 | 502 | 21.2 | 47 | 455 |  | 2020-09-17 13:58 | 44091.5819 | 21.2 | 47 | 455 |  |  | 2020-09-14 | B20022¦COURT 2 LAWYER¦¦Sep-17-2020 13:58
2020-09-17 13:58 | 44091.5822 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 judge |  | 1 | 18 | 50 | 404 |  |  |  | Occupied, no access | 2020-09-17 13:58 | 44091.5822 | [5 empty] | 2020-09-14 | B70235¦Court #1 judge ¦¦Sep-17-2020 13:58
2020-09-17 13:59 | 44091.5824 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Mediation room b |  | 0 | 19 | 53 | 381 | 22 | 47 | 406 |  | 2020-09-17 13:59 | 44091.5824 | 22 | 47 | 406 |  |  | 2020-09-14 | B20603¦Mediation room b¦¦Sep-17-2020 13:58
2020-09-17 13:59 | 44091.5824 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Basement corridor prisoner holding area |  | 0 | 18.6 | 45.2 | 404 | 21.6 | 54.4 | 511 | No access to Courtroom C due to trial proceedings | 2020-09-17 13:59 | 44091.5824 | 21.6 | 54.4 | 511 |  |  | 2020-09-14 | B20478¦Basement corridor prisoner holding area¦¦Sep-17-2020 13:58
2020-09-17 13:59 | 44091.5826 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 JUDGE |  | 2 | 17 | 54 | 502 | 22 | 49 | 458 |  | 2020-09-17 13:59 | 44091.5826 | 22 | 49 | 458 |  |  | 2020-09-14 | B20022¦COURT 1 JUDGE¦¦Sep-17-2020 13:58
2020-09-17 13:59 | 44091.5827 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Front desk |  | 5 | 21.2 | 34.1 | 399 | 22.9 | 36.3 | 544 |  | 2020-09-17 13:59 | 44091.5827 | 22.9 | 36.3 | 544 |  | caution | 2020-09-14 | B21554¦Front desk¦¦Sep-17-2020 13:59
2020-09-17 13:59 | 44091.5828 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 114 |  | 0 | 25 | 24 | 370 | 22.1 | 41.8 | 403 | No | 2020-09-17 13:59 | 44091.5828 | 22.1 | 41.8 | 403 |  |  | 2020-09-14 | B14660¦114¦¦Sep-17-2020 13:59
2020-09-17 13:59 | 44091.5828 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 lawyer |  | 1 | 18 | 50 | 404 |  |  |  | Occupied, no access | 2020-09-17 13:59 | 44091.5828 | [5 empty] | 2020-09-14 | B70235¦Court #1 lawyer ¦¦Sep-17-2020 13:59
2020-09-17 13:59 | 44091.5829 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 405 |  | 2 | 21.1 | 45.6 | 426 | 24 | 40.3 | 440 | No | 2020-09-17 13:59 | 44091.5829 | 24 | 40.3 | 440 |  |  | 2020-09-14 | B21128¦405¦¦Sep-17-2020 13:59
2020-09-17 14:00 | 44091.5831 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 RIGHT SIDE |  | 2 | 17 | 54 | 502 | 22.7 | 47 | 472 |  | 2020-09-17 14:00 | 44091.5831 | 22.7 | 47 | 472 |  |  | 2020-09-14 | B20022¦COURT 1 RIGHT SIDE¦¦Sep-17-2020 13:59
2020-09-17 14:00 | 44091.5834 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Police Sergeant office |  | 1 | 18 | 50 | 404 |  |  |  | Occupied, no access | 2020-09-17 14:00 | 44091.5834 | [5 empty] | 2020-09-14 | B70235¦Police Sergeant office ¦¦Sep-17-2020 14:00
2020-09-17 14:00 | 44091.5834 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Judicial offices corridor |  | 0 | 18.6 | 45.2 | 404 | 23.1 | 46.2 | 464 | No access to Courtroom C due to trial proceedings | 2020-09-17 14:00 | 44091.5834 | 23.1 | 46.2 | 464 |  |  | 2020-09-14 | B20478¦Judicial offices corridor ¦¦Sep-17-2020 14:00
2020-09-17 14:00 | 44091.5835 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 LEFT SIDE |  | 2 | 17 | 54 | 502 | 22.8 | 48 | 503 |  | 2020-09-17 14:00 | 44091.5835 | 22.8 | 48 | 503 |  |  | 2020-09-14 | B20022¦COURT 1 LEFT SIDE¦¦Sep-17-2020 14:00
2020-09-17 14:00 | 44091.5837 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Administrative office |  | 2 | 21.8 | 43.8 | 390 | 24.2 | 36.2 | 420 |  | 2020-09-17 14:01 | 44091.5837 | 24.2 | 36.2 | 420 |  | caution | 2020-09-14 | B20550¦Administrative office¦¦Sep-17-2020 14:00
2020-09-17 14:01 | 44091.5838 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 406 |  | 4 | 21.1 | 45.6 | 426 | 23.4 | 42.1 | 430 | No | 2020-09-17 14:01 | 44091.5838 | 23.4 | 42.1 | 430 |  |  | 2020-09-14 | B21128¦406¦¦Sep-17-2020 14:00
2020-09-17 14:01 | 44091.5839 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main lobby |  | 5 | 18 | 50 | 404 | 23 | 42 | 550 |  | 2020-09-17 14:01 | 44091.5839 | 23 | 42 | 550 |  |  | 2020-09-14 | B70235¦Main lobby ¦¦Sep-17-2020 14:00
2020-09-17 14:01 | 44091.5841 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JURY ROOM |  | 2 | 17 | 54 | 503 | 23 | 44.7 | 500 |  | 2020-09-17 14:01 | 44091.5841 | 23 | 44.7 | 500 |  |  | 2020-09-14 | B20022¦JURY ROOM¦¦Sep-17-2020 14:01
2020-09-17 14:02 | 44091.5844 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 0 | 23 | 26 | 396 | 21.2 | 32 | 453 |  | 2020-09-17 14:02 | 44091.5844 | 21.2 | 32 | 453 |  | low | 2020-09-14 | B16187¦Court 3¦¦Sep-17-2020 14:01
2020-09-17 14:02 | 44091.5846 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR LEFT MEETING |  | 2 | 17 | 54 | 503 | 22.8 | 48 | 522 |  | 2020-09-17 14:02 | 44091.5846 | 22.8 | 48 | 522 |  |  | 2020-09-14 | B20022¦2 FLOOR LEFT MEETING¦¦Sep-17-2020 14:01
2020-09-17 14:03 | 44091.5851 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 104 |  | 0 | 25 | 24 | 370 | 21.2 | 40 | 443 | No | 2020-09-17 14:03 | 44091.5851 | 21.2 | 40 | 443 |  | caution | 2020-09-14 | B14660¦104¦¦Sep-17-2020 14:02
2020-09-17 14:03 | 44091.5852 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Front lobby |  | 3 | 21 | 46 | 390 | 19.6 | 61 | 415 |  | 2020-09-17 14:03 | 44091.5852 | 19.6 | 61 | 415 |  | caution | 2020-09-14 | B11228¦Front lobby¦¦Sep-17-2020 14:02
2020-09-17 14:03 | 44091.5852 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 0 | 23 | 26 | 396 | 21.8 | 29.7 | 538 |  | 2020-09-17 14:03 | 44091.5852 | 21.8 | 29.7 | 538 |  | low | 2020-09-14 | B16187¦Court 3¦¦Sep-17-2020 14:02
2020-09-17 14:03 | 44091.5852 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 407 |  | 2 | 21.1 | 45.6 | 426 | 23.5 | 44 | 417 | No | 2020-09-17 14:03 | 44091.5852 | 23.5 | 44 | 417 |  |  | 2020-09-14 | B21128¦407¦¦Sep-17-2020 14:02
2020-09-17 14:03 | 44091.5853 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR RIGHT MEETING |  | 2 | 17 | 54 | 503 | 22.3 | 48 | 570 |  | 2020-09-17 14:03 | 44091.5853 | 22.3 | 48 | 570 |  |  | 2020-09-14 | B20022¦2 FLOOR RIGHT MEETING¦¦Sep-17-2020 14:02
2020-09-17 14:03 | 44091.5855 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Crown attorney office |  | 2 | 15 | 68 | 421 | 22.2 | 47.2 | 528 | No | 2020-09-17 14:03 | 44091.5855 | 22.2 | 47.2 | 528 |  |  | 2020-09-14 | B20489¦Crown attorney office ¦¦Sep-17-2020 14:03
2020-09-17 14:03 | 44091.5856 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 0 | 23 | 26 | 396 | 22 | 31 | 555 |  | 2020-09-17 14:03 | 44091.5856 | 22 | 31 | 555 |  | low | 2020-09-14 | B16187¦Court 3¦¦Sep-17-2020 14:03
2020-09-17 14:04 | 44091.5858 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 1 FLOOR MAIN HALL |  | 3 | 17 | 54 | 503 | 21.1 | 51.5 | 540 |  | 2020-09-17 14:04 | 44091.5858 | 21.1 | 51.5 | 540 |  |  | 2020-09-14 | B20022¦1 FLOOR MAIN HALL¦¦Sep-17-2020 14:03
2020-09-17 14:04 | 44091.5859 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Mediation room a |  | 0 | 19 | 53 | 381 | 22 | 46 | 406 |  | 2020-09-17 14:04 | 44091.5859 | 22 | 46 | 406 |  |  | 2020-09-14 | B20603¦Mediation room a¦¦Sep-17-2020 14:03
2020-09-17 14:04 | 44091.586 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Entrance |  | 0 | 23 | 26 | 396 | 19.4 | 31.4 | 396 |  | 2020-09-17 14:04 | 44091.586 | 19.4 | 31.4 | 396 |  | low | 2020-09-14 | B16187¦Entrance ¦¦Sep-17-2020 14:03
2020-09-17 14:04 | 44091.5863 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 101 |  | 0 | 25 | 24 | 370 | 20.3 | 47.4 | 415 | No | 2020-09-17 14:04 | 44091.5863 | 20.3 | 47.4 | 415 |  |  | 2020-09-14 | B14660¦101¦¦Sep-17-2020 14:04
2020-09-17 14:04 | 44091.5863 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | SOUTH WING ENTERANCE |  | 2 | 17 | 54 | 503 | 21 | 51 | 544 |  | 2020-09-17 14:04 | 44091.5863 | 21 | 51 | 544 |  |  | 2020-09-14 | B20022¦SOUTH WING ENTERANCE¦¦Sep-17-2020 14:04
2020-09-17 14:04 | 44091.5864 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 4 |  | 0 | 23 | 26 | 396 | 22.2 | 29.4 | 481 |  | 2020-09-17 14:04 | 44091.5864 | 22.2 | 29.4 | 481 |  | low | 2020-09-14 | B16187¦Court 4¦¦Sep-17-2020 14:04
2020-09-17 14:05 | 44091.5866 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom f1 |  | 0 | 20.3 | 46.1 | 420 | 20.9 | 48.8 | 399 |  | 2020-09-17 14:05 | 44091.5866 | 20.9 | 48.8 | 399 |  |  | 2020-09-14 | Pearso¦Ballroom f1 ¦¦Sep-17-2020 14:04
2020-09-17 14:05 | 44091.5867 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 408 |  | 2 | 21.1 | 45.6 | 426 | 24.6 | 41.3 | 540 | No | 2020-09-17 14:05 | 44091.5867 | 24.6 | 41.3 | 540 |  |  | 2020-09-14 | B21128¦408¦¦Sep-17-2020 14:04
2020-09-17 14:05 | 44091.5868 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 23 | 26 | 396 | 22.1 | 29.6 | 441 |  | 2020-09-17 14:05 | 44091.5868 | 22.1 | 29.6 | 441 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 14:05
2020-09-17 14:05 | 44091.587 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Crown attorney waiting area |  | 0 | 15 | 68 | 421 | 22.9 | 46.6 | 568 | No | 2020-09-17 14:05 | 44091.587 | 22.9 | 46.6 | 568 |  |  | 2020-09-14 | B20489¦Crown attorney waiting area ¦¦Sep-17-2020 14:05
2020-09-17 14:06 | 44091.5872 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 23 | 26 | 396 | 21.8 | 31.4 | 453 |  | 2020-09-17 14:06 | 44091.5872 | 21.8 | 31.4 | 453 |  | low | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 14:05
2020-09-17 14:06 | 44091.5874 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 134 |  | 0 | 25 | 24 | 370 | 20.5 | 43.5 | 406 | No | 2020-09-17 14:06 | 44091.5874 | 20.5 | 43.5 | 406 |  |  | 2020-09-14 | B14660¦134¦¦Sep-17-2020 14:05
2020-09-17 14:06 | 44091.5875 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 414 |  | 2 | 21.1 | 45.6 | 426 | 23.8 | 40.9 | 452 | No | 2020-09-17 14:06 | 44091.5875 | 23.8 | 40.9 | 452 |  |  | 2020-09-14 | B21128¦414¦¦Sep-17-2020 14:06
2020-09-17 14:06 | 44091.5876 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom waiting room - right side |  | 1 | 20.7 | 33.8 | 383 | 23.8 | 33.2 | 388 |  | 2020-09-17 14:06 | 44091.5876 | 23.8 | 33.2 | 388 |  | low | 2020-09-14 | B70277¦Courtroom waiting room - right side¦¦Sep-17-2020 14:06
2020-09-17 14:06 | 44091.5877 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 23 | 26 | 396 | 22.2 | 31.6 | 449 |  | 2020-09-17 14:06 | 44091.5877 | 22.2 | 31.6 | 449 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 14:06
2020-09-17 14:07 | 44091.5881 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 23 | 26 | 396 | 22.3 | 31.9 | 446 |  | 2020-09-17 14:07 | 44091.5881 | 22.3 | 31.9 | 446 |  | low | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 14:06
2020-09-17 14:07 | 44091.5882 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom f2 |  | 0 | 20.3 | 46.1 | 420 | 21 | 49 | 397 |  | 2020-09-17 14:07 | 44091.5882 | 21 | 49 | 397 |  |  | 2020-09-14 | Pearso¦Ballroom f2¦¦Sep-17-2020 14:07
2020-09-17 14:07 | 44091.5883 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 136 |  | 4 | 25 | 24 | 370 | 21.6 | 39.7 | 418 | No | 2020-09-17 14:07 | 44091.5883 | 21.6 | 39.7 | 418 |  | caution | 2020-09-14 | B14660¦136¦¦Sep-17-2020 14:07
2020-09-17 14:07 | 44091.5883 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom waiting room - left side |  | 1 | 20.7 | 33.8 | 383 | 23.7 | 33.4 | 390 |  | 2020-09-17 14:07 | 44091.5883 | 23.7 | 33.4 | 390 |  | low | 2020-09-14 | B70277¦Courtroom waiting room - left side¦¦Sep-17-2020 14:07
2020-09-17 14:07 | 44091.5884 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 413 |  | 2 | 21.1 | 45.6 | 426 | 24 | 42.1 | 570 | No | 2020-09-17 14:07 | 44091.5884 | 24 | 42.1 | 570 |  |  | 2020-09-14 | B21128¦413¦¦Sep-17-2020 14:07
2020-09-17 14:07 | 44091.5884 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 23 | 26 | 396 | 22.5 | 31.8 | 443 |  | 2020-09-17 14:07 | 44091.5884 | 22.5 | 31.8 | 443 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 14:07
2020-09-17 14:07 | 44091.5885 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 2nd floor hallway |  | 2 | 15 | 68 | 421 | 22.8 | 44.1 | 429 | No | 2020-09-17 14:07 | 44091.5885 | 22.8 | 44.1 | 429 |  |  | 2020-09-14 | B20489¦2nd floor hallway ¦¦Sep-17-2020 14:07
2020-09-17 14:08 | 44091.5888 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Front stairs |  | 1 | 21 | 46 | 390 | 21.5 | 54 | 431 |  | 2020-09-17 14:08 | 44091.5888 | 21.5 | 54 | 431 |  |  | 2020-09-14 | B11228¦Front stairs¦¦Sep-17-2020 14:07
2020-09-17 14:08 | 44091.5889 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 1 |  | 0 | 23 | 26 | 396 | 21.9 | 28 | 429 |  | 2020-09-17 14:08 | 44091.5889 | 21.9 | 28 | 429 |  | low | 2020-09-14 | B16187¦Court 1¦¦Sep-17-2020 14:08
2020-09-17 14:08 | 44091.5891 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Administration office east |  | 1 | 22 | 47 | 430 | 25 | 40 | 551 |  | 2020-09-17 14:08 | 44091.5891 | 25 | 40 | 551 |  | caution | 2020-09-14 | B25479¦Administration office east ¦¦Sep-17-2020 14:08
2020-09-17 14:09 | 44091.5893 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 23 | 26 | 396 | 21.6 | 31 | 422 |  | 2020-09-17 14:09 | 44091.5893 | 21.6 | 31 | 422 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 14:08
2020-09-17 14:09 | 44091.5895 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 412 |  | 2 | 21.1 | 45.6 | 426 | 23.3 | 41.3 | 451 | No | 2020-09-17 14:09 | 44091.5895 | 23.3 | 41.3 | 451 |  |  | 2020-09-14 | B21128¦412¦¦Sep-17-2020 14:08
2020-09-17 14:09 | 44091.5897 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - back right, facing judge |  | 2 | 20.7 | 33.8 | 383 | 23.5 | 34.1 | 392 |  | 2020-09-17 14:09 | 44091.5897 | 23.5 | 34.1 | 392 |  | low | 2020-09-14 | B70277¦Courtroom - back right, facing judge¦¦Sep-17-2020 14:09
2020-09-17 14:09 | 44091.5898 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Administration office west |  | 2 | 21 | 47 | 430 | 24 | 41 | 592 |  | 2020-09-17 14:09 | 44091.5898 | 24 | 41 | 592 |  |  | 2020-09-14 | B25479¦Administration office west ¦¦Sep-17-2020 14:09
2020-09-17 14:10 | 44091.59 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 23 | 26 | 396 | 22.1 | 31.2 | 429 |  | 2020-09-17 14:10 | 44091.59 | 22.1 | 31.2 | 429 |  | low | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 14:09
2020-09-17 14:10 | 44091.5901 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 144 |  | 0 | 25 | 24 | 370 | 22.5 | 37.1 | 405 | No | 2020-09-17 14:10 | 44091.5901 | 22.5 | 37.1 | 405 |  | caution | 2020-09-14 | B14660¦144¦¦Sep-17-2020 14:09
2020-09-17 14:10 | 44091.5902 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Motion office |  | 0 | 15 | 68 | 421 | 22.2 | 46.1 | 442 | No | 2020-09-17 14:10 | 44091.5902 | 22.2 | 46.1 | 442 |  |  | 2020-09-14 | B20489¦Motion office ¦¦Sep-17-2020 14:09
2020-09-17 14:10 | 44091.5902 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom f |  | 0 | 20.3 | 46.1 | 420 | 21 | 48.8 | 397 |  | 2020-09-17 14:10 | 44091.5902 | 21 | 48.8 | 397 |  |  | 2020-09-14 | Pearso¦Ballroom f¦¦Sep-17-2020 14:09
2020-09-17 14:10 | 44091.5904 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 23 | 26 | 396 | 22.2 | 31.6 | 434 |  | 2020-09-17 14:10 | 44091.5904 | 22.2 | 31.6 | 434 |  | low | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 14:10
2020-09-17 14:10 | 44091.5905 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Intake office |  | 0 | 21 | 47 | 430 | 24 | 40 | 585 |  | 2020-09-17 14:10 | 44091.5905 | 24 | 40 | 585 |  | caution | 2020-09-14 | B25479¦Intake office¦¦Sep-17-2020 14:10
2020-09-17 14:11 | 44091.5906 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 411 |  | 5 | 21.1 | 45.6 | 426 | 21.7 | 47 | 483 | No | 2020-09-17 14:11 | 44091.5906 | 21.7 | 47 | 483 |  |  | 2020-09-14 | B21128¦411¦¦Sep-17-2020 14:10
2020-09-17 14:11 | 44091.5907 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Upper courtroom |  | 1 | 21 | 46 | 390 | 22.2 | 53.6 | 441 |  | 2020-09-17 14:11 | 44091.5907 | 22.2 | 53.6 | 441 |  |  | 2020-09-14 | B11228¦Upper courtroom¦¦Sep-17-2020 14:10
2020-09-17 14:11 | 44091.5908 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | OPP |  | 0 | 23 | 26 | 396 | 21.9 | 31.4 | 432 |  | 2020-09-17 14:11 | 44091.5908 | 21.9 | 31.4 | 432 |  | low | 2020-09-14 | B16187¦OPP¦¦Sep-17-2020 14:10
2020-09-17 14:11 | 44091.5909 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Supervisors office |  | 0 | 21 | 47 | 430 | 24 | 39 | 576 |  | 2020-09-17 14:11 | 44091.5909 | 24 | 39 | 576 |  | caution | 2020-09-14 | B25479¦Supervisors office ¦¦Sep-17-2020 14:10
2020-09-17 14:11 | 44091.5912 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 122 |  | 0 | 25 | 24 | 370 | 22.6 | 37.5 | 428 | No | 2020-09-17 14:11 | 44091.5912 | 22.6 | 37.5 | 428 |  | caution | 2020-09-14 | B14660¦122¦¦Sep-17-2020 14:11
2020-09-17 14:11 | 44091.5912 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | OPP |  | 2 | 23 | 26 | 396 | 22.4 | 30.6 | 435 |  | 2020-09-17 14:11 | 44091.5912 | 22.4 | 30.6 | 435 |  | low | 2020-09-14 | B16187¦OPP¦¦Sep-17-2020 14:11
2020-09-17 14:11 | 44091.5913 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - back left, facing judge |  | 2 | 20.7 | 33.8 | 383 | 23 | 34.5 | 393 |  | 2020-09-17 14:11 | 44091.5913 | 23 | 34.5 | 393 |  | low | 2020-09-14 | B70277¦Courtroom - back left, facing judge¦¦Sep-17-2020 14:11
2020-09-17 14:11 | 44091.5913 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Upper office |  | 1 | 21 | 46 | 390 | 22.6 | 53 | 429 |  | 2020-09-17 14:11 | 44091.5913 | 22.6 | 53 | 429 |  |  | 2020-09-14 | B11228¦Upper office¦¦Sep-17-2020 14:11
2020-09-17 14:12 | 44091.5914 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Lunchroom |  | 0 | 21 | 47 | 430 | 23 | 41 | 573 |  | 2020-09-17 14:12 | 44091.5914 | 23 | 41 | 573 |  |  | 2020-09-14 | B25479¦Lunchroom ¦¦Sep-17-2020 14:11
2020-09-17 14:12 | 44091.5917 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Crown attorney |  | 0 | 23 | 26 | 396 | 21.8 | 30.3 | 430 |  | 2020-09-17 14:12 | 44091.5917 | 21.8 | 30.3 | 430 |  | low | 2020-09-14 | B16187¦Crown attorney ¦¦Sep-17-2020 14:11
2020-09-17 14:13 | 44091.5921 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 105 |  | 0 | 25 | 24 | 370 | 22.6 | 36.7 | 418 | No | 2020-09-17 14:13 | 44091.5921 | 22.6 | 36.7 | 418 |  | caution | 2020-09-14 | B14660¦105¦¦Sep-17-2020 14:12
2020-09-17 14:13 | 44091.5921 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 2 |  | 0 | 21 | 47 | 430 | 23 | 42 | 535 |  | 2020-09-17 14:13 | 44091.5921 | 23 | 42 | 535 |  |  | 2020-09-14 | B25479¦Courtroom 2¦¦Sep-17-2020 14:12
2020-09-17 14:13 | 44091.5921 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 410 |  | 2 | 21.1 | 45.6 | 426 | 21.3 | 46.9 | 471 | No | 2020-09-17 14:13 | 44091.5921 | 21.3 | 46.9 | 471 |  |  | 2020-09-14 | B21128¦410¦¦Sep-17-2020 14:12
2020-09-17 14:13 | 44091.5921 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Upper hall |  | 1 | 21 | 46 | 390 | 22.6 | 52 | 438 |  | 2020-09-17 14:13 | 44091.5921 | 22.6 | 52 | 438 |  |  | 2020-09-14 | B11228¦Upper hall¦¦Sep-17-2020 14:12
2020-09-17 14:13 | 44091.5922 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 3rd floor hallway |  | 0 | 15 | 68 | 421 | 22.7 | 45.2 | 441 | No | 2020-09-17 14:13 | 44091.5922 | 22.7 | 45.2 | 441 |  |  | 2020-09-14 | B20489¦3rd floor hallway ¦¦Sep-17-2020 14:12
2020-09-17 14:13 | 44091.5923 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - middle left, facing the judge |  | 2 | 20.7 | 33.8 | 383 | 22.6 | 35.2 | 392 |  | 2020-09-17 14:13 | 44091.5923 | 22.6 | 35.2 | 392 |  | caution | 2020-09-14 | B70277¦Courtroom - middle left, facing the judge¦¦Sep-17-2020 14:12
2020-09-17 14:13 | 44091.5925 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 2 |  | 0 | 23 | 26 | 396 | 21.7 | 30.1 | 426 |  | 2020-09-17 14:13 | 44091.5925 | 21.7 | 30.1 | 426 |  | low | 2020-09-14 | B16187¦Court 2¦¦Sep-17-2020 14:13
2020-09-17 14:13 | 44091.5927 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Back stairs |  | 1 | 21 | 46 | 390 | 23.3 | 52 | 460 |  | 2020-09-17 14:13 | 44091.5927 | 23.3 | 52 | 460 |  |  | 2020-09-14 | B11228¦Back stairs¦¦Sep-17-2020 14:13
2020-09-17 14:14 | 44091.5928 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 2 |  | 0 | 23 | 26 | 396 | 21.5 | 30.7 | 421 |  | 2020-09-17 14:14 | 44091.5928 | 21.5 | 30.7 | 421 |  | low | 2020-09-14 | B16187¦Court 2¦¦Sep-17-2020 14:13
2020-09-17 14:14 | 44091.5928 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Library |  | 0 | 21 | 47 | 430 | 23 | 42 | 537 |  | 2020-09-17 14:14 | 44091.5928 | 23 | 42 | 537 |  |  | 2020-09-14 | B25479¦Library ¦¦Sep-17-2020 14:13
2020-09-17 14:14 | 44091.5931 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 23 | 26 | 396 | 21.8 | 31 | 416 |  | 2020-09-17 14:14 | 44091.5931 | 21.8 | 31 | 416 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 14:14
2020-09-17 14:14 | 44091.5931 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 409 |  | 7 | 21.1 | 45.6 | 426 | 21.8 | 45.5 | 488 | No | 2020-09-17 14:14 | 44091.5931 | 21.8 | 45.5 | 488 |  |  | 2020-09-14 | B21128¦409¦¦Sep-17-2020 14:14
2020-09-17 14:14 | 44091.5933 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Lower courtroom lobby |  | 1 | 21 | 46 | 390 | 22.8 | 50 | 470 |  | 2020-09-17 14:14 | 44091.5933 | 22.8 | 50 | 470 |  |  | 2020-09-14 | B11228¦Lower courtroom lobby¦¦Sep-17-2020 14:14
2020-09-17 14:15 | 44091.5934 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 23 | 26 | 396 | 21.6 | 37.7 | 419 |  | 2020-09-17 14:15 | 44091.5934 | 21.6 | 37.7 | 419 |  | caution | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 14:14
2020-09-17 14:15 | 44091.5935 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Tc office |  | 1 | 21 | 47 | 430 | 24 | 43 | 554 |  | 2020-09-17 14:15 | 44091.5935 | 24 | 43 | 554 |  |  | 2020-09-14 | B25479¦Tc office ¦¦Sep-17-2020 14:14
2020-09-17 14:15 | 44091.5939 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 23 | 26 | 396 | 22 | 68.6 | 469 |  | 2020-09-17 14:15 | 44091.5939 | 22 | 68.6 | 469 |  | high | 2020-09-14 | B16187¦Common ¦¦Sep-17-2020 14:15
2020-09-17 14:15 | 44091.5939 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Jury room |  | 0 | 15 | 68 | 421 | 23 | 45.6 | 433 | No | 2020-09-17 14:15 | 44091.5939 | 23 | 45.6 | 433 |  |  | 2020-09-14 | B20489¦Jury room ¦¦Sep-17-2020 14:15
2020-09-17 14:15 | 44091.594 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Lower courtroom |  | 1 | 21 | 46 | 390 | 22 | 51.6 | 438 |  | 2020-09-17 14:15 | 44091.594 | 22 | 51.6 | 438 |  |  | 2020-09-14 | B11228¦Lower courtroom¦¦Sep-17-2020 14:15
2020-09-17 14:15 | 44091.5941 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | JP lobby |  | 0 | 21 | 47 | 430 | 24 | 41 | 553 | Couldn't get into courtroom 1,3,4 and 5 | 2020-09-17 14:15 | 44091.5941 | 24 | 41 | 553 |  |  | 2020-09-14 | B25479¦JP lobby ¦¦Sep-17-2020 14:15
2020-09-17 14:15 | 44091.5941 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 111 |  | 0 | 25 | 24 | 370 | 22.4 | 38.2 | 426 | No | 2020-09-17 14:16 | 44091.5941 | 22.4 | 38.2 | 426 |  | caution | 2020-09-14 | B14660¦111¦¦Sep-17-2020 14:15
2020-09-17 14:16 | 44091.5941 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 400 |  | 3 | 21.1 | 45.6 | 426 | 22.3 | 46.9 | 526 | No | 2020-09-17 14:16 | 44091.5941 | 22.3 | 46.9 | 526 |  |  | 2020-09-14 | B21128¦400¦¦Sep-17-2020 14:15
2020-09-17 14:16 | 44091.5942 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Cell waiting area |  | 0 | 23 | 26 | 396 | 21.4 | 33.4 | 441 |  | 2020-09-17 14:16 | 44091.5942 | 21.4 | 33.4 | 441 |  | low | 2020-09-14 | B16187¦Cell waiting area ¦¦Sep-17-2020 14:15
2020-09-17 14:16 | 44091.5945 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - middle right, facing the judge |  | 2 | 20.7 | 33.8 | 383 | 22.5 | 35.6 | 385 |  | 2020-09-17 14:16 | 44091.5945 | 22.5 | 35.6 | 385 |  | caution | 2020-09-14 | B70277¦Courtroom - middle right, facing the judge¦¦Sep-17-2020 14:16
2020-09-17 14:16 | 44091.5947 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Basement hallway |  | 0 | 23 | 26 | 396 | 21.7 | 36.9 | 452 |  | 2020-09-17 14:16 | 44091.5947 | 21.7 | 36.9 | 452 |  | caution | 2020-09-14 | B16187¦Basement hallway¦¦Sep-17-2020 14:16
2020-09-17 14:17 | 44091.5948 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Office lobby |  | 1 | 21 | 46 | 390 | 21.8 | 53 | 473 |  | 2020-09-17 14:17 | 44091.5948 | 21.8 | 53 | 473 |  |  | 2020-09-14 | B11228¦Office lobby¦¦Sep-17-2020 14:16
2020-09-17 14:17 | 44091.5951 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 23 | 26 | 396 | 21.2 | 40.8 | 467 |  | 2020-09-17 14:17 | 44091.5951 | 21.2 | 40.8 | 467 |  |  | 2020-09-14 | B16187¦Common¦¦Sep-17-2020 14:16
2020-09-17 14:17 | 44091.5953 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 401 |  | 7 | 21.1 | 45.6 | 426 | 23.2 | 45.5 | 495 | No | 2020-09-17 14:17 | 44091.5953 | 23.2 | 45.5 | 495 |  |  | 2020-09-14 | B21128¦401¦¦Sep-17-2020 14:17
2020-09-17 14:17 | 44091.5953 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Main lobby south |  | 2 | 21 | 47 | 430 | 24 | 39 | 558 |  | 2020-09-17 14:17 | 44091.5953 | 24 | 39 | 558 |  | caution | 2020-09-14 | B25479¦Main lobby south ¦¦Sep-17-2020 14:17
2020-09-17 14:18 | 44091.5955 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - judges desk, left side |  | 2 | 20.7 | 33.8 | 383 | 22.6 | 35.5 | 393 |  | 2020-09-17 14:18 | 44091.5955 | 22.6 | 35.5 | 393 |  | caution | 2020-09-14 | B70277¦Courtroom - judges desk, left side¦¦Sep-17-2020 14:17
2020-09-17 14:18 | 44091.5956 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Office lower |  | 2 | 21 | 46 | 390 | 22 | 54 | 477 |  | 2020-09-17 14:18 | 44091.5956 | 22 | 54 | 477 |  |  | 2020-09-14 | B11228¦Office lower¦¦Sep-17-2020 14:17
2020-09-17 14:18 | 44091.5957 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Main lobby north |  | 0 | 21 | 47 | 430 | 23 | 40 | 556 |  | 2020-09-17 14:18 | 44091.5957 | 23 | 40 | 556 |  | caution | 2020-09-14 | B25479¦Main lobby north ¦¦Sep-17-2020 14:17
2020-09-17 14:18 | 44091.5958 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Private room |  | 0 | 15 | 68 | 421 | 22.8 | 45.8 | 430 | No | 2020-09-17 14:18 | 44091.5958 | 22.8 | 45.8 | 430 |  |  | 2020-09-14 | B20489¦Private room ¦¦Sep-17-2020 14:18
2020-09-17 14:18 | 44091.5959 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 203 |  | 0 | 25 | 24 | 370 | 22.5 | 41.5 | 466 | No | 2020-09-17 14:18 | 44091.5959 | 22.5 | 41.5 | 466 |  |  | 2020-09-14 | B14660¦203¦¦Sep-17-2020 14:18
2020-09-17 14:18 | 44091.596 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 402 |  | 4 | 21.1 | 45.6 | 426 | 23.2 | 43.3 | 481 | No | 2020-09-17 14:18 | 44091.596 | 23.2 | 43.3 | 481 |  |  | 2020-09-14 | B21128¦402¦¦Sep-17-2020 14:18
2020-09-17 14:19 | 44091.5963 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - judges desk, centre/right side |  | 2 | 20.7 | 33.8 | 383 | 22.8 | 35.4 | 393 |  | 2020-09-17 14:19 | 44091.5963 | 22.8 | 35.4 | 393 |  | caution | 2020-09-14 | B70277¦Courtroom - judges desk, centre/right side¦¦Sep-17-2020 14:18
2020-09-17 14:20 | 44091.5969 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 213 |  | 1 | 25 | 24 | 370 | 22.5 | 37.6 | 435 | No | 2020-09-17 14:20 | 44091.5969 | 22.5 | 37.6 | 435 |  | caution | 2020-09-14 | B14660¦213¦¦Sep-17-2020 14:19
2020-09-17 14:20 | 44091.597 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Crown attorneys office |  | 4 | 21.1 | 45.6 | 426 | 23.2 | 43.4 | 455 | No | 2020-09-17 14:20 | 44091.597 | 23.2 | 43.4 | 455 |  |  | 2020-09-14 | B21128¦Crown attorneys office¦¦Sep-17-2020 14:19
2020-09-17 14:20 | 44091.5974 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - witness stand |  | 2 | 20.7 | 33.8 | 383 | 22.9 | 35.3 | 393 |  | 2020-09-17 14:20 | 44091.5974 | 22.9 | 35.3 | 393 |  | caution | 2020-09-14 | B70277¦Courtroom - witness stand¦¦Sep-17-2020 14:20
2020-09-17 14:20 | 44091.5975 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Court room 1 judge's desk |  | 0 | 15 | 68 | 421 | 22.8 | 46.8 | 454 | No | 2020-09-17 14:20 | 44091.5975 | 22.8 | 46.8 | 454 |  |  | 2020-09-14 | B20489¦Court room 1 judge's desk ¦¦Sep-17-2020 14:20
2020-09-17 14:21 | 44091.598 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 209 |  | 1 | 25 | 24 | 370 | 22.5 | 42.7 | 436 | No | 2020-09-17 14:21 | 44091.598 | 22.5 | 42.7 | 436 |  |  | 2020-09-14 | B14660¦209¦¦Sep-17-2020 14:21
2020-09-17 14:23 | 44091.5992 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Court room 1 gallery |  | 0 | 15 | 68 | 421 | 22.8 | 46.8 | 442 | No | 2020-09-17 14:23 | 44091.5992 | 22.8 | 46.8 | 442 |  |  | 2020-09-14 | B20489¦Court room 1 gallery ¦¦Sep-17-2020 14:22
2020-09-17 14:23 | 44091.5994 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Judges chamber - Front desk |  | 2 | 20.7 | 33.8 | 383 | 23 | 36.6 | 393 |  | 2020-09-17 14:23 | 44091.5994 | 23 | 36.6 | 393 |  | caution | 2020-09-14 | B70277¦Judges chamber - Front desk¦¦Sep-17-2020 14:23
2020-09-17 14:24 | 44091.5997 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 210a |  | 2 | 25 | 24 | 370 | 23 | 41.2 | 455 | No | 2020-09-17 14:24 | 44091.5997 | 23 | 41.2 | 455 |  |  | 2020-09-14 | B14660¦210a¦¦Sep-17-2020 14:23
2020-09-17 14:25 | 44091.6005 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 206 |  | 0 | 25 | 24 | 370 | 22.8 | 41.3 | 442 | No | 2020-09-17 14:25 | 44091.6005 | 22.8 | 41.3 | 442 |  |  | 2020-09-14 | B14660¦206¦¦Sep-17-2020 14:24
2020-09-17 14:25 | 44091.6006 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 3rd floor hallway south |  | 0 | 15 | 68 | 421 | 23 | 45.3 | 450 |  | 2020-09-17 14:25 | 44091.6006 | 23 | 45.3 | 450 |  |  | 2020-09-14 | B20489¦3rd floor hallway south ¦¦Sep-17-2020 14:24
2020-09-17 14:25 | 44091.6008 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Judges chamber - behind desk, beside back door |  | 2 | 20.7 | 33.8 | 383 | 23.2 | 36.8 | 392 |  | 2020-09-17 14:25 | 44091.6008 | 23.2 | 36.8 | 392 |  | caution | 2020-09-14 | B70277¦Judges chamber - behind desk, beside back door¦¦Sep-17-2020 14:25
2020-09-17 14:26 | 44091.6017 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation office |  | 2 | 20.7 | 33.8 | 383 | 23.2 | 35.2 | 396 |  | 2020-09-17 14:26 | 44091.6017 | 23.2 | 35.2 | 396 |  | caution | 2020-09-14 | B70277¦Mediation office¦¦Sep-17-2020 14:26
2020-09-17 14:28 | 44091.6027 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation Office - printer area |  | 2 | 20.7 | 33.8 | 383 | 23.2 | 35.9 | 428 |  | 2020-09-17 14:28 | 44091.6027 | 23.2 | 35.9 | 428 |  | caution | 2020-09-14 | B70277¦Mediation Office - printer area¦¦Sep-17-2020 14:27
2020-09-17 14:30 | 44091.6041 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Lunch/kitchen room - counter |  | 1 | 20.7 | 33.8 | 383 | 23.1 | 35.6 | 447 |  | 2020-09-17 14:30 | 44091.6041 | 23.1 | 35.6 | 447 |  | caution | 2020-09-14 | B70277¦Lunch/kitchen room - counter¦¦Sep-17-2020 14:29
2020-09-17 14:30 | 44091.6044 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 303 |  | 0 | 25 | 24 | 370 | 22.4 | 39.2 | 415 | No | 2020-09-17 14:30 | 44091.6044 | 22.4 | 39.2 | 415 |  | caution | 2020-09-14 | B14660¦303¦¦Sep-17-2020 14:30
2020-09-17 14:31 | 44091.6047 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | North hallway |  | 0 | 19 | 53 | 381 | 22 | 45 | 410 |  | 2020-09-17 14:31 | 44091.6047 | 22 | 45 | 410 |  |  | 2020-09-14 | B20603¦North hallway¦¦Sep-17-2020 14:30
2020-09-17 14:31 | 44091.6048 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 303 |  | 0 | 25 | 24 | 370 | 22.4 | 39.2 | 415 | No | 2020-09-17 14:31 | 44091.6048 | 22.4 | 39.2 | 415 |  | caution | 2020-09-14 | B14660¦303¦¦Sep-17-2020 14:30
2020-09-17 14:32 | 44091.6053 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 302 |  | 4 | 25 | 24 | 370 | 22.7 | 38.7 | 494 | No | 2020-09-17 14:32 | 44091.6053 | 22.7 | 38.7 | 494 |  | caution | 2020-09-14 | B14660¦302¦¦Sep-17-2020 14:31
2020-09-17 14:33 | 44091.6059 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation Room - kitchen entrance area |  | 2 | 20.7 | 33.8 | 383 | 23.2 | 35.4 | 407 |  | 2020-09-17 14:33 | 44091.6059 | 23.2 | 35.4 | 407 |  | caution | 2020-09-14 | B70277¦Mediation Room - kitchen entrance area¦¦Sep-17-2020 14:32
2020-09-17 14:33 | 44091.6062 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Main entrance |  | 0 | 21.2 | 41.5 | 413 | 23.3 | 40.4 | 443 |  | 2020-09-17 14:33 | 44091.6062 | 23.3 | 40.4 | 443 |  |  | 2020-09-14 | B25039¦Main entrance¦¦Sep-17-2020 14:32
2020-09-17 14:33 | 44091.6063 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Tribunal |  | 2 | 19 | 53 | 381 | 22 | 46 | 423 |  | 2020-09-17 14:33 | 44091.6063 | 22 | 46 | 423 |  |  | 2020-09-14 | B20603¦Tribunal¦¦Sep-17-2020 14:33
2020-09-17 14:34 | 44091.6069 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - centre table |  | 2 | 20.7 | 33.8 | 383 | 23.2 | 35 | 408 |  | 2020-09-17 14:34 | 44091.6069 | 23.2 | 35 | 408 |  | caution | 2020-09-14 | B70277¦Mediation room - centre table¦¦Sep-17-2020 14:33
2020-09-17 14:34 | 44091.607 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Basement waiting area inside dbl doors |  | 1 | 22 | 31.2 | 396 | 20.8 | 48.8 | 556 |  | 2020-09-17 14:34 | 44091.607 | 20.8 | 48.8 | 556 |  |  | 2020-09-14 | B21554¦Basement waiting area inside dbl doors¦¦Sep-17-2020 14:34
2020-09-17 14:34 | 44091.607 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 301b |  | 0 | 25 | 24 | 370 | 22.8 | 38.8 | 405 | No | 2020-09-17 14:34 | 44091.607 | 22.8 | 38.8 | 405 |  | caution | 2020-09-14 | B14660¦301b¦¦Sep-17-2020 14:34
2020-09-17 14:34 | 44091.6072 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Lunch room |  | 0 | 21.2 | 41.5 | 413 | 23.1 | 45.9 | 553 |  | 2020-09-17 14:34 | 44091.6072 | 23.1 | 45.9 | 553 |  |  | 2020-09-14 | B25039¦Lunch room¦¦Sep-17-2020 14:34
2020-09-17 14:35 | 44091.6076 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Front entrance |  | 0 | 25.5 | 29.6 | 406 | 24.2 | 30.7 | 430 |  | 2020-09-17 14:35 | 44091.6076 | 24.2 | 30.7 | 430 |  | low | 2020-09-14 | B17477¦Front entrance ¦¦Sep-17-2020 14:34
2020-09-17 14:35 | 44091.6079 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Reception room |  | 2 | 19 | 53 | 381 | 22 | 46 | 431 |  | 2020-09-17 14:35 | 44091.6079 | 22 | 46 | 431 |  |  | 2020-09-14 | B20603¦Reception room¦¦Sep-17-2020 14:35
2020-09-17 14:36 | 44091.6081 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 301A |  | 0 | 25 | 24 | 370 | 23.4 | 38.4 | 403 | No | 2020-09-17 14:36 | 44091.6081 | 23.4 | 38.4 | 403 |  | caution | 2020-09-14 | B14660¦301A¦¦Sep-17-2020 14:35
2020-09-17 14:36 | 44091.6082 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Lunch room hall |  | 0 | 21.2 | 41.5 | 413 | 23 | 47 | 561 |  | 2020-09-17 14:36 | 44091.6082 | 23 | 47 | 561 |  |  | 2020-09-14 | B25039¦Lunch room hall¦¦Sep-17-2020 14:35
2020-09-17 14:36 | 44091.6086 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - hallway entrance area |  | 2 | 20.7 | 33.8 | 383 | 23.7 | 34.9 | 431 |  | 2020-09-17 14:36 | 44091.6086 | 23.7 | 34.9 | 431 |  | low | 2020-09-14 | B70277¦Mediation room - hallway entrance area¦¦Sep-17-2020 14:36
2020-09-17 14:37 | 44091.6088 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area inside dbl doors |  | 1 | 22 | 31.2 | 396 | 20.8 | 49 | 565 |  | 2020-09-17 14:37 | 44091.6088 | 20.8 | 49 | 565 |  |  | 2020-09-14 | B20474¦Basement waiting area inside dbl doors¦¦Sep-17-2020 14:36
2020-09-17 14:37 | 44091.6091 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Open space |  | 2 | 19 | 53 | 381 | 22 | 46 | 427 |  | 2020-09-17 14:37 | 44091.6091 | 22 | 46 | 427 |  |  | 2020-09-14 | B20603¦Open space¦¦Sep-17-2020 14:37
2020-09-17 14:37 | 44091.6091 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | Crown Attorney |  | 1 | 25 | 24 | 370 | 23.3 | 37 | 412 | Np | 2020-09-17 14:37 | 44091.6091 | 23.3 | 37 | 412 |  | caution | 2020-09-14 | B14660¦Crown Attorney¦¦Sep-17-2020 14:37
2020-09-17 14:38 | 44091.6094 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Service Ontario |  | 3 | 21.2 | 41.5 | 413 | 23.3 | 46.8 | 583 |  | 2020-09-17 14:38 | 44091.6094 | 23.3 | 46.8 | 583 |  |  | 2020-09-14 | B25039¦Service Ontario¦¦Sep-17-2020 14:37
2020-09-17 14:38 | 44091.6097 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Security |  | 2 | 25.5 | 29.6 | 406 | 23.8 | 38.3 | 540 |  | 2020-09-17 14:38 | 44091.6097 | 23.8 | 38.3 | 540 |  | caution | 2020-09-14 | B17477¦Security ¦¦Sep-17-2020 14:37
2020-09-17 14:38 | 44091.61 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Robing corridor |  | 1 | 22 | 31.2 | 396 | 20.9 | 47.2 | 495 |  | 2020-09-17 14:38 | 44091.61 | 20.9 | 47.2 | 495 |  |  | 2020-09-14 | B20474¦Robing corridor¦¦Sep-17-2020 14:38
2020-09-17 14:38 | 44091.61 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 616 |  | 1 | 19 | 53 | 381 | 22 | 46 | 446 |  | 2020-09-17 14:38 | 44091.61 | 22 | 46 | 446 |  |  | 2020-09-14 | B20603¦616¦¦Sep-17-2020 14:38
2020-09-17 14:39 | 44091.6102 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Duty council office - desk area |  | 1 | 20.7 | 33.8 | 383 | 23.6 | 34.5 | 408 |  | 2020-09-17 14:39 | 44091.6102 | 23.6 | 34.5 | 408 |  | low | 2020-09-14 | B70277¦Duty council office - desk area¦¦Sep-17-2020 14:38
2020-09-17 14:39 | 44091.6104 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Water fountain |  | 0 | 21.2 | 41.5 | 413 | 23.2 | 46.7 | 573 |  | 2020-09-17 14:39 | 44091.6104 | 23.2 | 46.7 | 573 |  |  | 2020-09-14 | B25039¦Water fountain¦¦Sep-17-2020 14:39
2020-09-17 14:39 | 44091.6105 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 308 |  | 0 | 25 | 24 | 370 | 22.7 | 39.5 | 406 | Np | 2020-09-17 14:39 | 44091.6105 | 22.7 | 39.5 | 406 |  | caution | 2020-09-14 | B14660¦308¦¦Sep-17-2020 14:39
2020-09-17 14:39 | 44091.6108 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 1 seating area |  | 0 | 25.5 | 29.6 | 406 | 23.6 | 41.1 | 454 |  | 2020-09-17 14:40 | 44091.6108 | 23.6 | 41.1 | 454 |  |  | 2020-09-14 | B17477¦Level 1 seating area ¦¦Sep-17-2020 14:39
2020-09-17 14:40 | 44091.6111 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Duty council office - back right seating area |  | 1 | 20.7 | 33.8 | 383 | 23.7 | 34.7 | 406 |  | 2020-09-17 14:40 | 44091.6111 | 23.7 | 34.7 | 406 |  | low | 2020-09-14 | B70277¦Duty council office - back right seating area¦¦Sep-17-2020 14:40
2020-09-17 14:41 | 44091.6115 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 615 |  | 0 | 19 | 53 | 381 | 22 | 46 | 425 |  | 2020-09-17 14:41 | 44091.6115 | 22 | 46 | 425 |  |  | 2020-09-14 | B20603¦615¦¦Sep-17-2020 14:40
2020-09-17 14:41 | 44091.6116 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 1 seating area 2 |  | 0 | 25.5 | 29.6 | 406 | 23.6 | 41.3 | 455 |  | 2020-09-17 14:41 | 44091.6116 | 23.6 | 41.3 | 455 |  |  | 2020-09-14 | B17477¦Level 1 seating area 2¦¦Sep-17-2020 14:40
2020-09-17 14:41 | 44091.6116 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Meditation room |  | 0 | 21.2 | 41.5 | 413 | 22.6 | 48.5 | 570 |  | 2020-09-17 14:41 | 44091.6116 | 22.6 | 48.5 | 570 |  |  | 2020-09-14 | B25039¦Meditation room¦¦Sep-17-2020 14:40
2020-09-17 14:41 | 44091.6119 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area at mens washroom |  | 1 | 22 | 31.2 | 396 | 21 | 49.5 | 518 |  | 2020-09-17 14:41 | 44091.6119 | 21 | 49.5 | 518 |  |  | 2020-09-14 | B20474¦Basement waiting area at mens washroom¦¦Sep-17-2020 14:41
2020-09-17 14:41 | 44091.6121 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 Center |  | 0 | 22.3 | 48.6 | 399 | 23.3 | 48.7 | 665 |  | 2020-09-17 14:41 | 44091.6121 | 23.3 | 48.7 | 665 |  |  | 2020-09-14 | B10577¦Courtroom 1 Center¦¦Sep-17-2020 14:41
2020-09-17 14:42 | 44091.6124 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Printing room |  | 0 | 19 | 53 | 381 | 22 | 47 | 426 |  | 2020-09-17 14:42 | 44091.6124 | 22 | 47 | 426 |  |  | 2020-09-14 | B20603¦Printing room¦¦Sep-17-2020 14:41
2020-09-17 14:42 | 44091.6124 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside of door “302” |  | 1 | 20.7 | 33.8 | 383 | 23 | 35.5 | 424 |  | 2020-09-17 14:42 | 44091.6124 | 23 | 35.5 | 424 |  | caution | 2020-09-14 | B70277¦Hallway - outside of door “302”¦¦Sep-17-2020 14:41
2020-09-17 14:42 | 44091.6128 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Handicapped washroom |  | 0 | 21.2 | 41.5 | 413 | 22.7 | 47.8 | 574 |  | 2020-09-17 14:42 | 44091.6128 | 22.7 | 47.8 | 574 |  |  | 2020-09-14 | B25039¦Handicapped washroom¦¦Sep-17-2020 14:42
2020-09-17 14:43 | 44091.6133 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Entrance |  | 0 | 21.7 | 39.3 | 402 | 23.1 | 42.6 | 493 |  | 2020-09-17 14:43 | 44091.6133 | 23.1 | 42.6 | 493 |  |  | 2020-09-14 | B10577¦Main Entrance¦¦Sep-17-2020 14:43
2020-09-17 14:43 | 44091.6135 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NW hall |  | 0 | 19 | 65 | 440 | 23 | 54 | 585 |  | 2020-09-17 14:43 | 44091.6135 | 23 | 54 | 585 |  |  | 2020-09-14 | B25548¦NW hall¦¦Sep-17-2020 14:43
2020-09-17 14:43 | 44091.6135 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside of duty council office |  | 1 | 20.7 | 33.8 | 383 | 22.7 | 35.1 | 421 |  | 2020-09-17 14:43 | 44091.6135 | 22.7 | 35.1 | 421 |  | caution | 2020-09-14 | B70277¦Hallway - outside of duty council office¦¦Sep-17-2020 14:43
2020-09-17 14:44 | 44091.6136 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area courtroom3 |  | 1 | 22 | 31.2 | 396 | 20.8 | 50.3 | 540 |  | 2020-09-17 14:44 | 44091.6136 | 20.8 | 50.3 | 540 |  |  | 2020-09-14 | B20474¦Basement waiting area courtroom3¦¦Sep-17-2020 14:43
2020-09-17 14:44 | 44091.6136 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 626 |  | 0 | 19 | 53 | 381 | 22 | 46 | 424 |  | 2020-09-17 14:44 | 44091.6136 | 22 | 46 | 424 |  |  | 2020-09-14 | B20603¦626¦¦Sep-17-2020 14:43
2020-09-17 14:44 | 44091.614 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Lobby South |  | 1 | 21.7 | 39.3 | 402 | 22.5 | 45.11 | 65.3 |  | 2020-09-17 14:44 | 44091.614 | 22.5 | 45.11 | 65.3 |  |  | 2020-09-14 | B10577¦Main Lobby South¦¦Sep-17-2020 14:44
2020-09-17 14:44 | 44091.6141 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Fire extinguisher |  | 0 | 21.2 | 41.5 | 413 | 22.7 | 48.6 | 566 |  | 2020-09-17 14:44 | 44091.6141 | 22.7 | 48.6 | 566 |  |  | 2020-09-14 | B25039¦Fire extinguisher¦¦Sep-17-2020 14:44
2020-09-17 14:45 | 44091.6145 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NE hall |  | 0 | 19 | 65 | 440 | 24 | 53 | 580 |  | 2020-09-17 14:45 | 44091.6145 | 24 | 53 | 580 |  |  | 2020-09-14 | B25548¦NE hall¦¦Sep-17-2020 14:44
2020-09-17 14:45 | 44091.6145 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 612 |  | 0 | 19 | 53 | 381 | 22 | 46 | 432 |  | 2020-09-17 14:45 | 44091.6145 | 22 | 46 | 432 |  |  | 2020-09-14 | B20603¦612¦¦Sep-17-2020 14:44
2020-09-17 14:45 | 44091.6146 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Court Service Office |  | 2 | 21.7 | 39.3 | 402 | 23.3 | 44.7 | 841 |  | 2020-09-17 14:45 | 44091.6146 | 23.3 | 44.7 | 841 |  |  | 2020-09-14 | B10577¦Court Service Office¦¦Sep-17-2020 14:45
2020-09-17 14:45 | 44091.6149 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - elevator lobby |  | 1 | 20.7 | 33.8 | 383 | 22.6 | 34.7 | 422 |  | 2020-09-17 14:45 | 44091.6149 | 22.6 | 34.7 | 422 |  | low | 2020-09-14 | B70277¦Hallway - elevator lobby¦¦Sep-17-2020 14:45
2020-09-17 14:46 | 44091.6151 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Bottom stairs foyer |  | 1 | 22 | 31.2 | 396 | 20.5 | 50 | 592 |  | 2020-09-17 14:46 | 44091.6151 | 20.5 | 50 | 592 |  |  | 2020-09-14 | B20474¦Bottom stairs foyer¦¦Sep-17-2020 14:45
2020-09-17 14:46 | 44091.6152 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Rear hall |  | 0 | 21.2 | 41.5 | 413 | 22.6 | 49.3 | 576 |  | 2020-09-17 14:46 | 44091.6152 | 22.6 | 49.3 | 576 |  |  | 2020-09-14 | B25039¦Rear hall¦¦Sep-17-2020 14:45
2020-09-17 14:46 | 44091.6153 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Witness Area |  | 0 | 21.7 | 39.3 | 402 | 23.6 | 44.7 | 831 |  | 2020-09-17 14:46 | 44091.6153 | 23.6 | 44.7 | 831 |  |  | 2020-09-14 | B10577¦Witness Area¦¦Sep-17-2020 14:45
2020-09-17 14:46 | 44091.6153 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 seating area |  | 0 | 25.5 | 29.6 | 406 | 23 | 43.6 | 461 |  | 2020-09-17 14:46 | 44091.6153 | 23 | 43.6 | 461 |  |  | 2020-09-14 | B17477¦Courtroom 100 seating area ¦¦Sep-17-2020 14:46
2020-09-17 14:46 | 44091.6155 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Open space 2 |  | 0 | 19 | 53 | 381 | 22 | 46 | 422 |  | 2020-09-17 14:46 | 44091.6155 | 22 | 46 | 422 |  |  | 2020-09-14 | B20603¦Open space 2¦¦Sep-17-2020 14:46
2020-09-17 14:46 | 44091.6156 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | E hall |  | 0 | 19 | 65 | 440 | 24 | 52 | 585 |  | 2020-09-17 14:46 | 44091.6156 | 24 | 52 | 585 |  |  | 2020-09-14 | B25548¦E hall¦¦Sep-17-2020 14:46
2020-09-17 14:47 | 44091.6158 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside washrooms |  | 1 | 20.7 | 33.8 | 383 | 22.7 | 34.2 | 425 |  | 2020-09-17 14:47 | 44091.6158 | 22.7 | 34.2 | 425 |  | low | 2020-09-14 | B70277¦Hallway - outside washrooms¦¦Sep-17-2020 14:46
2020-09-17 14:47 | 44091.616 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Lobby North |  | 3 | 21.7 | 39.3 | 402 | 23.3 | 45.5 | 811 |  | 2020-09-17 14:47 | 44091.616 | 23.3 | 45.5 | 811 |  |  | 2020-09-14 | B10577¦Main Lobby North ¦¦Sep-17-2020 14:47
2020-09-17 14:47 | 44091.6161 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | 911 entrance |  | 0 | 21.2 | 41.5 | 413 | 22.6 | 48.8 | 576 |  | 2020-09-17 14:47 | 44091.6161 | 22.6 | 48.8 | 576 |  |  | 2020-09-14 | B25039¦911 entrance¦¦Sep-17-2020 14:47
2020-09-17 14:48 | 44091.6163 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 seating area 2 |  | 0 | 25.5 | 29.6 | 444 | 22.8 | 44.8 | 437 |  | 2020-09-17 14:48 | 44091.6163 | 22.8 | 44.8 | 437 |  |  | 2020-09-14 | B17477¦Courtroom 100 seating area 2¦¦Sep-17-2020 14:47
2020-09-17 14:48 | 44091.6165 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Hallway room b |  | 0 | 19 | 53 | 381 | 22 | 46 | 427 |  | 2020-09-17 14:48 | 44091.6165 | 22 | 46 | 427 |  |  | 2020-09-14 | B20603¦Hallway room b¦¦Sep-17-2020 14:47
2020-09-17 14:48 | 44091.6166 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | 3rd Floor Stairwell |  | 1 | 20.7 | 33.8 | 383 | 23.2 | 36.2 | 451 |  | 2020-09-17 14:48 | 44091.6166 | 23.2 | 36.2 | 451 |  | caution | 2020-09-14 | B70277¦3rd Floor Stairwell¦¦Sep-17-2020 14:47
2020-09-17 14:48 | 44091.6166 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Lower landing of stairs |  | 1 | 22 | 31.2 | 396 | 20.2 | 50.4 | 589 |  | 2020-09-17 14:48 | 44091.6166 | 20.2 | 50.4 | 589 |  |  | 2020-09-14 | B20474¦Lower landing of stairs¦¦Sep-17-2020 14:47
2020-09-17 14:48 | 44091.6167 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom waiting room |  | 0 | 15.9 | 47.9 | 408 | 21.6 | 50.1 | 726 |  | 2020-09-17 14:48 | 44091.6167 | 21.6 | 50.1 | 726 |  |  | 2020-09-14 | B90631¦Courtroom waiting room ¦¦Sep-17-2020 14:48
2020-09-17 14:48 | 44091.6168 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main stairwell |  | 0 | 21.7 | 39.3 | 402 | 23.2 | 45.6 | 810 |  | 2020-09-17 14:48 | 44091.6168 | 23.2 | 45.6 | 810 |  |  | 2020-09-14 | B10577¦Main stairwell¦¦Sep-17-2020 14:48
2020-09-17 14:49 | 44091.6172 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Office 1 |  | 0 | 21.2 | 41.5 | 413 | 22.5 | 48.6 | 574 |  | 2020-09-17 14:49 | 44091.6172 | 22.5 | 48.6 | 574 |  |  | 2020-09-14 | B25039¦Office 1¦¦Sep-17-2020 14:48
2020-09-17 14:49 | 44091.6173 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | SE hall |  | 0 | 19 | 65 | 440 | 27 | 44 | 590 |  | 2020-09-17 14:49 | 44091.6173 | 27 | 44 | 590 | caution |  | 2020-09-14 | B25548¦SE hall¦¦Sep-17-2020 14:48
2020-09-17 14:50 | 44091.6182 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 1 |  | 5 | 20.6 | 33 | 405 | 20.6 | 40.6 | 595 |  | 2020-09-17 14:50 | 44091.6182 | 20.6 | 40.6 | 595 |  |  | 2020-09-14 | B20367¦Courtroom 1¦¦Sep-17-2020 14:50
2020-09-17 14:51 | 44091.6185 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Inside Elevator on 3rd Floor |  | 1 | 20.7 | 33.8 | 383 | 23.1 | 37.8 | 457 |  | 2020-09-17 14:51 | 44091.6185 | 23.1 | 37.8 | 457 |  | caution | 2020-09-14 | B70277¦Inside Elevator on 3rd Floor¦¦Sep-17-2020 14:50
2020-09-17 14:51 | 44091.6185 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2 floor waiting area north |  | 0 | 21.7 | 39.3 | 402 | 23.1 | 46.8 | 772 |  | 2020-09-17 14:51 | 44091.6185 | 23.1 | 46.8 | 772 |  |  | 2020-09-14 | B10577¦2 floor waiting area north¦¦Sep-17-2020 14:50
2020-09-17 14:51 | 44091.6187 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | SW hall |  | 0 | 19 | 65 | 440 | 26 | 46 | 590 |  | 2020-09-17 14:51 | 44091.6187 | 26 | 46 | 590 | caution |  | 2020-09-14 | B25548¦SW hall¦¦Sep-17-2020 14:50
2020-09-17 14:51 | 44091.6189 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom b |  | 0 | 19 | 53 | 381 | 22 | 46 | 410 |  | 2020-09-17 14:51 | 44091.6189 | 22 | 46 | 410 |  |  | 2020-09-14 | B20603¦Courtroom b¦¦Sep-17-2020 14:51
2020-09-17 14:51 | 44091.6189 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area main office |  | 1 | 22 | 31.2 | 396 | 21 | 45.3 | 499 |  | 2020-09-17 14:51 | 44091.6189 | 21 | 45.3 | 499 |  |  | 2020-09-14 | B20474¦Waiting area main office¦¦Sep-17-2020 14:51
2020-09-17 14:51 | 44091.6189 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 doors |  | 0 | 25.5 | 29.6 | 406 | 22 | 48 | 432 |  | 2020-09-17 14:51 | 44091.6189 | 22 | 48 | 432 |  |  | 2020-09-14 | B17477¦Courtroom 100 doors ¦¦Sep-17-2020 14:51
2020-09-17 14:52 | 44091.6192 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 1 judges chamber |  | 0 | 20.6 | 33 | 405 | 21.7 | 45.2 | 565 |  | 2020-09-17 14:52 | 44091.6192 | 21.7 | 45.2 | 565 |  |  | 2020-09-14 | B20367¦Courtroom 1 judges chamber ¦¦Sep-17-2020 14:51
2020-09-17 14:52 | 44091.6195 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Copier room |  | 0 | 21.2 | 41.5 | 413 | 22.2 | 49.3 | 567 |  | 2020-09-17 14:52 | 44091.6195 | 22.2 | 49.3 | 567 |  |  | 2020-09-14 | B25039¦Copier room¦¦Sep-17-2020 14:52
2020-09-17 14:52 | 44091.6195 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2 floor waiting area center |  | 0 | 21.7 | 39.3 | 402 | 23 | 47.2 | 741 |  | 2020-09-17 14:52 | 44091.6195 | 23 | 47.2 | 741 |  |  | 2020-09-14 | B10577¦2 floor waiting area center ¦¦Sep-17-2020 14:52
2020-09-17 14:53 | 44091.6199 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 bench |  | 0 | 25.5 | 29.6 | 406 | 21.7 | 48 | 427 |  | 2020-09-17 14:53 | 44091.6199 | 21.7 | 48 | 427 |  |  | 2020-09-14 | B17477¦Courtroom 100 bench ¦¦Sep-17-2020 14:52
2020-09-17 14:53 | 44091.62 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | Center hall |  | 0 | 19 | 65 | 440 | 25 | 48 | 600 |  | 2020-09-17 14:53 | 44091.62 | 25 | 48 | 600 |  |  | 2020-09-14 | B25548¦Center hall¦¦Sep-17-2020 14:52
2020-09-17 14:53 | 44091.6201 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judicial stairwell |  | 0 | 20.6 | 33 | 405 | 21.7 | 46.2 | 543 |  | 2020-09-17 14:53 | 44091.6201 | 21.7 | 46.2 | 543 |  |  | 2020-09-14 | B20367¦Judicial stairwell ¦¦Sep-17-2020 14:52
2020-09-17 14:53 | 44091.6202 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2 floor waiting area south |  | 0 | 21.7 | 39.3 | 402 | 23.1 | 47.5 | 723 |  | 2020-09-17 14:53 | 44091.6202 | 23.1 | 47.5 | 723 |  |  | 2020-09-14 | B10577¦2 floor waiting area south ¦¦Sep-17-2020 14:53
2020-09-17 14:53 | 44091.6202 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Front lobby |  | 4 | 18 | 54 | 404 | 20 | 54 | 439 |  | 2020-09-17 14:53 | 44091.6202 | 20 | 54 | 439 |  |  | 2020-09-14 | B19570¦Front lobby¦¦Sep-17-2020 14:53
2020-09-17 14:53 | 44091.6203 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Trial office |  | 3 | 22 | 31.2 | 396 | 21.5 | 44.8 | 498 |  | 2020-09-17 14:53 | 44091.6203 | 21.5 | 44.8 | 498 |  |  | 2020-09-14 | B20474¦Trial office¦¦Sep-17-2020 14:53
2020-09-17 14:53 | 44091.6204 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom a |  | 0 | 19 | 53 | 381 | 22 | 45 | 404 |  | 2020-09-17 14:53 | 44091.6204 | 22 | 45 | 404 |  |  | 2020-09-14 | B20603¦Courtroom a¦¦Sep-17-2020 14:53
2020-09-17 14:54 | 44091.6209 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 west |  | 0 | 21.7 | 39.3 | 402 | 23 | 46 | 591 |  | 2020-09-17 14:54 | 44091.6209 | 23 | 46 | 591 |  |  | 2020-09-14 | B10577¦Courtroom 2 west¦¦Sep-17-2020 14:54
2020-09-17 14:54 | 44091.6209 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judges chamber foyers |  | 0 | 20.6 | 33 | 405 | 22.9 | 44.1 | 522 |  | 2020-09-17 14:54 | 44091.6209 | 22.9 | 44.1 | 522 |  |  | 2020-09-14 | B20367¦Judges chamber foyers ¦¦Sep-17-2020 14:54
2020-09-17 14:54 | 44091.621 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 1 ramp |  | 0 | 25.5 | 29.6 | 406 | 22 | 46.6 | 455 |  | 2020-09-17 14:54 | 44091.621 | 22 | 46.6 | 455 |  |  | 2020-09-14 | B17477¦Level 1 ramp ¦¦Sep-17-2020 14:54
2020-09-17 14:54 | 44091.621 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Office 2 |  | 0 | 21.2 | 41.5 | 413 | 21.7 | 51.4 | 571 |  | 2020-09-17 14:54 | 44091.621 | 21.7 | 51.4 | 571 |  |  | 2020-09-14 | B25039¦Office 2¦¦Sep-17-2020 14:54
2020-09-17 14:54 | 44091.6212 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-E wall |  | 0 | 19 | 65 | 440 | 25 | 50 | 600 |  | 2020-09-17 14:54 | 44091.6212 | 25 | 50 | 600 |  |  | 2020-09-14 | B25548¦1-E wall¦¦Sep-17-2020 14:54
2020-09-17 14:55 | 44091.6215 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Main floor at stairway |  | 1 | 22 | 31.2 | 396 | 20.2 | 50.6 | 602 |  | 2020-09-17 14:55 | 44091.6215 | 20.2 | 50.6 | 602 |  |  | 2020-09-14 | B20474¦Main floor at stairway¦¦Sep-17-2020 14:55
2020-09-17 14:55 | 44091.6216 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 2 seating area |  | 0 | 25.5 | 29.6 | 406 | 22.3 | 45.4 | 460 |  | 2020-09-17 14:55 | 44091.6216 | 22.3 | 45.4 | 460 |  |  | 2020-09-14 | B17477¦Level 2 seating area ¦¦Sep-17-2020 14:55
2020-09-17 14:55 | 44091.6216 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 south |  | 0 | 21.7 | 39.3 | 402 | 23.2 | 45.5 | 569 |  | 2020-09-17 14:55 | 44091.6216 | 23.2 | 45.5 | 569 |  |  | 2020-09-14 | B10577¦Courtroom 2 south¦¦Sep-17-2020 14:55
2020-09-17 14:55 | 44091.6216 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | South hallway |  | 0 | 19 | 53 | 381 | 23 | 45 | 405 |  | 2020-09-17 14:55 | 44091.6216 | 23 | 45 | 405 |  |  | 2020-09-14 | B20603¦South hallway¦¦Sep-17-2020 14:55
2020-09-17 14:55 | 44091.6217 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judges chamber foyers |  | 0 | 20.6 | 33 | 405 | 22 | 43 | 512 |  | 2020-09-17 14:55 | 44091.6217 | 22 | 43 | 512 |  |  | 2020-09-14 | B20367¦Judges chamber foyers ¦¦Sep-17-2020 14:55
2020-09-17 14:56 | 44091.6219 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 106 |  | 0 | 25 | 24 | 370 | 22.1 | 37.6 | 424 | No | 2020-09-17 14:56 | 44091.6219 | 22.1 | 37.6 | 424 |  | caution | 2020-09-14 | B14660¦106¦¦Sep-17-2020 14:55
2020-09-17 14:56 | 44091.622 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court servicea office |  | 5 | 18 | 54 | 404 | 22 | 45 | 428 |  | 2020-09-17 14:56 | 44091.622 | 22 | 45 | 428 |  |  | 2020-09-14 | B19570¦Court servicea office¦¦Sep-17-2020 14:55
2020-09-17 14:56 | 44091.6224 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 2 ramp |  | 0 | 25.5 | 29.6 | 406 | 22.5 | 44.3 | 455 |  | 2020-09-17 14:56 | 44091.6224 | 22.5 | 44.3 | 455 |  |  | 2020-09-14 | B17477¦Level 2 ramp ¦¦Sep-17-2020 14:56
2020-09-17 14:56 | 44091.6224 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- E wall |  | 0 | 19 | 65 | 440 | 25 | 48 | 590 |  | 2020-09-17 14:56 | 44091.6224 | 25 | 48 | 590 |  |  | 2020-09-14 | B25548¦1- E wall¦¦Sep-17-2020 14:56
2020-09-17 14:56 | 44091.6225 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 east |  | 0 | 21.7 | 39.3 | 402 | 23.1 | 45.9 | 569 |  | 2020-09-17 14:56 | 44091.6225 | 23.1 | 45.9 | 569 |  |  | 2020-09-14 | B10577¦Courtroom 2 east¦¦Sep-17-2020 14:56
2020-09-17 14:56 | 44091.6225 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 1 |  | 0 | 20.6 | 33 | 405 | 22 | 38.2 | 481 |  | 2020-09-17 14:56 | 44091.6225 | 22 | 38.2 | 481 |  | caution | 2020-09-14 | B20367¦Waiting room 1¦¦Sep-17-2020 14:56
2020-09-17 14:57 | 44091.6226 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court admin hall |  | 1 | 18 | 54 | 404 | 23 | 45 | 445 |  | 2020-09-17 14:57 | 44091.6226 | 23 | 45 | 445 |  |  | 2020-09-14 | B19570¦Court admin hall¦¦Sep-17-2020 14:56
2020-09-17 14:57 | 44091.623 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Crown attorneys office |  | 4 | 21.1 | 45.6 | 426 | 23.2 | 43.4 | 455 | No | 2020-09-17 14:57 | 44091.623 | 23.2 | 43.4 | 455 |  |  | 2020-09-14 | B21128¦Crown attorneys office¦¦Sep-17-2020 14:57
2020-09-17 14:57 | 44091.6231 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 3 seating area |  | 0 | 25.5 | 29.6 | 406 | 22.5 | 44.9 | 451 |  | 2020-09-17 14:57 | 44091.6231 | 22.5 | 44.9 | 451 |  |  | 2020-09-14 | B17477¦Level 3 seating area ¦¦Sep-17-2020 14:57
2020-09-17 14:58 | 44091.6233 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 North |  | 0 | 21.7 | 39.3 | 402 | 22.6 | 46.7 | 495 |  | 2020-09-17 14:58 | 44091.6233 | 22.6 | 46.7 | 495 |  |  | 2020-09-14 | B10577¦Courtroom 2 North¦¦Sep-17-2020 14:57
2020-09-17 14:58 | 44091.6233 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Foyers |  | 2 | 20.6 | 33 | 405 | 21.9 | 38.7 | 466 |  | 2020-09-17 14:58 | 44091.6233 | 21.9 | 38.7 | 466 |  | caution | 2020-09-14 | B20367¦Foyers ¦¦Sep-17-2020 14:57
2020-09-17 14:58 | 44091.6234 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- E wall |  | 0 | 19 | 65 | 440 | 25 | 48 | 585 |  | 2020-09-17 14:58 | 44091.6234 | 25 | 48 | 585 |  |  | 2020-09-14 | B25548¦1- E wall¦¦Sep-17-2020 14:57
2020-09-17 14:58 | 44091.6238 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 2 |  | 3 | 18 | 54 | 404 | 23 | 46 | 431 |  | 2020-09-17 14:58 | 44091.6238 | 23 | 46 | 431 |  |  | 2020-09-14 | B19570¦Court 2¦¦Sep-17-2020 14:58
2020-09-17 14:58 | 44091.6239 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 3 seating area 2 |  | 0 | 25.5 | 29.6 | 406 | 22.5 | 44.6 | 452 |  | 2020-09-17 14:58 | 44091.6239 | 22.5 | 44.6 | 452 |  |  | 2020-09-14 | B17477¦Level 3 seating area 2¦¦Sep-17-2020 14:58
2020-09-17 14:59 | 44091.6242 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 outside |  | 0 | 21.7 | 39.3 | 402 | 22.5 | 48.3 | 65.8 |  | 2020-09-17 14:59 | 44091.6242 | 22.5 | 48.3 | 65.8 |  |  | 2020-09-14 | B10577¦Courtroom 3 outside ¦¦Sep-17-2020 14:58
2020-09-17 14:59 | 44091.6245 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 1 |  | 2 | 18 | 54 | 404 | 23 | 48 | 449 |  | 2020-09-17 14:59 | 44091.6245 | 23 | 48 | 449 |  |  | 2020-09-14 | B19570¦Court 1¦¦Sep-17-2020 14:59
2020-09-17 14:59 | 44091.6245 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom4 corridor |  | 1 | 22 | 31.2 | 396 | 19.8 | 51.3 | 525 |  | 2020-09-17 14:59 | 44091.6245 | 19.8 | 51.3 | 525 |  |  | 2020-09-14 | B20474¦Courtroom4 corridor¦¦Sep-17-2020 14:59
2020-09-17 14:59 | 44091.6246 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 19 | 65 | 440 | 25 | 48 | 610 |  | 2020-09-17 14:59 | 44091.6246 | 25 | 48 | 610 |  |  | 2020-09-14 | B25548¦1-S wall¦¦Sep-17-2020 14:59
2020-09-17 15:00 | 44091.6248 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 seating area |  | 0 | 25.5 | 29.6 | 406 | 22.6 | 45.1 | 446 |  | 2020-09-17 15:00 | 44091.6248 | 22.6 | 45.1 | 446 |  |  | 2020-09-14 | B17477¦Courtroom 300 seating area ¦¦Sep-17-2020 14:59
2020-09-17 15:00 | 44091.6252 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 3 |  | 2 | 18 | 54 | 404 | 21 | 47 | 448 |  | 2020-09-17 15:00 | 44091.6252 | 21 | 47 | 448 |  |  | 2020-09-14 | B19570¦Court 3¦¦Sep-17-2020 15:00
2020-09-17 15:00 | 44091.6253 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Administration office |  | 7 | 20.6 | 39.1 | 405 | 22.1 | 39.3 | 649 |  | 2020-09-17 15:00 | 44091.6253 | 22.1 | 39.3 | 649 |  | caution | 2020-09-14 | B20367¦Administration office ¦¦Sep-17-2020 15:00
2020-09-17 15:01 | 44091.6256 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 waiting area |  | 0 | 21.7 | 39.3 | 402 | 22.6 | 48.1 | 479 |  | 2020-09-17 15:01 | 44091.6256 | 22.6 | 48.1 | 479 |  |  | 2020-09-14 | B10577¦Courtroom 3 waiting area ¦¦Sep-17-2020 15:00
2020-09-17 15:01 | 44091.6257 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 19 | 65 | 440 | 26 | 46 | 595 |  | 2020-09-17 15:01 | 44091.6257 | 26 | 46 | 595 | caution |  | 2020-09-14 | B25548¦1-S wall¦¦Sep-17-2020 15:00
2020-09-17 15:01 | 44091.626 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 seating area 2 |  | 0 | 25.5 | 29.6 | 406 | 22.7 | 44.9 | 443 |  | 2020-09-17 15:01 | 44091.626 | 22.7 | 44.9 | 443 |  |  | 2020-09-14 | B17477¦Courtroom 300 seating area 2 ¦¦Sep-17-2020 15:01
2020-09-17 15:01 | 44091.626 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 4 |  | 3 | 18 | 54 | 404 | 21 | 48 | 432 |  | 2020-09-17 15:01 | 44091.626 | 21 | 48 | 432 |  |  | 2020-09-14 | B19570¦Court 4¦¦Sep-17-2020 15:01
2020-09-17 15:02 | 44091.6263 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 South |  | 0 | 21.7 | 39.3 | 402 | 22.6 | 48.2 | 464 |  | 2020-09-17 15:02 | 44091.6263 | 22.6 | 48.2 | 464 |  |  | 2020-09-14 | B10577¦Courtroom 3 South¦¦Sep-17-2020 15:01
2020-09-17 15:02 | 44091.6265 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 251 |  | 1 | 18 | 54 | 404 | 21 | 51 | 430 |  | 2020-09-17 15:02 | 44091.6265 | 21 | 51 | 430 |  |  | 2020-09-14 | B19570¦251¦¦Sep-17-2020 15:02
2020-09-17 15:02 | 44091.6265 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Administration |  | 8 | 20.6 | 38.9 | 405 | 22.3 | 38.4 | 611 |  | 2020-09-17 15:02 | 44091.6265 | 22.3 | 38.4 | 611 |  | caution | 2020-09-14 | B20367¦Administration ¦¦Sep-17-2020 15:02
2020-09-17 15:02 | 44091.6267 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom2 2nd door |  | 1 | 22 | 31.2 | 396 | 19.7 | 51.4 | 505 |  | 2020-09-17 15:02 | 44091.6267 | 19.7 | 51.4 | 505 |  |  | 2020-09-14 | B20474¦Waiting area courtroom2 2nd door¦¦Sep-17-2020 15:02
2020-09-17 15:03 | 44091.6268 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 doors |  | 0 | 25.5 | 29.6 | 406 | 22.8 | 45.4 | 433 |  | 2020-09-17 15:03 | 44091.6268 | 22.8 | 45.4 | 433 |  |  | 2020-09-14 | B17477¦Courtroom 300 doors ¦¦Sep-17-2020 15:02
2020-09-17 15:03 | 44091.6269 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 East |  | 0 | 21.7 | 39.3 | 402 | 22.8 | 48.3 | 467 |  | 2020-09-17 15:03 | 44091.6269 | 22.8 | 48.3 | 467 |  |  | 2020-09-14 | B10577¦Courtroom 3 East¦¦Sep-17-2020 15:02
2020-09-17 15:03 | 44091.6269 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 250 |  | 1 | 18 | 54 | 404 | 22 | 48 | 424 |  | 2020-09-17 15:03 | 44091.6269 | 22 | 48 | 424 |  |  | 2020-09-14 | B19570¦250¦¦Sep-17-2020 15:02
2020-09-17 15:03 | 44091.6273 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 19 | 65 | 440 | 26 | 45 | 630 |  | 2020-09-17 15:03 | 44091.6273 | 26 | 45 | 630 | caution |  | 2020-09-14 | B25548¦1-S wall¦¦Sep-17-2020 15:03
2020-09-17 15:03 | 44091.6273 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Hallway ne |  | 1 | 18 | 54 | 404 | 22 | 47 | 424 |  | 2020-09-17 15:03 | 44091.6273 | 22 | 47 | 424 |  |  | 2020-09-14 | B19570¦Hallway ne ¦¦Sep-17-2020 15:03
2020-09-17 15:03 | 44091.6274 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main lobby |  | 5 | 18 | 50 | 404 | 23 | 42 | 550 |  | 2020-09-17 15:03 | 44091.6274 | 23 | 42 | 550 |  |  | 2020-09-14 | B70235¦Main lobby ¦¦Sep-17-2020 15:03
2020-09-17 15:04 | 44091.6275 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Court operations |  | 2 | 20.6 | 33 | 405 | 21.8 | 42.9 | 520 |  | 2020-09-17 15:04 | 44091.6275 | 21.8 | 42.9 | 520 |  |  | 2020-09-14 | B20367¦Court operations ¦¦Sep-17-2020 15:03
2020-09-17 15:04 | 44091.6276 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 bench |  | 0 | 25.5 | 29.6 | 406 | 22.9 | 45.3 | 426 |  | 2020-09-17 15:04 | 44091.6276 | 22.9 | 45.3 | 426 |  |  | 2020-09-14 | B17477¦Courtroom 300 bench ¦¦Sep-17-2020 15:03
2020-09-17 15:04 | 44091.6276 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 245 |  | 1 | 18 | 54 | 404 | 22 | 47 | 417 |  | 2020-09-17 15:04 | 44091.6276 | 22 | 47 | 417 |  |  | 2020-09-14 | B19570¦245¦¦Sep-17-2020 15:03
2020-09-17 15:04 | 44091.6277 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 North |  | 1 | 21.7 | 39.3 | 402 | 23.2 | 50.9 | 472 |  | 2020-09-17 15:04 | 44091.6277 | 23.2 | 50.9 | 472 |  |  | 2020-09-14 | B10577¦Courtroom 3 North¦¦Sep-17-2020 15:03
2020-09-17 15:04 | 44091.628 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 247 |  | 1 | 18 | 54 | 404 | 22 | 47 | 410 |  | 2020-09-17 15:04 | 44091.628 | 22 | 47 | 410 |  |  | 2020-09-14 | B19570¦247¦¦Sep-17-2020 15:04
2020-09-17 15:04 | 44091.6281 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- S wall |  | 0 | 19 | 65 | 440 | 26 | 46 | 605 |  | 2020-09-17 15:04 | 44091.6281 | 26 | 46 | 605 | caution |  | 2020-09-14 | B25548¦1- S wall¦¦Sep-17-2020 15:04
2020-09-17 15:05 | 44091.6284 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 244 |  | 1 | 18 | 54 | 404 | 23 | 46 | 408 |  | 2020-09-17 15:05 | 44091.6284 | 23 | 46 | 408 |  |  | 2020-09-14 | B19570¦244¦¦Sep-17-2020 15:04
2020-09-17 15:05 | 44091.6286 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 West |  | 0 | 21.7 | 39.3 | 402 | 23.2 | 48.5 | 473 |  | 2020-09-17 15:05 | 44091.6286 | 23.2 | 48.5 | 473 |  |  | 2020-09-14 | B10577¦Courtroom 3 West¦¦Sep-17-2020 15:05
2020-09-17 15:05 | 44091.6287 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom2 2nd door |  | 1 | 22 | 31.2 | 396 | 20 | 51 | 547 |  | 2020-09-17 15:05 | 44091.6287 | 20 | 51 | 547 |  |  | 2020-09-14 | B20474¦Waiting area courtroom2 2nd door¦¦Sep-17-2020 15:05
2020-09-17 15:06 | 44091.6288 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 4 top |  | 1 | 18 | 54 | 404 | 22 | 47 | 414 |  | 2020-09-17 15:06 | 44091.6288 | 22 | 47 | 414 |  |  | 2020-09-14 | B19570¦Stairwell 4 top¦¦Sep-17-2020 15:05
2020-09-17 15:06 | 44091.6291 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 2 |  | 0 | 20.6 | 33 | 405 | 21.4 | 37.9 | 472 |  | 2020-09-17 15:06 | 44091.6291 | 21.4 | 37.9 | 472 |  | caution | 2020-09-14 | B20367¦Waiting room 2¦¦Sep-17-2020 15:05
2020-09-17 15:06 | 44091.6292 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 4 bottom |  | 1 | 18 | 54 | 404 | 22 | 47 | 425 |  | 2020-09-17 15:06 | 44091.6292 | 22 | 47 | 425 |  |  | 2020-09-14 | B19570¦Stairwell 4 bottom ¦¦Sep-17-2020 15:06
2020-09-17 15:06 | 44091.6295 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 3 ramp |  | 0 | 25.5 | 29.6 | 406 | 22.5 | 44.5 | 457 |  | 2020-09-17 15:06 | 44091.6295 | 22.5 | 44.5 | 457 |  |  | 2020-09-14 | B17477¦Level 3 ramp ¦¦Sep-17-2020 15:06
2020-09-17 15:07 | 44091.6296 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Basement hall w |  | 1 | 18 | 54 | 404 | 22 | 49 | 436 |  | 2020-09-17 15:07 | 44091.6296 | 22 | 49 | 436 |  |  | 2020-09-14 | B19570¦Basement hall w ¦¦Sep-17-2020 15:06
2020-09-17 15:07 | 44091.6297 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- S wall |  | 0 | 19 | 65 | 440 | 26 | 50 | 585 |  | 2020-09-17 15:07 | 44091.6297 | 26 | 50 | 585 | caution |  | 2020-09-14 | B25548¦1- S wall¦¦Sep-17-2020 15:06
2020-09-17 15:07 | 44091.63 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 2 |  | 0 | 20.6 | 33 | 405 | 21.3 | 38.9 | 461 |  | 2020-09-17 15:07 | 44091.63 | 21.3 | 38.9 | 461 |  | caution | 2020-09-14 | B20367¦Courtroom 2¦¦Sep-17-2020 15:07
2020-09-17 15:07 | 44091.6301 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Crown attorney office |  | 1 | 18 | 54 | 404 | 21 | 52 | 424 |  | 2020-09-17 15:07 | 44091.6301 | 21 | 52 | 424 |  |  | 2020-09-14 | B19570¦Crown attorney office ¦¦Sep-17-2020 15:07
2020-09-17 15:08 | 44091.6302 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 4 seating area |  | 0 | 25.5 | 29.6 | 406 | 22.8 | 42 | 438 |  | 2020-09-17 15:08 | 44091.6302 | 22.8 | 42 | 438 |  |  | 2020-09-14 | B17477¦Level 4 seating area ¦¦Sep-17-2020 15:07
2020-09-17 15:08 | 44091.6308 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Employee entrance |  | 1 | 18 | 54 | 404 | 22 | 48 | 445 |  | 2020-09-17 15:08 | 44091.6308 | 22 | 48 | 445 |  |  | 2020-09-14 | B19570¦Employee entrance ¦¦Sep-17-2020 15:08
2020-09-17 15:09 | 44091.6309 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office a |  | 0 | 20.6 | 33 | 405 | 21.8 | 39.5 | 437 |  | 2020-09-17 15:09 | 44091.6309 | 21.8 | 39.5 | 437 |  | caution | 2020-09-14 | B20367¦Office a¦¦Sep-17-2020 15:08
2020-09-17 15:09 | 44091.631 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 4 seating area 2 |  | 0 | 25.5 | 29.6 | 406 | 22.8 | 42.1 | 436 |  | 2020-09-17 15:09 | 44091.631 | 22.8 | 42.1 | 436 |  |  | 2020-09-14 | B17477¦Level 4 seating area 2 ¦¦Sep-17-2020 15:08
2020-09-17 15:09 | 44091.6313 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- S wall |  | 0 | 19 | 65 | 440 | 26 | 48 | 600 |  | 2020-09-17 15:09 | 44091.6313 | 26 | 48 | 600 | caution |  | 2020-09-14 | B25548¦1- S wall¦¦Sep-17-2020 15:09
2020-09-17 15:09 | 44091.6314 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #2 |  | 2 | 22 | 31.2 | 396 | 20.1 | 49.3 | 489 |  | 2020-09-17 15:09 | 44091.6314 | 20.1 | 49.3 | 489 |  |  | 2020-09-14 | B20474¦Courtroom #2¦¦Sep-17-2020 15:09
2020-09-17 15:09 | 44091.6315 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office b |  | 0 | 20.6 | 33 | 405 | 21.8 | 38.6 | 435 |  | 2020-09-17 15:09 | 44091.6315 | 21.8 | 38.6 | 435 |  | caution | 2020-09-14 | B20367¦Office b¦¦Sep-17-2020 15:09
2020-09-17 15:09 | 44091.6315 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Poa office |  | 3 | 18 | 54 | 404 | 22 | 51 | 496 |  | 2020-09-17 15:09 | 44091.6315 | 22 | 51 | 496 |  |  | 2020-09-14 | B19570¦Poa office ¦¦Sep-17-2020 15:09
2020-09-17 15:10 | 44091.6319 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 seating area |  | 0 | 25.5 | 29.6 | 406 | 22.9 | 42.2 | 438 |  | 2020-09-17 15:10 | 44091.6319 | 22.9 | 42.2 | 438 |  |  | 2020-09-14 | B17477¦Courtroom 400 seating area ¦¦Sep-17-2020 15:09
2020-09-17 15:10 | 44091.632 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | JUDGE BAKDWIN |  | 0 | 21 | 48 | 430 | 22.2 | 47 | 500 | 11 | 2020-09-17 15:10 | 44091.632 | 22.2 | 47 | 500 |  |  | 2020-09-14 | B70740¦JUDGE BAKDWIN¦¦Sep-17-2020 15:10
2020-09-17 15:10 | 44091.632 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 5 |  | 1 | 18 | 54 | 404 | 22 | 49 | 463 |  | 2020-09-17 15:10 | 44091.632 | 22 | 49 | 463 |  |  | 2020-09-14 | B19570¦Court 5¦¦Sep-17-2020 15:10
2020-09-17 15:10 | 44091.6321 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st Floor Main lobby |  | 8 | 15.8 | 45.1 | 402 | 18.5 | 49.7 | 449 | no | 2020-09-17 15:10 | 44091.6321 | 18.5 | 49.7 | 449 |  |  | 2020-09-14 | B70496¦1st Floor Main lobby ¦¦Sep-17-2020 15:10
2020-09-17 15:11 | 44091.6325 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office c |  | 0 | 20.6 | 33 | 405 | 21.7 | 38.5 | 436 |  | 2020-09-17 15:11 | 44091.6325 | 21.7 | 38.5 | 436 |  | caution | 2020-09-14 | B20367¦Office c¦¦Sep-17-2020 15:10
2020-09-17 15:11 | 44091.6326 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Basement hall e |  | 1 | 18 | 54 | 404 | 22 | 48 | 449 |  | 2020-09-17 15:11 | 44091.6326 | 22 | 48 | 449 |  |  | 2020-09-14 | B19570¦Basement hall e ¦¦Sep-17-2020 15:11
2020-09-17 15:11 | 44091.6327 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | judge rm 14 |  | 1 | 21 | 48 | 430 | 22 | 48 | 440 |  | 2020-09-17 15:11 | 44091.6327 | 22 | 48 | 440 |  |  | 2020-09-14 | B70740¦judge rm 14¦¦Sep-17-2020 15:11
2020-09-17 15:11 | 44091.6329 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #1 |  | 2 | 22 | 31.2 | 396 | 20 | 50.2 | 492 |  | 2020-09-17 15:11 | 44091.6329 | 20 | 50.2 | 492 |  |  | 2020-09-14 | B20474¦Courtroom #1¦¦Sep-17-2020 15:11
2020-09-17 15:11 | 44091.633 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- W wall |  | 0 | 19 | 65 | 440 | 26 | 46 | 580 |  | 2020-09-17 15:11 | 44091.633 | 26 | 46 | 580 | caution |  | 2020-09-14 | B25548¦1- W wall¦¦Sep-17-2020 15:11
2020-09-17 15:12 | 44091.633 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 5 bottom |  | 1 | 18 | 54 | 404 | 22 | 48 | 444 |  | 2020-09-17 15:11 | 44091.633 | 22 | 48 | 444 |  |  | 2020-09-14 | B19570¦Stairwell 5 bottom ¦¦Sep-17-2020 15:11
2020-09-17 15:12 | 44091.633 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 seating area 2 |  | 0 | 25.5 | 29.6 | 406 | 22.6 | 42.7 | 443 |  | 2020-09-17 15:12 | 44091.633 | 22.6 | 42.7 | 443 |  |  | 2020-09-14 | B17477¦Courtroom 400 seating area 2 ¦¦Sep-17-2020 15:11
2020-09-17 15:12 | 44091.6334 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 5 top |  | 1 | 18 | 54 | 404 | 22 | 47 | 438 |  | 2020-09-17 15:12 | 44091.6334 | 22 | 47 | 438 |  |  | 2020-09-14 | B19570¦Stairwell 5 top ¦¦Sep-17-2020 15:12
2020-09-17 15:12 | 44091.6334 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 South |  | 0 | 21.7 | 39.3 | 402 | 22.8 | 50.3 | 837 |  | 2020-09-17 15:12 | 44091.6334 | 22.8 | 50.3 | 837 |  |  | 2020-09-14 | B10577¦Courtroom 1 South¦¦Sep-17-2020 15:12
2020-09-17 15:13 | 44091.6338 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 3 |  | 0 | 20.6 | 33 | 405 | 22.3 | 42.1 | 470 |  | 2020-09-17 15:13 | 44091.6338 | 22.3 | 42.1 | 470 |  |  | 2020-09-14 | B20367¦Courtroom 3¦¦Sep-17-2020 15:12
2020-09-17 15:13 | 44091.6338 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Law library hall s |  | 1 | 18 | 54 | 404 | 22 | 46 | 423 |  | 2020-09-17 15:13 | 44091.6338 | 22 | 46 | 423 |  |  | 2020-09-14 | B19570¦Law library hall s ¦¦Sep-17-2020 15:12
2020-09-17 15:13 | 44091.634 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 East |  | 0 | 21.7 | 39.3 | 402 | 22.9 | 51.7 | 749 |  | 2020-09-17 15:13 | 44091.634 | 22.9 | 51.7 | 749 |  |  | 2020-09-14 | B10577¦Courtroom 1 East¦¦Sep-17-2020 15:13
2020-09-17 15:13 | 44091.6342 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Law library hall n |  | 1 | 18 | 54 | 404 | 22 | 47 | 417 |  | 2020-09-17 15:13 | 44091.6342 | 22 | 47 | 417 |  |  | 2020-09-14 | B19570¦Law library hall n ¦¦Sep-17-2020 15:13
2020-09-17 15:13 | 44091.6342 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- W wall |  | 0 | 19 | 65 | 440 | 25 | 47 | 580 |  | 2020-09-17 15:13 | 44091.6342 | 25 | 47 | 580 |  |  | 2020-09-14 | B25548¦1- W wall¦¦Sep-17-2020 15:13
2020-09-17 15:14 | 44091.6345 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 doors |  | 3 | 25.5 | 29.6 | 406 | 22.8 | 42.7 | 435 |  | 2020-09-17 15:14 | 44091.6345 | 22.8 | 42.7 | 435 |  |  | 2020-09-14 | B17477¦Courtroom 400 doors ¦¦Sep-17-2020 15:13
2020-09-17 15:14 | 44091.6346 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 259 |  | 1 | 18 | 54 | 404 | 22 | 46 | 416 |  | 2020-09-17 15:14 | 44091.6346 | 22 | 46 | 416 |  |  | 2020-09-14 | B19570¦259¦¦Sep-17-2020 15:13
2020-09-17 15:14 | 44091.6346 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 3 |  | 0 | 20.6 | 33 | 405 | 22.5 | 39 | 470 |  | 2020-09-17 15:14 | 44091.6346 | 22.5 | 39 | 470 |  | caution | 2020-09-14 | B20367¦Waiting room 3¦¦Sep-17-2020 15:13
2020-09-17 15:14 | 44091.6349 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #3 |  | 2 | 22 | 31.2 | 396 | 20.1 | 50.1 | 491 |  | 2020-09-17 15:14 | 44091.6349 | 20.1 | 50.1 | 491 |  |  | 2020-09-14 | B20474¦Courtroom #3¦¦Sep-17-2020 15:14
2020-09-17 15:14 | 44091.6349 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 265 |  | 1 | 18 | 54 | 404 | 23 | 47 | 415 |  | 2020-09-17 15:14 | 44091.6349 | 23 | 47 | 415 |  |  | 2020-09-14 | B19570¦265¦¦Sep-17-2020 15:14
2020-09-17 15:14 | 44091.635 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 West |  | 2 | 21.7 | 39.3 | 402 | 22.7 | 49 | 682 |  | 2020-09-17 15:14 | 44091.635 | 22.7 | 49 | 682 |  |  | 2020-09-14 | B10577¦Courtroom 1 West¦¦Sep-17-2020 15:14
2020-09-17 15:15 | 44091.6353 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 264 |  | 1 | 18 | 54 | 404 | 23 | 45 | 414 |  | 2020-09-17 15:15 | 44091.6353 | 23 | 45 | 414 |  |  | 2020-09-14 | B19570¦264¦¦Sep-17-2020 15:14
2020-09-17 15:15 | 44091.6354 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Interview room 402b |  | 0 | 20.6 | 33 | 405 | 22.6 | 39.1 | 472 |  | 2020-09-17 15:15 | 44091.6354 | 22.6 | 39.1 | 472 |  | caution | 2020-09-14 | B20367¦Interview room 402b¦¦Sep-17-2020 15:14
2020-09-17 15:15 | 44091.6355 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- W wall |  | 0 | 19 | 65 | 440 | 25 | 48 | 600 |  | 2020-09-17 15:15 | 44091.6355 | 25 | 48 | 600 |  |  | 2020-09-14 | B25548¦1- W wall¦¦Sep-17-2020 15:15
2020-09-17 15:15 | 44091.6356 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 Center |  | 0 | 21.7 | 39.3 | 402 | 22.5 |  | 648 |  | 2020-09-17 15:15 | 44091.6356 | 22.5 |  | 648 |  |  | 2020-09-14 | B10577¦Courtroom 1 Center¦¦Sep-17-2020 15:15
2020-09-17 15:15 | 44091.6356 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 260 |  | 1 | 18 | 54 | 404 | 23 | 45 | 412 |  | 2020-09-17 15:15 | 44091.6356 | 23 | 45 | 412 |  |  | 2020-09-14 | B19570¦260¦¦Sep-17-2020 15:15
2020-09-17 15:15 | 44091.6357 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 Center |  | 0 | 21.7 | 39.3 | 402 | 22.5 |  | 648 |  | 2020-09-17 15:15 | 44091.6357 | 22.5 |  | 648 |  |  | 2020-09-14 | B10577¦Courtroom 1 Center¦¦Sep-17-2020 15:15
2020-09-17 15:16 | 44091.6359 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 bench |  | 3 | 25.5 | 29.6 | 406 | 22.3 | 43.3 | 430 |  | 2020-09-17 15:16 | 44091.6359 | 22.3 | 43.3 | 430 |  |  | 2020-09-14 | B17477¦Courtroom 400 bench ¦¦Sep-17-2020 15:15
2020-09-17 15:16 | 44091.636 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 261 |  | 1 | 18 | 54 | 404 | 23 | 45 | 410 |  | 2020-09-17 15:16 | 44091.636 | 23 | 45 | 410 |  |  | 2020-09-14 | B19570¦261¦¦Sep-17-2020 15:15
2020-09-17 15:16 | 44091.6361 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Interview room 402a |  | 0 | 20.6 | 33 | 405 | 22.5 | 38.7 | 476 |  | 2020-09-17 15:16 | 44091.6361 | 22.5 | 38.7 | 476 |  | caution | 2020-09-14 | B20367¦Interview room 402a¦¦Sep-17-2020 15:15
2020-09-17 15:16 | 44091.6364 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 14 |  | 0 | 21 | 48 | 430 | 22 | 47 | 430 |  | 2020-09-17 15:16 | 44091.6364 | 22 | 47 | 430 |  |  | 2020-09-14 | B70740¦14¦¦Sep-17-2020 15:16
2020-09-17 15:17 | 44091.6365 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Hallway nw |  | 1 | 18 | 54 | 404 | 23 | 45 | 410 |  | 2020-09-17 15:17 | 44091.6365 | 23 | 45 | 410 |  |  | 2020-09-14 | B19570¦Hallway nw ¦¦Sep-17-2020 15:16
2020-09-17 15:17 | 44091.6367 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | S foyer |  | 0 | 19 | 65 | 440 | 25 | 48 | 610 |  | 2020-09-17 15:17 | 44091.6367 | 25 | 48 | 610 |  |  | 2020-09-14 | B25548¦S foyer¦¦Sep-17-2020 15:16
2020-09-17 15:17 | 44091.6369 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | FRONT HRPS |  | 0 | 21 | 48 | 430 | 22 | 43 | 420 |  | 2020-09-17 15:17 | 44091.6369 | 22 | 43 | 420 |  |  | 2020-09-14 | B70740¦FRONT HRPS¦¦Sep-17-2020 15:17
2020-09-17 15:17 | 44091.6369 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 4 interview room |  | 0 | 25.5 | 29.6 | 406 | 22.6 | 43.9 | 422 |  | 2020-09-17 15:17 | 44091.6369 | 22.6 | 43.9 | 422 |  |  | 2020-09-14 | B17477¦Level 4 interview room ¦¦Sep-17-2020 15:17
2020-09-17 15:18 | 44091.6374 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | COURT OFFICER |  | 0 | 21 | 48 | 430 | 22.2 | 38 | 460 |  | 2020-09-17 15:18 | 44091.6374 | 22.2 | 38 | 460 |  | caution | 2020-09-14 | B70740¦COURT OFFICER¦¦Sep-17-2020 15:17
2020-09-17 15:18 | 44091.6376 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Room 301 |  | 0 | 20.6 | 33 | 405 | 21.8 | 37 | 477 |  | 2020-09-17 15:18 | 44091.6376 | 21.8 | 37 | 477 |  | caution | 2020-09-14 | B20367¦Room 301¦¦Sep-17-2020 15:18
2020-09-17 15:19 | 44091.6379 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 4 ramp |  | 0 | 25.5 | 29.6 | 406 | 22.7 | 44.8 | 441 |  | 2020-09-17 15:19 | 44091.6379 | 22.7 | 44.8 | 441 |  |  | 2020-09-14 | B17477¦Level 4 ramp ¦¦Sep-17-2020 15:18
2020-09-17 15:19 | 44091.6379 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | CROWN ATORNEY |  | 0 | 21 | 48 | 430 | 22.5 | 38 | 440 |  | 2020-09-17 15:19 | 44091.6379 | 22.5 | 38 | 440 |  | caution | 2020-09-14 | B70740¦CROWN ATORNEY¦¦Sep-17-2020 15:18
2020-09-17 15:19 | 44091.6379 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | N foyer |  | 0 | 19 | 65 | 440 | 24 | 49 | 580 |  | 2020-09-17 15:19 | 44091.6379 | 24 | 49 | 580 |  |  | 2020-09-14 | B25548¦N foyer¦¦Sep-17-2020 15:18
2020-09-17 15:19 | 44091.6384 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Trial office |  | 3 | 22 | 31.2 | 396 | 21.5 | 44.8 | 498 |  | 2020-09-17 15:19 | 44091.6384 | 21.5 | 44.8 | 498 |  |  | 2020-09-14 | B20474¦Trial office¦¦Sep-17-2020 15:19
2020-09-17 15:19 | 44091.6384 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | CROWN OFFICE 1 |  | 0 | 21 | 48 | 430 | 22.5 | 42 | 440 |  | 2020-09-17 15:19 | 44091.6384 | 22.5 | 42 | 440 |  |  | 2020-09-14 | B70740¦CROWN OFFICE 1¦¦Sep-17-2020 15:19
2020-09-17 15:20 | 44091.6386 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 seating area |  | 0 | 25.5 | 29.6 | 406 | 22.9 | 44.4 | 453 |  | 2020-09-17 15:20 | 44091.6386 | 22.9 | 44.4 | 453 |  |  | 2020-09-14 | B17477¦Level 5 seating area ¦¦Sep-17-2020 15:19
2020-09-17 15:20 | 44091.6388 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN WR CORR |  | 0 | 21 | 48 | 430 | 22 | 43 | 420 |  | 2020-09-17 15:20 | 44091.6388 | 22 | 43 | 420 |  |  | 2020-09-14 | B70740¦MAIN WR CORR¦¦Sep-17-2020 15:19
2020-09-17 15:20 | 44091.6392 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 13 |  | 0 | 21 | 48 | 430 | 22.5 | 45 | 450 |  | 2020-09-17 15:20 | 44091.6392 | 22.5 | 45 | 450 |  |  | 2020-09-14 | B70740¦13¦¦Sep-17-2020 15:20
2020-09-17 15:21 | 44091.6394 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 19 | 65 | 440 | 25 | 49 | 590 |  | 2020-09-17 15:21 | 44091.6394 | 25 | 49 | 590 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-17-2020 15:20
2020-09-17 15:21 | 44091.6398 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | SEATING 13 |  | 0 | 21 | 48 | 430 | 22.2 | 46 | 520 |  | 2020-09-17 15:21 | 44091.6398 | 22.2 | 46 | 520 |  |  | 2020-09-14 | B70740¦SEATING 13¦¦Sep-17-2020 15:21
2020-09-17 15:21 | 44091.6398 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 seating area 2 |  | 0 | 25.5 | 29.6 | 406 | 22.8 | 44.1 | 447 |  | 2020-09-17 15:21 | 44091.6398 | 22.8 | 44.1 | 447 |  |  | 2020-09-14 | B17477¦Level 5 seating area 2¦¦Sep-17-2020 15:21
2020-09-17 15:22 | 44091.6402 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Judges panel |  | 0 | 21.2 | 41.5 | 413 | 21.5 | 52 | 580 |  | 2020-09-17 15:22 | 44091.6402 | 21.5 | 52 | 580 |  |  | 2020-09-14 | B25039¦Judges panel¦¦Sep-17-2020 15:21
2020-09-17 15:22 | 44091.6404 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | SEATING 12 |  | 0 | 21 | 48 | 430 | 22.3 | 46 | 500 |  | 2020-09-17 15:22 | 44091.6404 | 22.3 | 46 | 500 |  |  | 2020-09-14 | B70740¦SEATING 12¦¦Sep-17-2020 15:22
2020-09-17 15:23 | 44091.6408 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Front desk |  | 4 | 22 | 31.2 | 396 | 20.3 | 50.2 | 572 |  | 2020-09-17 15:23 | 44091.6408 | 20.3 | 50.2 | 572 |  |  | 2020-09-14 | B20474¦Front desk¦¦Sep-17-2020 15:22
2020-09-17 15:23 | 44091.6409 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 12 |  | 0 | 21 | 48 | 430 | 22.2 | 47 | 500 |  | 2020-09-17 15:23 | 44091.6409 | 22.2 | 47 | 500 |  |  | 2020-09-14 | B70740¦12¦¦Sep-17-2020 15:22
2020-09-17 15:23 | 44091.6411 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Manage if operations seating area |  | 0 | 25.5 | 29.6 | 406 | 23 | 44.3 | 435 |  | 2020-09-17 15:23 | 44091.6411 | 23 | 44.3 | 435 |  |  | 2020-09-14 | B17477¦Manage if operations seating area ¦¦Sep-17-2020 15:23
2020-09-17 15:23 | 44091.6412 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Courtroom front east |  | 0 | 21.2 | 41.5 | 413 | 21.1 | 53 | 583 |  | 2020-09-17 15:23 | 44091.6412 | 21.1 | 53 | 583 |  |  | 2020-09-14 | B25039¦Courtroom front east¦¦Sep-17-2020 15:23
2020-09-17 15:23 | 44091.6413 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st floor Hall |  | 2 | 15.8 | 45.1 | 402 | 20 | 45.5 | 498 | no | 2020-09-17 15:23 | 44091.6413 | 20 | 45.5 | 498 |  |  | 2020-09-14 | B70496¦1st floor Hall¦¦Sep-17-2020 15:23
2020-09-17 15:24 | 44091.6414 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN AREA |  | 4 | 21 | 48 | 430 | 22.7 | 46 | 500 |  | 2020-09-17 15:24 | 44091.6414 | 22.7 | 46 | 500 |  |  | 2020-09-14 | B70740¦MAIN AREA¦¦Sep-17-2020 15:23
2020-09-17 15:24 | 44091.6416 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- N wall |  | 0 | 19 | 65 | 440 | 25 | 49 | 590 |  | 2020-09-17 15:24 | 44091.6416 | 25 | 49 | 590 |  |  | 2020-09-14 | B25548¦1- N wall¦¦Sep-17-2020 15:23
2020-09-17 15:24 | 44091.6417 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Hallway |  | 0 | 20.6 | 33 | 405 | 21.8 | 41.9 | 474 |  | 2020-09-17 15:24 | 44091.6417 | 21.8 | 41.9 | 474 |  |  | 2020-09-14 | B20367¦Hallway ¦¦Sep-17-2020 15:24
2020-09-17 15:24 | 44091.6418 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | NAIN OFFICE |  | 3 | 21 | 48 | 430 | 22.7 | 47 | 500 |  | 2020-09-17 15:24 | 44091.6418 | 22.7 | 47 | 500 |  |  | 2020-09-14 | B70740¦NAIN OFFICE¦¦Sep-17-2020 15:24
2020-09-17 15:24 | 44091.642 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st floor seating |  | 1 | 15.8 | 45.1 | 402 | 20.8 | 43.1 | 460 | no | 2020-09-17 15:24 | 44091.642 | 20.8 | 43.1 | 460 |  |  | 2020-09-14 | B70496¦1st floor seating¦¦Sep-17-2020 15:24
2020-09-17 15:24 | 44091.642 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Manage if operations seating area 2 |  | 0 | 25.5 | 29.6 | 406 | 22.8 | 44.7 | 432 |  | 2020-09-17 15:24 | 44091.642 | 22.8 | 44.7 | 432 |  |  | 2020-09-14 | B17477¦Manage if operations seating area 2 ¦¦Sep-17-2020 15:24
2020-09-17 15:25 | 44091.6423 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Lunch room |  | 0 | 20.6 | 33 | 405 | 21.6 | 50.3 | 589 |  | 2020-09-17 15:25 | 44091.6423 | 21.6 | 50.3 | 589 |  |  | 2020-09-14 | B90631¦Lunch room ¦¦Sep-17-2020 15:24
2020-09-17 15:25 | 44091.6424 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Courtroom front west |  | 0 | 21.2 | 41.5 | 413 | 21.2 | 53.3 | 579 |  | 2020-09-17 15:25 | 44091.6424 | 21.2 | 53.3 | 579 |  |  | 2020-09-14 | B25039¦Courtroom front west¦¦Sep-17-2020 15:25
2020-09-17 15:25 | 44091.6426 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 101 |  | 4 | 15.8 | 45.1 | 402 | 22.1 | 38.2 | 445 | no | 2020-09-17 15:25 | 44091.6426 | 22.1 | 38.2 | 445 |  | caution | 2020-09-14 | B70496¦101¦¦Sep-17-2020 15:25
2020-09-17 15:26 | 44091.6428 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 hallway |  | 0 | 25.5 | 29.6 | 406 | 22.6 | 44.6 | 427 |  | 2020-09-17 15:26 | 44091.6428 | 22.6 | 44.6 | 427 |  |  | 2020-09-14 | B17477¦Level 5 hallway ¦¦Sep-17-2020 15:25
2020-09-17 15:26 | 44091.6432 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Courtroom rear west |  | 0 | 21.2 | 41.5 | 413 | 21.1 | 53.6 | 582 |  | 2020-09-17 15:26 | 44091.6432 | 21.1 | 53.6 | 582 |  |  | 2020-09-14 | B25039¦Courtroom rear west¦¦Sep-17-2020 15:26
2020-09-17 15:26 | 44091.6434 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 102 |  | 3 | 15.8 | 45.1 | 402 | 22.6 | 35.7 | 467 | no | 2020-09-17 15:26 | 44091.6434 | 22.6 | 35.7 | 467 |  | caution | 2020-09-14 | B70496¦102¦¦Sep-17-2020 15:26
2020-09-17 15:27 | 44091.6437 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- N wall |  | 0 | 19 | 65 | 440 | 25 | 50 | 605 |  | 2020-09-17 15:27 | 44091.6437 | 25 | 50 | 605 |  |  | 2020-09-14 | B25548¦1- N wall¦¦Sep-17-2020 15:26
2020-09-17 15:27 | 44091.6437 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom1 |  | 1 | 22 | 31.2 | 396 | 20.1 | 50.9 | 595 |  | 2020-09-17 15:27 | 44091.6437 | 20.1 | 50.9 | 595 |  |  | 2020-09-14 | B20474¦Waiting area courtroom1¦¦Sep-17-2020 15:26
2020-09-17 15:27 | 44091.6438 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 hallway 2 |  | 0 | 25.5 | 29.6 | 406 | 22.3 | 45.4 | 429 |  | 2020-09-17 15:27 | 44091.6438 | 22.3 | 45.4 | 429 |  |  | 2020-09-14 | B17477¦Level 5 hallway 2 ¦¦Sep-17-2020 15:27
2020-09-17 15:27 | 44091.6439 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 102 |  | 3 | 15.8 | 45.1 | 402 | 22.9 | 36.1 | 455 | no | 2020-09-17 15:27 | 44091.6439 | 22.9 | 36.1 | 455 |  | caution | 2020-09-14 | B70496¦102¦¦Sep-17-2020 15:27
2020-09-17 15:28 | 44091.6444 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | Stairwell |  | 1 | 15.8 | 45.1 | 402 | 22.4 | 42.3 | 588 | no | 2020-09-17 15:28 | 44091.6444 | 22.4 | 42.3 | 588 |  |  | 2020-09-14 | B70496¦Stairwell¦¦Sep-17-2020 15:27
2020-09-17 15:28 | 44091.6445 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Courtroom rear east |  | 0 | 21.2 | 41.5 | 413 | 21.2 | 53.4 | 581 |  | 2020-09-17 15:28 | 44091.6445 | 21.2 | 53.4 | 581 |  |  | 2020-09-14 | B25039¦Courtroom rear east¦¦Sep-17-2020 15:28
2020-09-17 15:28 | 44091.6446 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 hallway 3 |  | 0 | 25.5 | 29.6 | 406 | 22.1 | 46.3 | 428 |  | 2020-09-17 15:28 | 44091.6446 | 22.1 | 46.3 | 428 |  |  | 2020-09-14 | B17477¦Level 5 hallway 3 ¦¦Sep-17-2020 15:28
2020-09-17 15:29 | 44091.645 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Case management |  | 4 | 20.6 | 33 | 405 | 22.1 | 50.6 | 1135 |  | 2020-09-17 15:29 | 44091.645 | 22.1 | 50.6 | 1135 |  |  | 2020-09-14 | B90631¦Case management ¦¦Sep-17-2020 15:28
2020-09-17 15:29 | 44091.645 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- N wall |  | 0 | 19 | 65 | 440 | 25 | 48 | 600 |  | 2020-09-17 15:29 | 44091.645 | 25 | 48 | 600 |  |  | 2020-09-14 | B25548¦1- N wall¦¦Sep-17-2020 15:28
2020-09-17 15:29 | 44091.645 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 2nd floor Elevator Lobby |  | 1 | 15.8 | 45.1 | 402 | 22.6 | 39.4 | 513 | no | 2020-09-17 15:29 | 44091.645 | 22.6 | 39.4 | 513 |  | caution | 2020-09-14 | B70496¦2nd floor Elevator Lobby¦¦Sep-17-2020 15:28
2020-09-17 15:30 | 44091.6455 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Waiting room |  | 0 | 21.2 | 41.5 | 413 | 21.3 | 53.8 | 581 |  | 2020-09-17 15:30 | 44091.6455 | 21.3 | 53.8 | 581 |  |  | 2020-09-14 | B25039¦Waiting room¦¦Sep-17-2020 15:29
2020-09-17 15:30 | 44091.6455 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 204 |  | 1 | 15.8 | 45.1 | 402 | 22 | 37 | 460 | no | 2020-09-17 15:30 | 44091.6455 | 22 | 37 | 460 |  | caution | 2020-09-14 | B70496¦204¦¦Sep-17-2020 15:29
2020-09-17 15:30 | 44091.6457 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 waiting room |  | 0 | 25.5 | 29.6 | 406 | 22 | 46.3 | 428 |  | 2020-09-17 15:30 | 44091.6457 | 22 | 46.3 | 428 |  |  | 2020-09-14 | B17477¦Level 5 waiting room ¦¦Sep-17-2020 15:29
2020-09-17 15:30 | 44091.6461 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 204 |  | 1 | 15.8 | 45.1 | 402 | 21.8 | 37.2 | 429 | no | 2020-09-17 15:30 | 44091.6461 | 21.8 | 37.2 | 429 |  | caution | 2020-09-14 | B70496¦204¦¦Sep-17-2020 15:30
2020-09-17 15:31 | 44091.6462 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Crown office 1 |  | 0 | 20.6 | 33 | 405 | 22.8 | 49.3 | 920 |  | 2020-09-17 15:31 | 44091.6462 | 22.8 | 49.3 | 920 |  |  | 2020-09-14 | B90631¦Crown office 1¦¦Sep-17-2020 15:30
2020-09-17 15:31 | 44091.6463 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Main office |  | 6 | 22 | 31.2 | 396 | 21 | 49.1 | 558 | courtroom #4 was in session | 2020-09-17 15:31 | 44091.6463 | 21 | 49.1 | 558 |  |  | 2020-09-14 | B20474¦Main office¦¦Sep-17-2020 15:30
2020-09-17 15:31 | 44091.6463 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- N wall |  | 0 | 19 | 65 | 440 | 25 | 49 | 590 |  | 2020-09-17 15:31 | 44091.6463 | 25 | 49 | 590 |  |  | 2020-09-14 | B25548¦1- N wall¦¦Sep-17-2020 15:30
2020-09-17 15:31 | 44091.6465 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Level 5 waiting room 2 |  | 0 | 25.5 | 29.6 | 406 | 22.2 | 46 | 423 |  | 2020-09-17 15:31 | 44091.6465 | 22.2 | 46 | 423 |  |  | 2020-09-14 | B17477¦Level 5 waiting room 2¦¦Sep-17-2020 15:30
2020-09-17 15:31 | 44091.6465 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Main hall |  | 0 | 21.2 | 41.5 | 413 | 22.1 | 51.3 | 580 |  | 2020-09-17 15:31 | 44091.6465 | 22.1 | 51.3 | 580 |  |  | 2020-09-14 | B25039¦Main hall¦¦Sep-17-2020 15:30
2020-09-17 15:31 | 44091.6466 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 2nd floor hallway |  | 1 | 15.8 | 45.1 | 402 | 22 | 39.7 | 429 | no | 2020-09-17 15:31 | 44091.6466 | 22 | 39.7 | 429 |  | caution | 2020-09-14 | B70496¦2nd floor hallway¦¦Sep-17-2020 15:31
2020-09-17 15:32 | 44091.6474 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Administration office |  | 0 | 20.6 | 33 | 405 | 22.8 | 50.6 | 1051 |  | 2020-09-17 15:32 | 44091.6474 | 22.8 | 50.6 | 1051 |  |  | 2020-09-14 | B90631¦Administration office ¦¦Sep-17-2020 15:32
2020-09-17 15:33 | 44091.6478 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Mediation room 2 |  | 0 | 21.2 | 41.5 | 413 | 21.7 | 53.1 | 580 |  | 2020-09-17 15:33 | 44091.6478 | 21.7 | 53.1 | 580 |  |  | 2020-09-14 | B25039¦Mediation room 2¦¦Sep-17-2020 15:32
2020-09-17 15:34 | 44091.6483 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Crown office 2 |  | 0 | 20.6 | 33 | 405 | 22.5 | 52.7 | 1061 |  | 2020-09-17 15:34 | 44091.6483 | 22.5 | 52.7 | 1061 |  |  | 2020-09-14 | B90631¦Crown office 2¦¦Sep-17-2020 15:33
2020-09-17 15:34 | 44091.6483 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 19 | 65 | 440 | 25 | 49 | 595 |  | 2020-09-17 15:34 | 44091.6483 | 25 | 49 | 595 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-17-2020 15:33
2020-09-17 15:34 | 44091.6487 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Mediation room 1 |  | 0 | 21.2 | 41.5 | 413 | 21.8 | 52.9 | 575 |  | 2020-09-17 15:34 | 44091.6487 | 21.8 | 52.9 | 575 |  |  | 2020-09-14 | B25039¦Mediation room 1¦¦Sep-17-2020 15:34
2020-09-17 15:34 | 44091.6487 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom office |  | 4 | 25.5 | 29.6 | 406 | 22.3 | 46.3 | 476 |  | 2020-09-17 15:34 | 44091.6487 | 22.3 | 46.3 | 476 |  |  | 2020-09-14 | B17477¦Courtroom office ¦¦Sep-17-2020 15:34
2020-09-17 15:34 | 44091.6489 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 203 |  | 1 | 15.8 | 45.1 | 402 | 21.2 | 42 | 497 | no | 2020-09-17 15:34 | 44091.6489 | 21.2 | 42 | 497 |  |  | 2020-09-14 | B70496¦203¦¦Sep-17-2020 15:34
2020-09-17 15:35 | 44091.6494 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 202 |  | 1 | 15.8 | 45.1 | 402 | 21.6 | 38.8 | 467 | No | 2020-09-17 15:35 | 44091.6494 | 21.6 | 38.8 | 467 |  | caution | 2020-09-14 | B70496¦202¦¦Sep-17-2020 15:35
2020-09-17 15:35 | 44091.6495 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 19 | 65 | 440 | 24 | 50 | 580 |  | 2020-09-17 15:35 | 44091.6495 | 24 | 50 | 580 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-17-2020 15:35
2020-09-17 15:36 | 44091.6497 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Washroom |  | 0 | 21.2 | 41.5 | 413 | 22 | 53.1 | 579 |  | 2020-09-17 15:36 | 44091.6497 | 22 | 53.1 | 579 |  |  | 2020-09-14 | B25039¦Washroom¦¦Sep-17-2020 15:35
2020-09-17 15:36 | 44091.6499 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 201 |  | 1 | 15.8 | 45.1 | 402 | 21.8 | 39.8 | 473 | no | 2020-09-17 15:36 | 44091.6499 | 21.8 | 39.8 | 473 |  | caution | 2020-09-14 | B70496¦201¦¦Sep-17-2020 15:35
2020-09-17 15:36 | 44091.6501 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 201 |  | 1 | 15.8 | 45.1 | 402 | 21.8 | 39.8 | 473 | no | 2020-09-17 15:36 | 44091.6501 | 21.8 | 39.8 | 473 |  | caution | 2020-09-14 | B70496¦201¦¦Sep-17-2020 15:36
2020-09-17 15:36 | 44091.6502 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Vwap waiting room |  | 0 | 20.6 | 33 | 405 | 21.3 | 50.5 | 583 |  | 2020-09-17 15:36 | 44091.6502 | 21.3 | 50.5 | 583 |  |  | 2020-09-14 | B90631¦Vwap waiting room ¦¦Sep-17-2020 15:36
2020-09-17 15:36 | 44091.6503 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 201 |  | 1 | 15.8 | 45.1 | 402 | 21.8 | 39.8 | 473 | no | 2020-09-17 15:36 | 44091.6503 | 21.8 | 39.8 | 473 |  | caution | 2020-09-14 | B70496¦201¦¦Sep-17-2020 15:36
2020-09-17 15:37 | 44091.6504 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 19 | 65 | 440 | 24 | 50 | 580 |  | 2020-09-17 15:37 | 44091.6504 | 24 | 50 | 580 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-17-2020 15:36
2020-09-17 15:37 | 44091.6505 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Emergency exit |  | 0 | 21.2 | 41.5 | 413 | 22.2 | 51.2 | 584 |  | 2020-09-17 15:37 | 44091.6505 | 22.2 | 51.2 | 584 |  |  | 2020-09-14 | B25039¦Emergency exit¦¦Sep-17-2020 15:36
2020-09-17 15:37 | 44091.6505 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom services |  | 0 | 25.5 | 29.6 | 496 | 22.3 | 46.7 | 452 |  | 2020-09-17 15:37 | 44091.6505 | 22.3 | 46.7 | 452 |  |  | 2020-09-14 | B17477¦Courtroom services ¦¦Sep-17-2020 15:36
2020-09-17 15:37 | 44091.6507 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | Administration Office |  | 5 | 15.8 | 45.1 | 402 | 21.8 | 39.8 | 473 | no | 2020-09-17 15:37 | 44091.6507 | 21.8 | 39.8 | 473 |  | caution | 2020-09-14 | B70496¦Administration Office¦¦Sep-17-2020 15:37
2020-09-17 15:37 | 44091.6509 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Judges foyers |  | 0 | 20.6 | 33 | 405 | 21.6 | 51.6 | 594 |  | 2020-09-17 15:37 | 44091.6509 | 21.6 | 51.6 | 594 |  |  | 2020-09-14 | B90631¦Judges foyers ¦¦Sep-17-2020 15:37
2020-09-17 15:38 | 44091.6512 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 19 | 65 | 440 | 24 | 51 | 580 |  | 2020-09-17 15:38 | 44091.6512 | 24 | 51 | 580 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-17-2020 15:37
2020-09-17 15:38 | 44091.6513 | AINSWORTH | B25039 | B25039 - 590 Rossland Rd E - Whitby | Common area |  | 0 | 21.2 | 41.5 | 413 | 22.2 | 50.8 | 590 |  | 2020-09-17 15:38 | 44091.6513 | 22.2 | 50.8 | 590 |  |  | 2020-09-14 | B25039¦Common area¦¦Sep-17-2020 15:37
2020-09-17 15:38 | 44091.6513 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | Outside customer service Entrance |  | 1 | 15.8 | 45.1 | 402 | 16.3 | 48 | 395 | no | 2020-09-17 15:38 | 44091.6513 | 16.3 | 48 | 395 |  |  | 2020-09-14 | B70496¦Outside customer service Entrance¦¦Sep-17-2020 15:37
2020-09-17 15:38 | 44091.6516 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Judges chamber |  | 0 | 20.6 | 33 | 405 | 21.5 | 50 | 568 |  | 2020-09-17 15:38 | 44091.6516 | 21.5 | 50 | 568 |  |  | 2020-09-14 | B90631¦Judges chamber ¦¦Sep-17-2020 15:38
2020-09-17 15:39 | 44091.6518 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 waiting area |  | 1 | 20 | 38 | 363 | 22 | 40 | 369 |  | 2020-09-17 15:39 | 44091.6518 | 22 | 40 | 369 |  | caution | 2020-09-14 | B20772¦H9 waiting area¦¦Sep-17-2020 15:38
2020-09-17 15:39 | 44091.6522 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 19 | 65 | 440 | 24 | 51 | 590 |  | 2020-09-17 15:39 | 44091.6522 | 24 | 51 | 590 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-17-2020 15:39
2020-09-17 15:39 | 44091.6524 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom |  | 0 | 20.6 | 33 | 405 | 21.8 | 50.9 | 650 |  | 2020-09-17 15:39 | 44091.6524 | 21.8 | 50.9 | 650 |  |  | 2020-09-14 | B90631¦Courtroom ¦¦Sep-17-2020 15:39
2020-09-17 15:40 | 44091.653 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- S wall |  | 0 | 19 | 65 | 440 | 24 | 51 | 585 |  | 2020-09-17 15:40 | 44091.653 | 24 | 51 | 585 |  |  | 2020-09-14 | B25548¦2- S wall¦¦Sep-17-2020 15:40
2020-09-17 15:41 | 44091.6532 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 rear left |  | 1 | 20 | 38 | 363 | 22 | 40 | 369 |  | 2020-09-17 15:41 | 44091.6532 | 22 | 40 | 369 |  | caution | 2020-09-14 | B20772¦H9 rear left ¦¦Sep-17-2020 15:40
2020-09-17 15:41 | 44091.6537 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom waiting room |  | 0 | 20.6 | 33 | 405 | 21.4 | 49.7 | 820 |  | 2020-09-17 15:41 | 44091.6537 | 21.4 | 49.7 | 820 |  |  | 2020-09-14 | B90631¦Courtroom waiting room ¦¦Sep-17-2020 15:41
2020-09-17 15:42 | 44091.6539 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 19 | 65 | 440 | 24 | 51 | 640 |  | 2020-09-17 15:42 | 44091.6539 | 24 | 51 | 640 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-17-2020 15:41
2020-09-17 15:42 | 44091.654 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 rear right |  | 1 | 20 | 38 | 363 | 22 | 40 | 370 |  | 2020-09-17 15:42 | 44091.654 | 22 | 40 | 370 |  | caution | 2020-09-14 | B20772¦H9 rear right¦¦Sep-17-2020 15:41
2020-09-17 15:43 | 44091.6551 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 defendant |  | 1 | 20 | 38 | 363 | 23 | 40 | 367 |  | 2020-09-17 15:43 | 44091.6551 | 23 | 40 | 367 |  | caution | 2020-09-14 | B20772¦H9 defendant¦¦Sep-17-2020 15:43
2020-09-17 15:44 | 44091.6553 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-W wall |  | 0 | 19 | 65 | 440 | 24 | 54 | 620 |  | 2020-09-17 15:44 | 44091.6553 | 24 | 54 | 620 |  |  | 2020-09-14 | B25548¦2-W wall¦¦Sep-17-2020 15:43
2020-09-17 15:45 | 44091.656 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 plaintiff |  | 1 | 20 | 38 | 363 | 23 | 40 | 371 |  | 2020-09-17 15:45 | 44091.656 | 23 | 40 | 371 |  | caution | 2020-09-14 | B20772¦H9 plaintiff¦¦Sep-17-2020 15:44
2020-09-17 15:45 | 44091.6564 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-W wall |  | 0 | 19 | 65 | 440 | 24 | 50 | 590 |  | 2020-09-17 15:45 | 44091.6564 | 24 | 50 | 590 |  |  | 2020-09-14 | B25548¦2-W wall¦¦Sep-17-2020 15:45
2020-09-17 15:46 | 44091.6567 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 judge |  | 1 | 20 | 38 | 363 | 23 | 40 | 371 |  | 2020-09-17 15:46 | 44091.6567 | 23 | 40 | 371 |  | caution | 2020-09-14 | B20772¦H9 judge¦¦Sep-17-2020 15:45
2020-09-17 15:47 | 44091.6579 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-W wall |  | 0 | 19 | 65 | 440 | 24 | 51 | 595 |  | 2020-09-17 15:47 | 44091.6579 | 24 | 51 | 595 |  |  | 2020-09-14 | B25548¦2-W wall¦¦Sep-17-2020 15:47
2020-09-17 15:48 | 44091.6584 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 judge |  | 1 | 20 | 38 | 363 | 23 | 38 | 371 |  | 2020-09-17 15:48 | 44091.6584 | 23 | 38 | 371 |  | caution | 2020-09-14 | B20772¦H15 judge¦¦Sep-17-2020 15:48
2020-09-17 15:49 | 44091.6592 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- N wall |  | 0 | 19 | 65 | 440 | 24 | 51 | 640 |  | 2020-09-17 15:49 | 44091.6592 | 24 | 51 | 640 |  |  | 2020-09-14 | B25548¦2- N wall¦¦Sep-17-2020 15:49
2020-09-17 15:49 | 44091.6593 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 plaintiff |  | 1 | 20 | 38 | 363 | 23 | 38 | 370 |  | 2020-09-17 15:49 | 44091.6593 | 23 | 38 | 370 |  | caution | 2020-09-14 | B20772¦H15 plaintiff¦¦Sep-17-2020 15:49
2020-09-17 15:51 | 44091.6602 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- N wall |  | 0 | 19 | 65 | 440 | 24 | 53 | 740 |  | 2020-09-17 15:51 | 44091.6602 | 24 | 53 | 740 |  |  | 2020-09-14 | B25548¦2- N wall¦¦Sep-17-2020 15:50
2020-09-17 15:51 | 44091.6603 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 defendant |  | 1 | 20 | 38 | 363 | 22 | 39 | 371 |  | 2020-09-17 15:51 | 44091.6603 | 22 | 39 | 371 |  | caution | 2020-09-14 | B20772¦H15 defendant¦¦Sep-17-2020 15:50
2020-09-17 15:53 | 44091.6615 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 19 | 65 | 440 | 25 | 53 | 620 |  | 2020-09-17 15:53 | 44091.6615 | 25 | 53 | 620 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-17-2020 15:52
2020-09-17 15:53 | 44091.662 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 rear right |  | 1 | 20 | 38 | 363 | 22 | 38 | 371 |  | 2020-09-17 15:53 | 44091.662 | 22 | 38 | 371 |  | caution | 2020-09-14 | B20772¦H15 rear right¦¦Sep-17-2020 15:53
2020-09-17 15:54 | 44091.6627 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 rear left |  | 1 | 20 | 38 | 363 | 22 | 38 | 375 |  | 2020-09-17 15:54 | 44091.6627 | 22 | 38 | 375 |  | caution | 2020-09-14 | B20772¦H15 rear left¦¦Sep-17-2020 15:54
2020-09-17 15:54 | 44091.6628 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 19 | 65 | 440 | 24 | 51 | 620 |  | 2020-09-17 15:54 | 44091.6628 | 24 | 51 | 620 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-17-2020 15:54
2020-09-17 15:56 | 44091.6638 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- N wall |  | 0 | 19 | 65 | 440 | 24 | 51 | 615 |  | 2020-09-17 15:56 | 44091.6638 | 24 | 51 | 615 |  |  | 2020-09-14 | B25548¦2- N wall¦¦Sep-17-2020 15:55
2020-09-17 15:56 | 44091.6638 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 waiting area |  | 1 | 20 | 38 | 363 | 22 | 40 | 373 |  | 2020-09-17 15:56 | 44091.6638 | 22 | 40 | 373 |  | caution | 2020-09-14 | B20772¦H15 waiting area ¦¦Sep-17-2020 15:55
2020-09-17 15:57 | 44091.6646 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 19 | 65 | 440 | 24 | 51 | 610 |  | 2020-09-17 15:57 | 44091.6646 | 24 | 51 | 610 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-17-2020 15:56
2020-09-17 15:58 | 44091.6656 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-E wall |  | 0 | 19 | 65 | 440 | 24 | 51 | 605 |  | 2020-09-17 15:58 | 44091.6656 | 24 | 51 | 605 |  |  | 2020-09-14 | B25548¦2-E wall¦¦Sep-17-2020 15:58
2020-09-17 15:59 | 44091.6662 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 rear right |  | 1 | 20 | 38 | 363 | 23 | 40 | 372 |  | 2020-09-17 15:59 | 44091.6662 | 23 | 40 | 372 |  | caution | 2020-09-14 | B20772¦H12 rear right ¦¦Sep-17-2020 15:59
2020-09-17 16:00 | 44091.6665 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- E wall |  | 0 | 19 | 65 | 440 | 24 | 51 | 630 |  | 2020-09-17 16:00 | 44091.6665 | 24 | 51 | 630 |  |  | 2020-09-14 | B25548¦1- E wall¦¦Sep-17-2020 15:59
2020-09-17 16:01 | 44091.6672 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 rear left |  | 1 | 20 | 38 | 363 | 23 | 39 | 370 |  | 2020-09-17 16:01 | 44091.6672 | 23 | 39 | 370 |  | caution | 2020-09-14 | B20772¦H12 rear left¦¦Sep-17-2020 16:00
2020-09-17 16:02 | 44091.6677 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-E wall |  | 0 | 19 | 65 | 440 | 24 | 53 | 630 |  | 2020-09-17 16:02 | 44091.6677 | 24 | 53 | 630 |  |  | 2020-09-14 | B25548¦2-E wall¦¦Sep-17-2020 16:01
2020-09-17 16:02 | 44091.6681 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 plaintiff |  | 1 | 20 | 38 | 363 | 23 | 39 | 371 |  | 2020-09-17 16:02 | 44091.6681 | 23 | 39 | 371 |  | caution | 2020-09-14 | B20772¦H12 plaintiff¦¦Sep-17-2020 16:02
2020-09-17 16:03 | 44091.6691 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | Mediation room |  | 0 | 19 | 65 | 440 | 24 | 50 | 610 |  | 2020-09-17 16:04 | 44091.6691 | 24 | 50 | 610 |  |  | 2020-09-14 | B25548¦Mediation room¦¦Sep-17-2020 16:03
2020-09-17 16:05 | 44091.6698 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 defendant |  | 1 | 20 | 38 | 363 | 23 | 40 | 373 |  | 2020-09-17 16:05 | 44091.6698 | 23 | 40 | 373 |  | caution | 2020-09-14 | B20772¦H12 defendant ¦¦Sep-17-2020 16:04
2020-09-17 16:06 | 44091.6705 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 judge |  | 1 | 20 | 38 | 363 | 24 | 37 | 374 |  | 2020-09-17 16:06 | 44091.6705 | 24 | 37 | 374 |  | caution | 2020-09-14 | B20772¦H12 judge ¦¦Sep-17-2020 16:05
2020-09-17 16:08 | 44091.6725 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 retiring room |  | 1 | 20 | 38 | 363 | 23 | 38 | 366 |  | 2020-09-17 16:08 | 44091.6725 | 23 | 38 | 366 |  | caution | 2020-09-14 | B20772¦H12 retiring room¦¦Sep-17-2020 16:08
2020-09-17 16:10 | 44091.6735 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 retiring room |  | 1 | 20 | 38 | 363 | 23 | 38 | 368 |  | 2020-09-17 16:10 | 44091.6735 | 23 | 38 | 368 |  | caution | 2020-09-14 | B20772¦H11 retiring room¦¦Sep-17-2020 16:09
2020-09-17 16:11 | 44091.6744 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 judge |  | 1 | 20 | 38 | 363 | 23 | 37 | 369 |  | 2020-09-17 16:11 | 44091.6744 | 23 | 37 | 369 |  | caution | 2020-09-14 | B20772¦H11 judge ¦¦Sep-17-2020 16:11
2020-09-17 16:13 | 44091.6759 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby1 |  | 0 | 19.5 | 36 | 388 | 21.7 | 45.9 | 416 |  | 2020-09-17 16:13 | 44091.6759 | 21.7 | 45.9 | 416 |  |  | 2020-09-14 | Pearso¦Lobby1¦¦Sep-17-2020 16:13
2020-09-17 16:14 | 44091.6764 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 2 |  | 0 | 19.5 | 36 | 388 | 21.3 | 43.2 | 414 |  | 2020-09-17 16:14 | 44091.6764 | 21.3 | 43.2 | 414 |  |  | 2020-09-14 | Pearso¦Lobby 2 ¦¦Sep-17-2020 16:14
2020-09-17 16:15 | 44091.6768 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 plaintiff |  | 1 | 20 | 38 | 363 | 23 | 37 | 367 |  | 2020-09-17 16:15 | 44091.6768 | 23 | 37 | 367 |  | caution | 2020-09-14 | B20772¦H11 plaintiff¦¦Sep-17-2020 16:14
2020-09-17 16:15 | 44091.677 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 3 |  | 0 | 19.5 | 36 | 388 | 20.5 | 44 | 404 |  | 2020-09-17 16:15 | 44091.677 | 20.5 | 44 | 404 |  |  | 2020-09-14 | Pearso¦Lobby 3¦¦Sep-17-2020 16:14
2020-09-17 16:16 | 44091.6776 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom #1 |  | 2 | 24 | 24.8 | 388 | 22 | 29.5 | 432 |  | 2020-09-17 16:16 | 44091.6776 | 22 | 29.5 | 432 |  | low | 2020-09-14 | B21554¦Courtroom #1¦¦Sep-17-2020 16:15
2020-09-17 16:16 | 44091.6776 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Policeroom 1 |  | 0 | 19.5 | 36 | 388 | 20.8 | 42.3 | 42.3 | 400 | 2020-09-17 16:16 | 44091.6776 | 20.8 | 42.3 | 42.3 |  |  | 2020-09-14 | Pearso¦Policeroom 1¦¦Sep-17-2020 16:15
2020-09-17 16:16 | 44091.6779 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 defendant |  | 1 | 20 | 38 | 363 | 23 | 37 | 373 |  | 2020-09-17 16:16 | 44091.6779 | 23 | 37 | 373 |  | caution | 2020-09-14 | B20772¦H11 defendant¦¦Sep-17-2020 16:16
2020-09-17 16:17 | 44091.6781 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Policeroom 2 |  | 0 | 19.5 | 36 | 388 | 21 | 41.9 | 396 |  | 2020-09-17 16:17 | 44091.6781 | 21 | 41.9 | 396 |  |  | 2020-09-14 | Pearso¦Policeroom 2 ¦¦Sep-17-2020 16:16
2020-09-17 16:17 | 44091.6787 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Policeroom 3 |  | 0 | 19.5 | 36 | 388 | 21 | 41.4 | 395 |  | 2020-09-17 16:17 | 44091.6787 | 21 | 41.4 | 395 |  |  | 2020-09-14 | Pearso¦Policeroom 3¦¦Sep-17-2020 16:17
2020-09-17 16:18 | 44091.6789 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 rear right |  | 1 | 20 | 38 | 363 | 23 | 37 | 373 |  | 2020-09-17 16:18 | 44091.6789 | 23 | 37 | 373 |  | caution | 2020-09-14 | B20772¦H11 rear right¦¦Sep-17-2020 16:17
2020-09-17 16:19 | 44091.6796 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 rear left |  | 1 | 20 | 38 | 363 | 23 | 37 | 371 |  | 2020-09-17 16:19 | 44091.6796 | 23 | 37 | 371 |  | caution | 2020-09-14 | B20772¦H11 rear left¦¦Sep-17-2020 16:18
2020-09-17 16:20 | 44091.6802 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroon #2 |  | 2 | 24.1 | 24.8 | 388 | 22.4 | 28.4 | 414 |  | 2020-09-17 16:20 | 44091.6802 | 22.4 | 28.4 | 414 |  | low | 2020-09-14 | B21554¦Courtroon #2¦¦Sep-17-2020 16:19
2020-09-17 16:20 | 44091.6804 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Policeroom 4 |  | 0 | 19.5 | 36 | 388 | 21.1 | 42.8 | 394 |  | 2020-09-17 16:20 | 44091.6804 | 21.1 | 42.8 | 394 |  |  | 2020-09-14 | Pearso¦Policeroom 4¦¦Sep-17-2020 16:19
2020-09-17 16:21 | 44091.681 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom f |  | 0 | 19.5 | 36 | 388 | 22 | 43.8 | 396 |  | 2020-09-17 16:21 | 44091.681 | 22 | 43.8 | 396 |  |  | 2020-09-14 | Pearso¦Ballroom f ¦¦Sep-17-2020 16:20
2020-09-17 16:22 | 44091.6816 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom f 1 |  | 0 | 19.5 | 36 | 388 | 21.3 | 43.6 | 402 |  | 2020-09-17 16:22 | 44091.6816 | 21.3 | 43.6 | 402 |  |  | 2020-09-14 | Pearso¦Ballroom f 1¦¦Sep-17-2020 16:21
2020-09-17 16:23 | 44091.6825 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom #3 |  | 2 | 24.1 | 24.8 | 388 | 22.8 | 35.9 | 687 |  | 2020-09-17 16:23 | 44091.6825 | 22.8 | 35.9 | 687 |  | caution | 2020-09-14 | B21554¦Courtroom #3¦¦Sep-17-2020 16:22
2020-09-17 16:25 | 44091.6837 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom f 2 |  | 0 | 19.5 | 36 | 388 | 21.1 | 45.1 | 403 |  | 2020-09-17 16:25 | 44091.6837 | 21.1 | 45.1 | 403 |  |  | 2020-09-14 | Pearso¦Ballroom f 2 ¦¦Sep-17-2020 16:24
2020-09-17 16:26 | 44091.6851 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Waiting area outside courtroom3 |  | 1 | 24.1 | 24.8 | 388 | 22.9 | 32.8 | 502 |  | 2020-09-17 16:26 | 44091.6851 | 22.9 | 32.8 | 502 |  | low | 2020-09-14 | B21554¦Waiting area outside courtroom3¦¦Sep-17-2020 16:26
2020-09-17 16:27 | 44091.6852 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom e |  | 0 | 19.5 | 36 | 388 | 20.8 | 43.8 | 400 |  | 2020-09-17 16:27 | 44091.6852 | 20.8 | 43.8 | 400 |  |  | 2020-09-14 | Pearso¦Ballroom e ¦¦Sep-17-2020 16:26
2020-09-17 16:27 | 44091.6856 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H14 table near exit |  | 1 | 20 | 38 | 363 | 23 | 37 | 365 |  | 2020-09-17 16:27 | 44091.6856 | 23 | 37 | 365 |  | caution | 2020-09-14 | B20772¦H14 table near exit ¦¦Sep-17-2020 16:27
2020-09-17 16:28 | 44091.6863 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom e 1 |  | 0 | 19.5 | 36 | 388 | 21.1 | 43.1 | 395 |  | 2020-09-17 16:28 | 44091.6863 | 21.1 | 43.1 | 395 |  |  | 2020-09-14 | Pearso¦Ballroom e 1¦¦Sep-17-2020 16:28
2020-09-17 16:28 | 44091.6863 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H14 table near entrance |  | 1 | 20 | 38 | 363 | 23 | 37 | 368 |  | 2020-09-17 16:28 | 44091.6863 | 23 | 37 | 368 |  | caution | 2020-09-14 | B20772¦H14 table near entrance ¦¦Sep-17-2020 16:28
2020-09-17 16:29 | 44091.6868 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Basement corridor at washrooms |  | 1 | 24.1 | 24.8 | 388 | 23.7 | 33.4 | 409 |  | 2020-09-17 16:29 | 44091.6868 | 23.7 | 33.4 | 409 |  | low | 2020-09-14 | B21554¦Basement corridor at washrooms¦¦Sep-17-2020 16:29
2020-09-17 16:30 | 44091.6874 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom e 2 |  | 0 | 19.5 | 36 | 388 | 21.1 | 43.3 | 396 |  | 2020-09-17 16:30 | 44091.6874 | 21.1 | 43.3 | 396 |  |  | 2020-09-14 | Pearso¦Ballroom e 2¦¦Sep-17-2020 16:29
2020-09-17 16:31 | 44091.6881 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom e 3 |  | 0 | 19.5 | 36 | 388 | 21.1 | 43 | 398 |  | 2020-09-17 16:31 | 44091.6881 | 21.1 | 43 | 398 |  |  | 2020-09-14 | Pearso¦Ballroom e 3¦¦Sep-17-2020 16:30
2020-09-17 16:31 | 44091.6882 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 judge |  | 1 | 20 | 38 | 363 | 23 | 37 | 365 |  | 2020-09-17 16:31 | 44091.6882 | 23 | 37 | 365 |  | caution | 2020-09-14 | B20772¦H13 judge¦¦Sep-17-2020 16:30
2020-09-17 16:32 | 44091.6886 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Basement corridor at exit door |  | 1 | 24.1 | 24.8 | 388 | 24.2 | 34.8 | 488 |  | 2020-09-17 16:32 | 44091.6886 | 24.2 | 34.8 | 488 |  | low | 2020-09-14 | B21554¦Basement corridor at exit door¦¦Sep-17-2020 16:31
2020-09-17 16:32 | 44091.6887 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom d |  | 0 | 19.5 | 36 | 388 | 20.1 | 44.7 | 395 |  | 2020-09-17 16:32 | 44091.6887 | 20.1 | 44.7 | 395 |  |  | 2020-09-14 | Pearso¦Ballroom d ¦¦Sep-17-2020 16:31
2020-09-17 16:32 | 44091.6889 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 plaintiff |  | 1 | 20 | 38 | 363 | 23 | 37 | 364 |  | 2020-09-17 16:32 | 44091.6889 | 23 | 37 | 364 |  | caution | 2020-09-14 | B20772¦H13 plaintiff¦¦Sep-17-2020 16:31
2020-09-17 16:33 | 44091.6894 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom d 1 |  | 0 | 19.5 | 36 | 388 | 20.9 | 44.7 | 395 |  | 2020-09-17 16:33 | 44091.6894 | 20.9 | 44.7 | 395 |  |  | 2020-09-14 | Pearso¦Ballroom d 1 ¦¦Sep-17-2020 16:32
2020-09-17 16:34 | 44091.6899 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Stairway landing |  | 1 | 24.1 | 24.8 | 388 | 24.7 | 36 | 474 |  | 2020-09-17 16:34 | 44091.6899 | 24.7 | 36 | 474 |  | caution | 2020-09-14 | B21554¦Stairway landing¦¦Sep-17-2020 16:33
2020-09-17 16:34 | 44091.6902 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom d 2 |  | 0 | 19.5 | 36 | 388 | 20.8 | 44.2 | 397 |  | 2020-09-17 16:34 | 44091.6902 | 20.8 | 44.2 | 397 |  |  | 2020-09-14 | Pearso¦Ballroom d 2¦¦Sep-17-2020 16:33
2020-09-17 16:34 | 44091.6903 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 defendant |  | 1 | 20 | 38 | 363 | 23 | 37 | 367 |  | 2020-09-17 16:34 | 44091.6903 | 23 | 37 | 367 |  | caution | 2020-09-14 | B20772¦H13 defendant¦¦Sep-17-2020 16:33
2020-09-17 16:34 | 44091.6904 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE STAFF ROOM |  | 2 | 18 | 48 | 424 | 23 | 44 | 556 |  | 2020-09-17 16:34 | 44091.6904 | 23 | 44 | 556 |  |  | 2020-09-14 | B20022¦JUDGE STAFF ROOM¦¦Sep-17-2020 16:34
2020-09-17 16:35 | 44091.6907 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom d 3 |  | 0 | 19.5 | 36 | 388 | 20.9 | 44.4 | 397 |  | 2020-09-17 16:35 | 44091.6907 | 20.9 | 44.4 | 397 |  |  | 2020-09-14 | Pearso¦Ballroom d 3 ¦¦Sep-17-2020 16:34
2020-09-17 16:35 | 44091.691 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 rear right |  | 1 | 20 | 38 | 363 | 23 | 37 | 367 |  | 2020-09-17 16:35 | 44091.691 | 23 | 37 | 367 |  | caution | 2020-09-14 | B20772¦H13 rear right¦¦Sep-17-2020 16:35
2020-09-17 16:35 | 44091.6913 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE CORKERY |  | 2 | 18 | 48 | 424 | 23 | 44.8 | 496 |  | 2020-09-17 16:35 | 44091.6913 | 23 | 44.8 | 496 |  |  | 2020-09-14 | B20022¦JUDGE CORKERY¦¦Sep-17-2020 16:35
2020-09-17 16:36 | 44091.6915 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 rear left |  | 1 | 20 | 38 | 363 | 23 | 37 | 368 |  | 2020-09-17 16:36 | 44091.6915 | 23 | 37 | 368 |  | caution | 2020-09-14 | B20772¦H13 rear left¦¦Sep-17-2020 16:35
2020-09-17 16:36 | 44091.6919 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom c |  | 0 | 19.5 | 36 | 388 | 21 | 44.6 | 399 |  | 2020-09-17 16:36 | 44091.6919 | 21 | 44.6 | 399 |  |  | 2020-09-14 | Pearso¦Ballroom c ¦¦Sep-17-2020 16:36
2020-09-17 16:36 | 44091.6919 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | VISITING JUDGE |  | 1 | 18 | 48 | 424 | 23 | 47 | 482 |  | 2020-09-17 16:36 | 44091.6919 | 23 | 47 | 482 |  |  | 2020-09-14 | B20022¦VISITING JUDGE¦¦Sep-17-2020 16:36
2020-09-17 16:37 | 44091.6923 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom c 1 |  | 0 | 19.5 | 36 | 388 | 21.1 | 44 | 402 |  | 2020-09-17 16:37 | 44091.6923 | 21.1 | 44 | 402 |  |  | 2020-09-14 | Pearso¦Ballroom c 1 ¦¦Sep-17-2020 16:36
2020-09-17 16:37 | 44091.6924 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Legal aid office corridor |  | 1 | 24.1 | 24.8 | 388 | 25.1 | 40.4 | 465 |  | 2020-09-17 16:37 | 44091.6924 | 25.1 | 40.4 | 465 |  |  | 2020-09-14 | B21554¦Legal aid office corridor¦¦Sep-17-2020 16:37
2020-09-17 16:38 | 44091.6932 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | VISITING JUDGE |  | 2 | 18 | 48 | 424 | 23 | 47 | 482 |  | 2020-09-17 16:38 | 44091.6932 | 23 | 47 | 482 |  |  | 2020-09-14 | B20022¦VISITING JUDGE¦¦Sep-17-2020 16:38
2020-09-17 16:38 | 44091.6933 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroo. C 2 |  | 0 | 19.5 | 36 | 388 | 21.5 | 43 | 399 |  | 2020-09-17 16:38 | 44091.6933 | 21.5 | 43 | 399 |  |  | 2020-09-14 | Pearso¦Ballroo. C 2 ¦¦Sep-17-2020 16:38
2020-09-17 16:39 | 44091.6937 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE INGRAM |  | 1 | 18 | 48 | 424 | 22 | 48 | 488 |  | 2020-09-17 16:39 | 44091.6937 | 22 | 48 | 488 |  |  | 2020-09-14 | B20022¦JUDGE INGRAM¦¦Sep-17-2020 16:38
2020-09-17 16:40 | 44091.6942 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE MCLEOD |  | 2 | 18 | 48 | 424 | 22 | 49 | 493 |  | 2020-09-17 16:40 | 44091.6942 | 22 | 49 | 493 |  |  | 2020-09-14 | B20022¦JUDGE MCLEOD¦¦Sep-17-2020 16:39
2020-09-17 16:40 | 44091.6944 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Main waiting area |  | 1 | 24.1 | 24.8 | 388 | 24.3 | 28.4 | 465 |  | 2020-09-17 16:40 | 44091.6944 | 24.3 | 28.4 | 465 |  | low | 2020-09-14 | B21554¦Main waiting area¦¦Sep-17-2020 16:39
2020-09-17 16:40 | 44091.6947 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom c 3 |  | 0 | 19.5 | 36 | 388 | 21.3 | 42.9 | 399 |  | 2020-09-17 16:40 | 44091.6947 | 21.3 | 42.9 | 399 |  |  | 2020-09-14 | Pearso¦Ballroom c 3¦¦Sep-17-2020 16:40
2020-09-17 16:40 | 44091.6948 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 JUDGE |  | 3 | 18 | 48 | 424 | 22 | 48 | 507 |  | 2020-09-17 16:40 | 44091.6948 | 22 | 48 | 507 |  |  | 2020-09-14 | B20022¦COURT 3 JUDGE¦¦Sep-17-2020 16:40
2020-09-17 16:41 | 44091.6948 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 printer |  | 1 | 20 | 38 | 363 | 23 | 37 | 362 |  | 2020-09-17 16:41 | 44091.6948 | 23 | 37 | 362 |  | caution | 2020-09-14 | B20772¦H16 printer¦¦Sep-17-2020 16:40
2020-09-17 16:41 | 44091.6955 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 LAWYER |  | 3 | 18 | 48 | 424 | 21 | 47 | 478 |  | 2020-09-17 16:41 | 44091.6955 | 21 | 47 | 478 |  |  | 2020-09-14 | B20022¦COURT 3 LAWYER¦¦Sep-17-2020 16:41
2020-09-17 16:42 | 44091.6955 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 judge |  | 1 | 20 | 38 | 363 | 23 | 37 | 374 |  | 2020-09-17 16:42 | 44091.6955 | 23 | 37 | 374 |  | caution | 2020-09-14 | B20772¦H16 judge ¦¦Sep-17-2020 16:41
2020-09-17 16:42 | 44091.6956 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom b |  | 0 | 19.5 | 36 | 388 | 21.4 | 43.1 | 400 |  | 2020-09-17 16:42 | 44091.6956 | 21.4 | 43.1 | 400 |  |  | 2020-09-14 | Pearso¦Ballroom b ¦¦Sep-17-2020 16:41
2020-09-17 16:42 | 44091.6961 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | ADVICE COUNSEL |  | 2 | 18 | 48 | 424 | 21 | 47 | 455 |  | 2020-09-17 16:42 | 44091.6961 | 21 | 47 | 455 |  |  | 2020-09-14 | B20022¦ADVICE COUNSEL¦¦Sep-17-2020 16:42
2020-09-17 16:43 | 44091.6962 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 typer desk |  | 1 | 20 | 38 | 363 | 23 | 37 | 376 |  | 2020-09-17 16:43 | 44091.6962 | 23 | 37 | 376 |  | caution | 2020-09-14 | B20772¦H16 typer desk¦¦Sep-17-2020 16:42
2020-09-17 16:43 | 44091.6967 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 WAITING AREA |  | 3 | 18 | 48 | 424 | 21.5 | 46 | 441 |  | 2020-09-17 16:43 | 44091.6967 | 21.5 | 46 | 441 |  |  | 2020-09-14 | B20022¦COURT 3 WAITING AREA¦¦Sep-17-2020 16:43
2020-09-17 16:43 | 44091.6968 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Front desk |  | 3 | 24.1 | 24.8 | 388 | 23.5 | 29.1 | 464 |  | 2020-09-17 16:43 | 44091.6968 | 23.5 | 29.1 | 464 |  | low | 2020-09-14 | B21554¦Front desk¦¦Sep-17-2020 16:43
2020-09-17 16:44 | 44091.6969 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 typer desk |  | 1 | 20 | 38 | 363 | 23 | 37 | 376 |  | 2020-09-17 16:44 | 44091.6969 | 23 | 37 | 376 |  | caution | 2020-09-14 | B20772¦H16 typer desk ¦¦Sep-17-2020 16:43
2020-09-17 16:44 | 44091.697 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom b 1 |  | 0 | 19.5 | 36 | 388 | 21.3 | 42.8 | 400 |  | 2020-09-17 16:44 | 44091.697 | 21.3 | 42.8 | 400 |  |  | 2020-09-14 | Pearso¦Ballroom b 1¦¦Sep-17-2020 16:43
2020-09-17 16:44 | 44091.6971 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT OFFICE LOBBY |  | 3 | 18 | 48 | 424 | 21.8 | 50 | 525 |  | 2020-09-17 16:44 | 44091.6971 | 21.8 | 50 | 525 |  |  | 2020-09-14 | B20022¦COURT OFFICE LOBBY¦¦Sep-17-2020 16:43
2020-09-17 16:44 | 44091.6976 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 plaintiff |  | 1 | 20 | 38 | 363 | 23 | 37 | 370 |  | 2020-09-17 16:44 | 44091.6976 | 23 | 37 | 370 |  | caution | 2020-09-14 | B20772¦H16 plaintiff ¦¦Sep-17-2020 16:44
2020-09-17 16:45 | 44091.6977 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom b 2 |  | 0 | 19.5 | 36 | 388 | 20.9 | 45.6 | 400 |  | 2020-09-17 16:45 | 44091.6977 | 20.9 | 45.6 | 400 |  |  | 2020-09-14 | Pearso¦Ballroom b 2 ¦¦Sep-17-2020 16:44
2020-09-17 16:45 | 44091.6977 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT OFFICE |  | 3 | 18 | 48 | 424 | 22.1 | 50.2 | 747 |  | 2020-09-17 16:45 | 44091.6977 | 22.1 | 50.2 | 747 |  |  | 2020-09-14 | B20022¦COURT OFFICE¦¦Sep-17-2020 16:44
2020-09-17 16:45 | 44091.6982 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 defendant |  | 1 | 20 | 38 | 363 | 23 | 37 | 370 |  | 2020-09-17 16:45 | 44091.6982 | 23 | 37 | 370 |  | caution | 2020-09-14 | B20772¦H16 defendant¦¦Sep-17-2020 16:45
2020-09-17 16:46 | 44091.6983 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | MEDIATION ROOM |  | 2 | 18 | 48 | 424 | 21.8 | 48 | 680 |  | 2020-09-17 16:46 | 44091.6983 | 21.8 | 48 | 680 |  |  | 2020-09-14 | B20022¦MEDIATION ROOM¦¦Sep-17-2020 16:45
2020-09-17 16:46 | 44091.6987 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom b 3 |  | 0 | 19.5 | 36 | 388 | 20.9 | 45.6 | 402 |  | 2020-09-17 16:46 | 44091.6987 | 20.9 | 45.6 | 402 |  |  | 2020-09-14 | Pearso¦Ballroom b 3¦¦Sep-17-2020 16:46
2020-09-17 16:46 | 44091.6988 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | OFFICER ROOM |  | 2 | 18 | 48 | 424 | 21.7 | 54 | 616 |  | 2020-09-17 16:46 | 44091.6988 | 21.7 | 54 | 616 |  |  | 2020-09-14 | B20022¦OFFICER ROOM¦¦Sep-17-2020 16:46
2020-09-17 16:47 | 44091.6991 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Main office |  | 2 | 24.1 | 24.8 | 388 | 23.4 | 29.9 | 467 |  | 2020-09-17 16:47 | 44091.6991 | 23.4 | 29.9 | 467 |  | low | 2020-09-14 | B21554¦Main office¦¦Sep-17-2020 16:46
2020-09-17 16:47 | 44091.6994 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 1 FLOOR LOBBY |  | 4 | 18 | 48 | 424 | 22 | 49.4 | 651 |  | 2020-09-17 16:47 | 44091.6994 | 22 | 49.4 | 651 |  |  | 2020-09-14 | B20022¦1 FLOOR LOBBY¦¦Sep-17-2020 16:47
2020-09-17 16:47 | 44091.6995 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area south |  | 1 | 20 | 38 | 363 | 24 | 37 | 366 |  | 2020-09-17 16:47 | 44091.6995 | 24 | 37 | 366 |  | caution | 2020-09-14 | B20772¦Courtroom waiting area south ¦¦Sep-17-2020 16:47
2020-09-17 16:48 | 44091.6999 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR LUNCH ROOM |  | 2 | 18 | 48 | 424 | 22 | 45 | 455 |  | 2020-09-17 16:48 | 44091.6999 | 22 | 45 | 455 |  |  | 2020-09-14 | B20022¦2 FLOOR LUNCH ROOM¦¦Sep-17-2020 16:47
2020-09-17 16:48 | 44091.7 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom a |  | 0 | 19.5 | 36 | 388 | 21.6 | 47 | 414 |  | 2020-09-17 16:48 | 44091.7 | 21.6 | 47 | 414 |  |  | 2020-09-14 | Pearso¦Ballroom a ¦¦Sep-17-2020 16:48
2020-09-17 16:48 | 44091.7002 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area north |  | 1 | 20 | 38 | 363 | 23 | 37 | 365 |  | 2020-09-17 16:48 | 44091.7002 | 23 | 37 | 365 |  | caution | 2020-09-14 | B20772¦Courtroom waiting area north ¦¦Sep-17-2020 16:48
2020-09-17 16:49 | 44091.7007 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom a 1 |  | 0 | 19.5 | 36 | 388 | 21.2 | 47.7 | 412 |  | 2020-09-17 16:49 | 44091.7007 | 21.2 | 47.7 | 412 |  |  | 2020-09-14 | Pearso¦Ballroom a 1¦¦Sep-17-2020 16:49
2020-09-17 16:49 | 44091.7007 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 2 JUDGE |  | 3 | 18 | 48 | 424 | 22 | 45 | 452 |  | 2020-09-17 16:49 | 44091.7007 | 22 | 45 | 452 |  |  | 2020-09-14 | B20022¦COURT 2 JUDGE¦¦Sep-17-2020 16:49
2020-09-17 16:50 | 44091.7012 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom a 2 |  | 0 | 19.5 | 36 | 388 | 21.2 | 48.3 | 410 |  | 2020-09-17 16:50 | 44091.7012 | 21.2 | 48.3 | 410 |  |  | 2020-09-14 | Pearso¦Ballroom a 2 ¦¦Sep-17-2020 16:49
2020-09-17 16:50 | 44091.7014 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 2 LAWYER |  | 3 | 18 | 48 | 424 | 21.8 | 45 | 447 |  | 2020-09-17 16:50 | 44091.7014 | 21.8 | 45 | 447 |  |  | 2020-09-14 | B20022¦COURT 2 LAWYER¦¦Sep-17-2020 16:49
2020-09-17 16:51 | 44091.7019 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 JUDGE |  | 3 | 18 | 48 | 424 | 22.1 | 46 | 447 |  | 2020-09-17 16:51 | 44091.7019 | 22.1 | 46 | 447 |  |  | 2020-09-14 | B20022¦COURT 1 JUDGE¦¦Sep-17-2020 16:50
2020-09-17 16:51 | 44091.7019 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom a 3 |  | 0 | 19.5 | 36 | 388 | 20.6 | 49.8 | 408 |  | 2020-09-17 16:51 | 44091.7019 | 20.6 | 49.8 | 408 |  |  | 2020-09-14 | Pearso¦Ballroom a 3¦¦Sep-17-2020 16:50
2020-09-17 16:52 | 44091.7024 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 RIGHT SIDE |  | 2 | 18 | 48 | 424 | 22.5 | 45 | 471 |  | 2020-09-17 16:52 | 44091.7024 | 22.5 | 45 | 471 |  |  | 2020-09-14 | B20022¦COURT 1 RIGHT SIDE¦¦Sep-17-2020 16:51
2020-09-17 16:52 | 44091.703 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 LEFT SIDE |  | 3 | 18 | 48 | 424 | 22.2 | 46 | 569 |  | 2020-09-17 16:52 | 44091.703 | 22.2 | 46 | 569 |  |  | 2020-09-14 | B20022¦COURT 1 LEFT SIDE¦¦Sep-17-2020 16:52
2020-09-17 16:53 | 44091.7035 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JURY ROOM |  | 2 | 18 | 48 | 424 | 22.7 | 45.3 | 508 |  | 2020-09-17 16:53 | 44091.7035 | 22.7 | 45.3 | 508 |  |  | 2020-09-14 | B20022¦JURY ROOM¦¦Sep-17-2020 16:53
2020-09-17 16:54 | 44091.704 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR LEFT MEETING |  | 2 | 18 | 48 | 424 | 21.8 | 51 | 642 |  | 2020-09-17 16:54 | 44091.704 | 21.8 | 51 | 642 |  |  | 2020-09-14 | B20022¦2 FLOOR LEFT MEETING¦¦Sep-17-2020 16:53
2020-09-17 16:55 | 44091.7046 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR RIGHT MEETING |  | 3 | 18 | 48 | 424 | 22.3 | 48.7 | 464 |  | 2020-09-17 16:55 | 44091.7046 | 22.3 | 48.7 | 464 |  |  | 2020-09-14 | B20022¦2 FLOOR RIGHT MEETING¦¦Sep-17-2020 16:54
2020-09-17 16:55 | 44091.7051 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 1 FLOOR MAIN HALL |  | 1 | 18 | 48 | 424 | 22.6 | 47.5 | 620 |  | 2020-09-17 16:55 | 44091.7051 | 22.6 | 47.5 | 620 |  |  | 2020-09-14 | B20022¦1 FLOOR MAIN HALL¦¦Sep-17-2020 16:55
2020-09-17 16:56 | 44091.7056 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | SOUTH WING ENTRANCE |  | 3 | 18 | 48 | 424 | 22.9 | 46.1 | 601 |  | 2020-09-17 16:56 | 44091.7056 | 22.9 | 46.1 | 601 |  |  | 2020-09-14 | B20022¦SOUTH WING ENTRANCE¦¦Sep-17-2020 16:56
2020-09-17 17:06 | 44091.7127 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area north |  | 1 | 20 | 38 | 363 | 23 | 37 | 365 |  | 2020-09-17 17:06 | 44091.7127 | 23 | 37 | 365 |  | caution | 2020-09-14 | B20772¦Courtroom waiting area north ¦¦Sep-17-2020 17:06
2020-09-18 07:58 | 44092.3322 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 106 |  | 0 | 25 | 24 | 370 | 22.1 | 37.6 | 424 | No | 2020-09-18 07:58 | 44092.3322 | 22.1 | 37.6 | 424 |  | caution | 2020-09-14 | B14660¦106¦¦Sep-18-2020 07:58
2020-09-18 08:06 | 44092.3375 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 128 |  | 0 | 6 | 67 | 399 | 15.3 | 49.9 | 402 | No | 2020-09-18 08:06 | 44092.3375 | 15.3 | 49.9 | 402 |  |  | 2020-09-14 | B14660¦128¦¦Sep-18-2020 08:05
2020-09-18 08:10 | 44092.3403 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 001 |  | 1 | 6 | 67 | 399 | 18.5 | 47.5 | 408 | No | 2020-09-18 08:10 | 44092.3403 | 18.5 | 47.5 | 408 |  |  | 2020-09-14 | B14660¦001¦¦Sep-18-2020 08:09
2020-09-18 08:13 | 44092.3422 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 028 |  | 0 | 6 | 67 | 399 | 20.6 | 38.5 | 416 | No | 2020-09-18 08:13 | 44092.3422 | 20.6 | 38.5 | 416 |  | caution | 2020-09-14 | B14660¦028¦¦Sep-18-2020 08:12
2020-09-18 08:15 | 44092.3441 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 019 |  | 0 | 6 | 67 | 399 | 21.6 | 36.3 | 412 | No | 2020-09-18 08:15 | 44092.3441 | 21.6 | 36.3 | 412 |  | caution | 2020-09-14 | B14660¦019¦¦Sep-18-2020 08:15
2020-09-18 08:18 | 44092.3458 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 011 |  | 0 | 6 | 67 | 399 | 22.1 | 36.7 | 439 | No | 2020-09-18 08:18 | 44092.3458 | 22.1 | 36.7 | 439 |  | caution | 2020-09-14 | B14660¦011¦¦Sep-18-2020 08:17
2020-09-18 08:22 | 44092.3486 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 118 |  | 0 | 6 | 67 | 399 | 22.8 | 29 | 425 | No | 2020-09-18 08:22 | 44092.3486 | 22.8 | 29 | 425 |  | low | 2020-09-14 | B14660¦118¦¦Sep-18-2020 08:22
2020-09-18 08:24 | 44092.35 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 115 |  | 0 | 6 | 67 | 399 | 23.9 | 31.9 | 412 | No | 2020-09-18 08:24 | 44092.35 | 23.9 | 31.9 | 412 |  | low | 2020-09-14 | B14660¦115¦¦Sep-18-2020 08:23
2020-09-18 08:29 | 44092.3533 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 107 |  | 0 | 6 | 67 | 399 | 19.7 | 39.4 | 430 | No | 2020-09-18 08:29 | 44092.3533 | 19.7 | 39.4 | 430 |  | caution | 2020-09-14 | B14660¦107¦¦Sep-18-2020 08:28
2020-09-18 08:31 | 44092.355 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 113 |  | 0 | 6 | 67 | 399 | 22 | 32.2 | 412 | No | 2020-09-18 08:31 | 44092.355 | 22 | 32.2 | 412 |  | low | 2020-09-14 | B14660¦113¦¦Sep-18-2020 08:31
2020-09-18 08:31 | 44092.3551 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NW hall |  | 0 | 14 | 48 | 440 | 21 | 52 | 550 |  | 2020-09-18 08:31 | 44092.3551 | 21 | 52 | 550 |  |  | 2020-09-14 | B25548¦NW hall¦¦Sep-18-2020 08:31
2020-09-18 08:33 | 44092.356 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NE hall |  | 0 | 14 | 48 | 440 | 21 | 53 | 590 |  | 2020-09-18 08:33 | 44092.356 | 21 | 53 | 590 |  |  | 2020-09-14 | B25548¦NE hall¦¦Sep-18-2020 08:32
2020-09-18 08:34 | 44092.3567 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | E hall |  | 0 | 14 | 48 | 440 | 22 | 51 | 570 |  | 2020-09-18 08:34 | 44092.3567 | 22 | 51 | 570 |  |  | 2020-09-14 | B25548¦E hall¦¦Sep-18-2020 08:33
2020-09-18 08:34 | 44092.3571 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 114 |  | 0 | 6 | 67 | 399 | 22 | 28.4 | 412 | No | 2020-09-18 08:34 | 44092.3571 | 22 | 28.4 | 412 |  | low | 2020-09-14 | B14660¦114¦¦Sep-18-2020 08:34
2020-09-18 08:35 | 44092.3576 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | SE hall |  | 0 | 14 | 48 | 440 | 22 | 50 | 555 |  | 2020-09-18 08:35 | 44092.3576 | 22 | 50 | 555 |  |  | 2020-09-14 | B25548¦SE hall¦¦Sep-18-2020 08:34
2020-09-18 08:36 | 44092.358 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area mens washroom |  | 1 | 10.9 | 41.1 | 414 | 19.3 | 38.8 | 431 |  | 2020-09-18 08:36 | 44092.358 | 19.3 | 38.8 | 431 |  | caution | 2020-09-14 | B20474¦Basement waiting area mens washroom¦¦Sep-18-2020 08:35
2020-09-18 08:36 | 44092.3585 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 104 |  | 0 | 6 | 67 | 399 | 22.1 | 33.6 | 431 | No | 2020-09-18 08:36 | 44092.3585 | 22.1 | 33.6 | 431 |  | low | 2020-09-14 | B14660¦104¦¦Sep-18-2020 08:36
2020-09-18 08:36 | 44092.3585 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | SW hall |  | 0 | 14 | 48 | 440 | 22 | 50 | 560 |  | 2020-09-18 08:36 | 44092.3585 | 22 | 50 | 560 |  |  | 2020-09-14 | B25548¦SW hall¦¦Sep-18-2020 08:36
2020-09-18 08:38 | 44092.3595 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Robing corridor |  | 1 | 10.9 | 41.4 | 414 | 19.1 | 39.1 | 427 |  | 2020-09-18 08:38 | 44092.3595 | 19.1 | 39.1 | 427 |  | caution | 2020-09-14 | B20474¦Robing corridor¦¦Sep-18-2020 08:37
2020-09-18 08:38 | 44092.3597 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | Center hall |  | 0 | 14 | 48 | 440 | 22 | 49 | 570 |  | 2020-09-18 08:38 | 44092.3597 | 22 | 49 | 570 |  |  | 2020-09-14 | B25548¦Center hall¦¦Sep-18-2020 08:37
2020-09-18 08:39 | 44092.3605 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 101 |  | 0 | 6 | 67 | 399 | 21.7 | 40.3 | 399 | No | 2020-09-18 08:39 | 44092.3605 | 21.7 | 40.3 | 399 |  |  | 2020-09-14 | B14660¦101¦¦Sep-18-2020 08:39
2020-09-18 08:39 | 44092.3606 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-E wall |  | 0 | 14 | 48 | 440 | 22 | 50 | 605 |  | 2020-09-18 08:39 | 44092.3606 | 22 | 50 | 605 |  |  | 2020-09-14 | B25548¦1-E wall¦¦Sep-18-2020 08:39
2020-09-18 08:40 | 44092.3609 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | OPP office |  | 1 | 10 | 45 | 415 | 18 | 43 | 486 |  | 2020-09-18 08:40 | 44092.3609 | 18 | 43 | 486 |  |  | 2020-09-14 | B70235¦OPP office ¦¦Sep-18-2020 08:39
2020-09-18 08:41 | 44092.3616 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area courtroom3 |  | 1 | 10.9 | 41.1 | 414 | 19.4 | 37.6 | 459 |  | 2020-09-18 08:41 | 44092.3616 | 19.4 | 37.6 | 459 |  | caution | 2020-09-14 | B20474¦Basement waiting area courtroom3¦¦Sep-18-2020 08:40
2020-09-18 08:41 | 44092.3618 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-E hall |  | 0 | 14 | 48 | 440 | 23 | 49 | 590 |  | 2020-09-18 08:41 | 44092.3618 | 23 | 49 | 590 |  |  | 2020-09-14 | B25548¦1-E hall¦¦Sep-18-2020 08:41
2020-09-18 08:41 | 44092.3619 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office E |  | 2 | 10 | 45 | 415 | 20 | 35 | 461 |  | 2020-09-18 08:41 | 44092.3619 | 20 | 35 | 461 |  | caution | 2020-09-14 | B70235¦Main office E ¦¦Sep-18-2020 08:41
2020-09-18 08:42 | 44092.3624 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 134 |  | 0 | 6 | 67 | 399 | 22.1 | 36.9 | 414 | No | 2020-09-18 08:42 | 44092.3624 | 22.1 | 36.9 | 414 |  | caution | 2020-09-14 | B14660¦134¦¦Sep-18-2020 08:41
2020-09-18 08:42 | 44092.3625 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-E wall |  | 0 | 14 | 48 | 440 | 23 | 47 | 580 |  | 2020-09-18 08:42 | 44092.3625 | 23 | 47 | 580 |  |  | 2020-09-14 | B25548¦1-E wall¦¦Sep-18-2020 08:42
2020-09-18 08:42 | 44092.3628 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office C |  | 3 | 10 | 45 | 415 | 21 | 34 | 467 |  | 2020-09-18 08:42 | 44092.3628 | 21 | 34 | 467 |  | low | 2020-09-14 | B70235¦Main office C ¦¦Sep-18-2020 08:42
2020-09-18 08:43 | 44092.3631 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 136 |  | 2 | 6 | 67 | 399 | 23.1 | 33.9 | 422 | No | 2020-09-18 08:43 | 44092.3631 | 23.1 | 33.9 | 422 |  | low | 2020-09-14 | B14660¦136¦¦Sep-18-2020 08:42
2020-09-18 08:43 | 44092.3633 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 14 | 48 | 440 | 22 | 48 | 730 |  | 2020-09-18 08:43 | 44092.3633 | 22 | 48 | 730 |  |  | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 08:43
2020-09-18 08:44 | 44092.3636 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area inside dbl doors |  | 1 | 10.9 | 41.1 | 414 | 19.5 | 37.1 | 464 |  | 2020-09-18 08:44 | 44092.3636 | 19.5 | 37.1 | 464 |  | caution | 2020-09-14 | B20474¦Basement waiting area inside dbl doors¦¦Sep-18-2020 08:43
2020-09-18 08:44 | 44092.3639 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office W |  | 3 | 10 | 45 | 415 | 21 | 32 | 442 |  | 2020-09-18 08:44 | 44092.3639 | 21 | 32 | 442 |  | low | 2020-09-14 | B70235¦Main office W¦¦Sep-18-2020 08:43
2020-09-18 08:44 | 44092.3642 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- S wall |  | 0 | 14 | 48 | 440 | 22 | 49 | 630 |  | 2020-09-18 08:44 | 44092.3642 | 22 | 49 | 630 |  |  | 2020-09-14 | B25548¦1- S wall¦¦Sep-18-2020 08:44
2020-09-18 08:44 | 44092.3642 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 144 |  | 0 | 6 | 67 | 399 | 23.2 | 33.2 | 429 | No | 2020-09-18 08:44 | 44092.3642 | 23.2 | 33.2 | 429 |  | low | 2020-09-14 | B14660¦144¦¦Sep-18-2020 08:44
2020-09-18 08:45 | 44092.3647 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 14 | 48 | 440 | 21 | 49 | 620 |  | 2020-09-18 08:45 | 44092.3647 | 21 | 49 | 620 |  |  | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 08:45
2020-09-18 08:45 | 44092.3649 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Trial office |  | 0 | 10 | 45 | 415 | 21 | 33 | 436 |  | 2020-09-18 08:46 | 44092.3649 | 21 | 33 | 436 |  | low | 2020-09-14 | B70235¦Trial office ¦¦Sep-18-2020 08:45
2020-09-18 08:46 | 44092.3651 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 122 |  | 0 | 6 | 67 | 399 | 23.3 | 32.1 | 421 | No | 2020-09-18 08:46 | 44092.3651 | 23.3 | 32.1 | 421 |  | low | 2020-09-14 | B14660¦122¦¦Sep-18-2020 08:45
2020-09-18 08:46 | 44092.3652 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Bottom stairs foyer |  | 1 | 10.9 | 41.1 | 414 | 19.3 | 36.7 | 474 |  | 2020-09-18 08:46 | 44092.3652 | 19.3 | 36.7 | 474 |  | caution | 2020-09-14 | B20474¦Bottom stairs foyer¦¦Sep-18-2020 08:45
2020-09-18 08:46 | 44092.3654 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 14 | 48 | 440 | 21 | 50 | 590 |  | 2020-09-18 08:46 | 44092.3654 | 21 | 50 | 590 |  |  | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 08:46
2020-09-18 08:47 | 44092.3657 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jason Mariasine office |  | 0 | 10 | 45 | 415 | 22 | 31 | 432 |  | 2020-09-18 08:47 | 44092.3657 | 22 | 31 | 432 |  | low | 2020-09-14 | B70235¦Jason Mariasine office ¦¦Sep-18-2020 08:46
2020-09-18 08:47 | 44092.3661 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 14 | 48 | 440 | 22 | 50 | 570 |  | 2020-09-18 08:47 | 44092.3661 | 22 | 50 | 570 |  |  | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 08:47
2020-09-18 08:48 | 44092.3664 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 105 |  | 0 | 6 | 67 | 399 | 23.6 | 30.9 | 419 | No | 2020-09-18 08:48 | 44092.3664 | 23.6 | 30.9 | 419 |  | low | 2020-09-14 | B14660¦105¦¦Sep-18-2020 08:47
2020-09-18 08:48 | 44092.3668 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Lower landing of stairway |  | 1 | 10.7 | 41.1 | 414 | 19 | 37.1 | 472 |  | 2020-09-18 08:48 | 44092.3668 | 19 | 37.1 | 472 |  | caution | 2020-09-14 | B20474¦Lower landing of stairway¦¦Sep-18-2020 08:48
2020-09-18 08:48 | 44092.367 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jennifer Mumby office |  | 0 | 10 | 45 | 415 | 22 | 29 | 430 |  | 2020-09-18 08:48 | 44092.367 | 22 | 29 | 430 |  | low | 2020-09-14 | B70235¦Jennifer Mumby office ¦¦Sep-18-2020 08:48
2020-09-18 08:49 | 44092.367 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 14 | 48 | 440 | 22 | 49 | 570 |  | 2020-09-18 08:49 | 44092.367 | 22 | 49 | 570 |  |  | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 08:48
2020-09-18 08:49 | 44092.3674 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 106 |  | 0 | 6 | 67 | 399 | 23.6 | 29.4 | 424 | No | 2020-09-18 08:49 | 44092.3674 | 23.6 | 29.4 | 424 |  | low | 2020-09-14 | B14660¦106¦¦Sep-18-2020 08:49
2020-09-18 08:49 | 44092.3674 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Administration office east |  | 3 | 11 | 42 | 425 | 18 | 45 | 446 |  | 2020-09-18 08:49 | 44092.3674 | 18 | 45 | 446 |  |  | 2020-09-14 | B25479¦Administration office east ¦¦Sep-18-2020 08:49
2020-09-18 08:49 | 44092.3676 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area north |  | 1 | 20 | 38 | 363 | 23 | 37 | 365 |  | 2020-09-18 08:49 | 44092.3676 | 23 | 37 | 365 |  | caution | 2020-09-14 | B20772¦Courtroom waiting area north ¦¦Sep-18-2020 08:49
2020-09-18 08:50 | 44092.3678 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-W wall |  | 0 | 14 | 48 | 440 | 22 | 49 | 580 |  | 2020-09-18 08:50 | 44092.3678 | 22 | 49 | 580 |  |  | 2020-09-14 | B25548¦1-W wall¦¦Sep-18-2020 08:49
2020-09-18 08:50 | 44092.368 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jennifer Broderick office |  | 0 | 10 | 45 | 415 | 22 | 30 | 426 |  | 2020-09-18 08:50 | 44092.368 | 22 | 30 | 426 |  | low | 2020-09-14 | B70235¦Jennifer Broderick office ¦¦Sep-18-2020 08:49
2020-09-18 08:50 | 44092.3682 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Administration office west |  | 1 | 11 | 42 | 425 | 19 | 43 | 468 |  | 2020-09-18 08:50 | 44092.3682 | 19 | 43 | 468 |  |  | 2020-09-14 | B25479¦Administration office west ¦¦Sep-18-2020 08:50
2020-09-18 08:50 | 44092.3682 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 waiting room |  | 1 | 12 | 40 | 365 | 21 | 29 | 366 |  | 2020-09-18 08:50 | 44092.3682 | 21 | 29 | 366 |  | low | 2020-09-14 | B20772¦H9 waiting room ¦¦Sep-18-2020 08:50
2020-09-18 08:50 | 44092.3684 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Entrance |  | 0 | 10 | 42 | 418 | 12.5 | 54 | 451 |  | 2020-09-18 08:50 | 44092.3684 | 12.5 | 54 | 451 |  |  | 2020-09-14 | B16187¦Entrance ¦¦Sep-18-2020 08:50
2020-09-18 08:51 | 44092.3686 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-W wall |  | 0 | 14 | 48 | 440 | 21 | 50 | 580 |  | 2020-09-18 08:51 | 44092.3686 | 21 | 50 | 580 |  |  | 2020-09-14 | B25548¦1-W wall¦¦Sep-18-2020 08:50
2020-09-18 08:51 | 44092.3687 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Robert Beninger office |  | 0 | 10 | 45 | 415 | 22 | 30 | 432 |  | 2020-09-18 08:51 | 44092.3687 | 22 | 30 | 432 |  | low | 2020-09-14 | B70235¦Robert Beninger office ¦¦Sep-18-2020 08:50
2020-09-18 08:51 | 44092.3688 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 0 | 10 | 42 | 418 | 15.3 | 48.8 | 512 |  | 2020-09-18 08:51 | 44092.3688 | 15.3 | 48.8 | 512 |  |  | 2020-09-14 | B16187¦Court 3¦¦Sep-18-2020 08:51
2020-09-18 08:51 | 44092.3688 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 111 |  | 0 | 6 | 67 | 399 | 23.3 | 32.8 | 434 | No | 2020-09-18 08:51 | 44092.3688 | 23.3 | 32.8 | 434 |  | low | 2020-09-14 | B14660¦111¦¦Sep-18-2020 08:51
2020-09-18 08:51 | 44092.369 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Administrative office |  | 3 | 9.6 | 54.2 | 394 | 20.2 | 36.6 | 464 |  | 2020-09-18 08:51 | 44092.369 | 20.2 | 36.6 | 464 |  | caution | 2020-09-14 | B90558¦Administrative office¦¦Sep-18-2020 08:51
2020-09-18 08:52 | 44092.3692 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 0 | 10 | 42 | 418 | 17.5 | 40.5 | 525 |  | 2020-09-18 08:52 | 44092.3692 | 17.5 | 40.5 | 525 |  |  | 2020-09-14 | B16187¦Court 3¦¦Sep-18-2020 08:51
2020-09-18 08:52 | 44092.3692 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 2nd floor SE hall |  | 1 | 9 | 51 | 392 | 20.7 | 43.8 | 433 |  | 2020-09-18 08:52 | 44092.3692 | 20.7 | 43.8 | 433 |  |  | 2020-09-14 | B20494¦2nd floor SE hall¦¦Sep-18-2020 08:51
2020-09-18 08:52 | 44092.3692 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 judge |  | 1 | 12 | 40 | 365 | 21 | 29 | 368 |  | 2020-09-18 08:52 | 44092.3692 | 21 | 29 | 368 |  | low | 2020-09-14 | B20772¦H9 judge ¦¦Sep-18-2020 08:51
2020-09-18 08:52 | 44092.3693 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 5 |  | 3 | 11 | 43 | 425 | 21 | 33 | 466 |  | 2020-09-18 08:52 | 44092.3693 | 21 | 33 | 466 |  | low | 2020-09-14 | B25479¦Courtroom 5¦¦Sep-18-2020 08:51
2020-09-18 08:52 | 44092.3693 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #2 |  | 2 | 10.7 | 41.1 | 414 | 18.8 | 36.1 | 432 |  | 2020-09-18 08:52 | 44092.3693 | 18.8 | 36.1 | 432 |  | caution | 2020-09-14 | B20474¦Courtroom #2¦¦Sep-18-2020 08:51
2020-09-18 08:52 | 44092.3693 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-W wall |  | 0 | 14 | 48 | 440 | 21 | 50 | 585 |  | 2020-09-18 08:52 | 44092.3693 | 21 | 50 | 585 |  |  | 2020-09-14 | B25548¦1-W wall¦¦Sep-18-2020 08:51
2020-09-18 08:52 | 44092.3697 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Library |  | 0 | 11 | 425 | 425 | 21 | 35 | 456 |  | 2020-09-18 08:52 | 44092.3697 | 21 | 35 | 456 |  | caution | 2020-09-14 | B25479¦Library ¦¦Sep-18-2020 08:52
2020-09-18 08:52 | 44092.3698 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Stuart Konyer office |  | 0 | 10 | 45 | 415 | 22 | 31 | 432 |  | 2020-09-18 08:52 | 44092.3698 | 22 | 31 | 432 |  | low | 2020-09-14 | B70235¦Stuart Konyer office ¦¦Sep-18-2020 08:52
2020-09-18 08:52 | 44092.3698 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 0 | 10 | 42 | 418 | 19 | 38.3 | 524 |  | 2020-09-18 08:52 | 44092.3698 | 19 | 38.3 | 524 |  | caution | 2020-09-14 | B16187¦Court 3¦¦Sep-18-2020 08:52
2020-09-18 08:53 | 44092.37 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 plaintiff |  | 1 | 12 | 40 | 365 | 21 | 29 | 365 |  | 2020-09-18 08:53 | 44092.37 | 21 | 29 | 365 |  | low | 2020-09-14 | B20772¦H9 plaintiff¦¦Sep-18-2020 08:52
2020-09-18 08:53 | 44092.3701 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | S foyer |  | 0 | 14 | 48 | 440 | 21 | 50 | 600 |  | 2020-09-18 08:53 | 44092.3701 | 21 | 50 | 600 |  |  | 2020-09-14 | B25548¦S foyer¦¦Sep-18-2020 08:52
2020-09-18 08:53 | 44092.3702 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | TC office |  | 1 | 11 | 42 | 425 | 21 | 35 | 457 |  | 2020-09-18 08:53 | 44092.3702 | 21 | 35 | 457 |  | caution | 2020-09-14 | B25479¦TC office ¦¦Sep-18-2020 08:53
2020-09-18 08:53 | 44092.3702 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 4 |  | 0 | 10 | 42 | 418 | 20 | 33.8 | 509 |  | 2020-09-18 08:53 | 44092.3702 | 20 | 33.8 | 509 |  | low | 2020-09-14 | B16187¦Court 4¦¦Sep-18-2020 08:53
2020-09-18 08:54 | 44092.3707 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #4 |  | 3 | 10.7 | 41.1 | 414 | 18.7 | 37 | 437 |  | 2020-09-18 08:54 | 44092.3707 | 18.7 | 37 | 437 |  | caution | 2020-09-14 | B20474¦Courtroom #4¦¦Sep-18-2020 08:53
2020-09-18 08:54 | 44092.3708 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | N foyer |  | 0 | 14 | 48 | 440 | 21 | 50 | 580 |  | 2020-09-18 08:54 | 44092.3708 | 21 | 50 | 580 |  |  | 2020-09-14 | B25548¦N foyer¦¦Sep-18-2020 08:53
2020-09-18 08:54 | 44092.3709 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 203 |  | 0 | 6 | 67 | 399 | 23 | 30.8 | 425 | No | 2020-09-18 08:54 | 44092.3709 | 23 | 30.8 | 425 |  | low | 2020-09-14 | B14660¦203¦¦Sep-18-2020 08:54
2020-09-18 08:54 | 44092.3709 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 defendant |  | 1 | 12 | 40 | 365 | 21 | 29 | 365 |  | 2020-09-18 08:54 | 44092.3709 | 21 | 29 | 365 |  | low | 2020-09-14 | B20772¦H9 defendant¦¦Sep-18-2020 08:54
2020-09-18 08:54 | 44092.371 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Lunch room |  | 0 | 10 | 45 | 415 | 23 | 30 | 439 |  | 2020-09-18 08:54 | 44092.371 | 23 | 30 | 439 |  | low | 2020-09-14 | B70235¦Lunch room ¦¦Sep-18-2020 08:54
2020-09-18 08:54 | 44092.3711 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 10 | 42 | 418 | 21 | 31.9 | 473 |  | 2020-09-18 08:54 | 44092.3711 | 21 | 31.9 | 473 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 08:54
2020-09-18 08:55 | 44092.3714 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 10 | 42 | 418 | 21 | 31.7 | 465 |  | 2020-09-18 08:55 | 44092.3714 | 21 | 31.7 | 465 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 08:54
2020-09-18 08:55 | 44092.3715 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 3 |  | 1 | 8.4 | 54.9 | 371 | 20.5 | 47 | 437 |  | 2020-09-18 08:55 | 44092.3715 | 20.5 | 47 | 437 |  |  | 2020-09-14 | B20494¦Courtroom 3¦¦Sep-18-2020 08:54
2020-09-18 08:55 | 44092.3715 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 rear right |  | 1 | 12 | 40 | 365 | 21 | 29 | 365 |  | 2020-09-18 08:55 | 44092.3715 | 21 | 29 | 365 |  | low | 2020-09-14 | B20772¦H9 rear right ¦¦Sep-18-2020 08:55
2020-09-18 08:55 | 44092.3717 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 10 | 42 | 418 | 22 | 31.3 | 463 |  | 2020-09-18 08:55 | 44092.3717 | 22 | 31.3 | 463 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 08:55
2020-09-18 08:55 | 44092.3718 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 14 | 48 | 440 | 22 | 50 | 580 |  | 2020-09-18 08:55 | 44092.3718 | 22 | 50 | 580 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 08:55
2020-09-18 08:55 | 44092.3718 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Criminal justice office |  | 1 | 9 | 51 | 392 | 21.5 | 45.2 | 446 |  | 2020-09-18 08:55 | 44092.3718 | 21.5 | 45.2 | 446 |  |  | 2020-09-14 | B20494¦Criminal justice office¦¦Sep-18-2020 08:55
2020-09-18 08:56 | 44092.3719 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | JP lobby |  | 0 | 11 | 42 | 425 | 22 | 31 | 454 |  | 2020-09-18 08:56 | 44092.3719 | 22 | 31 | 454 |  | low | 2020-09-14 | B25479¦JP lobby ¦¦Sep-18-2020 08:55
2020-09-18 08:56 | 44092.3719 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom 2 |  | 2 | 9.6 | 54.2 | 394 | 20.7 | 35 | 418 |  | 2020-09-18 08:56 | 44092.3719 | 20.7 | 35 | 418 |  | caution | 2020-09-14 | B90558¦Courtroom 2¦¦Sep-18-2020 08:55
2020-09-18 08:56 | 44092.372 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 rear left |  | 1 | 12 | 40 | 365 | 21 | 29 | 366 |  | 2020-09-18 08:56 | 44092.372 | 21 | 29 | 366 |  | low | 2020-09-14 | B20772¦H9 rear left¦¦Sep-18-2020 08:55
2020-09-18 08:56 | 44092.3722 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court staff room |  | 0 | 10 | 45 | 415 | 23 | 30 | 441 |  | 2020-09-18 08:56 | 44092.3722 | 23 | 30 | 441 |  | low | 2020-09-14 | B70235¦Court staff room ¦¦Sep-18-2020 08:56
2020-09-18 08:56 | 44092.3723 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 10 | 42 | 418 | 21.5 | 29.5 | 474 |  | 2020-09-18 08:56 | 44092.3723 | 21.5 | 29.5 | 474 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 08:56
2020-09-18 08:56 | 44092.3724 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #3 |  | 3 | 10.7 | 41.1 | 414 | 19 | 37.4 | 441 |  | 2020-09-18 08:56 | 44092.3724 | 19 | 37.4 | 441 |  | caution | 2020-09-14 | B20474¦Courtroom #3¦¦Sep-18-2020 08:56
2020-09-18 08:56 | 44092.3725 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Second floor hallway nw |  | 1 | 8.4 | 54.9 | 371 | 20.7 | 46.2 | 430 |  | 2020-09-18 08:56 | 44092.3725 | 20.7 | 46.2 | 430 |  |  | 2020-09-14 | B20494¦Second floor hallway nw¦¦Sep-18-2020 08:56
2020-09-18 08:57 | 44092.3727 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 4 |  | 0 | 11 | 42 | 425 | 21 | 24 | 447 |  | 2020-09-18 08:57 | 44092.3727 | 21 | 24 | 447 |  | low | 2020-09-14 | B25479¦Courtroom 4¦¦Sep-18-2020 08:56
2020-09-18 08:57 | 44092.3728 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 10 | 42 | 418 | 21.2 | 26.1 | 456 |  | 2020-09-18 08:57 | 44092.3728 | 21.2 | 26.1 | 456 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 08:56
2020-09-18 08:57 | 44092.3728 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 14 | 48 | 440 | 22 | 49 | 570 |  | 2020-09-18 08:57 | 44092.3728 | 22 | 49 | 570 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 08:56
2020-09-18 08:58 | 44092.3735 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 1 |  | 0 | 10 | 42 | 418 | 20.7 | 26.4 | 469 |  | 2020-09-18 08:58 | 44092.3735 | 20.7 | 26.4 | 469 |  | low | 2020-09-14 | B16187¦Court 1¦¦Sep-18-2020 08:57
2020-09-18 08:58 | 44092.3735 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Crown staff office |  | 1 | 10 | 45 | 415 | 22 | 28 | 456 |  | 2020-09-18 08:58 | 44092.3735 | 22 | 28 | 456 |  | low | 2020-09-14 | B70235¦Crown staff office ¦¦Sep-18-2020 08:57
2020-09-18 08:58 | 44092.3737 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Second floor hallway sw |  | 1 | 8.4 | 54.9 | 371 | 20.6 | 43.8 | 421 |  | 2020-09-18 08:58 | 44092.3737 | 20.6 | 43.8 | 421 |  |  | 2020-09-14 | B20494¦Second floor hallway sw¦¦Sep-18-2020 08:58
2020-09-18 08:58 | 44092.3738 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 14 | 48 | 440 | 22 | 49 | 580 |  | 2020-09-18 08:58 | 44092.3738 | 22 | 49 | 580 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 08:58
2020-09-18 08:58 | 44092.3739 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 10 | 42 | 418 | 20.9 | 28.4 | 452 |  | 2020-09-18 08:58 | 44092.3739 | 20.9 | 28.4 | 452 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 08:58
2020-09-18 08:59 | 44092.3741 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 2 |  | 3 | 9 | 51 | 392 | 21.5 | 35.5 | 414 |  | 2020-09-18 08:59 | 44092.3741 | 21.5 | 35.5 | 414 |  | caution | 2020-09-14 | B20494¦Courtroom 2¦¦Sep-18-2020 08:58
2020-09-18 08:59 | 44092.3741 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 1 |  | 1 | 11 | 42 | 425 | 21 | 28 | 434 |  | 2020-09-18 08:59 | 44092.3741 | 21 | 28 | 434 |  | low | 2020-09-14 | B25479¦Courtroom 1¦¦Sep-18-2020 08:58
2020-09-18 08:59 | 44092.3742 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 judge |  | 1 | 12 | 40 | 365 | 20 | 28 | 368 |  | 2020-09-18 08:59 | 44092.3742 | 20 | 28 | 368 |  | low | 2020-09-14 | B20772¦H15 judge¦¦Sep-18-2020 08:58
2020-09-18 08:59 | 44092.3743 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #1 |  | 2 | 10.7 | 41.1 | 414 | 18.6 | 37 | 445 |  | 2020-09-18 08:59 | 44092.3743 | 18.6 | 37 | 445 |  | caution | 2020-09-14 | B20474¦Courtroom #1¦¦Sep-18-2020 08:58
2020-09-18 08:59 | 44092.3743 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 10 | 42 | 418 | 21.2 | 29.8 | 448 |  | 2020-09-18 08:59 | 44092.3743 | 21.2 | 29.8 | 448 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 08:58
2020-09-18 08:59 | 44092.3744 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom 1 |  | 0 | 9.6 | 54.2 | 394 | 20.4 | 35 | 408 |  | 2020-09-18 08:59 | 44092.3744 | 20.4 | 35 | 408 |  | caution | 2020-09-14 | B90558¦ Courtroom 1¦¦Sep-18-2020 08:59
2020-09-18 08:59 | 44092.3744 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Crown attorney office |  | 0 | 8 | 55 | 374 | 18.5 | 47.7 | 421 | No | 2020-09-18 08:59 | 44092.3744 | 18.5 | 47.7 | 421 |  |  | 2020-09-14 | B20489¦Crown attorney office ¦¦Sep-18-2020 08:59
2020-09-18 09:00 | 44092.3747 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1- N wall |  | 0 | 14 | 48 | 440 | 22 | 49 | 580 |  | 2020-09-18 09:00 | 44092.3747 | 22 | 49 | 580 |  |  | 2020-09-14 | B25548¦1- N wall¦¦Sep-18-2020 08:59
2020-09-18 09:00 | 44092.3747 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 10 | 42 | 418 | 21.4 | 29.3 | 463 |  | 2020-09-18 09:00 | 44092.3747 | 21.4 | 29.3 | 463 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 08:59
2020-09-18 09:00 | 44092.3748 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family court waiting room |  | 1 | 8.4 | 54.9 | 371 | 20.9 | 47.9 | 435 |  | 2020-09-18 09:00 | 44092.3748 | 20.9 | 47.9 | 435 |  |  | 2020-09-14 | B20494¦Family court waiting room ¦¦Sep-18-2020 08:59
2020-09-18 09:00 | 44092.3749 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Peterborough Police |  | 3 | 10 | 45 | 415 | 22 | 31 | 533 |  | 2020-09-18 09:00 | 44092.3749 | 22 | 31 | 533 |  | low | 2020-09-14 | B70235¦Peterborough Police ¦¦Sep-18-2020 08:59
2020-09-18 09:00 | 44092.375 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 plaintiff |  | 1 | 12 | 40 | 365 | 20 | 29 | 369 |  | 2020-09-18 09:00 | 44092.375 | 20 | 29 | 369 |  | low | 2020-09-14 | B20772¦H15 plaintiff¦¦Sep-18-2020 08:59
2020-09-18 09:00 | 44092.3752 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | OPP |  | 0 | 10 | 42 | 418 | 21.4 | 29.8 | 456 |  | 2020-09-18 09:00 | 44092.3752 | 21.4 | 29.8 | 456 |  | low | 2020-09-14 | B16187¦OPP¦¦Sep-18-2020 09:00
2020-09-18 09:00 | 44092.3752 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 14 | 48 | 440 | 22 | 48 | 590 |  | 2020-09-18 09:00 | 44092.3752 | 22 | 48 | 590 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 09:00
2020-09-18 09:01 | 44092.3754 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 2 |  | 0 | 11 | 42 | 425 | 21 | 26 | 425 |  | 2020-09-18 09:01 | 44092.3754 | 21 | 26 | 425 |  | low | 2020-09-14 | B25479¦Courtroom 2¦¦Sep-18-2020 09:00
2020-09-18 09:01 | 44092.3755 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | OPP |  | 1 | 10 | 42 | 418 | 21.6 | 29.1 | 461 |  | 2020-09-18 09:01 | 44092.3755 | 21.6 | 29.1 | 461 |  | low | 2020-09-14 | B16187¦OPP¦¦Sep-18-2020 09:00
2020-09-18 09:01 | 44092.3759 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 judge |  | 0 | 10 | 45 | 415 | 30 | 27 | 427 |  | 2020-09-18 09:01 | 44092.3759 | 30 | 27 | 427 | high | low | 2020-09-14 | B70235¦Court #4 judge ¦¦Sep-18-2020 09:01
2020-09-18 09:01 | 44092.3759 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Crown attorney waiting area |  | 0 | 8 | 55 | 374 | 19.3 | 46 | 427 | No | 2020-09-18 09:01 | 44092.3759 | 19.3 | 46 | 427 |  |  | 2020-09-14 | B20489¦Crown attorney waiting area ¦¦Sep-18-2020 09:01
2020-09-18 09:01 | 44092.376 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Crown attorney |  | 0 | 10 | 42 | 418 | 21.8 | 28.5 | 476 |  | 2020-09-18 09:01 | 44092.376 | 21.8 | 28.5 | 476 |  | low | 2020-09-14 | B16187¦Crown attorney ¦¦Sep-18-2020 09:01
2020-09-18 09:01 | 44092.376 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family court office |  | 5 | 8.4 | 54.9 | 371 | 21.6 | 46.2 | 517 |  | 2020-09-18 09:01 | 44092.376 | 21.6 | 46.2 | 517 |  |  | 2020-09-14 | B20494¦Family court office¦¦Sep-18-2020 09:01
2020-09-18 09:01 | 44092.376 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 14 | 48 | 440 | 22 | 48 | 585 |  | 2020-09-18 09:01 | 44092.376 | 22 | 48 | 585 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 09:01
2020-09-18 09:01 | 44092.376 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 3 |  | 2 | 11 | 42 | 425 | 21 | 32 | 421 |  | 2020-09-18 09:01 | 44092.376 | 21 | 32 | 421 |  | low | 2020-09-14 | B25479¦Courtroom 3¦¦Sep-18-2020 09:01
2020-09-18 09:02 | 44092.3763 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 2 |  | 0 | 10 | 42 | 418 | 21.4 | 28.1 | 477 |  | 2020-09-18 09:02 | 44092.3763 | 21.4 | 28.1 | 477 |  | low | 2020-09-14 | B16187¦Court 2¦¦Sep-18-2020 09:01
2020-09-18 09:02 | 44092.3764 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 2nd floor NE hall |  | 2 | 9 | 51 | 392 | 21.9 | 41 | 455 |  | 2020-09-18 09:02 | 44092.3764 | 21.9 | 41 | 455 |  |  | 2020-09-14 | B20494¦2nd floor NE hall ¦¦Sep-18-2020 09:02
2020-09-18 09:02 | 44092.3766 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom #1 |  | 1 | 10.7 | 41.1 | 414 | 18.5 | 38.7 | 501 |  | 2020-09-18 09:02 | 44092.3766 | 18.5 | 38.7 | 501 |  | caution | 2020-09-14 | B20474¦Waiting area courtroom #1¦¦Sep-18-2020 09:02
2020-09-18 09:02 | 44092.3766 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 defendant |  | 1 | 12 | 40 | 365 | 20 | 29 | 371 |  | 2020-09-18 09:02 | 44092.3766 | 20 | 29 | 371 |  | low | 2020-09-14 | B20772¦H15 defendant¦¦Sep-18-2020 09:02
2020-09-18 09:03 | 44092.3768 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 2 |  | 0 | 10 | 42 | 418 | 21.6 | 27.7 | 467 |  | 2020-09-18 09:03 | 44092.3768 | 21.6 | 27.7 | 467 |  | low | 2020-09-14 | B16187¦Court 2¦¦Sep-18-2020 09:02
2020-09-18 09:03 | 44092.3769 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom 3 |  | 0 | 9.6 | 54.2 | 394 | 20.6 | 34.7 | 412 |  | 2020-09-18 09:03 | 44092.3769 | 20.6 | 34.7 | 412 |  | low | 2020-09-14 | B90558¦Courtroom 3¦¦Sep-18-2020 09:02
2020-09-18 09:03 | 44092.3769 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 lawyer |  | 0 | 10 | 45 | 415 | 22 | 27 | 439 |  | 2020-09-18 09:03 | 44092.3769 | 22 | 27 | 439 |  | low | 2020-09-14 | B70235¦Court #4 lawyer ¦¦Sep-18-2020 09:02
2020-09-18 09:03 | 44092.377 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Lunchroom |  | 1 | 11 | 42 | 425 | 21 | 33 | 469 |  | 2020-09-18 09:03 | 44092.377 | 21 | 33 | 469 |  | low | 2020-09-14 | B25479¦Lunchroom ¦¦Sep-18-2020 09:02
2020-09-18 09:03 | 44092.3771 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family court common |  | 1 | 8.4 | 54.9 | 371 | 21.8 | 43.9 | 486 |  | 2020-09-18 09:03 | 44092.3771 | 21.8 | 43.9 | 486 |  |  | 2020-09-14 | B20494¦Family court common ¦¦Sep-18-2020 09:03
2020-09-18 09:03 | 44092.3771 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 14 | 48 | 440 | 22 | 48 | 570 |  | 2020-09-18 09:03 | 44092.3771 | 22 | 48 | 570 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 09:03
2020-09-18 09:03 | 44092.3772 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 10 | 42 | 418 | 21.3 | 28 | 454 |  | 2020-09-18 09:03 | 44092.3772 | 21.3 | 28 | 454 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 09:03
2020-09-18 09:03 | 44092.3774 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 rear right |  | 1 | 12 | 40 | 365 | 19 | 30 | 370 |  | 2020-09-18 09:03 | 44092.3774 | 19 | 30 | 370 |  | low | 2020-09-14 | B20772¦H15 rear right ¦¦Sep-18-2020 09:03
2020-09-18 09:04 | 44092.3776 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Supervisors office |  | 1 | 11 | 42 | 425 | 21 | 33 | 484 |  | 2020-09-18 09:04 | 44092.3776 | 21 | 33 | 484 |  | low | 2020-09-14 | B25479¦Supervisors office ¦¦Sep-18-2020 09:03
2020-09-18 09:04 | 44092.3777 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 10 | 42 | 418 | 21.5 | 29.7 | 451 |  | 2020-09-18 09:04 | 44092.3777 | 21.5 | 29.7 | 451 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 09:03
2020-09-18 09:04 | 44092.3777 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 2nd floor hallway |  | 1 | 8 | 55 | 374 | 19.6 | 43.7 | 402 | No | 2020-09-18 09:04 | 44092.3777 | 19.6 | 43.7 | 402 |  |  | 2020-09-14 | B20489¦2nd floor hallway ¦¦Sep-18-2020 09:03
2020-09-18 09:04 | 44092.3778 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 213 |  | 0 | 6 | 67 | 399 | 22.3 | 30.6 | 430 | No | 2020-09-18 09:04 | 44092.3778 | 22.3 | 30.6 | 430 |  | low | 2020-09-14 | B14660¦213¦¦Sep-18-2020 09:04
2020-09-18 09:04 | 44092.3779 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 vestibule |  | 0 | 10 | 45 | 415 | 22 | 27 | 443 |  | 2020-09-18 09:04 | 44092.3779 | 22 | 27 | 443 |  | low | 2020-09-14 | B70235¦Court #4 vestibule ¦¦Sep-18-2020 09:04
2020-09-18 09:04 | 44092.3779 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 14 | 48 | 440 | 22 | 48 | 565 |  | 2020-09-18 09:04 | 44092.3779 | 22 | 48 | 565 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 09:04
2020-09-18 09:04 | 44092.378 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 10 | 42 | 418 | 21.7 | 30.3 | 457 |  | 2020-09-18 09:04 | 44092.378 | 21.7 | 30.3 | 457 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 09:04
2020-09-18 09:04 | 44092.378 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 rear left |  | 1 | 12 | 40 | 365 | 19 | 30 | 372 |  | 2020-09-18 09:04 | 44092.378 | 19 | 30 | 372 |  | low | 2020-09-14 | B20772¦H15 rear left¦¦Sep-18-2020 09:04
2020-09-18 09:05 | 44092.3782 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family office east |  | 2 | 8.4 | 54.9 | 371 | 22 | 43.9 | 472 |  | 2020-09-18 09:05 | 44092.3782 | 22 | 43.9 | 472 |  |  | 2020-09-14 | B20494¦Family office east¦¦Sep-18-2020 09:04
2020-09-18 09:05 | 44092.3784 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Upper landing of stairway |  | 1 | 10.7 | 41.1 | 414 | 18.6 | 38.6 | 527 |  | 2020-09-18 09:05 | 44092.3784 | 18.6 | 38.6 | 527 |  | caution | 2020-09-14 | B20474¦Upper landing of stairway¦¦Sep-18-2020 09:04
2020-09-18 09:05 | 44092.3786 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Cell waiting area |  | 0 | 10 | 42 | 418 | 21.4 | 29.7 | 485 |  | 2020-09-18 09:05 | 44092.3786 | 21.4 | 29.7 | 485 |  | low | 2020-09-14 | B16187¦Cell waiting area¦¦Sep-18-2020 09:05
2020-09-18 09:05 | 44092.3786 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 14 | 48 | 440 | 22 | 48 | 560 |  | 2020-09-18 09:05 | 44092.3786 | 22 | 48 | 560 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 09:05
2020-09-18 09:05 | 44092.3788 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 209 |  | 0 | 6 | 67 | 399 | 22.6 | 30.9 | 424 | No | 2020-09-18 09:05 | 44092.3788 | 22.6 | 30.9 | 424 |  | low | 2020-09-14 | B14660¦209¦¦Sep-18-2020 09:05
2020-09-18 09:05 | 44092.3788 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Intake office |  | 0 | 11 | 42 | 425 | 22 | 31 | 485 |  | 2020-09-18 09:05 | 44092.3788 | 22 | 31 | 485 |  | low | 2020-09-14 | B25479¦Intake office¦¦Sep-18-2020 09:05
2020-09-18 09:06 | 44092.3788 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice Letourneau |  | 0 | 9.6 | 54.2 | 394 | 20.8 | 38.7 | 411 |  | 2020-09-18 09:06 | 44092.3788 | 20.8 | 38.7 | 411 |  | caution | 2020-09-14 | B90558¦Justice Letourneau¦¦Sep-18-2020 09:05
2020-09-18 09:06 | 44092.379 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Basement hallway |  | 0 | 10 | 42 | 418 | 21.2 | 37.9 | 487 |  | 2020-09-18 09:06 | 44092.379 | 21.2 | 37.9 | 487 |  | caution | 2020-09-14 | B16187¦Basement hallway ¦¦Sep-18-2020 09:05
2020-09-18 09:06 | 44092.379 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 4 |  | 2 | 9 | 51 | 392 | 22 | 37.4 | 422 |  | 2020-09-18 09:06 | 44092.379 | 22 | 37.4 | 422 |  | caution | 2020-09-14 | B20494¦Courtroom 4¦¦Sep-18-2020 09:05
2020-09-18 09:06 | 44092.3791 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview Room 4 |  | 0 | 10 | 45 | 415 | 22 | 29 | 462 |  | 2020-09-18 09:06 | 44092.3791 | 22 | 29 | 462 |  | low | 2020-09-14 | B70235¦Interview Room 4¦¦Sep-18-2020 09:05
2020-09-18 09:06 | 44092.3793 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 waiting area |  | 1 | 12 | 40 | 365 | 20 | 31 | 371 |  | 2020-09-18 09:06 | 44092.3793 | 20 | 31 | 371 |  | low | 2020-09-14 | B20772¦H15 waiting area ¦¦Sep-18-2020 09:06
2020-09-18 09:06 | 44092.3793 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 10 | 42 | 418 | 21.5 | 33.3 | 465 |  | 2020-09-18 09:06 | 44092.3793 | 21.5 | 33.3 | 465 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 09:06
2020-09-18 09:07 | 44092.3796 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Main lobby south |  | 7 | 11 | 42 | 425 | 23 | 45 | 567 |  | 2020-09-18 09:07 | 44092.3796 | 23 | 45 | 567 |  |  | 2020-09-14 | B25479¦Main lobby south ¦¦Sep-18-2020 09:06
2020-09-18 09:07 | 44092.3797 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 14 | 48 | 440 | 22 | 48 | 600 |  | 2020-09-18 09:07 | 44092.3797 | 22 | 48 | 600 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 09:06
2020-09-18 09:07 | 44092.3797 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 5 |  | 1 | 8.4 | 54.9 | 371 |  |  |  | Locked door no access | 2020-09-18 09:07 | 44092.3797 | [5 empty] | 2020-09-14 | B20494¦Courtroom 5¦¦Sep-18-2020 09:06
2020-09-18 09:07 | 44092.38 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Main lobby north |  | 0 | 11 | 42 | 425 | 22 | 40 | 540 |  | 2020-09-18 09:07 | 44092.38 | 22 | 40 | 540 |  | caution | 2020-09-14 | B25479¦Main lobby north ¦¦Sep-18-2020 09:07
2020-09-18 09:07 | 44092.3801 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice Wheeler office |  | 0 | 9.6 | 54.2 | 394 | 20.7 | 38.7 | 418 |  | 2020-09-18 09:07 | 44092.3801 | 20.7 | 38.7 | 418 |  | caution | 2020-09-14 | B90558¦Justice Wheeler office¦¦Sep-18-2020 09:07
2020-09-18 09:08 | 44092.3803 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 14 | 48 | 440 | 22 | 47 | 580 |  | 2020-09-18 09:08 | 44092.3803 | 22 | 47 | 580 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 09:07
2020-09-18 09:08 | 44092.3803 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 3rd floor hallway |  | 0 | 8 | 55 | 374 | 20.6 | 43.8 | 403 | No | 2020-09-18 09:08 | 44092.3803 | 20.6 | 43.8 | 403 |  |  | 2020-09-14 | B20489¦3rd floor hallway ¦¦Sep-18-2020 09:07
2020-09-18 09:08 | 44092.3806 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Main floor at stairway |  | 1 | 10.7 | 41.1 | 414 | 18.7 | 38.6 | 585 |  | 2020-09-18 09:08 | 44092.3806 | 18.7 | 38.6 | 585 |  | caution | 2020-09-14 | B20474¦Main floor at stairway¦¦Sep-18-2020 09:08
2020-09-18 09:08 | 44092.3806 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 vestibule |  | 0 | 10 | 45 | 415 | 22 | 29 | 445 |  | 2020-09-18 09:08 | 44092.3806 | 22 | 29 | 445 |  | low | 2020-09-14 | B70235¦Court #3 vestibule ¦¦Sep-18-2020 09:08
2020-09-18 09:08 | 44092.3808 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Interview room 2 |  | 1 | 9 | 51 | 392 | 22 | 37.1 | 425 |  | 2020-09-18 09:08 | 44092.3808 | 22 | 37.1 | 425 |  | caution | 2020-09-14 | B20494¦Interview room 2¦¦Sep-18-2020 09:08
2020-09-18 09:08 | 44092.3808 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway ne |  | 1 | 8.4 | 54.9 | 371 | 22 | 40.6 | 456 |  | 2020-09-18 09:08 | 44092.3808 | 22 | 40.6 | 456 |  |  | 2020-09-14 | B20494¦Third floor hallway ne¦¦Sep-18-2020 09:08
2020-09-18 09:09 | 44092.3809 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 14 | 48 | 440 | 23 | 48 | 580 |  | 2020-09-18 09:09 | 44092.3809 | 23 | 48 | 580 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 09:08
2020-09-18 09:09 | 44092.381 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 210a |  | 1 | 6 | 67 | 399 | 22.8 | 30.9 | 437 | No | 2020-09-18 09:09 | 44092.381 | 22.8 | 30.9 | 437 |  | low | 2020-09-14 | B14660¦210a¦¦Sep-18-2020 09:08
2020-09-18 09:09 | 44092.3812 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | courtroom D |  | 1 | 8.7 | 58.7 | 419 | 16.8 | 70.6 | 489 |  | 2020-09-18 09:09 | 44092.3812 | 16.8 | 70.6 | 489 |  | high | 2020-09-14 | B20478¦courtroom D¦¦Sep-18-2020 09:08
2020-09-18 09:09 | 44092.3816 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | entryway |  | 3 | 12.6 | 56.2 | 435 | 17 | 53.3 | 592 |  | 2020-09-18 09:09 | 44092.3816 | 17 | 53.3 | 592 |  |  | 2020-09-14 | B20390¦entryway¦¦Sep-18-2020 09:09
2020-09-18 09:10 | 44092.3817 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-W wall |  | 0 | 14 | 48 | 440 | 23 | 49 | 605 |  | 2020-09-18 09:10 | 44092.3817 | 23 | 49 | 605 |  |  | 2020-09-14 | B25548¦2-W wall¦¦Sep-18-2020 09:09
2020-09-18 09:10 | 44092.3818 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview Room 2 |  | 0 | 10 | 45 | 415 | 22 | 29 | 472 |  | 2020-09-18 09:10 | 44092.3818 | 22 | 29 | 472 |  | low | 2020-09-14 | B70235¦Interview Room 2¦¦Sep-18-2020 09:09
2020-09-18 09:10 | 44092.3818 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom waiting room/entrance - Right side |  | 1 | 16.2 | 33.8 | 391 | 21 | 29.2 | 398 |  | 2020-09-18 09:10 | 44092.3818 | 21 | 29.2 | 398 |  | low | 2020-09-14 | B70277¦Courtroom waiting room/entrance - Right side¦¦Sep-18-2020 09:09
2020-09-18 09:10 | 44092.382 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Jury room |  | 0 | 8 | 55 | 374 | 21.5 | 43.1 | 399 | No | 2020-09-18 09:10 | 44092.382 | 21.5 | 43.1 | 399 |  |  | 2020-09-14 | B20489¦Jury room ¦¦Sep-18-2020 09:10
2020-09-18 09:10 | 44092.382 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice O'Brien office |  | 0 | 9.6 | 54.2 | 394 | 19.4 | 38.8 | 434 | Air conditioner running set at 17 | 2020-09-18 09:10 | 44092.382 | 19.4 | 38.8 | 434 |  | caution | 2020-09-14 | B90558¦Justice O'Brien office¦¦Sep-18-2020 09:10
2020-09-18 09:10 | 44092.382 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | courtroom B |  | 1 | 8.7 | 58.7 | 419 | 18.9 | 61.2 | 498 |  | 2020-09-18 09:10 | 44092.382 | 18.9 | 61.2 | 498 |  | caution | 2020-09-14 | B20478¦courtroom B¦¦Sep-18-2020 09:10
2020-09-18 09:10 | 44092.3822 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway se |  | 1 | 8.4 | 54.9 | 371 | 22.8 | 41.7 | 465 |  | 2020-09-18 09:10 | 44092.3822 | 22.8 | 41.7 | 465 |  |  | 2020-09-14 | B20494¦Third floor hallway se¦¦Sep-18-2020 09:10
2020-09-18 09:11 | 44092.3824 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 206 |  | 0 | 6 | 67 | 399 | 22.4 | 30.5 | 433 | No | 2020-09-18 09:11 | 44092.3824 | 22.4 | 30.5 | 433 |  | low | 2020-09-14 | B14660¦206¦¦Sep-18-2020 09:10
2020-09-18 09:11 | 44092.3824 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-W wall |  | 0 | 14 | 48 | 440 | 23 | 47 | 620 |  | 2020-09-18 09:11 | 44092.3824 | 23 | 47 | 620 |  |  | 2020-09-14 | B25548¦2-W wall¦¦Sep-18-2020 09:10
2020-09-18 09:11 | 44092.3826 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Interview room 1 |  | 1 | 9 | 51 | 392 | 21.9 | 36.8 | 440 |  | 2020-09-18 09:11 | 44092.3826 | 21.9 | 36.8 | 440 |  | caution | 2020-09-14 | B20494¦Interview room 1¦¦Sep-18-2020 09:11
2020-09-18 09:11 | 44092.3828 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room waiting room/ entrance - left side |  | 1 | 16.2 | 33.8 | 391 | 21.2 | 28.9 | 391 |  | 2020-09-18 09:11 | 44092.3828 | 21.2 | 28.9 | 391 |  | low | 2020-09-14 | B70277¦Court room waiting room/ entrance - left side¦¦Sep-18-2020 09:11
2020-09-18 09:11 | 44092.3829 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 vestibule |  | 0 | 10 | 45 | 415 | 22 | 28 | 473 |  | 2020-09-18 09:11 | 44092.3829 | 22 | 28 | 473 |  | low | 2020-09-14 | B70235¦Court #2 vestibule ¦¦Sep-18-2020 09:11
2020-09-18 09:12 | 44092.383 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-W wall |  | 0 | 14 | 48 | 440 | 23 | 48 | 620 |  | 2020-09-18 09:12 | 44092.383 | 23 | 48 | 620 |  |  | 2020-09-14 | B25548¦2-W wall¦¦Sep-18-2020 09:11
2020-09-18 09:12 | 44092.3833 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main floor waiting area |  | 7 | 12.6 | 56.2 | 435 | 19.4 | 50.5 | 527 |  | 2020-09-18 09:12 | 44092.3833 | 19.4 | 50.5 | 527 |  |  | 2020-09-14 | B20390¦Main floor waiting area¦¦Sep-18-2020 09:11
2020-09-18 09:12 | 44092.3833 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Library |  | 0 | 9.6 | 54.2 | 394 | 20.3 | 37.4 | 436 |  | 2020-09-18 09:12 | 44092.3833 | 20.3 | 37.4 | 436 |  | caution | 2020-09-14 | B90558¦Library¦¦Sep-18-2020 09:11
2020-09-18 09:13 | 44092.3838 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 14 | 48 | 440 | 23 | 47 | 650 |  | 2020-09-18 09:13 | 44092.3838 | 23 | 47 | 650 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 09:12
2020-09-18 09:13 | 44092.3838 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 judge |  | 1 | 12 | 40 | 365 | 22 | 26 | 371 |  | 2020-09-18 09:13 | 44092.3838 | 22 | 26 | 371 |  | low | 2020-09-14 | B20772¦H12 judge¦¦Sep-18-2020 09:12
2020-09-18 09:13 | 44092.3839 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | courtroom C |  | 1 | 8.7 | 58.7 | 419 | 20.8 | 50.2 | 496 |  | 2020-09-18 09:13 | 44092.3839 | 20.8 | 50.2 | 496 |  |  | 2020-09-14 | B20478¦courtroom C¦¦Sep-18-2020 09:12
2020-09-18 09:14 | 44092.3845 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 14 | 48 | 440 | 22 | 47 | 605 |  | 2020-09-18 09:14 | 44092.3845 | 22 | 47 | 605 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 09:13
2020-09-18 09:14 | 44092.3846 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 plaintiff |  | 1 | 12 | 40 | 365 | 22 | 27 | 370 |  | 2020-09-18 09:14 | 44092.3846 | 22 | 27 | 370 |  | low | 2020-09-14 | B20772¦H12 plaintiff¦¦Sep-18-2020 09:13
2020-09-18 09:14 | 44092.3846 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 2 |  | 2 | 12.6 | 56.2 | 435 | 20 | 50.2 | 548 |  | 2020-09-18 09:14 | 44092.3846 | 20 | 50.2 | 548 |  |  | 2020-09-14 | B20390¦Outside courtroom 2¦¦Sep-18-2020 09:13
2020-09-18 09:14 | 44092.3848 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - back right, facing judge |  | 1 | 16.2 | 33.8 | 391 | 21.5 | 27.5 | 391 |  | 2020-09-18 09:14 | 44092.3848 | 21.5 | 27.5 | 391 |  | low | 2020-09-14 | B70277¦Court room - back right, facing judge¦¦Sep-18-2020 09:14
2020-09-18 09:14 | 44092.3849 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Duty counsel room |  | 0 | 10 | 45 | 415 | 22 | 28 | 485 |  | 2020-09-18 09:14 | 44092.3849 | 22 | 28 | 485 |  | low | 2020-09-14 | B70235¦Duty counsel room ¦¦Sep-18-2020 09:14
2020-09-18 09:14 | 44092.385 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway nw |  | 1 | 8.5 | 54.9 | 371 | 22 | 40.7 | 425 |  | 2020-09-18 09:14 | 44092.385 | 22 | 40.7 | 425 |  |  | 2020-09-14 | B20494¦Third floor hallway nw¦¦Sep-18-2020 09:14
2020-09-18 09:15 | 44092.3851 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 14 | 48 | 440 | 22 | 47 | 640 |  | 2020-09-18 09:15 | 44092.3851 | 22 | 47 | 640 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 09:14
2020-09-18 09:15 | 44092.3852 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | TC office |  | 1 | 9.6 | 54.2 | 394 | 20.8 | 40.5 | 556 |  | 2020-09-18 09:15 | 44092.3852 | 20.8 | 40.5 | 556 |  |  | 2020-09-14 | B90558¦TC office¦¦Sep-18-2020 09:14
2020-09-18 09:15 | 44092.3852 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 303 |  | 0 | 6 | 67 | 399 | 22.6 | 31.6 | 430 | No | 2020-09-18 09:15 | 44092.3852 | 22.6 | 31.6 | 430 |  | low | 2020-09-14 | B14660¦303¦¦Sep-18-2020 09:14
2020-09-18 09:15 | 44092.3853 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 defendant |  | 1 | 12 | 40 | 365 | 22 | 27 | 370 |  | 2020-09-18 09:15 | 44092.3853 | 22 | 27 | 370 |  | low | 2020-09-14 | B20772¦H12 defendant¦¦Sep-18-2020 09:14
2020-09-18 09:15 | 44092.3853 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | courtroom A |  | 0 | 8.7 | 58.7 | 419 | 22.2 | 44.6 | 466 | No | 2020-09-18 09:15 | 44092.3853 | 22.2 | 44.6 | 466 |  |  | 2020-09-14 | B20478¦courtroom A¦¦Sep-18-2020 09:14
2020-09-18 09:15 | 44092.3855 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Private room |  | 0 | 8 | 55 | 374 | 21.6 | 44 | 407 | No | 2020-09-18 09:15 | 44092.3855 | 21.6 | 44 | 407 |  |  | 2020-09-14 | B20489¦Private room ¦¦Sep-18-2020 09:15
2020-09-18 09:15 | 44092.3856 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - back left, facing judge |  | 1 | 16.2 | 33.8 | 391 | 21.6 | 27.2 | 384 |  | 2020-09-18 09:15 | 44092.3856 | 21.6 | 27.2 | 384 |  | low | 2020-09-14 | B70277¦Court room - back left, facing judge¦¦Sep-18-2020 09:15
2020-09-18 09:15 | 44092.3856 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 3 |  | 2 | 12.6 | 56.2 | 435 | 20.2 | 48.4 | 528 |  | 2020-09-18 09:15 | 44092.3856 | 20.2 | 48.4 | 528 |  |  | 2020-09-14 | B20390¦Outside courtroom 3¦¦Sep-18-2020 09:15
2020-09-18 09:15 | 44092.3858 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 judge |  | 1 | 10 | 45 | 415 | 22 | 25 | 447 |  | 2020-09-18 09:15 | 44092.3858 | 22 | 25 | 447 |  | low | 2020-09-14 | B70235¦Court #1 judge ¦¦Sep-18-2020 09:15
2020-09-18 09:16 | 44092.3858 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 14 | 48 | 440 | 23 | 48 | 620 |  | 2020-09-18 09:16 | 44092.3858 | 23 | 48 | 620 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 09:15
2020-09-18 09:16 | 44092.386 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom waiting room |  | 0 | 20.6 | 33 | 405 | 21.4 | 49.7 | 820 |  | 2020-09-18 09:16 | 44092.386 | 21.4 | 49.7 | 820 |  |  | 2020-09-14 | B90631¦Courtroom waiting room ¦¦Sep-18-2020 09:15
2020-09-18 09:16 | 44092.386 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family service |  | 1 | 9 | 51 | 392 | 22.1 | 46.6 | 427 |  | 2020-09-18 09:16 | 44092.386 | 22.1 | 46.6 | 427 |  |  | 2020-09-14 | B20494¦Family service¦¦Sep-18-2020 09:15
2020-09-18 09:16 | 44092.3862 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 rear right |  | 1 | 12 | 40 | 365 | 22 | 27 | 371 |  | 2020-09-18 09:16 | 44092.3862 | 22 | 27 | 371 |  | low | 2020-09-14 | B20772¦H12 rear right¦¦Sep-18-2020 09:16
2020-09-18 09:16 | 44092.3863 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 302 |  | 4 | 6 | 67 | 399 | 22.6 | 28.9 | 466 | No | 2020-09-18 09:16 | 44092.3863 | 22.6 | 28.9 | 466 |  | low | 2020-09-14 | B14660¦302¦¦Sep-18-2020 09:16
2020-09-18 09:17 | 44092.3866 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 14 | 48 | 440 | 23 | 48 | 605 |  | 2020-09-18 09:17 | 44092.3866 | 23 | 48 | 605 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 09:16
2020-09-18 09:17 | 44092.3866 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 lawyer |  | 1 | 10 | 45 | 415 | 22 | 25 | 453 |  | 2020-09-18 09:17 | 44092.3866 | 22 | 25 | 453 |  | low | 2020-09-14 | B70235¦Court #1 lawyer ¦¦Sep-18-2020 09:16
2020-09-18 09:17 | 44092.3867 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Common area behind courtroom D |  | 0 | 8.7 | 58.7 | 419 | 22.5 | 43.1 | 465 | No | 2020-09-18 09:17 | 44092.3867 | 22.5 | 43.1 | 465 |  |  | 2020-09-14 | B20478¦Common area behind courtroom D¦¦Sep-18-2020 09:16
2020-09-18 09:17 | 44092.3869 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway sw |  | 1 | 8.4 | 54.9 | 371 | 23.6 | 38.1 | 424 |  | 2020-09-18 09:17 | 44092.3869 | 23.6 | 38.1 | 424 |  | caution | 2020-09-14 | B20494¦Third floor hallway sw¦¦Sep-18-2020 09:17
2020-09-18 09:17 | 44092.3869 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Court room 1 judge's desk |  | 1 | 8 | 55 | 374 | 22 | 43.2 | 397 | No | 2020-09-18 09:17 | 44092.3869 | 22 | 43.2 | 397 |  |  | 2020-09-14 | B20489¦Court room 1 judge's desk ¦¦Sep-18-2020 09:17
2020-09-18 09:17 | 44092.3869 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Civil/small claims waiting area |  | 2 | 12.6 | 56.2 | 435 | 21 | 54.4 | 530 |  | 2020-09-18 09:17 | 44092.3869 | 21 | 54.4 | 530 |  |  | 2020-09-14 | B20390¦Civil/small claims waiting area¦¦Sep-18-2020 09:17
2020-09-18 09:17 | 44092.3869 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Waiting area 2 floor |  | 1 | 9.6 | 54.2 | 394 | 20.1 | 36.3 | 417 |  | 2020-09-18 09:17 | 44092.3869 | 20.1 | 36.3 | 417 |  | caution | 2020-09-14 | B90558¦Waiting area 2 floor¦¦Sep-18-2020 09:17
2020-09-18 09:18 | 44092.3872 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom A |  | 0 | 15.1 | 32.9 | 430 | 22.3 | 25.8 | 433 |  | 2020-09-18 09:18 | 44092.3872 | 22.3 | 25.8 | 433 |  | low | 2020-09-14 | B20603¦Courtroom A¦¦Sep-18-2020 09:17
2020-09-18 09:17 | 44092.3871 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom4 corridor |  | 1 | 10.9 | 41.1 | 414 | 18.8 | 38.1 | 452 |  | 2020-09-18 09:17 | 44092.3871 | 18.8 | 38.1 | 452 |  | caution | 2020-09-14 | B20474¦Courtroom4 corridor¦¦Sep-18-2020 09:17
2020-09-18 09:17 | 44092.3871 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 14 | 48 | 440 | 23 | 48 | 600 |  | 2020-09-18 09:17 | 44092.3871 | 23 | 48 | 600 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 09:17
2020-09-18 09:17 | 44092.3871 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - facing judge, middle left |  | 1 | 16.2 | 33.8 | 391 | 21.7 | 27.1 | 380 |  | 2020-09-18 09:17 | 44092.3871 | 21.7 | 27.1 | 380 |  | low | 2020-09-14 | B70277¦Court room - facing judge, middle left¦¦Sep-18-2020 09:17
2020-09-18 09:18 | 44092.3873 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | RM14 JUDGE |  | 0 | 15 | 36 | 430 | 18 | 40 | 450 |  | 2020-09-18 09:18 | 44092.3873 | 18 | 40 | 450 |  | caution | 2020-09-14 | B70740¦RM14 JUDGE¦¦Sep-18-2020 09:17
2020-09-18 09:18 | 44092.3875 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Law library |  | 0 | 8.7 | 58.7 | 419 | 22.6 | 43.5 | 473 | No | 2020-09-18 09:18 | 44092.3875 | 22.6 | 43.5 | 473 |  |  | 2020-09-14 | B20478¦Law library¦¦Sep-18-2020 09:18
2020-09-18 09:18 | 44092.3878 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Finance waiting area |  | 1 | 12.6 | 56.2 | 435 | 21.4 | 52.2 | 534 |  | 2020-09-18 09:18 | 44092.3878 | 21.4 | 52.2 | 534 |  |  | 2020-09-14 | B20390¦Finance waiting area¦¦Sep-18-2020 09:18
2020-09-18 09:18 | 44092.3878 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- E wall |  | 0 | 14 | 48 | 440 | 23 | 47 | 580 |  | 2020-09-18 09:18 | 44092.3878 | 23 | 47 | 580 |  |  | 2020-09-14 | B25548¦2- E wall¦¦Sep-18-2020 09:18
2020-09-18 09:18 | 44092.3878 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 1w |  | 3 | 8.4 | 54.9 | 371 | 23.1 | 28.5 | 400 |  | 2020-09-18 09:18 | 44092.3878 | 23.1 | 28.5 | 400 |  | low | 2020-09-14 | B20494¦Courtroom 1w¦¦Sep-18-2020 09:18
2020-09-18 09:19 | 44092.388 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 14 |  | 0 | 15 | 36 | 430 | 18 | 36 | 440 |  | 2020-09-18 09:19 | 44092.388 | 18 | 36 | 440 |  | caution | 2020-09-14 | B70740¦14¦¦Sep-18-2020 09:18
2020-09-18 09:19 | 44092.3881 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Front hallway entrance |  | 6 | 15 | 32.6 | 435 | 19.3 | 30.2 | 446 | No | 2020-09-18 09:19 | 44092.3881 | 19.3 | 30.2 | 446 |  | low | 2020-09-14 | B21128¦Front hallway entrance ¦¦Sep-18-2020 09:18
2020-09-18 09:19 | 44092.3883 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Court room 1 gallery |  | 1 | 8 | 55 | 374 | 22.3 | 42.2 | 393 | No | 2020-09-18 09:19 | 44092.3883 | 22.3 | 42.2 | 393 |  |  | 2020-09-14 | B20489¦Court room 1 gallery ¦¦Sep-18-2020 09:19
2020-09-18 09:19 | 44092.3883 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - facing judge, middle right |  | 1 | 16.2 | 33.8 | 391 | 21.7 | 26.9 | 377 |  | 2020-09-18 09:19 | 44092.3883 | 21.7 | 26.9 | 377 |  | low | 2020-09-14 | B70277¦Court room - facing judge, middle right¦¦Sep-18-2020 09:19
2020-09-18 09:19 | 44092.3884 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 301b |  | 0 | 6 | 67 | 399 | 23 | 31.9 | 418 | No | 2020-09-18 09:19 | 44092.3884 | 23 | 31.9 | 418 |  | low | 2020-09-14 | B14660¦301b¦¦Sep-18-2020 09:19
2020-09-18 09:19 | 44092.3884 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Fire pump |  | 1 | 9 | 51 | 392 | 22.8 | 44.3 | 428 |  | 2020-09-18 09:19 | 44092.3884 | 22.8 | 44.3 | 428 |  |  | 2020-09-14 | B20494¦Fire pump¦¦Sep-18-2020 09:19
2020-09-18 09:19 | 44092.3885 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom A bench |  | 0 | 15.1 | 32.9 | 430 | 22.3 | 25.9 | 432 |  | 2020-09-18 09:19 | 44092.3885 | 22.3 | 25.9 | 432 |  | low | 2020-09-14 | B20603¦Courtroom A bench¦¦Sep-18-2020 09:19
2020-09-18 09:20 | 44092.3886 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | SEATING 14 |  | 0 | 15 | 36 | 430 | 19 | 35 | 440 |  | 2020-09-18 09:20 | 44092.3886 | 19 | 35 | 440 |  | caution | 2020-09-14 | B70740¦SEATING 14¦¦Sep-18-2020 09:19
2020-09-18 09:20 | 44092.3886 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | east stairwell |  | 0 | 8.7 | 58.7 | 419 | 23.3 | 36.7 | 474 | No | 2020-09-18 09:20 | 44092.3886 | 23.3 | 36.7 | 474 |  | caution | 2020-09-14 | B20478¦east stairwell¦¦Sep-18-2020 09:19
2020-09-18 09:20 | 44092.3886 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2- N wall |  | 0 | 14 | 48 | 440 | 23 | 47 | 630 |  | 2020-09-18 09:20 | 44092.3886 | 23 | 47 | 630 |  |  | 2020-09-14 | B25548¦2- N wall¦¦Sep-18-2020 09:19
2020-09-18 09:20 | 44092.3888 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Family services waiting area |  | 3 | 12.6 | 56.2 | 435 | 21.7 | 51.6 | 553 |  | 2020-09-18 09:20 | 44092.3888 | 21.7 | 51.6 | 553 |  |  | 2020-09-14 | B20390¦Family services waiting area¦¦Sep-18-2020 09:19
2020-09-18 09:20 | 44092.3888 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 1e |  | 3 | 8.4 | 54.9 | 371 | 22.6 | 29.4 | 391 |  | 2020-09-18 09:20 | 44092.3888 | 22.6 | 29.4 | 391 |  | low | 2020-09-14 | B20494¦Courtroom 1e¦¦Sep-18-2020 09:19
2020-09-18 09:20 | 44092.3888 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom2 2nd door |  | 1 | 10.9 | 41.1 | 414 | 18.7 | 37.7 | 451 |  | 2020-09-18 09:20 | 44092.3888 | 18.7 | 37.7 | 451 |  | caution | 2020-09-14 | B20474¦Waiting area courtroom2 2nd door¦¦Sep-18-2020 09:19
2020-09-18 09:20 | 44092.389 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 vestibule |  | 0 | 10 | 45 | 415 | 22 | 30 | 700 |  | 2020-09-18 09:20 | 44092.389 | 22 | 30 | 700 |  | low | 2020-09-14 | B70235¦Court #1 vestibule ¦¦Sep-18-2020 09:20
2020-09-18 09:20 | 44092.3892 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | FRONT HPRS |  | 0 | 15 | 36 | 430 | 20 | 33 | 450 |  | 2020-09-18 09:20 | 44092.3892 | 20 | 33 | 450 |  | low | 2020-09-14 | B70740¦FRONT HPRS¦¦Sep-18-2020 09:20
2020-09-18 09:20 | 44092.3892 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - judges desk, left side |  | 2 | 16.2 | 33.8 | 391 | 21.9 | 26.3 | 381 |  | 2020-09-18 09:20 | 44092.3892 | 21.9 | 26.3 | 381 |  | low | 2020-09-14 | B70277¦Court room - judges desk, left side¦¦Sep-18-2020 09:20
2020-09-18 09:21 | 44092.3894 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-E wall |  | 0 | 14 | 48 | 440 | 23 | 48 | 620 |  | 2020-09-18 09:21 | 44092.3894 | 23 | 48 | 620 |  |  | 2020-09-14 | B25548¦2-E wall¦¦Sep-18-2020 09:20
2020-09-18 09:21 | 44092.3895 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 403 |  | 2 | 15 | 32.6 | 435 | 20.9 | 25.3 | 435 | No | 2020-09-18 09:21 | 44092.3895 | 20.9 | 25.3 | 435 |  | low | 2020-09-14 | B21128¦403¦¦Sep-18-2020 09:20
2020-09-18 09:21 | 44092.3897 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN WR CORR |  | 0 | 15 | 36 | 430 | 20.5 | 32 | 450 |  | 2020-09-18 09:21 | 44092.3897 | 20.5 | 32 | 450 |  | low | 2020-09-14 | B70740¦MAIN WR CORR¦¦Sep-18-2020 09:21
2020-09-18 09:21 | 44092.3897 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Foyers |  | 2 | 10.3 | 58.9 | 420 | 18.1 | 43.8 | 552 |  | 2020-09-18 09:21 | 44092.3897 | 18.1 | 43.8 | 552 |  |  | 2020-09-14 | B20367¦Foyers ¦¦Sep-18-2020 09:21
2020-09-18 09:21 | 44092.3899 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Main floor common area |  | 2 | 8.7 | 58.7 | 419 | 22.3 | 36.7 | 470 | No | 2020-09-18 09:21 | 44092.3899 | 22.3 | 36.7 | 470 |  | caution | 2020-09-14 | B20478¦Main floor common area¦¦Sep-18-2020 09:21
2020-09-18 09:22 | 44092.39 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 rear left |  | 1 | 12 | 40 | 365 | 22 | 26 | 379 |  | 2020-09-18 09:22 | 44092.39 | 22 | 26 | 379 |  | low | 2020-09-14 | B20772¦H12 rear left¦¦Sep-18-2020 09:21
2020-09-18 09:22 | 44092.3901 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom B chairs |  | 0 | 15.1 | 32.9 | 430 | 22.6 | 27.3 | 434 |  | 2020-09-18 09:22 | 44092.3901 | 22.6 | 27.3 | 434 |  | low | 2020-09-14 | B20603¦Courtroom B chairs ¦¦Sep-18-2020 09:21
2020-09-18 09:22 | 44092.3901 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 13 |  | 0 | 15 | 36 | 430 | 21.3 | 35 | 470 |  | 2020-09-18 09:22 | 44092.3901 | 21.3 | 35 | 470 |  | caution | 2020-09-14 | B70740¦13¦¦Sep-18-2020 09:21
2020-09-18 09:22 | 44092.3901 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 301a |  | 0 | 6 | 67 | 399 | 22.7 | 31.2 | 405 | No | 2020-09-18 09:22 | 44092.3901 | 22.7 | 31.2 | 405 |  | low | 2020-09-14 | B14660¦301a¦¦Sep-18-2020 09:21
2020-09-18 09:22 | 44092.3902 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell, first floor |  | 1 | 12.6 | 56.2 | 435 | 21.6 | 44.6 | 472 |  | 2020-09-18 09:22 | 44092.3902 | 21.6 | 44.6 | 472 |  |  | 2020-09-14 | B20390¦Main stairwell, first floor¦¦Sep-18-2020 09:21
2020-09-18 09:22 | 44092.3903 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | Mediation room |  | 0 | 14 | 48 | 440 | 27 | 46 | 580 |  | 2020-09-18 09:22 | 44092.3903 | 27 | 46 | 580 | caution |  | 2020-09-14 | B25548¦Mediation room¦¦Sep-18-2020 09:22
2020-09-18 09:22 | 44092.3903 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 3rd floor hallway south |  | 0 | 8 | 55 | 374 | 22.1 | 39.7 | 417 | No | 2020-09-18 09:22 | 44092.3903 | 22.1 | 39.7 | 417 |  | caution | 2020-09-14 | B20489¦3rd floor hallway south ¦¦Sep-18-2020 09:22
2020-09-18 09:22 | 44092.3904 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom2 1st door |  | 1 | 10.9 | 41.1 | 414 | 18.7 | 38.2 | 493 |  | 2020-09-18 09:22 | 44092.3904 | 18.7 | 38.2 | 493 |  | caution | 2020-09-14 | B20474¦Waiting area courtroom2 1st door¦¦Sep-18-2020 09:22
2020-09-18 09:22 | 44092.3906 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | SEATING 13 |  | 0 | 15 | 36 | 430 | 21.7 | 30 | 460 |  | 2020-09-18 09:22 | 44092.3906 | 21.7 | 30 | 460 |  | low | 2020-09-14 | B70740¦SEATING 13¦¦Sep-18-2020 09:22
2020-09-18 09:23 | 44092.3906 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 retiring room |  | 1 | 12 | 40 | 365 | 22 | 28 | 375 |  | 2020-09-18 09:22 | 44092.3906 | 22 | 28 | 375 |  | low | 2020-09-14 | B20772¦H12 retiring room¦¦Sep-18-2020 09:22
2020-09-18 09:23 | 44092.3906 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | N.W hallway |  | 3 | 15 | 32.6 | 435 | 21.7 | 26.8 | 444 | No | 2020-09-18 09:23 | 44092.3906 | 21.7 | 26.8 | 444 |  | low | 2020-09-14 | B21128¦N.W hallway ¦¦Sep-18-2020 09:22
2020-09-18 09:23 | 44092.3907 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Court operations |  | 0 | 10.3 | 58.9 | 420 | 19.2 | 39.7 | 470 |  | 2020-09-18 09:23 | 44092.3907 | 19.2 | 39.7 | 470 |  | caution | 2020-09-14 | B20367¦Court operations ¦¦Sep-18-2020 09:22
2020-09-18 09:23 | 44092.3908 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - Judges desk, right side/ centre |  | 2 | 16.2 | 33.8 | 391 | 22.1 | 26 | 380 |  | 2020-09-18 09:23 | 44092.3908 | 22.1 | 26 | 380 |  | low | 2020-09-14 | B70277¦Court room - Judges desk, right side/ centre¦¦Sep-18-2020 09:22
2020-09-18 09:23 | 44092.3909 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Corridor at admin office |  | 0 | 8.7 | 58.7 | 419 | 22.1 | 37.5 | 482 | No | 2020-09-18 09:23 | 44092.3909 | 22.1 | 37.5 | 482 |  | caution | 2020-09-14 | B20478¦Corridor at admin office¦¦Sep-18-2020 09:22
2020-09-18 09:23 | 44092.3909 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom B |  | 0 | 15.1 | 27.7 | 431 | 22.3 | 28.3 | 430 |  | 2020-09-18 09:23 | 44092.3909 | 22.3 | 28.3 | 430 |  | low | 2020-09-14 | B20603¦Courtroom B¦¦Sep-18-2020 09:22
2020-09-18 09:23 | 44092.3909 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | Crown Attorney |  | 0 | 6 | 67 | 399 | 22.5 | 31.6 | 410 | No | 2020-09-18 09:23 | 44092.3909 | 22.5 | 31.6 | 410 |  | low | 2020-09-14 | B14660¦Crown Attorney¦¦Sep-18-2020 09:22
2020-09-18 09:23 | 44092.3911 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 12 |  | 0 | 15 | 36 | 430 | 22 | 32 | 470 |  | 2020-09-18 09:23 | 44092.3911 | 22 | 32 | 470 |  | low | 2020-09-14 | B70740¦12¦¦Sep-18-2020 09:23
2020-09-18 09:23 | 44092.3912 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell, second floor |  | 1 | 12.6 | 56.2 | 435 | 21.6 | 45 | 464 |  | 2020-09-18 09:23 | 44092.3912 | 21.6 | 45 | 464 |  |  | 2020-09-14 | B20390¦Main stairwell, second floor¦¦Sep-18-2020 09:23
2020-09-18 09:24 | 44092.3915 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | SEATING 12 |  | 0 | 15 | 36 | 430 | 22 | 30 | 450 |  | 2020-09-18 09:24 | 44092.3915 | 22 | 30 | 450 |  | low | 2020-09-14 | B70740¦SEATING 12¦¦Sep-18-2020 09:23
2020-09-18 09:24 | 44092.3916 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 5 |  | 0 | 10.3 | 58.9 | 420 |  |  |  | No access | 2020-09-18 09:24 | 44092.3916 | [5 empty] | 2020-09-14 | B20367¦Courtroom 5¦¦Sep-18-2020 09:23
2020-09-18 09:24 | 44092.3917 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Main office |  | 4 | 10.9 | 41.1 | 414 | 19.2 | 37.2 | 485 |  | 2020-09-18 09:24 | 44092.3917 | 19.2 | 37.2 | 485 |  | caution | 2020-09-14 | B20474¦Main office¦¦Sep-18-2020 09:24
2020-09-18 09:24 | 44092.3917 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 1st floor hall by elevator |  | 1 | 9 | 51 | 392 | 23.3 | 38.3 | 434 |  | 2020-09-18 09:24 | 44092.3917 | 23.3 | 38.3 | 434 |  | caution | 2020-09-14 | B20494¦1st floor hall by elevator¦¦Sep-18-2020 09:24
2020-09-18 09:24 | 44092.3918 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - witness stand |  | 2 | 16.2 | 33.8 | 391 | 22.1 | 25.9 | 381 |  | 2020-09-18 09:24 | 44092.3918 | 22.1 | 25.9 | 381 |  | low | 2020-09-14 | B70277¦Courtroom - witness stand¦¦Sep-18-2020 09:24
2020-09-18 09:24 | 44092.3918 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 retiring room |  | 1 | 12 | 40 | 365 | 22 | 27 | 372 |  | 2020-09-18 09:24 | 44092.3918 | 22 | 27 | 372 |  | low | 2020-09-14 | B20772¦H11 retiring room ¦¦Sep-18-2020 09:24
2020-09-18 09:24 | 44092.3919 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | 2nd floor common area |  | 0 | 8.7 | 58.7 | 419 | 22.7 | 41.2 | 502 | No | 2020-09-18 09:24 | 44092.3919 | 22.7 | 41.2 | 502 |  |  | 2020-09-14 | B20478¦2nd floor common area¦¦Sep-18-2020 09:24
2020-09-18 09:25 | 44092.3921 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom B bench |  | 0 | 15.1 | 32.9 | 430 | 22.3 | 27.5 | 431 |  | 2020-09-18 09:25 | 44092.3921 | 22.3 | 27.5 | 431 |  | low | 2020-09-14 | B20603¦Courtroom B bench ¦¦Sep-18-2020 09:24
2020-09-18 09:25 | 44092.3921 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | POLICE WAITING |  | 0 | 15 | 36 | 430 | 21.5 | 31 | 450 |  | 2020-09-18 09:25 | 44092.3921 | 21.5 | 31 | 450 |  | low | 2020-09-14 | B70740¦POLICE WAITING¦¦Sep-18-2020 09:24
2020-09-18 09:25 | 44092.3926 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 1 |  | 2 | 10.3 | 58.9 | 420 | 20.7 | 35.7 | 480 |  | 2020-09-18 09:25 | 44092.3926 | 20.7 | 35.7 | 480 |  | caution | 2020-09-14 | B20367¦Waiting room 1¦¦Sep-18-2020 09:25
2020-09-18 09:25 | 44092.3924 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 405 |  | 2 | 15 | 32.6 | 435 | 22.3 | 22.5 | 462 | No | 2020-09-18 09:25 | 44092.3924 | 22.3 | 22.5 | 462 |  | low | 2020-09-14 | B21128¦405¦¦Sep-18-2020 09:24
2020-09-18 09:25 | 44092.3927 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 11 |  | 0 | 15 | 36 | 430 | 21.7 | 35 | 440 |  | 2020-09-18 09:25 | 44092.3927 | 21.7 | 35 | 440 |  | caution | 2020-09-14 | B70740¦11¦¦Sep-18-2020 09:25
2020-09-18 09:26 | 44092.3927 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Second floor waiting area |  | 1 | 12.6 | 56.2 | 435 | 22 | 40.5 | 440 |  | 2020-09-18 09:26 | 44092.3927 | 22 | 40.5 | 440 |  |  | 2020-09-14 | B20390¦Second floor waiting area¦¦Sep-18-2020 09:25
2020-09-18 09:26 | 44092.3932 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 judge |  | 1 | 12 | 40 | 365 | 22 | 26 | 367 |  | 2020-09-18 09:26 | 44092.3932 | 22 | 26 | 367 |  | low | 2020-09-14 | B20772¦H11 judge ¦¦Sep-18-2020 09:26
2020-09-18 09:26 | 44092.3932 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN AREA |  | 2 | 15 | 36 | 430 | 21.3 | 31 | 460 |  | 2020-09-18 09:26 | 44092.3932 | 21.3 | 31 | 460 |  | low | 2020-09-14 | B70740¦MAIN AREA¦¦Sep-18-2020 09:26
2020-09-18 09:26 | 44092.3934 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | 2nd floor crown attorney corridor |  | 0 | 8.7 | 58.7 | 419 | 22.6 | 35.5 | 467 | No | 2020-09-18 09:26 | 44092.3934 | 22.6 | 35.5 | 467 |  | caution | 2020-09-14 | B20478¦2nd floor crown attorney corridor¦¦Sep-18-2020 09:26
2020-09-18 09:27 | 44092.3936 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judges chamber foyers |  | 0 | 10.3 | 58.9 | 420 | 21.5 | 37 | 487 |  | 2020-09-18 09:27 | 44092.3936 | 21.5 | 37 | 487 |  | caution | 2020-09-14 | B20367¦Judges chamber foyers ¦¦Sep-18-2020 09:26
2020-09-18 09:27 | 44092.3936 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 647 |  | 0 | 15.1 | 26.6 | 438 | 22.1 | 27.2 | 437 |  | 2020-09-18 09:27 | 44092.3936 | 22.1 | 27.2 | 437 |  | low | 2020-09-14 | B20603¦Office 647 ¦¦Sep-18-2020 09:26
2020-09-18 09:27 | 44092.3936 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 309 |  | 0 | 6 | 67 | 399 | 22.7 | 30.3 | 404 | No | 2020-09-18 09:27 | 44092.3936 | 22.7 | 30.3 | 404 |  | low | 2020-09-14 | B14660¦309¦¦Sep-18-2020 09:26
2020-09-18 09:27 | 44092.3936 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area main office |  | 1 | 10.9 | 41.1 | 414 | 19.5 | 36.6 | 484 |  | 2020-09-18 09:27 | 44092.3936 | 19.5 | 36.6 | 484 |  | caution | 2020-09-14 | B20474¦Waiting area main office ¦¦Sep-18-2020 09:26
2020-09-18 09:27 | 44092.3936 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 406 |  | 2 | 15 | 32.6 | 435 | 22.7 | 23.9 | 446 | No | 2020-09-18 09:27 | 44092.3936 | 22.7 | 23.9 | 446 |  | low | 2020-09-14 | B21128¦406¦¦Sep-18-2020 09:26
2020-09-18 09:27 | 44092.3938 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Judges chamber - |  | 2 | 16.2 | 33.8 | 391 | 21.7 | 26.4 | 387 |  | 2020-09-18 09:27 | 44092.3938 | 21.7 | 26.4 | 387 |  | low | 2020-09-14 | B70277¦Judges chamber - ¦¦Sep-18-2020 09:27
2020-09-18 09:27 | 44092.3939 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 plaintiff |  | 1 | 12 | 40 | 365 | 22 | 26 | 368 |  | 2020-09-18 09:27 | 44092.3939 | 22 | 26 | 368 |  | low | 2020-09-14 | B20772¦H11 plaintiff¦¦Sep-18-2020 09:27
2020-09-18 09:27 | 44092.3939 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Jury room waiting area |  | 1 | 12.6 | 56.2 | 435 | 22.1 | 42.7 | 432 |  | 2020-09-18 09:27 | 44092.3939 | 22.1 | 42.7 | 432 |  |  | 2020-09-14 | B20390¦Jury room waiting area¦¦Sep-18-2020 09:27
2020-09-18 09:28 | 44092.3941 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney printer room |  | 1 | 9 | 51 | 392 | 23.2 | 46.4 | 454 |  | 2020-09-18 09:28 | 44092.3941 | 23.2 | 46.4 | 454 |  |  | 2020-09-14 | B20494¦Crown attorney printer room ¦¦Sep-18-2020 09:27
2020-09-18 09:28 | 44092.3942 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judges chamber foyers |  | 0 | 10.3 | 58.9 | 420 | 21.7 |  | 498 |  | 2020-09-18 09:28 | 44092.3942 | 21.7 |  | 498 |  |  | 2020-09-14 | B20367¦Judges chamber foyers ¦¦Sep-18-2020 09:27
2020-09-18 09:28 | 44092.3943 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Judicial office corridor |  | 0 | 8.7 | 58.7 | 419 | 22.8 | 35.6 | 464 | No | 2020-09-18 09:28 | 44092.3943 | 22.8 | 35.6 | 464 |  | caution | 2020-09-14 | B20478¦Judicial office corridor¦¦Sep-18-2020 09:27
2020-09-18 09:28 | 44092.3945 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 defendant |  | 1 | 12 | 40 | 365 | 22 | 26 | 371 |  | 2020-09-18 09:28 | 44092.3945 | 22 | 26 | 371 |  | low | 2020-09-14 | B20772¦H11 defendant ¦¦Sep-18-2020 09:28
2020-09-18 09:28 | 44092.3948 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside museum |  | 1 | 12.6 | 56.2 | 435 | 22 | 42.5 | 433 |  | 2020-09-18 09:28 | 44092.3948 | 22 | 42.5 | 433 |  |  | 2020-09-14 | B20390¦Outside museum¦¦Sep-18-2020 09:28
2020-09-18 09:29 | 44092.3949 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Trial office |  | 3 | 10.9 | 41.1 | 414 | 19.4 | 36 | 469 |  | 2020-09-18 09:29 | 44092.3949 | 19.4 | 36 | 469 |  | caution | 2020-09-14 | B20474¦Trial office¦¦Sep-18-2020 09:28
2020-09-18 09:29 | 44092.395 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Judges chamber - behind desk, back door |  | 2 | 16.2 | 33.8 | 391 | 21.6 | 26.8 | 394 |  | 2020-09-18 09:29 | 44092.395 | 21.6 | 26.8 | 394 |  | low | 2020-09-14 | B70277¦Judges chamber - behind desk, back door¦¦Sep-18-2020 09:28
2020-09-18 09:29 | 44092.3951 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judicial stairwell |  | 0 | 10.3 | 58.9 | 420 | 21.7 | 39.7 | 509 |  | 2020-09-18 09:29 | 44092.3951 | 21.7 | 39.7 | 509 |  | caution | 2020-09-14 | B20367¦Judicial stairwell ¦¦Sep-18-2020 09:28
2020-09-18 09:29 | 44092.3951 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 rear right |  | 1 | 12 | 40 | 365 | 22 | 26 | 374 |  | 2020-09-18 09:29 | 44092.3951 | 22 | 26 | 374 |  | low | 2020-09-14 | B20772¦H11 rear right¦¦Sep-18-2020 09:28
2020-09-18 09:29 | 44092.3952 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 2 |  | 0 | 15.1 | 32.9 | 430 | 22.4 | 26.4 | 434 |  | 2020-09-18 09:29 | 44092.3952 | 22.4 | 26.4 | 434 |  | low | 2020-09-14 | B20603¦Office 2¦¦Sep-18-2020 09:29
2020-09-18 09:29 | 44092.3953 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | basement witness protection corridor |  | 0 | 8.7 | 58.7 | 489 | 22.6 | 40.3 | 492 | No | 2020-09-18 09:29 | 44092.3953 | 22.6 | 40.3 | 492 |  |  | 2020-09-14 | B20478¦basement witness protection corridor¦¦Sep-18-2020 09:29
2020-09-18 09:30 | 44092.3957 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 407 |  | 2 | 15 | 32.6 | 435 | 23.1 | 23.5 | 484 | No | 2020-09-18 09:30 | 44092.3957 | 23.1 | 23.5 | 484 |  | low | 2020-09-14 | B21128¦407¦¦Sep-18-2020 09:29
2020-09-18 09:30 | 44092.3957 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 rear left |  | 1 | 12 | 40 | 365 | 22 | 26 | 375 |  | 2020-09-18 09:30 | 44092.3957 | 22 | 26 | 375 |  | low | 2020-09-14 | B20772¦H11 rear left¦¦Sep-18-2020 09:29
2020-09-18 09:30 | 44092.3959 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 1 |  | 0 | 10.3 | 58.9 | 420 | 21.5 | 35.7 | 463 |  | 2020-09-18 09:30 | 44092.3959 | 21.5 | 35.7 | 463 |  | caution | 2020-09-14 | B20367¦Courtroom 1¦¦Sep-18-2020 09:30
2020-09-18 09:30 | 44092.396 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Museum |  | 1 | 12.6 | 56.2 | 435 | 21.5 | 45.6 | 437 |  | 2020-09-18 09:30 | 44092.396 | 21.5 | 45.6 | 437 |  |  | 2020-09-14 | B20390¦Museum¦¦Sep-18-2020 09:30
2020-09-18 09:31 | 44092.3962 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney office |  | 2 | 9 | 51 | 392 | 23.1 | 45.4 | 457 |  | 2020-09-18 09:31 | 44092.3962 | 23.1 | 45.4 | 457 |  |  | 2020-09-14 | B20494¦Crown attorney office¦¦Sep-18-2020 09:30
2020-09-18 09:31 | 44092.3964 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | basement corridor middle |  | 0 | 8.7 | 58.7 | 419 | 22.3 | 39.4 | 499 | No | 2020-09-18 09:31 | 44092.3964 | 22.3 | 39.4 | 499 |  | caution | 2020-09-14 | B20478¦basement corridor middle¦¦Sep-18-2020 09:30
2020-09-18 09:31 | 44092.3964 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 3 |  | 0 | 15.1 | 32.9 | 430 | 21.8 | 26.1 | 429 |  | 2020-09-18 09:31 | 44092.3964 | 21.8 | 26.1 | 429 |  | low | 2020-09-14 | B20603¦Office 3 ¦¦Sep-18-2020 09:30
2020-09-18 09:31 | 44092.3966 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Front desk |  | 6 | 10.9 | 41.1 | 414 | 19.2 | 38 | 704 |  | 2020-09-18 09:31 | 44092.3966 | 19.2 | 38 | 704 |  | caution | 2020-09-14 | B20474¦Front desk¦¦Sep-18-2020 09:31
2020-09-18 09:32 | 44092.3969 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 1 judges chamber |  | 0 | 10.3 | 58.9 | 420 | 21.4 | 38.6 | 471 |  | 2020-09-18 09:32 | 44092.3969 | 21.4 | 38.6 | 471 |  | caution | 2020-09-14 | B20367¦Courtroom 1 judges chamber ¦¦Sep-18-2020 09:31
2020-09-18 09:32 | 44092.3971 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation office - desk area |  | 2 | 16.2 | 33.8 | 391 | 21.6 | 27 | 401 |  | 2020-09-18 09:32 | 44092.3971 | 21.6 | 27 | 401 |  | low | 2020-09-14 | B70277¦Mediation office - desk area¦¦Sep-18-2020 09:31
2020-09-18 09:32 | 44092.3974 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Basement prisoner holding corridor |  | 0 | 8.7 | 58.7 | 419 | 21.7 | 49.4 | 507 | No | 2020-09-18 09:32 | 44092.3974 | 21.7 | 49.4 | 507 |  |  | 2020-09-14 | B20478¦Basement prisoner holding corridor¦¦Sep-18-2020 09:32
2020-09-18 09:32 | 44092.3974 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 6 |  | 1 | 12.6 | 56.2 | 435 | 23 | 42.5 | 438 |  | 2020-09-18 09:32 | 44092.3974 | 23 | 42.5 | 438 |  |  | 2020-09-14 | B20390¦Outside courtroom 6¦¦Sep-18-2020 09:32
2020-09-18 09:32 | 44092.3974 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H14 near exit |  | 1 | 12 | 40 | 365 | 22 | 27 | 373 |  | 2020-09-18 09:32 | 44092.3974 | 22 | 27 | 373 |  | low | 2020-09-14 | B20772¦H14 near exit¦¦Sep-18-2020 09:32
2020-09-18 09:33 | 44092.3979 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 4 |  | 0 | 15.1 | 32.9 | 430 | 21.7 | 26.9 | 437 |  | 2020-09-18 09:33 | 44092.3979 | 21.7 | 26.9 | 437 |  | low | 2020-09-14 | B20603¦Office 4 ¦¦Sep-18-2020 09:32
2020-09-18 09:33 | 44092.3979 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 408 |  | 2 | 15 | 32.6 | 435 | 23.8 | 22.7 | 540 | No | 2020-09-18 09:33 | 44092.3979 | 23.8 | 22.7 | 540 |  | low | 2020-09-14 | B21128¦408¦¦Sep-18-2020 09:32
2020-09-18 09:33 | 44092.3981 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H14 near judge entrance |  | 1 | 12 | 40 | 365 | 22 | 27 | 373 |  | 2020-09-18 09:33 | 44092.3981 | 22 | 27 | 373 |  | low | 2020-09-14 | B20772¦H14 near judge entrance ¦¦Sep-18-2020 09:33
2020-09-18 09:33 | 44092.3982 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main lobby S |  | 4 | 10 | 45 | 415 | 23 | 28 | 543 |  | 2020-09-18 09:33 | 44092.3982 | 23 | 28 | 543 |  | low | 2020-09-14 | B70235¦Main lobby S ¦¦Sep-18-2020 09:33
2020-09-18 09:34 | 44092.3984 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 2 |  | 0 | 10.3 | 58.9 | 420 | 21.2 | 32.4 | 470 |  | 2020-09-18 09:34 | 44092.3984 | 21.2 | 32.4 | 470 |  | low | 2020-09-14 | B20367¦Waiting room 2¦¦Sep-18-2020 09:33
2020-09-18 09:34 | 44092.3984 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Back stairwell, second floor |  | 1 | 12.6 | 56.2 | 435 | 22.5 | 44.7 | 433 |  | 2020-09-18 09:34 | 44092.3984 | 22.5 | 44.7 | 433 |  |  | 2020-09-14 | B20390¦Back stairwell, second floor¦¦Sep-18-2020 09:33
2020-09-18 09:34 | 44092.3986 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney library |  | 1 | 9 | 51 | 392 | 23.1 | 45.3 | 459 |  | 2020-09-18 09:34 | 44092.3986 | 23.1 | 45.3 | 459 |  |  | 2020-09-14 | B20494¦Crown attorney library ¦¦Sep-18-2020 09:33
2020-09-18 09:35 | 44092.399 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation office - printer area |  | 2 | 16.2 | 33.8 | 391 | 21.7 | 27 | 434 |  | 2020-09-18 09:35 | 44092.399 | 21.7 | 27 | 434 |  | low | 2020-09-14 | B70277¦Mediation office - printer area¦¦Sep-18-2020 09:34
2020-09-18 09:35 | 44092.3991 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Room 301 |  | 0 | 10.3 | 58.9 | 420 | 21.2 | 33.2 | 483 |  | 2020-09-18 09:35 | 44092.3991 | 21.2 | 33.2 | 483 |  | low | 2020-09-14 | B20367¦Room 301¦¦Sep-18-2020 09:34
2020-09-18 09:35 | 44092.3992 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 5 |  | 0 | 15.1 | 32.9 | 430 | 21.6 | 26.7 | 431 |  | 2020-09-18 09:35 | 44092.3992 | 21.6 | 26.7 | 431 |  | low | 2020-09-14 | B20603¦Office 5 ¦¦Sep-18-2020 09:34
2020-09-18 09:35 | 44092.3994 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Police Sergeant office |  | 1 | 10 | 45 | 415 | 23 | 28 | 572 |  | 2020-09-18 09:35 | 44092.3994 | 23 | 28 | 572 |  | low | 2020-09-14 | B70235¦Police Sergeant office ¦¦Sep-18-2020 09:35
2020-09-18 09:35 | 44092.3996 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 414 |  | 2 | 15 | 32.6 | 435 | 22.7 | 22 | 447 | No | 2020-09-18 09:35 | 44092.3996 | 22.7 | 22 | 447 |  | low | 2020-09-14 | B21128¦414¦¦Sep-18-2020 09:35
2020-09-18 09:36 | 44092.3998 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Front Lobby |  | 2 | 10.6 | 47.1 | 390 | 17.3 | 49.3 | 448 |  | 2020-09-18 09:36 | 44092.3998 | 17.3 | 49.3 | 448 |  |  | 2020-09-14 | B20550¦Front Lobby¦¦Sep-18-2020 09:35
2020-09-18 09:36 | 44092.3998 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Motion office |  | 0 | 8 | 55 | 374 | 18.3 | 49.6 | 417 | No | 2020-09-18 09:36 | 44092.3998 | 18.3 | 49.6 | 417 |  |  | 2020-09-14 | B20489¦Motion office ¦¦Sep-18-2020 09:35
2020-09-18 09:36 | 44092.4 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN OFFICE |  | 5 | 15 | 36 | 430 | 21.2 | 33 | 480 |  | 2020-09-18 09:36 | 44092.4 | 21.2 | 33 | 480 |  | low | 2020-09-14 | B70740¦MAIN OFFICE¦¦Sep-18-2020 09:36
2020-09-18 09:36 | 44092.4 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 2 |  | 0 | 10.3 | 58.9 | 420 | 20.9 | 34 | 462 |  | 2020-09-18 09:36 | 44092.4 | 20.9 | 34 | 462 |  | low | 2020-09-14 | B20367¦Courtroom 2¦¦Sep-18-2020 09:36
2020-09-18 09:36 | 44092.4002 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Crown attorneys waiting area |  | 1 | 12.6 | 56.2 | 435 | 22.3 | 36.9 | 392 |  | 2020-09-18 09:36 | 44092.4002 | 22.3 | 36.9 | 392 |  | caution | 2020-09-14 | B20390¦Crown attorneys waiting area¦¦Sep-18-2020 09:36
2020-09-18 09:36 | 44092.4003 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin waiting area |  | 1 | 12 | 37 | 392 | 17.1 | 41.2 | 481 | No | 2020-09-18 09:36 | 44092.4003 | 17.1 | 41.2 | 481 |  |  | 2020-09-14 | B20151¦Admin waiting area ¦¦Sep-18-2020 09:36
2020-09-18 09:37 | 44092.4005 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main lobby C |  | 4 | 10 | 45 | 415 | 23 | 28 | 531 |  | 2020-09-18 09:37 | 44092.4005 | 23 | 28 | 531 |  | low | 2020-09-14 | B70235¦Main lobby C ¦¦Sep-18-2020 09:36
2020-09-18 09:37 | 44092.4004 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Lunch room/kitchen - counter area |  | 2 | 16.2 | 33.8 | 391 | 21.8 | 27.3 | 426 |  | 2020-09-18 09:37 | 44092.4004 | 21.8 | 27.3 | 426 |  | low | 2020-09-14 | B70277¦Lunch room/kitchen - counter area¦¦Sep-18-2020 09:36
2020-09-18 09:37 | 44092.4008 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office a |  | 0 | 10.3 | 58.9 | 420 | 21.3 | 34.6 | 447 |  | 2020-09-18 09:37 | 44092.4008 | 21.3 | 34.6 | 447 |  | low | 2020-09-14 | B20367¦Office a¦¦Sep-18-2020 09:37
2020-09-18 09:37 | 44092.401 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 641 |  | 0 | 15.1 | 32.9 | 430 | 21.3 | 27.6 | 433 |  | 2020-09-18 09:37 | 44092.401 | 21.3 | 27.6 | 433 |  | low | 2020-09-14 | B20603¦Office 641¦¦Sep-18-2020 09:37
2020-09-18 09:37 | 44092.401 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney waiting room |  | 1 | 9 | 51 | 392 | 23.3 | 43.2 | 457 |  | 2020-09-18 09:37 | 44092.401 | 23.3 | 43.2 | 457 |  |  | 2020-09-14 | B20494¦Crown attorney waiting room¦¦Sep-18-2020 09:37
2020-09-18 09:38 | 44092.4011 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Crown attorneys reception area |  | 1 | 12.6 | 56.2 | 435 | 22.2 | 40.7 | 388 |  | 2020-09-18 09:38 | 44092.4011 | 22.2 | 40.7 | 388 |  |  | 2020-09-14 | B20390¦Crown attorneys reception area¦¦Sep-18-2020 09:37
2020-09-18 09:38 | 44092.4011 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | JUDGE COOPER OFFICE |  | 0 | 15 | 36 | 430 | 21.6 | 34 | 450 |  | 2020-09-18 09:38 | 44092.4011 | 21.6 | 34 | 450 |  | low | 2020-09-14 | B70740¦JUDGE COOPER OFFICE¦¦Sep-18-2020 09:37
2020-09-18 09:38 | 44092.4016 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | JUDGE BROWN RM |  | 0 | 15 | 36 | 430 | 21.4 | 33 | 440 |  | 2020-09-18 09:38 | 44092.4016 | 21.4 | 33 | 440 |  | low | 2020-09-14 | B70740¦JUDGE BROWN RM¦¦Sep-18-2020 09:38
2020-09-18 09:38 | 44092.4016 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - kitchen entrance area |  | 2 | 16.2 | 33.8 | 391 | 21.8 | 26.8 | 410 |  | 2020-09-18 09:38 | 44092.4016 | 21.8 | 26.8 | 410 |  | low | 2020-09-14 | B70277¦Mediation room - kitchen entrance area¦¦Sep-18-2020 09:38
2020-09-18 09:38 | 44092.4017 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office b |  | 0 | 10.3 | 58.9 | 420 | 21.7 | 32.9 | 456 |  | 2020-09-18 09:38 | 44092.4017 | 21.7 | 32.9 | 456 |  | low | 2020-09-14 | B20367¦Office b ¦¦Sep-18-2020 09:38
2020-09-18 09:39 | 44092.4023 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office c |  | 0 | 10.3 | 58.9 | 420 | 21.6 | 32.5 | 457 |  | 2020-09-18 09:39 | 44092.4023 | 21.6 | 32.5 | 457 |  | low | 2020-09-14 | B20367¦Office c¦¦Sep-18-2020 09:39
2020-09-18 09:40 | 44092.4025 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 413 |  | 2 | 15 | 32.6 | 435 | 22.4 | 24.6 | 426 | No | 2020-09-18 09:40 | 44092.4025 | 22.4 | 24.6 | 426 |  | low | 2020-09-14 | B21128¦413¦¦Sep-18-2020 09:39
2020-09-18 09:40 | 44092.4025 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 7 |  | 0 | 15.1 | 32.9 | 430 | 21.6 | 27.7 | 444 |  | 2020-09-18 09:40 | 44092.4025 | 21.6 | 27.7 | 444 |  | low | 2020-09-14 | B20603¦Office 7¦¦Sep-18-2020 09:39
2020-09-18 09:40 | 44092.4027 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 4 |  | 1 | 12.6 | 56.2 | 435 | 21.9 | 36.9 | 399 | Courtroom 4 locked | 2020-09-18 09:40 | 44092.4027 | 21.9 | 36.9 | 399 |  | caution | 2020-09-14 | B20390¦Outside courtroom 4¦¦Sep-18-2020 09:39
2020-09-18 09:41 | 44092.4034 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 3 |  | 2 | 10.3 | 58.9 | 420 |  |  |  | No access | 2020-09-18 09:41 | 44092.4034 | [5 empty] | 2020-09-14 | B20367¦Courtroom 3¦¦Sep-18-2020 09:40
2020-09-18 09:41 | 44092.4035 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Cell block |  | 1 | 9 | 51 | 392 | 22.1 | 40.2 | 438 |  | 2020-09-18 09:41 | 44092.4035 | 22.1 | 40.2 | 438 |  |  | 2020-09-14 | B20494¦Cell block¦¦Sep-18-2020 09:41
2020-09-18 09:42 | 44092.4039 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 gallery |  | 2 | 12 | 37 | 392 | 20.6 | 37.2 | 486 | No | 2020-09-18 09:42 | 44092.4039 | 20.6 | 37.2 | 486 |  | caution | 2020-09-14 | B20151¦Court room 2 gallery ¦¦Sep-18-2020 09:41
2020-09-18 09:42 | 44092.404 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 626 |  | 0 | 15.1 | 32.9 | 430 | 21.8 | 27.9 | 440 |  | 2020-09-18 09:42 | 44092.404 | 21.8 | 27.9 | 440 |  | low | 2020-09-14 | B20603¦Office 626¦¦Sep-18-2020 09:41
2020-09-18 09:42 | 44092.4041 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Courtroom 2 |  | 2 | 10.6 | 47.1 | 390 | 22.5 | 31 | 435 |  | 2020-09-18 09:42 | 44092.4041 | 22.5 | 31 | 435 |  | low | 2020-09-14 | B20550¦Courtroom 2¦¦Sep-18-2020 09:41
2020-09-18 09:42 | 44092.4042 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 3 |  | 0 | 10.3 | 58.9 | 420 | 22.2 | 32.2 | 466 |  | 2020-09-18 09:42 | 44092.4042 | 22.2 | 32.2 | 466 |  | low | 2020-09-14 | B20367¦Waiting room 3¦¦Sep-18-2020 09:42
2020-09-18 09:42 | 44092.4042 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Front lobby |  | 5 | 16 | 34 | 388 | 20 | 36 | 501 |  | 2020-09-18 09:42 | 44092.4042 | 20 | 36 | 501 |  | caution | 2020-09-14 | B19570¦Front lobby ¦¦Sep-18-2020 09:42
2020-09-18 09:42 | 44092.4045 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 5 |  | 1 | 12.6 | 56.2 | 435 | 22 | 36.6 | 406 | Courtroom 5 in use | 2020-09-18 09:42 | 44092.4045 | 22 | 36.6 | 406 |  | caution | 2020-09-14 | B20390¦Outside courtroom 5¦¦Sep-18-2020 09:42
2020-09-18 09:43 | 44092.4046 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - centre table area |  | 2 | 16.2 | 33.8 | 391 | 22.1 | 26.5 | 419 |  | 2020-09-18 09:43 | 44092.4046 | 22.1 | 26.5 | 419 |  | low | 2020-09-14 | B70277¦Mediation room - centre table area¦¦Sep-18-2020 09:42
2020-09-18 09:43 | 44092.405 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Interview room 402a |  | 0 | 10.3 | 58.9 | 420 | 23 | 30 | 469 |  | 2020-09-18 09:43 | 44092.405 | 23 | 30 | 469 |  | low | 2020-09-14 | B20367¦Interview room 402a¦¦Sep-18-2020 09:43
2020-09-18 09:43 | 44092.405 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 412 |  | 5 | 15 | 32.6 | 435 | 22.3 | 21 | 433 | No | 2020-09-18 09:43 | 44092.405 | 22.3 | 21 | 433 |  | low | 2020-09-14 | B21128¦412¦¦Sep-18-2020 09:43
2020-09-18 09:43 | 44092.4052 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Main entry |  | 4 | 9 | 51 | 392 | 22.2 | 38.1 | 481 |  | 2020-09-18 09:43 | 44092.4052 | 22.2 | 38.1 | 481 |  | caution | 2020-09-14 | B20494¦Main entry ¦¦Sep-18-2020 09:43
2020-09-18 09:44 | 44092.4054 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 judge |  | 1 | 12 | 40 | 365 | 22 | 26 | 370 |  | 2020-09-18 09:44 | 44092.4054 | 22 | 26 | 370 |  | low | 2020-09-14 | B20772¦H13 judge¦¦Sep-18-2020 09:43
2020-09-18 09:44 | 44092.4056 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Hallway nw |  | 1 | 16 | 34 | 388 | 23 | 26 | 420 |  | 2020-09-18 09:44 | 44092.4056 | 23 | 26 | 420 |  | low | 2020-09-14 | B19570¦Hallway nw ¦¦Sep-18-2020 09:44
2020-09-18 09:44 | 44092.4057 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main lobby N |  | 0 | 10 | 45 | 415 | 22 | 28 | 520 |  | 2020-09-18 09:44 | 44092.4057 | 22 | 28 | 520 |  | low | 2020-09-14 | B70235¦Main lobby N ¦¦Sep-18-2020 09:44
2020-09-18 09:44 | 44092.4057 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 judge |  | 2 | 12 | 37 | 392 | 21.3 | 35.9 | 533 | No | 2020-09-18 09:44 | 44092.4057 | 21.3 | 35.9 | 533 |  | caution | 2020-09-14 | B20151¦Court room 2 judge ¦¦Sep-18-2020 09:44
2020-09-18 09:44 | 44092.4057 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 10 |  | 0 | 15.1 | 32.9 | 430 | 21.7 | 28.9 | 440 |  | 2020-09-18 09:44 | 44092.4057 | 21.7 | 28.9 | 440 |  | low | 2020-09-14 | B20603¦Office 10¦¦Sep-18-2020 09:44
2020-09-18 09:44 | 44092.4058 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 plaintiff |  | 1 | 12 | 40 | 365 | 22 | 26 | 375 |  | 2020-09-18 09:44 | 44092.4058 | 22 | 26 | 375 |  | low | 2020-09-14 | B20772¦H13 plaintiff¦¦Sep-18-2020 09:44
2020-09-18 09:45 | 44092.4059 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 411 |  | 2 | 15 | 32.6 | 435 | 22.2 | 22.8 | 556 | No | 2020-09-18 09:44 | 44092.4059 | 22.2 | 22.8 | 556 |  | low | 2020-09-14 | B21128¦411¦¦Sep-18-2020 09:44
2020-09-18 09:45 | 44092.406 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 259 |  | 1 | 16 | 34 | 388 | 22 | 24 | 409 |  | 2020-09-18 09:45 | 44092.406 | 22 | 24 | 409 |  | low | 2020-09-14 | B19570¦259¦¦Sep-18-2020 09:44
2020-09-18 09:45 | 44092.4061 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Courtroom 1 |  | 1 | 10.6 | 47.1 | 390 | 22.5 | 31.5 | 446 |  | 2020-09-18 09:45 | 44092.4061 | 22.5 | 31.5 | 446 |  | low | 2020-09-14 | B20550¦Courtroom 1¦¦Sep-18-2020 09:44
2020-09-18 09:45 | 44092.4062 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 judge |  | 1 | 10 | 45 | 415 |  |  |  | Occupied, no access | 2020-09-18 09:45 | 44092.4062 | [5 empty] | 2020-09-14 | B70235¦Court #3 judge ¦¦Sep-18-2020 09:44
2020-09-18 09:45 | 44092.4065 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 265 |  | 1 | 16 | 34 | 388 | 22 | 25 | 406 |  | 2020-09-18 09:45 | 44092.4065 | 22 | 25 | 406 |  | low | 2020-09-14 | B19570¦265¦¦Sep-18-2020 09:45
2020-09-18 09:45 | 44092.4065 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 dependant |  | 1 | 12 | 40 | 365 | 22 | 26 | 376 |  | 2020-09-18 09:45 | 44092.4065 | 22 | 26 | 376 |  | low | 2020-09-14 | B20772¦H13 dependant¦¦Sep-18-2020 09:45
2020-09-18 09:46 | 44092.4068 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Between second floor washrooms |  | 1 | 12.6 | 56.2 | 435 | 22.3 | 41.1 | 385 |  | 2020-09-18 09:46 | 44092.4068 | 22.3 | 41.1 | 385 |  |  | 2020-09-14 | B20390¦Between second floor washrooms¦¦Sep-18-2020 09:45
2020-09-18 09:46 | 44092.4069 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - hallway entrance |  | 2 | 16.2 | 33.8 | 391 | 22.1 | 26.6 | 440 |  | 2020-09-18 09:46 | 44092.4069 | 22.1 | 26.6 | 440 |  | low | 2020-09-14 | B70277¦Mediation room - hallway entrance¦¦Sep-18-2020 09:45
2020-09-18 09:46 | 44092.4069 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 264 |  | 1 | 16 | 34 | 388 | 22 | 26 | 402 |  | 2020-09-18 09:46 | 44092.4069 | 22 | 26 | 402 |  | low | 2020-09-14 | B19570¦264¦¦Sep-18-2020 09:46
2020-09-18 09:46 | 44092.407 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 lawyer |  | 1 | 10 | 45 | 415 |  |  |  | Occupied, no access | 2020-09-18 09:46 | 44092.407 | [5 empty] | 2020-09-14 | B70235¦Court #3 lawyer ¦¦Sep-18-2020 09:46
2020-09-18 09:46 | 44092.407 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 410 |  | 2 | 15 | 32.6 | 435 | 22.1 | 21.1 | 471 | No | 2020-09-18 09:46 | 44092.407 | 22.1 | 21.1 | 471 |  | low | 2020-09-14 | B21128¦410¦¦Sep-18-2020 09:46
2020-09-18 09:46 | 44092.4071 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 rear right |  | 1 | 12 | 40 | 365 | 21 | 26 | 377 |  | 2020-09-18 09:46 | 44092.4071 | 21 | 26 | 377 |  | low | 2020-09-14 | B20772¦H13 rear right¦¦Sep-18-2020 09:46
2020-09-18 09:46 | 44092.4071 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Main entrance |  | 1 | 13.7 | 41.9 | 426 | 17.5 | 49.2 | 504 |  | 2020-09-18 09:46 | 44092.4071 | 17.5 | 49.2 | 504 |  |  | 2020-09-14 | B11228¦Main entrance¦¦Sep-18-2020 09:46
2020-09-18 09:47 | 44092.4074 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 261 |  | 1 | 16 | 34 | 388 | 22 | 25 | 403 |  | 2020-09-18 09:47 | 44092.4074 | 22 | 25 | 403 |  | low | 2020-09-14 | B19570¦261¦¦Sep-18-2020 09:46
2020-09-18 09:47 | 44092.4076 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview Room 3 |  | 1 | 10 | 45 | 415 |  |  |  | Occupied, no access | 2020-09-18 09:47 | 44092.4076 | [5 empty] | 2020-09-14 | B70235¦Interview Room 3¦¦Sep-18-2020 09:47
2020-09-18 09:47 | 44092.4076 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 rear left |  | 1 | 12 | 40 | 365 | 22 | 26 | 381 |  | 2020-09-18 09:47 | 44092.4076 | 22 | 26 | 381 |  | low | 2020-09-14 | B20772¦H13 rear left¦¦Sep-18-2020 09:47
2020-09-18 09:47 | 44092.4077 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space south |  | 0 | 15.1 | 32.9 | 430 | 21.3 | 27.1 | 441 |  | 2020-09-18 09:47 | 44092.4077 | 21.3 | 27.1 | 441 |  | low | 2020-09-14 | B20603¦Office space south¦¦Sep-18-2020 09:47
2020-09-18 09:47 | 44092.4078 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 260 |  | 1 | 16 | 34 | 388 | 22 | 25 | 401 |  | 2020-09-18 09:47 | 44092.4078 | 22 | 25 | 401 |  | low | 2020-09-14 | B19570¦260¦¦Sep-18-2020 09:47
2020-09-18 09:47 | 44092.408 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 409 |  | 6 | 15 | 32.6 | 435 | 22.1 | 22.5 | 444 | No | 2020-09-18 09:47 | 44092.408 | 22.1 | 22.5 | 444 |  | low | 2020-09-14 | B21128¦409¦¦Sep-18-2020 09:47
2020-09-18 09:48 | 44092.4082 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell, third floor |  | 1 | 12.6 | 56.2 | 435 | 22.2 | 41.4 | 416 |  | 2020-09-18 09:48 | 44092.4082 | 22.2 | 41.4 | 416 |  |  | 2020-09-14 | B20390¦Main stairwell, third floor¦¦Sep-18-2020 09:47
2020-09-18 09:48 | 44092.4082 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 3 gallery |  | 0 | 12 | 37 | 392 | 21.2 | 32.1 | 430 | No | 2020-09-18 09:48 | 44092.4082 | 21.2 | 32.1 | 430 |  | low | 2020-09-14 | B20151¦Court room 3 gallery ¦¦Sep-18-2020 09:47
2020-09-18 09:48 | 44092.4083 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Waiting area small |  | 0 | 10.6 | 47.1 | 390 | 23.1 | 28.5 | 439 |  | 2020-09-18 09:48 | 44092.4083 | 23.1 | 28.5 | 439 |  | low | 2020-09-14 | B20550¦Waiting area small¦¦Sep-18-2020 09:47
2020-09-18 09:48 | 44092.4083 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Law library n |  | 1 | 16 | 34 | 388 | 22 | 26 | 394 |  | 2020-09-18 09:48 | 44092.4083 | 22 | 26 | 394 |  | low | 2020-09-14 | B19570¦Law library n ¦¦Sep-18-2020 09:47
2020-09-18 09:48 | 44092.4083 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 judge |  | 1 | 10 | 45 | 415 |  |  |  | Occupied, no access | 2020-09-18 09:48 | 44092.4083 | [5 empty] | 2020-09-14 | B70235¦Court #2 judge ¦¦Sep-18-2020 09:47
2020-09-18 09:48 | 44092.4083 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Front stairway |  | 0 | 13.7 | 41.9 | 426 | 19.7 | 44.7 | 485 |  | 2020-09-18 09:48 | 44092.4083 | 19.7 | 44.7 | 485 |  |  | 2020-09-14 | B11228¦Front stairway¦¦Sep-18-2020 09:47
2020-09-18 09:48 | 44092.4087 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Law library s |  | 1 | 16 | 34 | 388 | 22 | 27 | 404 |  | 2020-09-18 09:48 | 44092.4087 | 22 | 27 | 404 |  | low | 2020-09-14 | B19570¦Law library s ¦¦Sep-18-2020 09:48
2020-09-18 09:49 | 44092.4089 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 lawyer |  | 1 | 10 | 45 | 415 |  |  |  | Occupied, no access | 2020-09-18 09:49 | 44092.4089 | [5 empty] | 2020-09-14 | B70235¦Court #2 lawyer ¦¦Sep-18-2020 09:48
2020-09-18 09:49 | 44092.4089 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space south 2 |  | 0 | 15.1 | 32.9 | 430 | 21.3 | 27.7 | 437 |  | 2020-09-18 09:49 | 44092.4089 | 21.3 | 27.7 | 437 |  | low | 2020-09-14 | B20603¦Office space south 2 ¦¦Sep-18-2020 09:48
2020-09-18 09:49 | 44092.4089 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 400 |  | 2 | 15 | 32.6 | 435 | 22.5 | 23 | 505 | No | 2020-09-18 09:49 | 44092.4089 | 22.5 | 23 | 505 |  | low | 2020-09-14 | B21128¦400¦¦Sep-18-2020 09:48
2020-09-18 09:49 | 44092.4091 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Third floor waiting area |  | 1 | 12.6 | 56.2 | 435 | 22.1 | 39.3 | 411 |  | 2020-09-18 09:49 | 44092.4091 | 22.1 | 39.3 | 411 |  | caution | 2020-09-14 | B20390¦Third floor waiting area¦¦Sep-18-2020 09:49
2020-09-18 09:49 | 44092.4092 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 5 top |  | 1 | 16 | 34 | 388 | 22 | 27 | 405 |  | 2020-09-18 09:49 | 44092.4092 | 22 | 27 | 405 |  | low | 2020-09-14 | B19570¦Stairwell 5 top¦¦Sep-18-2020 09:49
2020-09-18 09:49 | 44092.4092 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Duty council office - desk area |  | 2 | 16.2 | 26 | 400 | 22.2 | 26 | 399 |  | 2020-09-18 09:49 | 44092.4092 | 22.2 | 26 | 399 |  | low | 2020-09-14 | B70277¦Duty council office - desk area¦¦Sep-18-2020 09:49
2020-09-18 09:50 | 44092.4095 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Big courtroom benches |  | 0 | 13.7 | 41.9 | 426 | 20.3 | 41.5 | 431 |  | 2020-09-18 09:50 | 44092.4095 | 20.3 | 41.5 | 431 |  |  | 2020-09-14 | B11228¦Big courtroom benches¦¦Sep-18-2020 09:49
2020-09-18 09:50 | 44092.4096 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 5 bottom |  | 1 | 16 | 34 | 388 | 22 | 30 | 415 |  | 2020-09-18 09:50 | 44092.4096 | 22 | 30 | 415 |  | low | 2020-09-14 | B19570¦Stairwell 5 bottom ¦¦Sep-18-2020 09:49
2020-09-18 09:50 | 44092.4096 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Waiting area big |  | 0 | 10.6 | 47.1 | 390 | 22.8 | 28.4 | 442 |  | 2020-09-18 09:50 | 44092.4096 | 22.8 | 28.4 | 442 |  | low | 2020-09-14 | B20550¦Waiting area big¦¦Sep-18-2020 09:49
2020-09-18 09:50 | 44092.41 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE STAFF ROOM |  | 2 | 13 | 38 | 474 | 18 | 42 | 461 |  | 2020-09-18 09:50 | 44092.41 | 18 | 42 | 461 |  |  | 2020-09-14 | B20022¦JUDGE STAFF ROOM¦¦Sep-18-2020 09:50
2020-09-18 09:51 | 44092.4101 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 3 judge |  | 0 | 12 | 37 | 392 | 21 | 33 | 424 | No | 2020-09-18 09:51 | 44092.4101 | 21 | 33 | 424 |  | low | 2020-09-14 | B20151¦Court room 3 judge ¦¦Sep-18-2020 09:50
2020-09-18 09:51 | 44092.4101 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 401 |  | 7 | 15 | 32.6 | 435 | 22.3 | 20.8 | 466 | No | 2020-09-18 09:51 | 44092.4101 | 22.3 | 20.8 | 466 |  | low | 2020-09-14 | B21128¦401¦¦Sep-18-2020 09:50
2020-09-18 09:51 | 44092.4103 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Basement hall w |  | 1 | 16 | 34 | 388 | 22 | 29 | 430 |  | 2020-09-18 09:51 | 44092.4103 | 22 | 29 | 430 |  | low | 2020-09-14 | B19570¦Basement hall w ¦¦Sep-18-2020 09:50
2020-09-18 09:51 | 44092.4103 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Courtroom 1 waiting area |  | 1 | 12.6 | 56.2 | 435 | 21.6 | 39.7 | 397 |  | 2020-09-18 09:51 | 44092.4103 | 21.6 | 39.7 | 397 |  | caution | 2020-09-14 | B20390¦Courtroom 1 waiting area¦¦Sep-18-2020 09:50
2020-09-18 09:51 | 44092.4105 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space 3 |  | 0 | 15.1 | 32.9 | 430 | 21.7 | 27.2 | 448 |  | 2020-09-18 09:51 | 44092.4105 | 21.7 | 27.2 | 448 |  | low | 2020-09-14 | B20603¦Office space 3 ¦¦Sep-18-2020 09:51
2020-09-18 09:51 | 44092.4106 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Judges stand |  | 0 | 13.7 | 41.9 | 426 | 20.4 | 41.3 | 434 |  | 2020-09-18 09:51 | 44092.4106 | 20.4 | 41.3 | 434 |  |  | 2020-09-14 | B11228¦Judges stand¦¦Sep-18-2020 09:51
2020-09-18 09:51 | 44092.4106 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Security desk |  | 0 | 10.6 | 47.1 | 390 | 22.7 | 29.1 | 441 |  | 2020-09-18 09:51 | 44092.4106 | 22.7 | 29.1 | 441 |  | low | 2020-09-14 | B20550¦Security desk¦¦Sep-18-2020 09:51
2020-09-18 09:51 | 44092.4107 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court admin hall |  | 1 | 16 | 34 | 388 | 22 | 27 | 433 |  | 2020-09-18 09:51 | 44092.4107 | 22 | 27 | 433 |  | low | 2020-09-14 | B19570¦Court admin hall ¦¦Sep-18-2020 09:51
2020-09-18 09:52 | 44092.4108 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE CORKERY |  | 2 | 13 | 38 | 474 | 18 | 45 | 444 |  | 2020-09-18 09:52 | 44092.4108 | 18 | 45 | 444 |  |  | 2020-09-14 | B20022¦JUDGE CORKERY¦¦Sep-18-2020 09:51
2020-09-18 09:52 | 44092.4109 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 printer |  | 1 | 12 | 40 | 365 | 21 | 27 | 374 |  | 2020-09-18 09:52 | 44092.4109 | 21 | 27 | 374 |  | low | 2020-09-14 | B20772¦H16 printer¦¦Sep-18-2020 09:51
2020-09-18 09:52 | 44092.4112 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Employee entrance |  | 1 | 16 | 34 | 388 | 22 | 29 | 443 |  | 2020-09-18 09:52 | 44092.4112 | 22 | 29 | 443 |  | low | 2020-09-14 | B19570¦Employee entrance¦¦Sep-18-2020 09:52
2020-09-18 09:52 | 44092.4113 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 402 |  | 4 | 15 | 32.6 | 435 | 22.4 | 21.3 | 436 | No | 2020-09-18 09:52 | 44092.4113 | 22.4 | 21.3 | 436 |  | low | 2020-09-14 | B21128¦402¦¦Sep-18-2020 09:52
2020-09-18 09:52 | 44092.4114 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | VISITING JUDGE |  | 2 | 13 | 38 | 474 | 19 | 53 | 441 |  | 2020-09-18 09:52 | 44092.4114 | 19 | 53 | 441 |  |  | 2020-09-14 | B20022¦VISITING JUDGE¦¦Sep-18-2020 09:52
2020-09-18 09:53 | 44092.4115 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 judge |  | 1 | 12 | 40 | 365 | 21 | 28 | 386 |  | 2020-09-18 09:53 | 44092.4115 | 21 | 28 | 386 |  | low | 2020-09-14 | B20772¦H16 judge ¦¦Sep-18-2020 09:52
2020-09-18 09:53 | 44092.4116 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Council duty office - back right seating area |  | 2 | 16.2 | 33.8 | 391 | 16.2 | 33.8 | 391 |  | 2020-09-18 09:53 | 44092.4116 | 16.2 | 33.8 | 391 |  | low | 2020-09-14 | B70277¦Council duty office - back right seating area¦¦Sep-18-2020 09:52
2020-09-18 09:53 | 44092.4117 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Rear meeting room |  | 0 | 13.7 | 41.9 | 426 | 20.6 | 43.8 | 435 |  | 2020-09-18 09:53 | 44092.4117 | 20.6 | 43.8 | 435 |  |  | 2020-09-14 | B11228¦Rear meeting room¦¦Sep-18-2020 09:52
2020-09-18 09:53 | 44092.4117 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court servicea office |  | 1 | 16 | 34 | 388 | 22 | 28 | 448 |  | 2020-09-18 09:53 | 44092.4117 | 22 | 28 | 448 |  | low | 2020-09-14 | B19570¦Court servicea office ¦¦Sep-18-2020 09:52
2020-09-18 09:53 | 44092.4118 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space 4 |  | 1 | 15.1 | 32.9 | 430 | 22.7 | 26.7 | 453 |  | 2020-09-18 09:53 | 44092.4118 | 22.7 | 26.7 | 453 |  | low | 2020-09-14 | B20603¦Office space 4 ¦¦Sep-18-2020 09:52
2020-09-18 09:53 | 44092.4119 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE INGRAM |  | 2 | 13 | 38 | 474 | 20 | 47 | 444 |  | 2020-09-18 09:53 | 44092.4119 | 20 | 47 | 444 |  |  | 2020-09-14 | B20022¦JUDGE INGRAM¦¦Sep-18-2020 09:53
2020-09-18 09:54 | 44092.4124 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Crown attorneys office |  | 2 | 15 | 32.6 | 435 | 22.5 | 22.2 | 428 | No | 2020-09-18 09:54 | 44092.4124 | 22.5 | 22.2 | 428 |  | low | 2020-09-14 | B21128¦Crown attorneys office ¦¦Sep-18-2020 09:53
2020-09-18 09:54 | 44092.4124 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 typer |  | 1 | 12 | 40 | 365 | 21 | 28 | 384 |  | 2020-09-18 09:54 | 44092.4124 | 21 | 28 | 384 |  | low | 2020-09-14 | B20772¦H16 typer¦¦Sep-18-2020 09:53
2020-09-18 09:54 | 44092.4124 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Administration office |  | 5 | 10.3 | 58.9 | 420 | 22.5 | 36.2 | 940 |  | 2020-09-18 09:54 | 44092.4124 | 22.5 | 36.2 | 940 |  | caution | 2020-09-14 | B20367¦Administration office ¦¦Sep-18-2020 09:53
2020-09-18 09:54 | 44092.4125 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE MCLEOD |  | 2 | 13 | 38 | 474 | 20.3 | 52 | 449 |  | 2020-09-18 09:54 | 44092.4125 | 20.3 | 52 | 449 |  |  | 2020-09-14 | B20022¦JUDGE MCLEOD¦¦Sep-18-2020 09:53
2020-09-18 09:54 | 44092.4127 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Judges office |  | 0 | 13.7 | 41.9 | 426 | 20.8 | 40.6 | 431 |  | 2020-09-18 09:54 | 44092.4127 | 20.8 | 40.6 | 431 |  |  | 2020-09-14 | B11228¦Judges office¦¦Sep-18-2020 09:54
2020-09-18 09:54 | 44092.4127 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Poa office |  | 7 | 16 | 34 | 388 | 22 | 33 | 520 |  | 2020-09-18 09:54 | 44092.4127 | 22 | 33 | 520 |  | low | 2020-09-14 | B19570¦Poa office ¦¦Sep-18-2020 09:54
2020-09-18 09:54 | 44092.4127 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside third floor elevator |  | 1 | 12.6 | 56.2 | 435 | 22.1 | 40.3 | 431 |  | 2020-09-18 09:54 | 44092.4127 | 22.1 | 40.3 | 431 |  |  | 2020-09-14 | B20390¦Outside third floor elevator¦¦Sep-18-2020 09:54
2020-09-18 09:55 | 44092.4129 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Administrative office |  | 3 | 10.6 | 47.1 | 390 | 23.1 | 28.7 | 452 |  | 2020-09-18 09:55 | 44092.4129 | 23.1 | 28.7 | 452 |  | low | 2020-09-14 | B20550¦Administrative office¦¦Sep-18-2020 09:54
2020-09-18 09:55 | 44092.413 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 JUDGE |  | 2 | 13 | 38 | 474 | 20.3 | 43 | 449 |  | 2020-09-18 09:55 | 44092.413 | 20.3 | 43 | 449 |  |  | 2020-09-14 | B20022¦COURT 3 JUDGE¦¦Sep-18-2020 09:54
2020-09-18 09:55 | 44092.4131 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 plaintiff |  | 1 | 12 | 40 | 365 | 21 | 27 | 378 |  | 2020-09-18 09:55 | 44092.4131 | 21 | 27 | 378 |  | low | 2020-09-14 | B20772¦H16 plaintiff¦¦Sep-18-2020 09:54
2020-09-18 09:55 | 44092.4131 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 5 |  | 2 | 16 | 34 | 388 |  | 29 | 433 |  | 2020-09-18 09:55 | 44092.4131 |  | 29 | 433 |  | low | 2020-09-14 | B19570¦Court 5¦¦Sep-18-2020 09:54
2020-09-18 09:55 | 44092.4132 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 1 gallery |  | 2 | 12 | 37 | 392 | 21 | 26.7 | 455 | No | 2020-09-18 09:55 | 44092.4132 | 21 | 26.7 | 455 |  | low | 2020-09-14 | B20151¦Court room 1 gallery ¦¦Sep-18-2020 09:54
2020-09-18 09:55 | 44092.4132 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Administration office |  | 6 | 10.3 | 58.9 | 420 | 23 | 33.1 | 782 |  | 2020-09-18 09:55 | 44092.4132 | 23 | 33.1 | 782 |  | low | 2020-09-14 | B20367¦Administration office ¦¦Sep-18-2020 09:54
2020-09-18 09:55 | 44092.4133 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside door “302” |  | 1 | 16.2 | 33.8 | 391 | 21.9 | 26.5 | 411 |  | 2020-09-18 09:55 | 44092.4133 | 21.9 | 26.5 | 411 |  | low | 2020-09-14 | B70277¦Hallway - outside door “302”¦¦Sep-18-2020 09:55
2020-09-18 09:55 | 44092.4134 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 LAWYER |  | 2 | 13 | 38 | 474 | 20 | 43 | 442 |  | 2020-09-18 09:55 | 44092.4134 | 20 | 43 | 442 |  |  | 2020-09-14 | B20022¦COURT 3 LAWYER¦¦Sep-18-2020 09:55
2020-09-18 09:55 | 44092.4134 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Reception area office |  | 2 | 15.1 | 26.6 | 471 | 21.9 | 26.7 | 468 |  | 2020-09-18 09:55 | 44092.4134 | 21.9 | 26.7 | 468 |  | low | 2020-09-14 | B20603¦Reception area office ¦¦Sep-18-2020 09:55
2020-09-18 09:56 | 44092.4136 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 defendant |  | 1 | 12 | 40 | 365 | 21 | 27 | 374 |  | 2020-09-18 09:56 | 44092.4136 | 21 | 27 | 374 |  | low | 2020-09-14 | B20772¦H16 defendant¦¦Sep-18-2020 09:55
2020-09-18 09:56 | 44092.4138 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Side hallway |  | 0 | 13.7 | 41.9 | 426 | 21.6 | 45.3 | 485 |  | 2020-09-18 09:56 | 44092.4138 | 21.6 | 45.3 | 485 |  |  | 2020-09-14 | B11228¦Side hallway¦¦Sep-18-2020 09:55
2020-09-18 09:56 | 44092.4139 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | ADVICE COUNSEL |  | 2 | 13 | 38 | 474 | 19.7 | 35.3 | 432 |  | 2020-09-18 09:56 | 44092.4139 | 19.7 | 35.3 | 432 |  | caution | 2020-09-14 | B20022¦ADVICE COUNSEL¦¦Sep-18-2020 09:56
2020-09-18 09:56 | 44092.414 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside of duty council office |  | 1 | 16.2 | 33.8 | 391 | 22 | 25.7 | 411 |  | 2020-09-18 09:56 | 44092.414 | 22 | 25.7 | 411 |  | low | 2020-09-14 | B70277¦Hallway - outside of duty council office¦¦Sep-18-2020 09:56
2020-09-18 09:56 | 44092.4141 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 4 |  | 4 | 16 | 34 | 388 | 21 | 31 | 425 |  | 2020-09-18 09:56 | 44092.4141 | 21 | 31 | 425 |  | low | 2020-09-14 | B19570¦Court 4 ¦¦Sep-18-2020 09:56
2020-09-18 09:57 | 44092.4143 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Elevator |  | 1 | 12.6 | 56.2 | 435 | 22.9 | 41.1 | 446 |  | 2020-09-18 09:57 | 44092.4143 | 22.9 | 41.1 | 446 |  |  | 2020-09-14 | B20390¦Elevator ¦¦Sep-18-2020 09:56
2020-09-18 09:57 | 44092.4145 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 WAITING AREA |  | 2 | 13 | 38 | 474 | 19.7 | 35 | 429 |  | 2020-09-18 09:57 | 44092.4145 | 19.7 | 35 | 429 |  | caution | 2020-09-14 | B20022¦COURT 3 WAITING AREA¦¦Sep-18-2020 09:56
2020-09-18 09:57 | 44092.4145 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 3 |  | 2 | 16 | 34 | 388 | 21 | 32 | 420 |  | 2020-09-18 09:57 | 44092.4145 | 21 | 32 | 420 |  | low | 2020-09-14 | B19570¦Court 3¦¦Sep-18-2020 09:56
2020-09-18 09:57 | 44092.4146 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Lunch room |  | 0 | 10.3 | 58.9 | 420 | 20.5 | 47.7 | 515 |  | 2020-09-18 09:57 | 44092.4146 | 20.5 | 47.7 | 515 |  |  | 2020-09-14 | B90631¦Lunch room ¦¦Sep-18-2020 09:57
2020-09-18 09:57 | 44092.4148 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Back stairway |  | 0 | 13.7 | 41.9 | 426 | 22 | 39.9 | 471 |  | 2020-09-18 09:57 | 44092.4148 | 22 | 39.9 | 471 |  | caution | 2020-09-14 | B11228¦Back stairway¦¦Sep-18-2020 09:57
2020-09-18 09:57 | 44092.4148 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 waiting area |  | 0 | 12 | 37 | 392 | 21.3 | 31.3 | 448 | No | 2020-09-18 09:57 | 44092.4148 | 21.3 | 31.3 | 448 |  | low | 2020-09-14 | B20151¦Court room 2 waiting area ¦¦Sep-18-2020 09:57
2020-09-18 09:57 | 44092.4149 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Reception seating area |  | 0 | 15.1 | 32.9 | 430 | 32 | 25.3 | 474 |  | 2020-09-18 09:57 | 44092.4149 | 32 | 25.3 | 474 | high | low | 2020-09-14 | B20603¦Reception seating area ¦¦Sep-18-2020 09:57
2020-09-18 09:58 | 44092.415 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT OFFICE LOBBY |  | 2 | 13 | 38 | 474 | 19.9 | 35.9 | 447 |  | 2020-09-18 09:58 | 44092.415 | 19.9 | 35.9 | 447 |  | caution | 2020-09-14 | B20022¦COURT OFFICE LOBBY¦¦Sep-18-2020 09:57
2020-09-18 09:58 | 44092.415 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area south |  | 1 | 12 | 40 | 365 | 21 | 26 | 375 |  | 2020-09-18 09:58 | 44092.415 | 21 | 26 | 375 |  | low | 2020-09-14 | B20772¦Courtroom waiting area south¦¦Sep-18-2020 09:57
2020-09-18 09:58 | 44092.415 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - elevator lobby |  | 1 | 16.2 | 33.8 | 391 | 22.3 | 25.3 | 403 |  | 2020-09-18 09:58 | 44092.415 | 22.3 | 25.3 | 403 |  | low | 2020-09-14 | B70277¦Hallway - elevator lobby¦¦Sep-18-2020 09:57
2020-09-18 09:58 | 44092.4151 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 1 |  | 6 | 16 | 34 | 34 | 21 | 31 | 424 |  | 2020-09-18 09:58 | 44092.4151 | 21 | 31 | 424 |  | low | 2020-09-14 | B19570¦Court 1¦¦Sep-18-2020 09:57
2020-09-18 09:58 | 44092.4155 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT OFFICE |  | 2 | 13 | 38 | 474 | 20.7 | 44 | 580 |  | 2020-09-18 09:58 | 44092.4155 | 20.7 | 44 | 580 |  |  | 2020-09-14 | B20022¦COURT OFFICE¦¦Sep-18-2020 09:58
2020-09-18 09:58 | 44092.4155 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area north |  | 1 | 12 | 40 | 365 | 22 | 26 | 370 |  | 2020-09-18 09:58 | 44092.4155 | 22 | 26 | 370 |  | low | 2020-09-14 | B20772¦Courtroom waiting area north¦¦Sep-18-2020 09:58
2020-09-18 09:59 | 44092.4157 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 2 |  | 2 | 16 | 34 | 388 | 21 | 27 | 428 |  | 2020-09-18 09:59 | 44092.4157 | 21 | 27 | 428 |  | low | 2020-09-14 | B19570¦Court 2¦¦Sep-18-2020 09:58
2020-09-18 09:59 | 44092.416 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Security Area |  | 3 | 16.4 | 34.7 | 392 | 20.9 | 32.4 | 520 |  | 2020-09-18 09:59 | 44092.416 | 20.9 | 32.4 | 520 |  | low | 2020-09-14 | B17477¦Security Area¦¦Sep-18-2020 09:59
2020-09-18 09:59 | 44092.416 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Outside small courtroom |  | 0 | 13.7 | 41.9 | 426 | 21.8 | 39.2 | 467 |  | 2020-09-18 09:59 | 44092.416 | 21.8 | 39.2 | 467 |  | caution | 2020-09-14 | B11228¦Outside small courtroom¦¦Sep-18-2020 09:59
2020-09-18 09:59 | 44092.4161 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | MEDIATION ROOM |  | 2 | 13 | 38 | 474 | 20.6 | 41 | 571 |  | 2020-09-18 09:59 | 44092.4161 | 20.6 | 41 | 571 |  |  | 2020-09-14 | B20022¦MEDIATION ROOM¦¦Sep-18-2020 09:59
2020-09-18 09:59 | 44092.4161 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside of washrooms |  | 1 | 16.2 | 33.8 | 391 | 22.5 | 25 | 403 |  | 2020-09-18 09:59 | 44092.4161 | 22.5 | 25 | 403 |  | low | 2020-09-14 | B70277¦Hallway - outside of washrooms¦¦Sep-18-2020 09:59
2020-09-18 10:00 | 44092.4166 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Basement hall e |  | 1 | 16 | 34 | 388 | 22 | 27 | 422 |  | 2020-09-18 10:00 | 44092.4166 | 22 | 27 | 422 |  | low | 2020-09-14 | B19570¦Basement hall e ¦¦Sep-18-2020 09:59
2020-09-18 10:00 | 44092.4167 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | OFFICER ROOM |  | 2 | 13 | 38 | 474 | 20.3 | 39 | 517 |  | 2020-09-18 10:00 | 44092.4167 | 20.3 | 39 | 517 |  | caution | 2020-09-14 | B20022¦OFFICER ROOM¦¦Sep-18-2020 10:00
2020-09-18 10:00 | 44092.4169 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Case management |  | 4 | 10.3 | 58.9 | 420 | 21.6 | 45 | 900 |  | 2020-09-18 10:00 | 44092.4169 | 21.6 | 45 | 900 |  |  | 2020-09-14 | B90631¦Case management ¦¦Sep-18-2020 10:00
2020-09-18 10:01 | 44092.4172 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Small courtroom rear |  | 0 | 13.7 | 41.9 | 426 | 21 | 45.1 | 461 |  | 2020-09-18 10:01 | 44092.4172 | 21 | 45.1 | 461 |  |  | 2020-09-14 | B11228¦Small courtroom rear¦¦Sep-18-2020 10:00
2020-09-18 10:01 | 44092.4172 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 4 bottom |  | 1 | 16 | 34 | 388 | 21 | 32 | 437 |  | 2020-09-18 10:01 | 44092.4172 | 21 | 32 | 437 |  | low | 2020-09-14 | B19570¦Stairwell 4 bottom ¦¦Sep-18-2020 10:00
2020-09-18 10:01 | 44092.4173 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Front lobby |  | 2 | 15.6 | 25 | 434 | 16 | 44.1 | 599 |  | 2020-09-18 10:01 | 44092.4173 | 16 | 44.1 | 599 |  |  | 2020-09-14 | B19890¦Front lobby ¦¦Sep-18-2020 10:00
2020-09-18 10:01 | 44092.4173 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 1 FLOOR LOBBY |  | 4 | 13 | 38 | 474 | 20.6 | 35.6 | 536 |  | 2020-09-18 10:01 | 44092.4173 | 20.6 | 35.6 | 536 |  | caution | 2020-09-14 | B20022¦1 FLOOR LOBBY¦¦Sep-18-2020 10:00
2020-09-18 10:01 | 44092.4175 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 3 waiting area N |  | 0 | 16.4 | 34.7 | 392 | 21.6 | 33.7 | 500 |  | 2020-09-18 10:01 | 44092.4175 | 21.6 | 33.7 | 500 |  | low | 2020-09-14 | B17477¦LVL 3 waiting area N¦¦Sep-18-2020 10:01
2020-09-18 10:01 | 44092.4175 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Crown office 1 |  | 0 | 10.3 | 58.9 | 420 | 21.8 | 46.7 | 690 |  | 2020-09-18 10:01 | 44092.4175 | 21.8 | 46.7 | 690 |  |  | 2020-09-14 | B90631¦Crown office 1¦¦Sep-18-2020 10:01
2020-09-18 10:01 | 44092.4175 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 6th floor main hallway |  | 0 | 15.1 | 32.9 | 430 | 21.6 | 26 | 437 |  | 2020-09-18 10:01 | 44092.4175 | 21.6 | 26 | 437 |  | low | 2020-09-14 | B20603¦6th floor main hallway¦¦Sep-18-2020 10:01
2020-09-18 10:01 | 44092.4177 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 4 top |  | 1 | 16 | 34 | 388 | 21 | 32 | 434 |  | 2020-09-18 10:01 | 44092.4177 | 21 | 32 | 434 |  | low | 2020-09-14 | B19570¦Stairwell 4 top¦¦Sep-18-2020 10:01
2020-09-18 10:02 | 44092.4177 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | 3rd Floor Stairwell |  | 1 | 16.2 | 33.8 | 391 | 23 | 25.6 | 418 |  | 2020-09-18 10:02 | 44092.4177 | 23 | 25.6 | 418 |  | low | 2020-09-14 | B70277¦3rd Floor Stairwell¦¦Sep-18-2020 10:01
2020-09-18 10:02 | 44092.4179 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Public seating area |  | 0 | 15.6 | 25 | 434 | 17.5 | 45.1 | 547 |  | 2020-09-18 10:02 | 44092.4179 | 17.5 | 45.1 | 547 |  |  | 2020-09-14 | B19890¦Public seating area ¦¦Sep-18-2020 10:01
2020-09-18 10:02 | 44092.4179 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin office |  | 5 | 12 | 37 | 392 | 21.2 | 35.8 | 619 | No | 2020-09-18 10:02 | 44092.4179 | 21.2 | 35.8 | 619 |  | caution | 2020-09-14 | B20151¦Admin office ¦¦Sep-18-2020 10:01
2020-09-18 10:02 | 44092.418 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR LUNCH ROOM |  | 2 | 13 | 38 | 474 | 21.3 | 34.8 | 453 |  | 2020-09-18 10:02 | 44092.418 | 21.3 | 34.8 | 453 |  | low | 2020-09-14 | B20022¦2 FLOOR LUNCH ROOM¦¦Sep-18-2020 10:01
2020-09-18 10:02 | 44092.4182 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 3 waiting room S |  | 0 | 16.4 | 34.7 | 392 | 22 | 33 | 478 |  | 2020-09-18 10:02 | 44092.4182 | 22 | 33 | 478 |  | low | 2020-09-14 | B17477¦LVL 3 waiting room S¦¦Sep-18-2020 10:02
2020-09-18 10:02 | 44092.4183 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Small courtroom judges stand |  | 0 | 13.7 | 41.9 | 426 | 20.6 | 45.8 | 456 |  | 2020-09-18 10:02 | 44092.4183 | 20.6 | 45.8 | 456 |  |  | 2020-09-14 | B11228¦Small courtroom judges stand¦¦Sep-18-2020 10:02
2020-09-18 10:02 | 44092.4183 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Administration |  | 1 | 10.3 | 58.9 | 420 | 22.8 | 43.4 | 671 |  | 2020-09-18 10:02 | 44092.4183 | 22.8 | 43.4 | 671 |  |  | 2020-09-14 | B90631¦Administration ¦¦Sep-18-2020 10:02
2020-09-18 10:03 | 44092.4188 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Main entrance |  | 0 | 15.6 | 25 | 434 | 19.5 | 41.3 | 568 |  | 2020-09-18 10:03 | 44092.4188 | 19.5 | 41.3 | 568 |  |  | 2020-09-14 | B19890¦Main entrance ¦¦Sep-18-2020 10:03
2020-09-18 10:03 | 44092.4189 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 6th floor main hallway 2 |  | 0 | 15.1 | 32.9 | 430 | 21.6 | 26.4 | 432 |  | 2020-09-18 10:03 | 44092.4189 | 21.6 | 26.4 | 432 |  | low | 2020-09-14 | B20603¦6th floor main hallway 2 ¦¦Sep-18-2020 10:03
2020-09-18 10:03 | 44092.419 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Crown office 2 |  | 0 | 10.3 | 58.9 | 420 | 22.7 | 42.9 | 631 |  | 2020-09-18 10:03 | 44092.419 | 22.7 | 42.9 | 631 |  |  | 2020-09-14 | B90631¦Crown office 2¦¦Sep-18-2020 10:03
2020-09-18 10:03 | 44092.4191 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Inside elevator on 3rd floor |  | 1 | 16.2 | 33.8 | 391 | 23.2 | 26 | 450 |  | 2020-09-18 10:03 | 44092.4191 | 23.2 | 26 | 450 |  | low | 2020-09-14 | B70277¦Inside elevator on 3rd floor¦¦Sep-18-2020 10:03
2020-09-18 10:04 | 44092.4193 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Library |  | 0 | 13.7 | 41.9 | 426 | 20.2 | 44.3 | 457 |  | 2020-09-18 10:04 | 44092.4193 | 20.2 | 44.3 | 457 |  |  | 2020-09-14 | B11228¦Library¦¦Sep-18-2020 10:03
2020-09-18 10:04 | 44092.4193 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 waiting are |  | 0 | 16.4 | 34.7 | 392 | 22.6 | 32 | 415 |  | 2020-09-18 10:04 | 44092.4193 | 22.6 | 32 | 415 |  | low | 2020-09-14 | B17477¦Courtroom 300 waiting are ¦¦Sep-18-2020 10:03
2020-09-18 10:05 | 44092.4199 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 6th floor main hallway 3 |  | 0 | 15.1 | 32.9 | 430 | 21.7 | 26.3 | 433 |  | 2020-09-18 10:05 | 44092.4199 | 21.7 | 26.3 | 433 |  | low | 2020-09-14 | B20603¦6th floor main hallway 3 ¦¦Sep-18-2020 10:04
2020-09-18 10:05 | 44092.42 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin supervisor |  | 1 | 12 | 37 | 392 | 21.5 | 37 | 640 | No | 2020-09-18 10:05 | 44092.42 | 21.5 | 37 | 640 |  | caution | 2020-09-14 | B20151¦Admin supervisor ¦¦Sep-18-2020 10:04
2020-09-18 10:05 | 44092.4202 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | 1st Floor front door lobby |  | 3 | 16.2 | 33.8 | 391 | 23.2 | 25.7 | 580 |  | 2020-09-18 10:05 | 44092.4202 | 23.2 | 25.7 | 580 |  | low | 2020-09-14 | B70277¦1st Floor front door lobby¦¦Sep-18-2020 10:05
2020-09-18 10:05 | 44092.4202 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Admin office |  | 1 | 13.7 | 41.9 | 426 | 20.7 | 45.6 | 537 |  | 2020-09-18 10:05 | 44092.4202 | 20.7 | 45.6 | 537 |  |  | 2020-09-14 | B11228¦Admin office¦¦Sep-18-2020 10:05
2020-09-18 10:05 | 44092.4203 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 3 W |  | 2 | 16.4 | 34.7 | 392 | 22.7 | 33.5 | 418 |  | 2020-09-18 10:05 | 44092.4203 | 22.7 | 33.5 | 418 |  | low | 2020-09-14 | B17477¦Courtroom 3 W¦¦Sep-18-2020 10:05
2020-09-18 10:05 | 44092.4205 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Staff area |  | 2 | 15.6 | 25 | 434 | 20.8 | 36.2 | 532 |  | 2020-09-18 10:05 | 44092.4205 | 20.8 | 36.2 | 532 |  | caution | 2020-09-14 | B19890¦Staff area ¦¦Sep-18-2020 10:05
2020-09-18 10:06 | 44092.4205 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Vwap |  | 0 | 10.3 | 58.9 | 420 | 21.5 | 43.2 | 473 |  | 2020-09-18 10:06 | 44092.4205 | 21.5 | 43.2 | 473 |  |  | 2020-09-14 | B90631¦Vwap ¦¦Sep-18-2020 10:05
2020-09-18 10:06 | 44092.421 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | Courtroom 3 E |  | 2 | 16.4 | 34.7 | 392 | 23 | 33.5 | 430 |  | 2020-09-18 10:06 | 44092.421 | 23 | 33.5 | 430 |  | low | 2020-09-14 | B25548¦Courtroom 3 E¦¦Sep-18-2020 10:06
2020-09-18 10:07 | 44092.4213 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Crown office |  | 1 | 15.6 | 25 | 434 | 21.4 | 33.6 | 504 |  | 2020-09-18 10:07 | 44092.4213 | 21.4 | 33.6 | 504 |  | low | 2020-09-14 | B19890¦Crown office ¦¦Sep-18-2020 10:06
2020-09-18 10:07 | 44092.4215 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Judges chamber foyers |  | 0 | 10.3 | 58.9 | 420 | 21.5 | 43.5 | 496 |  | 2020-09-18 10:07 | 44092.4215 | 21.5 | 43.5 | 496 |  |  | 2020-09-14 | B90631¦Judges chamber foyers ¦¦Sep-18-2020 10:06
2020-09-18 10:07 | 44092.4216 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom #1 |  | 5 | 14 | 27.6 | 397 | 20.2 | 28.7 | 632 |  | 2020-09-18 10:07 | 44092.4216 | 20.2 | 28.7 | 632 |  | low | 2020-09-14 | B21554¦Courtroom #1¦¦Sep-18-2020 10:07
2020-09-18 10:07 | 44092.4219 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Court services |  | 0 | 16.4 | 34.7 | 392 | 23 | 31.8 | 424 |  | 2020-09-18 10:07 | 44092.4219 | 23 | 31.8 | 424 |  | low | 2020-09-14 | B17477¦Court services ¦¦Sep-18-2020 10:07
2020-09-18 10:08 | 44092.4221 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin file room |  | 3 | 12 | 37 | 392 | 21 | 33.7 | 613 | No | 2020-09-18 10:08 | 44092.4221 | 21 | 33.7 | 613 |  | low | 2020-09-14 | B20151¦Admin file room ¦¦Sep-18-2020 10:07
2020-09-18 10:08 | 44092.4222 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Judges chamber |  | 0 | 10.3 | 58.9 | 420 | 21.3 | 46.2 | 487 |  | 2020-09-18 10:08 | 44092.4222 | 21.3 | 46.2 | 487 |  |  | 2020-09-14 | B90631¦Judges chamber ¦¦Sep-18-2020 10:07
2020-09-18 10:08 | 44092.4222 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Duty crown hall |  | 1 | 16 | 34 | 388 | 22 | 30 | 442 |  | 2020-09-18 10:08 | 44092.4222 | 22 | 30 | 442 |  | low | 2020-09-14 | B19570¦Duty crown hall¦¦Sep-18-2020 10:08
2020-09-18 10:08 | 44092.4223 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st floor Main lobby |  | 4 | 11.4 | 44 | 420 | 16.6 | 41.2 | 487 | no | 2020-09-18 10:08 | 44092.4223 | 16.6 | 41.2 | 487 |  |  | 2020-09-14 | B70496¦1st floor Main lobby¦¦Sep-18-2020 10:08
2020-09-18 10:09 | 44092.4227 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Hallway ne |  | 1 | 16 | 34 | 388 | 22 | 26 | 433 |  | 2020-09-18 10:09 | 44092.4227 | 22 | 26 | 433 |  | low | 2020-09-14 | B19570¦Hallway ne ¦¦Sep-18-2020 10:08
2020-09-18 10:09 | 44092.4227 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL3 interview room |  | 0 | 16.4 | 34.7 | 392 | 22.9 | 31.4 | 416 |  | 2020-09-18 10:09 | 44092.4227 | 22.9 | 31.4 | 416 |  | low | 2020-09-14 | B17477¦LVL3 interview room¦¦Sep-18-2020 10:08
2020-09-18 10:09 | 44092.423 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st Floor Hall |  | 1 | 11.4 | 44 | 420 | 19 | 35.2 | 466 | no | 2020-09-18 10:09 | 44092.423 | 19 | 35.2 | 466 |  | caution | 2020-09-14 | B70496¦1st Floor Hall¦¦Sep-18-2020 10:09
2020-09-18 10:09 | 44092.423 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 251 |  | 1 | 16 | 34 | 388 | 21 | 25 | 415 |  | 2020-09-18 10:09 | 44092.423 | 21 | 25 | 415 |  | low | 2020-09-14 | B19570¦251¦¦Sep-18-2020 10:09
2020-09-18 10:09 | 44092.4231 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Public seating area 2 |  | 0 | 15.6 | 25 | 434 | 21.4 | 36.1 | 508 |  | 2020-09-18 10:09 | 44092.4231 | 21.4 | 36.1 | 508 |  | caution | 2020-09-14 | B19890¦Public seating area 2¦¦Sep-18-2020 10:09
2020-09-18 10:09 | 44092.4232 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom #2 |  | 2 | 14 | 27.6 | 397 | 20.8 | 27 | 497 |  | 2020-09-18 10:09 | 44092.4232 | 20.8 | 27 | 497 |  | low | 2020-09-14 | B21554¦Courtroom #2¦¦Sep-18-2020 10:09
2020-09-18 10:10 | 44092.4233 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom 4 |  | 0 | 10.3 | 58.9 | 420 | 22.2 | 46.6 | 535 |  | 2020-09-18 10:10 | 44092.4233 | 22.2 | 46.6 | 535 |  |  | 2020-09-14 | B90631¦Courtroom 4¦¦Sep-18-2020 10:09
2020-09-18 10:10 | 44092.4233 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center |  | 0 | 15.1 | 32.9 | 430 | 22.5 | 25.7 | 443 |  | 2020-09-18 10:10 | 44092.4233 | 22.5 | 25.7 | 443 |  | low | 2020-09-14 | B20603¦Prep center ¦¦Sep-18-2020 10:09
2020-09-18 10:10 | 44092.4234 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 251 |  | 1 | 16 | 34 | 388 | 21 | 26 | 404 |  | 2020-09-18 10:10 | 44092.4234 | 21 | 26 | 404 |  | low | 2020-09-14 | B19570¦251¦¦Sep-18-2020 10:09
2020-09-18 10:10 | 44092.4235 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL2 waiting area |  | 0 | 16.4 | 34.7 | 392 | 22.6 | 31 | 430 |  | 2020-09-18 10:10 | 44092.4235 | 22.6 | 31 | 430 |  | low | 2020-09-14 | B17477¦LVL2 waiting area¦¦Sep-18-2020 10:09
2020-09-18 10:10 | 44092.4235 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st Floor Seating |  | 1 | 11.4 | 44 | 420 | 19.7 | 32.4 | 419 | no | 2020-09-18 10:10 | 44092.4235 | 19.7 | 32.4 | 419 |  | low | 2020-09-14 | B70496¦1st Floor Seating¦¦Sep-18-2020 10:09
2020-09-18 10:10 | 44092.4238 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 245 |  | 1 | 16 | 34 | 388 | 21 | 26 | 403 |  | 2020-09-18 10:10 | 44092.4238 | 21 | 26 | 403 |  | low | 2020-09-14 | B19570¦245¦¦Sep-18-2020 10:10
2020-09-18 10:11 | 44092.424 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Courtroom 1 |  | 4 | 15.6 | 25 | 434 | 21.6 | 35.1 | 498 |  | 2020-09-18 10:11 | 44092.424 | 21.6 | 35.1 | 498 |  | caution | 2020-09-14 | B19890¦Courtroom 1¦¦Sep-18-2020 10:10
2020-09-18 10:11 | 44092.424 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center office 1 |  | 0 | 15.1 | 32.9 | 430 | 22.3 | 25.3 | 444 |  | 2020-09-18 10:11 | 44092.424 | 22.3 | 25.3 | 444 |  | low | 2020-09-14 | B20603¦Prep center office 1¦¦Sep-18-2020 10:10
2020-09-18 10:11 | 44092.4241 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 101 |  | 1 | 11.4 | 44 | 420 | 20.6 | 29.3 | 413 | no | 2020-09-18 10:11 | 44092.4241 | 20.6 | 29.3 | 413 |  | low | 2020-09-14 | B70496¦101¦¦Sep-18-2020 10:10
2020-09-18 10:11 | 44092.4242 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 247 |  | 1 | 16 | 34 | 388 | 22 | 25 | 401 |  | 2020-09-18 10:11 | 44092.4242 | 22 | 25 | 401 |  | low | 2020-09-14 | B19570¦247¦¦Sep-18-2020 10:10
2020-09-18 10:11 | 44092.4244 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Lvl1 waiting area N |  | 0 | 16.4 | 34.7 | 392 | 22.6 | 31.5 | 448 |  | 2020-09-18 10:11 | 44092.4244 | 22.6 | 31.5 | 448 |  | low | 2020-09-14 | B17477¦Lvl1 waiting area N¦¦Sep-18-2020 10:11
2020-09-18 10:11 | 44092.4245 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 2 JUDGE |  | 2 | 13 | 38 | 474 | 21.5 | 38 | 540 |  | 2020-09-18 10:11 | 44092.4245 | 21.5 | 38 | 540 |  | caution | 2020-09-14 | B20022¦COURT 2 JUDGE¦¦Sep-18-2020 10:11
2020-09-18 10:11 | 44092.4246 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 102 |  | 1 | 11.4 | 44 | 420 | 21.5 | 27.7 | 432 | no | 2020-09-18 10:11 | 44092.4246 | 21.5 | 27.7 | 432 |  | low | 2020-09-14 | B70496¦102¦¦Sep-18-2020 10:11
2020-09-18 10:11 | 44092.4246 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 244 |  | 1 | 16 | 34 | 388 | 22 | 25 | 398 |  | 2020-09-18 10:11 | 44092.4246 | 22 | 25 | 398 |  | low | 2020-09-14 | B19570¦244¦¦Sep-18-2020 10:11
2020-09-18 10:11 | 44092.4246 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom 4 waiting room |  | 0 | 10.3 | 58.9 | 420 | 21.2 | 44.2 | 584 |  | 2020-09-18 10:11 | 44092.4246 | 21.2 | 44.2 | 584 |  |  | 2020-09-14 | B90631¦Courtroom 4 waiting room ¦¦Sep-18-2020 10:11
2020-09-18 10:12 | 44092.4249 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Lvl1 waiting area S |  | 0 | 16.4 | 34.7 | 392 | 22.9 | 32.3 | 441 |  | 2020-09-18 10:12 | 44092.4249 | 22.9 | 32.3 | 441 |  | low | 2020-09-14 | B17477¦Lvl1 waiting area S¦¦Sep-18-2020 10:11
2020-09-18 10:12 | 44092.425 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom #3 |  | 4 | 14 | 27.6 | 397 | 21.3 | 31.6 | 629 |  | 2020-09-18 10:12 | 44092.425 | 21.3 | 31.6 | 629 |  | low | 2020-09-14 | B21554¦Courtroom #3¦¦Sep-18-2020 10:12
2020-09-18 10:12 | 44092.4251 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center office 610 |  | 0 | 15.1 | 32.9 | 430 | 22.4 | 24.5 | 431 |  | 2020-09-18 10:12 | 44092.4251 | 22.4 | 24.5 | 431 |  | low | 2020-09-14 | B20603¦Prep center office 610 ¦¦Sep-18-2020 10:12
2020-09-18 10:12 | 44092.4251 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 2 LAWYER |  | 2 | 13 | 38 | 474 | 21.2 | 39 | 486 |  | 2020-09-18 10:12 | 44092.4251 | 21.2 | 39 | 486 |  | caution | 2020-09-14 | B20022¦COURT 2 LAWYER¦¦Sep-18-2020 10:12
2020-09-18 10:12 | 44092.4252 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 102 |  | 1 | 11.4 | 44 | 420 | 21.6 | 26.5 | 422 | no | 2020-09-18 10:12 | 44092.4252 | 21.6 | 26.5 | 422 |  | low | 2020-09-14 | B70496¦102¦¦Sep-18-2020 10:12
2020-09-18 10:12 | 44092.4252 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Courtroom 2 |  | 0 | 15.6 | 25 | 434 | 22.9 | 36.4 | 494 |  | 2020-09-18 10:12 | 44092.4252 | 22.9 | 36.4 | 494 |  | caution | 2020-09-14 | B19890¦Courtroom 2¦¦Sep-18-2020 10:12
2020-09-18 10:13 | 44092.4256 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | stairwell |  | 1 | 11.4 | 44 | 420 | 22 | 29.6 | 435 | no | 2020-09-18 10:13 | 44092.4256 | 22 | 29.6 | 435 |  | low | 2020-09-14 | B70496¦stairwell¦¦Sep-18-2020 10:12
2020-09-18 10:13 | 44092.4258 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 JUDGE |  | 4 | 13 | 38 | 474 | 21 | 39 | 456 |  | 2020-09-18 10:13 | 44092.4258 | 21 | 39 | 456 |  | caution | 2020-09-14 | B20022¦COURT 1 JUDGE¦¦Sep-18-2020 10:13
2020-09-18 10:14 | 44092.4262 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 1 waiting area |  | 0 | 16.4 | 34.7 | 392 | 23.1 | 33.2 | 417 |  | 2020-09-18 10:14 | 44092.4262 | 23.1 | 33.2 | 417 |  | low | 2020-09-14 | B17477¦Courtroom 1 waiting area ¦¦Sep-18-2020 10:13
2020-09-18 10:14 | 44092.4264 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center office 618 |  | 0 | 15.1 | 32.9 | 430 | 22.4 | 25.5 | 433 |  | 2020-09-18 10:14 | 44092.4264 | 22.4 | 25.5 | 433 |  | low | 2020-09-14 | B20603¦Prep center office 618¦¦Sep-18-2020 10:14
2020-09-18 10:14 | 44092.4264 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 2nd floor elevator lobby |  | 1 | 11.4 | 44 | 420 | 22.3 | 31.6 | 502 | no | 2020-09-18 10:14 | 44092.4264 | 22.3 | 31.6 | 502 |  | low | 2020-09-14 | B70496¦2nd floor elevator lobby¦¦Sep-18-2020 10:14
2020-09-18 10:14 | 44092.4265 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Stairwells |  | 0 | 15.6 | 25 | 434 | 21.6 | 34 | 542 |  | 2020-09-18 10:14 | 44092.4265 | 21.6 | 34 | 542 |  | low | 2020-09-14 | B19890¦Stairwells ¦¦Sep-18-2020 10:14
2020-09-18 10:14 | 44092.4265 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 RIGHT SIDE |  | 4 | 13 | 38 | 474 | 21 | 34 | 438 |  | 2020-09-18 10:14 | 44092.4265 | 21 | 34 | 438 |  | low | 2020-09-14 | B20022¦COURT 1 RIGHT SIDE¦¦Sep-18-2020 10:14
2020-09-18 10:15 | 44092.4268 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Lvl1 interview room 1 |  | 0 | 16.4 | 34.7 | 392 | 22.8 | 32.6 | 421 |  | 2020-09-18 10:15 | 44092.4268 | 22.8 | 32.6 | 421 |  | low | 2020-09-14 | B17477¦Lvl1 interview room 1¦¦Sep-18-2020 10:14
2020-09-18 10:15 | 44092.4268 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 204 |  | 1 | 11.4 | 44 | 420 | 22.6 | 24.9 | 466 | no | 2020-09-18 10:15 | 44092.4268 | 22.6 | 24.9 | 466 |  | low | 2020-09-14 | B70496¦204¦¦Sep-18-2020 10:14
2020-09-18 10:15 | 44092.4272 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 LEFT SIDE |  | 4 | 13 | 38 | 474 | 20.9 | 34 | 434 |  | 2020-09-18 10:15 | 44092.4272 | 20.9 | 34 | 434 |  | low | 2020-09-14 | B20022¦COURT 1 LEFT SIDE¦¦Sep-18-2020 10:15
2020-09-18 10:15 | 44092.4272 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 204 |  | 1 | 11.4 | 44 | 420 | 22.3 | 25.5 | 582 | no | 2020-09-18 10:15 | 44092.4272 | 22.3 | 25.5 | 582 |  | low | 2020-09-14 | B70496¦204¦¦Sep-18-2020 10:15
2020-09-18 10:15 | 44092.4274 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Lvl1 interview room 2 |  | 0 | 16.4 | 34.7 | 392 | 22.8 | 32.6 | 425 |  | 2020-09-18 10:15 | 44092.4274 | 22.8 | 32.6 | 425 |  | low | 2020-09-14 | B17477¦Lvl1 interview room 2¦¦Sep-18-2020 10:15
2020-09-18 10:16 | 44092.4276 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JURY ROOM |  | 3 | 13 | 38 | 474 | 21 | 37 | 440 |  | 2020-09-18 10:16 | 44092.4276 | 21 | 37 | 440 |  | caution | 2020-09-14 | B20022¦JURY ROOM¦¦Sep-18-2020 10:15
2020-09-18 10:16 | 44092.4277 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Main hallway |  | 0 | 15.6 | 25 | 434 | 21.7 | 35.3 | 552 |  | 2020-09-18 10:16 | 44092.4277 | 21.7 | 35.3 | 552 |  | caution | 2020-09-14 | B19890¦Main hallway ¦¦Sep-18-2020 10:15
2020-09-18 10:16 | 44092.4277 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 2nd Floor hallway |  | 1 | 11.4 | 44 | 420 | 22.3 | 27.3 | 456 | no | 2020-09-18 10:16 | 44092.4277 | 22.3 | 27.3 | 456 |  | low | 2020-09-14 | B70496¦2nd Floor hallway¦¦Sep-18-2020 10:15
2020-09-18 10:17 | 44092.4281 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 203 |  | 1 | 11.4 | 44 | 420 | 21.3 | 31.1 | 437 | no | 2020-09-18 10:17 | 44092.4281 | 21.3 | 31.1 | 437 |  | low | 2020-09-14 | B70496¦203¦¦Sep-18-2020 10:16
2020-09-18 10:17 | 44092.4286 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Waiting area outside courtroom3 |  | 1 | 14 | 27.6 | 397 | 21.7 | 26.4 | 536 |  | 2020-09-18 10:17 | 44092.4286 | 21.7 | 26.4 | 536 |  | low | 2020-09-14 | B21554¦Waiting area outside courtroom3¦¦Sep-18-2020 10:17
2020-09-18 10:17 | 44092.4286 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 202 |  | 3 | 11.4 | 44 | 420 | 21.7 | 28.2 | 534 | no | 2020-09-18 10:17 | 44092.4286 | 21.7 | 28.2 | 534 |  | low | 2020-09-14 | B70496¦202¦¦Sep-18-2020 10:17
2020-09-18 10:18 | 44092.4291 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 201 |  | 8 | 11.4 | 44 | 420 | 21.7 | 29.4 | 486 | no | 2020-09-18 10:18 | 44092.4291 | 21.7 | 29.4 | 486 |  | low | 2020-09-14 | B70496¦201¦¦Sep-18-2020 10:17
2020-09-18 10:18 | 44092.4294 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center 2 |  | 0 | 15.1 | 32.9 | 430 | 22.2 | 25.5 | 457 |  | 2020-09-18 10:18 | 44092.4294 | 22.2 | 25.5 | 457 |  | low | 2020-09-14 | B20603¦Prep center 2 ¦¦Sep-18-2020 10:18
2020-09-18 10:18 | 44092.4294 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Lvl4 waiting room south |  | 0 | 16.4 | 34.7 | 392 | 22.7 | 30.8 | 441 | Could not access courtroom 1 | 2020-09-18 10:18 | 44092.4294 | 22.7 | 30.8 | 441 |  | low | 2020-09-14 | B17477¦Lvl4 waiting room south¦¦Sep-18-2020 10:18
2020-09-18 10:19 | 44092.4296 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | Administration Office |  | 3 | 11.4 | 44 | 420 | 21.7 | 29.4 | 486 | no | 2020-09-18 10:19 | 44092.4296 | 21.7 | 29.4 | 486 |  | low | 2020-09-14 | B70496¦Administration Office¦¦Sep-18-2020 10:18
2020-09-18 10:19 | 44092.4299 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR LEFT MEETING |  | 2 | 13 | 38 | 474 | 21.7 | 40.8 | 560 |  | 2020-09-18 10:19 | 44092.4299 | 21.7 | 40.8 | 560 |  |  | 2020-09-14 | B20022¦2 FLOOR LEFT MEETING¦¦Sep-18-2020 10:19
2020-09-18 10:20 | 44092.4302 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | Outside Customer Service Entrance |  | 1 | 11.4 | 44 | 420 | 9 | 56 | 401 | no | 2020-09-18 10:20 | 44092.4302 | 9 | 56 | 401 |  |  | 2020-09-14 | B70496¦Outside Customer Service Entrance ¦¦Sep-18-2020 10:19
2020-09-18 10:20 | 44092.4302 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Lvl4 waiting area N |  | 0 | 16.4 | 34.7 | 392 | 22.8 | 29.6 | 427 |  | 2020-09-18 10:20 | 44092.4302 | 22.8 | 29.6 | 427 |  | low | 2020-09-14 | B17477¦Lvl4 waiting area N¦¦Sep-18-2020 10:19
2020-09-18 10:20 | 44092.4304 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Basement corridor at washrooms |  | 1 | 14 | 27.6 | 397 | 22.3 | 27.6 | 553 |  | 2020-09-18 10:20 | 44092.4304 | 22.3 | 27.6 | 553 |  | low | 2020-09-14 | B21554¦Basement corridor at washrooms¦¦Sep-18-2020 10:19
2020-09-18 10:20 | 44092.4305 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR RIGHT MEETING |  | 2 | 13 | 38 | 474 | 21.7 | 41 | 459 |  | 2020-09-18 10:20 | 44092.4305 | 21.7 | 41 | 459 |  |  | 2020-09-14 | B20022¦2 FLOOR RIGHT MEETING¦¦Sep-18-2020 10:19
2020-09-18 10:20 | 44092.4306 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office hallway |  | 0 | 15.1 | 32.9 | 430 | 22.3 | 25.4 | 446 |  | 2020-09-18 10:20 | 44092.4306 | 22.3 | 25.4 | 446 |  | low | 2020-09-14 | B20603¦Office hallway ¦¦Sep-18-2020 10:20
2020-09-18 10:20 | 44092.4308 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 4 waiting area |  | 0 | 16.4 | 34.7 | 392 | 22.7 | 30.5 | 425 |  | 2020-09-18 10:20 | 44092.4308 | 22.7 | 30.5 | 425 |  | low | 2020-09-14 | B17477¦Courtroom 4 waiting area¦¦Sep-18-2020 10:20
2020-09-18 10:21 | 44092.4311 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 1 FLOOR MAIN HALL |  | 5 | 13 | 38 | 474 | 21.7 | 30.7 | 462 |  | 2020-09-18 10:21 | 44092.4311 | 21.7 | 30.7 | 462 |  | low | 2020-09-14 | B20022¦1 FLOOR MAIN HALL¦¦Sep-18-2020 10:20
2020-09-18 10:21 | 44092.4316 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Basement corridor at exit door |  | 1 | 14 | 27.6 | 558 | 22.5 | 24.7 | 526 |  | 2020-09-18 10:22 | 44092.4316 | 22.5 | 24.7 | 526 |  | low | 2020-09-14 | B21554¦Basement corridor at exit door¦¦Sep-18-2020 10:21
2020-09-18 10:22 | 44092.4318 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Lvl4 interview room |  | 0 | 16.4 | 34.7 | 392 | 22.8 | 30.9 | 422 |  | 2020-09-18 10:22 | 44092.4318 | 22.8 | 30.9 | 422 |  | low | 2020-09-14 | B17477¦Lvl4 interview room¦¦Sep-18-2020 10:21
2020-09-18 10:22 | 44092.4318 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | SOUTH WING ENTERANCE |  | 2 | 13 | 38 | 474 | 22.2 | 30.7 | 448 |  | 2020-09-18 10:22 | 44092.4318 | 22.2 | 30.7 | 448 |  | low | 2020-09-14 | B20022¦SOUTH WING ENTERANCE¦¦Sep-18-2020 10:21
2020-09-18 10:22 | 44092.432 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office hallway |  | 0 | 15.1 | 32.9 | 430 | 22.1 | 25.2 | 437 |  | 2020-09-18 10:22 | 44092.432 | 22.1 | 25.2 | 437 |  | low | 2020-09-14 | B20603¦Office hallway ¦¦Sep-18-2020 10:22
2020-09-18 10:23 | 44092.4324 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR HALLWAY |  | 2 | 13 | 38 | 474 | 22 | 42 | 450 |  | 2020-09-18 10:23 | 44092.4324 | 22 | 42 | 450 |  |  | 2020-09-14 | B20022¦2 FLOOR HALLWAY¦¦Sep-18-2020 10:22
2020-09-18 10:23 | 44092.4329 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office hallway 3 |  | 0 | 15.1 | 32.9 | 430 | 21.9 | 25.5 | 441 |  | 2020-09-18 10:23 | 44092.4329 | 21.9 | 25.5 | 441 |  | low | 2020-09-14 | B20603¦Office hallway 3¦¦Sep-18-2020 10:23
2020-09-18 10:24 | 44092.4333 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | SOUTH WING UPSTAIRS HALL |  | 2 | 13 | 38 | 474 | 21 | 33 | 449 | *ADDITIONAL ROOMS ADDED (2 FLOOR HALL) (SOUTH WING UPSTAIRS HALL)* | 2020-09-18 10:24 | 44092.4333 | 21 | 33 | 449 |  | low | 2020-09-14 | B20022¦SOUTH WING UPSTAIRS HALL¦¦Sep-18-2020 10:23
2020-09-18 10:24 | 44092.4335 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Stairway landing |  | 1 | 14 | 27.6 | 397 | 22.5 | 24.1 | 528 |  | 2020-09-18 10:24 | 44092.4335 | 22.5 | 24.1 | 528 |  | low | 2020-09-14 | B21554¦Stairway landing¦¦Sep-18-2020 10:24
2020-09-18 10:25 | 44092.4339 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Printer room |  | 0 | 15.1 | 32.9 | 430 | 22 | 25 | 442 |  | 2020-09-18 10:25 | 44092.4339 | 22 | 25 | 442 |  | low | 2020-09-14 | B20603¦Printer room ¦¦Sep-18-2020 10:24
2020-09-18 10:25 | 44092.4339 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Crown attorneys office |  | 0 | 16.4 | 34.7 | 392 | 22.8 | 31.5 | 423 | Could not access courtroom 4 | 2020-09-18 10:25 | 44092.4339 | 22.8 | 31.5 | 423 |  | low | 2020-09-14 | B17477¦Crown attorneys office¦¦Sep-18-2020 10:24
2020-09-18 10:25 | 44092.4342 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Entrance |  | 0 | 14.4 | 45 | 400 | 18.2 | 45.6 | 402 |  | 2020-09-18 10:25 | 44092.4342 | 18.2 | 45.6 | 402 |  |  | 2020-09-14 | B10577¦Main Entrance ¦¦Sep-18-2020 10:25
2020-09-18 10:26 | 44092.4348 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Lobby South |  | 1 | 14.4 | 45 | 400 | 19.8 | 52.9 | 569 |  | 2020-09-18 10:26 | 44092.4348 | 19.8 | 52.9 | 569 |  |  | 2020-09-14 | B10577¦Main Lobby South¦¦Sep-18-2020 10:26
2020-09-18 10:26 | 44092.4348 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 5 waiting area N |  | 0 | 16.4 | 34.7 | 392 | 22.7 | 31.4 | 427 |  | 2020-09-18 10:26 | 44092.4348 | 22.7 | 31.4 | 427 |  | low | 2020-09-14 | B17477¦LVL 5 waiting area N¦¦Sep-18-2020 10:26
2020-09-18 10:26 | 44092.4349 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Legal aid office corridor |  | 1 | 14 | 27.6 | 397 | 22.2 | 26.4 | 524 |  | 2020-09-18 10:26 | 44092.4349 | 22.2 | 26.4 | 524 |  | low | 2020-09-14 | B21554¦Legal aid office corridor¦¦Sep-18-2020 10:26
2020-09-18 10:26 | 44092.4349 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office hallway 4 |  | 0 | 15.1 | 32.9 | 430 | 22 | 25.3 | 445 |  | 2020-09-18 10:26 | 44092.4349 | 22 | 25.3 | 445 |  | low | 2020-09-14 | B20603¦Office hallway 4 ¦¦Sep-18-2020 10:26
2020-09-18 10:27 | 44092.4354 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 5 waiting area S |  | 0 | 16.4 | 34.7 | 392 | 22.8 | 31.6 | 429 |  | 2020-09-18 10:27 | 44092.4354 | 22.8 | 31.6 | 429 |  | low | 2020-09-14 | B17477¦LVL 5 waiting area S¦¦Sep-18-2020 10:26
2020-09-18 10:27 | 44092.4355 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Court Office |  | 2 | 14.4 | 45 | 400 | 20.7 | 50.1 | 553 |  | 2020-09-18 10:27 | 44092.4355 | 20.7 | 50.1 | 553 |  |  | 2020-09-14 | B10577¦Court Office¦¦Sep-18-2020 10:27
2020-09-18 10:28 | 44092.4361 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | courtroom 5 waiting area |  | 0 | 16.4 | 34.7 | 392 | 22.6 | 29.8 | 417 |  | 2020-09-18 10:28 | 44092.4361 | 22.6 | 29.8 | 417 |  | low | 2020-09-14 | B17477¦courtroom 5 waiting area¦¦Sep-18-2020 10:27
2020-09-18 10:29 | 44092.4365 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Main waiting area |  | 1 | 14 | 27.6 | 397 | 21.4 | 25.7 | 538 |  | 2020-09-18 10:29 | 44092.4365 | 21.4 | 25.7 | 538 |  | low | 2020-09-14 | B21554¦Main waiting area¦¦Sep-18-2020 10:28
2020-09-18 10:29 | 44092.4368 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Witness area |  | 0 | 14.4 | 45 | 400 | 20.2 | 52.1 | 575 |  | 2020-09-18 10:29 | 44092.4368 | 20.2 | 52.1 | 575 |  |  | 2020-09-14 | B10577¦Witness area ¦¦Sep-18-2020 10:28
2020-09-18 10:29 | 44092.4369 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Lvl5 interview room 1 |  | 0 | 16.4 | 34.7 | 392 | 22.8 | 30.4 | 414 |  | 2020-09-18 10:29 | 44092.4369 | 22.8 | 30.4 | 414 |  | low | 2020-09-14 | B17477¦Lvl5 interview room 1¦¦Sep-18-2020 10:29
2020-09-18 10:30 | 44092.4375 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 South |  | 0 | 14.4 | 45 | 400 | 21.5 | 48.2 | 558 |  | 2020-09-18 10:30 | 44092.4375 | 21.5 | 48.2 | 558 |  |  | 2020-09-14 | B10577¦Courtroom 1 South ¦¦Sep-18-2020 10:30
2020-09-18 10:30 | 44092.4376 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 5 interview room 2 |  | 0 | 16.4 | 34.7 | 392 | 22.7 | 30.2 | 412 |  | 2020-09-18 10:30 | 44092.4376 | 22.7 | 30.2 | 412 |  | low | 2020-09-14 | B17477¦LVL 5 interview room 2¦¦Sep-18-2020 10:30
2020-09-18 10:32 | 44092.4386 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 East |  | 0 | 14.4 | 45 | 400 | 21.5 | 48.3 | 545 |  | 2020-09-18 10:32 | 44092.4386 | 21.5 | 48.3 | 545 |  |  | 2020-09-14 | B10577¦Courtroom 1 East¦¦Sep-18-2020 10:31
2020-09-18 10:33 | 44092.4396 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 North |  | 2 | 14.4 | 45 | 400 | 21.5 | 48 | 531 |  | 2020-09-18 10:33 | 44092.4396 | 21.5 | 48 | 531 |  |  | 2020-09-14 | B10577¦Courtroom 1 North ¦¦Sep-18-2020 10:33
2020-09-18 10:34 | 44092.4401 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Front desk |  | 4 | 14 | 27.6 | 397 | 20.6 | 28.1 | 663 |  | 2020-09-18 10:34 | 44092.4401 | 20.6 | 28.1 | 663 |  | low | 2020-09-14 | B21554¦Front desk¦¦Sep-18-2020 10:33
2020-09-18 10:34 | 44092.4402 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 West |  | 0 | 14.4 | 45 | 400 | 21.5 | 48.3 | 530 |  | 2020-09-18 10:34 | 44092.4402 | 21.5 | 48.3 | 530 |  |  | 2020-09-14 | B10577¦Courtroom 1 West ¦¦Sep-18-2020 10:33
2020-09-18 10:34 | 44092.4403 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 309 |  | 0 | 6 | 67 | 399 | 22.7 | 30.3 | 404 | No | 2020-09-18 10:34 | 44092.4403 | 22.7 | 30.3 | 404 |  | low | 2020-09-14 | B14660¦309¦¦Sep-18-2020 10:34
2020-09-18 10:34 | 44092.4406 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 center |  | 0 | 14.4 | 45 | 400 | 21.5 | 48 | 527 |  | 2020-09-18 10:34 | 44092.4406 | 21.5 | 48 | 527 |  |  | 2020-09-14 | B10577¦Courtroom 1 center ¦¦Sep-18-2020 10:34
2020-09-18 10:35 | 44092.4412 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Lobby North |  | 2 | 14.4 | 45 | 400 | 21.5 | 47.2 | 537 |  | 2020-09-18 10:35 | 44092.4412 | 21.5 | 47.2 | 537 |  |  | 2020-09-14 | B10577¦Main Lobby North ¦¦Sep-18-2020 10:35
2020-09-18 10:36 | 44092.4414 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Main office |  | 3 | 14 | 27.6 | 397 | 20.3 | 31.9 | 718 |  | 2020-09-18 10:36 | 44092.4414 | 20.3 | 31.9 | 718 |  | low | 2020-09-14 | B21554¦Main office¦¦Sep-18-2020 10:35
2020-09-18 10:36 | 44092.4418 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Stairwell |  | 0 | 14.4 | 45 | 400 | 21.6 | 47.1 | 590 |  | 2020-09-18 10:36 | 44092.4418 | 21.6 | 47.1 | 590 |  |  | 2020-09-14 | B10577¦Main Stairwell ¦¦Sep-18-2020 10:36
2020-09-18 10:36 | 44092.4418 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Entrance |  | 0 | 13 | 34 | 445 | 17 | 43.5 | 620 |  | 2020-09-18 10:36 | 44092.4418 | 17 | 43.5 | 620 |  |  | 2020-09-14 | B16187¦Entrance ¦¦Sep-18-2020 10:36
2020-09-18 10:37 | 44092.4422 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 4 | 13 | 34 | 445 | 18.8 | 36.6 | 720 |  | 2020-09-18 10:37 | 44092.4422 | 18.8 | 36.6 | 720 |  | caution | 2020-09-14 | B16187¦Court 3¦¦Sep-18-2020 10:36
2020-09-18 10:37 | 44092.4426 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 4 | 13 | 34 | 445 | 20 | 33.5 | 762 |  | 2020-09-18 10:37 | 44092.4426 | 20 | 33.5 | 762 |  | low | 2020-09-14 | B16187¦Court 3¦¦Sep-18-2020 10:37
2020-09-18 10:38 | 44092.4427 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2 flopr wsiting area North |  | 0 | 14.4 | 45 | 400 | 21.8 | 48.1 | 634 |  | 2020-09-18 10:38 | 44092.4427 | 21.8 | 48.1 | 634 |  |  | 2020-09-14 | B10577¦2 flopr wsiting area North ¦¦Sep-18-2020 10:37
2020-09-18 10:38 | 44092.443 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 4 | 13 | 34 | 445 | 20.6 | 30.7 | 745 |  | 2020-09-18 10:38 | 44092.443 | 20.6 | 30.7 | 745 |  | low | 2020-09-14 | B16187¦Court 3¦¦Sep-18-2020 10:37
2020-09-18 10:38 | 44092.4432 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 128 |  | 0 | 10 | 47 | 373 | 15.5 | 47.4 | 385 | No | 2020-09-18 10:38 | 44092.4432 | 15.5 | 47.4 | 385 |  |  | 2020-09-14 | B14660¦128¦¦Sep-18-2020 10:38
2020-09-18 10:39 | 44092.4434 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2 floor waiting area center |  | 0 | 14.4 | 45 | 400 | 21.8 | 47.9 | 637 |  | 2020-09-18 10:39 | 44092.4434 | 21.8 | 47.9 | 637 |  |  | 2020-09-14 | B10577¦2 floor waiting area center¦¦Sep-18-2020 10:38
2020-09-18 10:39 | 44092.4434 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 4 |  | 0 | 13 | 34 | 445 | 21.1 | 27.2 | 524 |  | 2020-09-18 10:39 | 44092.4434 | 21.1 | 27.2 | 524 |  | low | 2020-09-14 | B16187¦Court 4¦¦Sep-18-2020 10:38
2020-09-18 10:39 | 44092.4438 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 34 | 445 | 21.4 | 26.6 | 483 |  | 2020-09-18 10:39 | 44092.4438 | 21.4 | 26.6 | 483 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 10:39
2020-09-18 10:40 | 44092.4442 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 34 | 445 | 21.6 | 26.8 | 474 |  | 2020-09-18 10:40 | 44092.4442 | 21.6 | 26.8 | 474 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 10:39
2020-09-18 10:40 | 44092.4444 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2 floor waiting area south |  | 0 | 14.4 | 45 | 400 | 21.9 | 47.6 | 638 |  | 2020-09-18 10:40 | 44092.4444 | 21.9 | 47.6 | 638 |  |  | 2020-09-14 | B10577¦2 floor waiting area south ¦¦Sep-18-2020 10:39
2020-09-18 10:40 | 44092.4445 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 34 | 445 | 21.5 | 26.9 | 483 |  | 2020-09-18 10:40 | 44092.4445 | 21.5 | 26.9 | 483 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 10:40
2020-09-18 10:41 | 44092.445 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 34 | 445 | 21.3 | 26.6 | 486 |  | 2020-09-18 10:41 | 44092.445 | 21.3 | 26.6 | 486 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 10:40
2020-09-18 10:41 | 44092.4452 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 West |  | 0 | 14.4 | 45 | 400 | 22.1 | 48.2 | 645 |  | 2020-09-18 10:41 | 44092.4452 | 22.1 | 48.2 | 645 |  |  | 2020-09-14 | B10577¦Courtroom 2 West¦¦Sep-18-2020 10:41
2020-09-18 10:41 | 44092.4454 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 34 | 445 | 21.1 | 25.4 | 473 |  | 2020-09-18 10:41 | 44092.4454 | 21.1 | 25.4 | 473 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 10:41
2020-09-18 10:42 | 44092.4457 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 South |  | 0 | 14.4 | 45 | 400 | 22.2 | 48 | 652 |  | 2020-09-18 10:42 | 44092.4457 | 22.2 | 48 | 652 |  |  | 2020-09-14 | B10577¦Courtroom 2 South¦¦Sep-18-2020 10:41
2020-09-18 10:42 | 44092.4457 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 1 |  | 0 | 13 | 34 | 445 | 21 | 23.7 | 477 |  | 2020-09-18 10:42 | 44092.4457 | 21 | 23.7 | 477 |  | low | 2020-09-14 | B16187¦Court 1¦¦Sep-18-2020 10:41
2020-09-18 10:42 | 44092.4461 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 34 | 445 | 21.2 | 25.8 | 457 |  | 2020-09-18 10:42 | 44092.4461 | 21.2 | 25.8 | 457 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 10:42
2020-09-18 10:42 | 44092.4462 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 East |  | 0 | 14.4 | 45 | 400 | 22.3 | 47.9 | 655 |  | 2020-09-18 10:42 | 44092.4462 | 22.3 | 47.9 | 655 |  |  | 2020-09-14 | B10577¦Courtroom 2 East ¦¦Sep-18-2020 10:42
2020-09-18 10:43 | 44092.4465 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 34 | 445 | 21.3 | 26.8 | 456 |  | 2020-09-18 10:43 | 44092.4465 | 21.3 | 26.8 | 456 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 10:43
2020-09-18 10:43 | 44092.4467 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 North |  | 1 | 14.4 | 45 | 400 | 22.4 | 47.5 | 656 |  | 2020-09-18 10:43 | 44092.4467 | 22.4 | 47.5 | 656 |  |  | 2020-09-14 | B10577¦Courtroom 2 North¦¦Sep-18-2020 10:43
2020-09-18 10:43 | 44092.4469 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 34 | 445 | 21.4 | 26.3 | 497 |  | 2020-09-18 10:44 | 44092.4469 | 21.4 | 26.3 | 497 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 10:43
2020-09-18 10:44 | 44092.4473 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | OPP |  | 0 | 13 | 34 | 445 | 21.6 | 25.7 | 506 |  | 2020-09-18 10:44 | 44092.4473 | 21.6 | 25.7 | 506 |  | low | 2020-09-14 | B16187¦OPP¦¦Sep-18-2020 10:44
2020-09-18 10:45 | 44092.4477 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 outside |  | 0 | 14.4 | 45 | 400 | 21.5 | 41.7 | 560 |  | 2020-09-18 10:45 | 44092.4477 | 21.5 | 41.7 | 560 |  |  | 2020-09-14 | B10577¦Courtroom 3 outside ¦¦Sep-18-2020 10:44
2020-09-18 10:45 | 44092.4477 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | OPP |  | 1 | 13 | 34 | 445 | 21.8 | 25 | 509 |  | 2020-09-18 10:45 | 44092.4477 | 21.8 | 25 | 509 |  | low | 2020-09-14 | B16187¦OPP¦¦Sep-18-2020 10:44
2020-09-18 10:45 | 44092.4481 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 waiting area |  | 0 | 14.4 | 45 | 400 | 21.3 | 40.6 | 535 |  | 2020-09-18 10:45 | 44092.4481 | 21.3 | 40.6 | 535 |  |  | 2020-09-14 | B10577¦Courtroom 3 waiting area ¦¦Sep-18-2020 10:45
2020-09-18 10:45 | 44092.4482 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Crown attorney |  | 0 | 13 | 34 | 445 | 21.4 | 24.3 | 486 |  | 2020-09-18 10:45 | 44092.4482 | 21.4 | 24.3 | 486 |  | low | 2020-09-14 | B16187¦Crown attorney ¦¦Sep-18-2020 10:45
2020-09-18 10:46 | 44092.4486 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Interview room 2 |  | 0 | 14.4 | 45 | 400 | 21.2 | 39.1 | 489 |  | 2020-09-18 10:46 | 44092.4486 | 21.2 | 39.1 | 489 |  | caution | 2020-09-14 | B10577¦Interview room 2¦¦Sep-18-2020 10:45
2020-09-18 10:46 | 44092.4486 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 2 |  | 0 | 13 | 34 | 445 | 21.6 | 24.5 | 473 |  | 2020-09-18 10:46 | 44092.4486 | 21.6 | 24.5 | 473 |  | low | 2020-09-14 | B16187¦Court 2¦¦Sep-18-2020 10:46
2020-09-18 10:47 | 44092.449 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 2 |  | 0 | 13 | 34 | 445 | 21.7 | 23.3 | 448 |  | 2020-09-18 10:47 | 44092.449 | 21.7 | 23.3 | 448 |  | low | 2020-09-14 | B16187¦Court 2¦¦Sep-18-2020 10:46
2020-09-18 10:47 | 44092.4492 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 South |  | 0 | 14.4 | 45 | 400 | 21.1 | 38.6 | 459 |  | 2020-09-18 10:47 | 44092.4492 | 21.1 | 38.6 | 459 |  | caution | 2020-09-14 | B10577¦Courtroom 3 South¦¦Sep-18-2020 10:46
2020-09-18 10:47 | 44092.4494 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 34 | 445 | 21.2 | 24.8 | 444 |  | 2020-09-18 10:47 | 44092.4494 | 21.2 | 24.8 | 444 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 10:47
2020-09-18 10:48 | 44092.4497 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 001 |  | 0 | 11 | 45 | 377 | 18.5 | 48 | 465 | No | 2020-09-18 10:48 | 44092.4497 | 18.5 | 48 | 465 |  |  | 2020-09-14 | B14660¦001¦¦Sep-18-2020 10:47
2020-09-18 10:48 | 44092.4497 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 34 | 445 | 21.9 | 30.5 | 446 |  | 2020-09-18 10:48 | 44092.4497 | 21.9 | 30.5 | 446 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 10:47
2020-09-18 10:48 | 44092.4497 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 East |  | 0 | 14.4 | 45 | 400 | 21.1 | 37.5 | 453 |  | 2020-09-18 10:48 | 44092.4497 | 21.1 | 37.5 | 453 |  | caution | 2020-09-14 | B10577¦Courtroom 3 East¦¦Sep-18-2020 10:47
2020-09-18 10:48 | 44092.4501 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 34 | 445 | 21.9 | 30 | 512 |  | 2020-09-18 10:48 | 44092.4501 | 21.9 | 30 | 512 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 10:48
2020-09-18 10:48 | 44092.4502 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 North |  | 0 | 14.4 | 45 | 400 | 21.1 | 37.6 | 450 |  | 2020-09-18 10:48 | 44092.4502 | 21.1 | 37.6 | 450 |  | caution | 2020-09-14 | B10577¦Courtroom 3 North ¦¦Sep-18-2020 10:48
2020-09-18 10:49 | 44092.4505 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Cell waiting area |  | 0 | 13 | 34 | 445 | 21.5 | 29.8 | 495 |  | 2020-09-18 10:49 | 44092.4505 | 21.5 | 29.8 | 495 |  | low | 2020-09-14 | B16187¦Cell waiting area ¦¦Sep-18-2020 10:48
2020-09-18 10:49 | 44092.4508 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 West |  | 0 | 14.4 | 45 | 400 | 21 | 36.9 | 447 |  | 2020-09-18 10:49 | 44092.4508 | 21 | 36.9 | 447 |  | caution | 2020-09-14 | B10577¦Courtroom 3 West ¦¦Sep-18-2020 10:49
2020-09-18 10:49 | 44092.4509 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Basement hallway |  | 0 | 13 | 34 | 445 | 21.4 | 30 | 481 |  | 2020-09-18 10:49 | 44092.4509 | 21.4 | 30 | 481 |  | low | 2020-09-14 | B16187¦Basement hallway ¦¦Sep-18-2020 10:49
2020-09-18 10:50 | 44092.4513 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 13 | 34 | 445 | 21.8 | 31.9 | 479 |  | 2020-09-18 10:50 | 44092.4513 | 21.8 | 31.9 | 479 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 10:49
2020-09-18 10:50 | 44092.4515 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 028 |  | 0 | 11 | 45 | 377 | 20.6 | 39 | 414 | No | 2020-09-18 10:50 | 44092.4515 | 20.6 | 39 | 414 |  | caution | 2020-09-14 | B14660¦028¦¦Sep-18-2020 10:50
2020-09-18 10:51 | 44092.4518 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Front lobby |  | 3 | 14.3 | 28.3 | 437 | 19.6 | 37.2 | 505 |  | 2020-09-18 10:51 | 44092.4518 | 19.6 | 37.2 | 505 |  | caution | 2020-09-14 | B25477¦Front lobby¦¦Sep-18-2020 10:50
2020-09-18 10:52 | 44092.4525 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | HR |  | 2 | 14.3 | 28.3 | 437 | 20.1 | 35.8 | 525 |  | 2020-09-18 10:52 | 44092.4525 | 20.1 | 35.8 | 525 |  | caution | 2020-09-14 | B25477¦HR¦¦Sep-18-2020 10:51
2020-09-18 10:52 | 44092.4529 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 019 |  | 0 | 11 | 45 | 377 | 21.5 | 36.1 | 418 | No | 2020-09-18 10:52 | 44092.4529 | 21.5 | 36.1 | 418 |  | caution | 2020-09-14 | B14660¦019¦¦Sep-18-2020 10:52
2020-09-18 10:53 | 44092.4534 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | ED office |  | 3 | 14.3 | 28.3 | 437 | 20.6 | 32.7 | 532 |  | 2020-09-18 10:53 | 44092.4534 | 20.6 | 32.7 | 532 |  | low | 2020-09-14 | B25477¦ED office ¦¦Sep-18-2020 10:52
2020-09-18 10:54 | 44092.4541 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 1e |  | 3 | 8.4 | 54.9 | 371 | 22.6 | 29.4 | 391 |  | 2020-09-18 10:54 | 44092.4541 | 22.6 | 29.4 | 391 |  | low | 2020-09-14 | B20494¦Courtroom 1e¦¦Sep-18-2020 10:53
2020-09-18 10:55 | 44092.4546 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area north |  | 1 | 12 | 40 | 365 | 22 | 26 | 370 |  | 2020-09-18 10:55 | 44092.4546 | 22 | 26 | 370 |  | low | 2020-09-14 | B20772¦Courtroom waiting area north¦¦Sep-18-2020 10:54
2020-09-18 10:55 | 44092.4551 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Admin office |  | 1 | 14.3 | 28.3 | 437 | 21.3 | 33.2 | 516 |  | 2020-09-18 10:55 | 44092.4551 | 21.3 | 33.2 | 516 |  | low | 2020-09-14 | B25477¦Admin office¦¦Sep-18-2020 10:55
2020-09-18 10:56 | 44092.4555 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 3 |  | 3 | 8.4 | 54.9 | 371 | 22.3 | 40.3 | 561 |  | 2020-09-18 10:56 | 44092.4555 | 22.3 | 40.3 | 561 |  |  | 2020-09-14 | B20494¦Courtroom 3¦¦Sep-18-2020 10:55
2020-09-18 10:57 | 44092.4559 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Financial services |  | 3 | 14.3 | 28.3 | 437 | 21.3 | 32.4 | 519 |  | 2020-09-18 10:57 | 44092.4559 | 21.3 | 32.4 | 519 |  | low | 2020-09-14 | B25477¦Financial services ¦¦Sep-18-2020 10:56
2020-09-18 10:57 | 44092.4563 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 011 |  | 0 | 11 | 45 | 377 | 22.3 | 36.7 | 454 | No | 2020-09-18 10:57 | 44092.4563 | 22.3 | 36.7 | 454 |  | caution | 2020-09-14 | B14660¦011¦¦Sep-18-2020 10:57
2020-09-18 10:57 | 44092.4564 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 2nd floor SE hall |  | 1 | 9 | 51 | 392 | 22.7 | 36.1 | 479 |  | 2020-09-18 10:57 | 44092.4564 | 22.7 | 36.1 | 479 |  | caution | 2020-09-14 | B20494¦2nd floor SE hall¦¦Sep-18-2020 10:57
2020-09-18 10:58 | 44092.4566 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Second floor hallway nw |  | 1 | 8.4 | 54.9 | 371 | 22.2 | 41.1 | 498 |  | 2020-09-18 10:58 | 44092.4566 | 22.2 | 41.1 | 498 |  |  | 2020-09-14 | B20494¦Second floor hallway nw¦¦Sep-18-2020 10:57
2020-09-18 10:58 | 44092.4568 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Courtroom |  | 3 | 14.3 | 28.3 | 437 | 21.2 | 30.5 | 474 |  | 2020-09-18 10:58 | 44092.4568 | 21.2 | 30.5 | 474 |  | low | 2020-09-14 | B25477¦Courtroom ¦¦Sep-18-2020 10:57
2020-09-18 10:59 | 44092.4576 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Mezzanine |  | 0 | 14.3 | 28.3 | 437 | 22 | 31.3 | 490 |  | 2020-09-18 10:59 | 44092.4576 | 22 | 31.3 | 490 |  | low | 2020-09-14 | B25477¦Mezzanine ¦¦Sep-18-2020 10:58
2020-09-18 10:59 | 44092.4578 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom 4 waiting room |  | 0 | 10.3 | 58.9 | 420 | 21.2 | 44.2 | 584 |  | 2020-09-18 10:59 | 44092.4578 | 21.2 | 44.2 | 584 |  |  | 2020-09-14 | B90631¦Courtroom 4 waiting room ¦¦Sep-18-2020 10:59
2020-09-18 10:59 | 44092.4579 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Second floor hallway sw |  | 2 | 8.4 | 54.9 | 371 | 22.1 | 42.8 | 461 |  | 2020-09-18 10:59 | 44092.4579 | 22.1 | 42.8 | 461 |  |  | 2020-09-14 | B20494¦Second floor hallway sw¦¦Sep-18-2020 10:59
2020-09-18 10:59 | 44092.4579 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Criminal justice office |  | 2 | 9 | 51 | 392 | 22.9 | 38.8 | 504 |  | 2020-09-18 10:59 | 44092.4579 | 22.9 | 38.8 | 504 |  | caution | 2020-09-14 | B20494¦Criminal justice office ¦¦Sep-18-2020 10:59
2020-09-18 11:00 | 44092.4581 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Crown attorney office |  | 1 | 8 | 55 | 374 | 20.5 | 41.2 | 499 | No | 2020-09-18 11:00 | 44092.4581 | 20.5 | 41.2 | 499 |  |  | 2020-09-14 | B20489¦Crown attorney office ¦¦Sep-18-2020 10:59
2020-09-18 11:00 | 44092.4583 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Library |  | 2 | 21.2 | 30.4 | 480 | 21.3 | 31.4 | 483 |  | 2020-09-18 11:00 | 44092.4583 | 21.3 | 31.4 | 483 |  | low | 2020-09-14 | B25477¦Library ¦¦Sep-18-2020 10:59
2020-09-18 11:00 | 44092.4586 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Foyers |  | 2 | 13.8 | 27.9 | 408 | 18.8 | 36.2 | 510 |  | 2020-09-18 11:00 | 44092.4586 | 18.8 | 36.2 | 510 |  | caution | 2020-09-14 | B20367¦Foyers ¦¦Sep-18-2020 11:00
2020-09-18 11:01 | 44092.4591 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family court waiting room |  | 1 | 8.4 | 54.9 | 371 | 22.2 | 40.3 | 481 |  | 2020-09-18 11:01 | 44092.4591 | 22.2 | 40.3 | 481 |  |  | 2020-09-14 | B20494¦Family court waiting room ¦¦Sep-18-2020 11:01
2020-09-18 11:01 | 44092.4591 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Board room |  | 2 | 14.3 | 28.3 | 437 | 22.1 | 32.2 | 512 |  | 2020-09-18 11:01 | 44092.4591 | 22.1 | 32.2 | 512 |  | low | 2020-09-14 | B25477¦Board room¦¦Sep-18-2020 11:01
2020-09-18 11:01 | 44092.4592 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Crown attorneys office |  | 2 | 15 | 32.6 | 435 | 22.5 | 22.2 | 428 | No | 2020-09-18 11:01 | 44092.4592 | 22.5 | 22.2 | 428 |  | low | 2020-09-14 | B21128¦Crown attorneys office ¦¦Sep-18-2020 11:01
2020-09-18 11:01 | 44092.4593 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Crown attorney waiting area |  | 0 | 8 | 55 | 374 | 20.8 | 41 | 498 | No | 2020-09-18 11:01 | 44092.4593 | 20.8 | 41 | 498 |  |  | 2020-09-14 | B20489¦Crown attorney waiting area ¦¦Sep-18-2020 11:01
2020-09-18 11:01 | 44092.4594 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 118 |  | 0 | 11 | 45 | 377 | 24 | 27 | 440 | No | 2020-09-18 11:01 | 44092.4594 | 24 | 27 | 440 |  | low | 2020-09-14 | B14660¦118¦¦Sep-18-2020 11:01
2020-09-18 11:03 | 44092.4602 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Front entrance hallway |  | 13 | 18 | 21.9 | 388 | 22.5 | 19.2 | 445 | No | 2020-09-18 11:03 | 44092.4602 | 22.5 | 19.2 | 445 |  | low | 2020-09-14 | B21128¦Front entrance hallway ¦¦Sep-18-2020 11:02
2020-09-18 11:03 | 44092.4603 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Administration |  | 7 | 13.8 | 27.9 | 408 | 27.9 | 35.3 | 860 |  | 2020-09-18 11:03 | 44092.4603 | 27.9 | 35.3 | 860 | high | caution | 2020-09-14 | B20367¦Administration ¦¦Sep-18-2020 11:02
2020-09-18 11:03 | 44092.4606 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family office west |  | 3 | 8.4 | 54.9 | 371 | 22.7 | 41.8 | 507 |  | 2020-09-18 11:03 | 44092.4606 | 22.7 | 41.8 | 507 |  |  | 2020-09-14 | B20494¦Family office west¦¦Sep-18-2020 11:03
2020-09-18 11:04 | 44092.4608 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 115 |  | 0 | 11 | 45 | 377 | 24.5 | 29.8 | 435 | No | 2020-09-18 11:04 | 44092.4608 | 24.5 | 29.8 | 435 |  | low | 2020-09-14 | B14660¦115¦¦Sep-18-2020 11:03
2020-09-18 11:04 | 44092.4609 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 2 |  | 1 | 9 | 51 | 392 | 22.8 | 31.8 | 435 |  | 2020-09-18 11:04 | 44092.4609 | 22.8 | 31.8 | 435 |  | low | 2020-09-14 | B20494¦Courtroom 2¦¦Sep-18-2020 11:03
2020-09-18 11:04 | 44092.461 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 2nd floor hallway |  | 2 | 8 | 55 | 374 | 21.1 | 39 | 470 | No | 2020-09-18 11:04 | 44092.461 | 21.1 | 39 | 470 |  | caution | 2020-09-14 | B20489¦2nd floor hallway ¦¦Sep-18-2020 11:03
2020-09-18 11:04 | 44092.4611 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Administration office |  | 7 | 13.8 | 27.9 | 408 | 22.9 | 32.7 | 810 |  | 2020-09-18 11:04 | 44092.4611 | 22.9 | 32.7 | 810 |  | low | 2020-09-14 | B20367¦Administration office ¦¦Sep-18-2020 11:03
2020-09-18 11:04 | 44092.4612 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 403 |  | 3 | 18 | 21.9 | 388 | 22.8 | 18.2 | 470 | No | 2020-09-18 11:04 | 44092.4612 | 22.8 | 18.2 | 470 |  | low | 2020-09-14 | B21128¦403¦¦Sep-18-2020 11:04
2020-09-18 11:05 | 44092.462 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 1 |  | 0 | 13.8 | 27.9 | 408 | 22.3 | 27.3 | 501 |  | 2020-09-18 11:05 | 44092.462 | 22.3 | 27.3 | 501 |  | low | 2020-09-14 | B20367¦Waiting room 1¦¦Sep-18-2020 11:05
2020-09-18 11:05 | 44092.462 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family office inner |  | 1 | 8.4 | 54.9 | 371 | 22.9 | 40.1 | 506 |  | 2020-09-18 11:05 | 44092.462 | 22.9 | 40.1 | 506 |  |  | 2020-09-14 | B20494¦Family office inner¦¦Sep-18-2020 11:05
2020-09-18 11:06 | 44092.4625 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Motion office |  | 0 | 8 | 55 | 374 | 21 | 41.4 | 456 | No | 2020-09-18 11:06 | 44092.4625 | 21 | 41.4 | 456 |  |  | 2020-09-14 | B20489¦Motion office ¦¦Sep-18-2020 11:05
2020-09-18 11:07 | 44092.4629 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judges chamber foyers |  | 0 | 13.8 | 27.9 | 408 | 22.5 | 33.2 | 474 |  | 2020-09-18 11:06 | 44092.4629 | 22.5 | 33.2 | 474 |  | low | 2020-09-14 | B20367¦Judges chamber foyers ¦¦Sep-18-2020 11:06
2020-09-18 11:07 | 44092.463 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family office east |  | 2 | 8.4 | 54.9 | 371 | 22.9 | 40.4 | 504 |  | 2020-09-18 11:07 | 44092.463 | 22.9 | 40.4 | 504 |  |  | 2020-09-14 | B20494¦Family office east¦¦Sep-18-2020 11:06
2020-09-18 11:07 | 44092.4632 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | N.W entrance |  | 3 | 18 | 21.9 | 388 | 23.4 | 17.8 | 480 | No | 2020-09-18 11:07 | 44092.4632 | 23.4 | 17.8 | 480 |  | low | 2020-09-14 | B21128¦N.W entrance ¦¦Sep-18-2020 11:06
2020-09-18 11:07 | 44092.4634 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judges chamber foyers |  | 0 | 13.8 | 27.9 | 408 | 22.5 | 33 | 477 |  | 2020-09-18 11:07 | 44092.4634 | 22.5 | 33 | 477 |  | low | 2020-09-14 | B20367¦Judges chamber foyers ¦¦Sep-18-2020 11:07
2020-09-18 11:07 | 44092.4634 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Administrative office |  | 2 | 13.2 | 31.2 | 384 | 20.1 | 35 | 466 |  | 2020-09-18 11:07 | 44092.4634 | 20.1 | 35 | 466 |  | caution | 2020-09-14 | B90558¦Administrative office¦¦Sep-18-2020 11:07
2020-09-18 11:08 | 44092.4639 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 2nd floor NE hall |  | 1 | 9 | 51 | 392 | 22.8 | 38.2 | 497 |  | 2020-09-18 11:08 | 44092.4639 | 22.8 | 38.2 | 497 |  | caution | 2020-09-14 | B20494¦2nd floor NE hall¦¦Sep-18-2020 11:08
2020-09-18 11:08 | 44092.4641 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judicial stairwell |  | 0 | 13.8 | 27.9 | 408 | 22.3 | 36.5 | 477 |  | 2020-09-18 11:08 | 44092.4641 | 22.3 | 36.5 | 477 |  | caution | 2020-09-14 | B20367¦Judicial stairwell ¦¦Sep-18-2020 11:08
2020-09-18 11:08 | 44092.4642 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 405 |  | 3 | 18 | 21.9 | 388 | 22.8 | 17.4 | 444 | No | 2020-09-18 11:08 | 44092.4642 | 22.8 | 17.4 | 444 |  | low | 2020-09-14 | B21128¦405¦¦Sep-18-2020 11:08
2020-09-18 11:09 | 44092.4645 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 3rd floor hallway |  | 1 | 8 | 55 | 374 | 21.6 | 42.5 | 442 | No | 2020-09-18 11:09 | 44092.4645 | 21.6 | 42.5 | 442 |  |  | 2020-09-14 | B20489¦3rd floor hallway ¦¦Sep-18-2020 11:08
2020-09-18 11:09 | 44092.4645 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 107 |  | 2 | 11 | 45 | 377 | 21.2 | 30.8 | 428 | No | 2020-09-18 11:09 | 44092.4645 | 21.2 | 30.8 | 428 |  | low | 2020-09-14 | B14660¦107¦¦Sep-18-2020 11:08
2020-09-18 11:10 | 44092.465 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 3 |  | 1 | 8.4 | 54.9 | 371 |  |  |  | Door locked, no access | 2020-09-18 11:10 | 44092.465 | [5 empty] | 2020-09-14 | B20494¦Courtroom 3¦¦Sep-18-2020 11:09
2020-09-18 11:10 | 44092.465 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 1 |  | 0 | 13.8 | 27.9 | 408 | 22 | 30 | 441 |  | 2020-09-18 11:10 | 44092.465 | 22 | 30 | 441 |  | low | 2020-09-14 | B20367¦Courtroom 1¦¦Sep-18-2020 11:09
2020-09-18 11:10 | 44092.4653 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 406 |  | 7 | 18 | 21.9 | 388 | 23 | 19.5 | 417 | No | 2020-09-18 11:10 | 44092.4653 | 23 | 19.5 | 417 |  | low | 2020-09-14 | B21128¦406¦¦Sep-18-2020 11:10
2020-09-18 11:11 | 44092.4657 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 113 |  | 0 | 11 | 45 | 377 | 22 | 29.7 | 406 | No | 2020-09-18 11:11 | 44092.4657 | 22 | 29.7 | 406 |  | low | 2020-09-14 | B14660¦113¦¦Sep-18-2020 11:10
2020-09-18 11:11 | 44092.4658 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judges chamber courtroom 1 |  | 0 | 13.8 | 27.9 | 408 | 21.8 | 34.5 | 439 |  | 2020-09-18 11:11 | 44092.4658 | 21.8 | 34.5 | 439 |  | low | 2020-09-14 | B20367¦Judges chamber courtroom 1¦¦Sep-18-2020 11:10
2020-09-18 11:11 | 44092.4661 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway ne |  | 1 | 8.4 | 54.9 | 371 | 22.5 | 38.4 | 476 |  | 2020-09-18 11:11 | 44092.4661 | 22.5 | 38.4 | 476 |  | caution | 2020-09-14 | B20494¦Third floor hallway ne¦¦Sep-18-2020 11:11
2020-09-18 11:11 | 44092.4662 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Main entry |  | 4 | 9 | 51 | 392 | 22.8 | 38.2 | 493 |  | 2020-09-18 11:11 | 44092.4662 | 22.8 | 38.2 | 493 |  | caution | 2020-09-14 | B20494¦Main entry¦¦Sep-18-2020 11:11
2020-09-18 11:12 | 44092.4664 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Jury room |  | 0 | 8 | 55 | 374 | 22.1 | 40.2 | 409 | No | 2020-09-18 11:12 | 44092.4664 | 22.1 | 40.2 | 409 |  |  | 2020-09-14 | B20489¦Jury room ¦¦Sep-18-2020 11:11
2020-09-18 11:12 | 44092.4668 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 2 |  | 0 | 13.8 | 27.9 | 408 | 21.1 | 27.1 | 456 |  | 2020-09-18 11:12 | 44092.4668 | 21.1 | 27.1 | 456 |  | low | 2020-09-14 | B20367¦Waiting room 2¦¦Sep-18-2020 11:12
2020-09-18 11:12 | 44092.4669 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NW hall |  | 0 | 14 | 38 | 430 | 20 | 49 | 570 |  | 2020-09-18 11:12 | 44092.4669 | 20 | 49 | 570 |  |  | 2020-09-14 | B25548¦NW hall¦¦Sep-18-2020 11:12
2020-09-18 11:12 | 44092.4669 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom 2 |  | 3 | 13.2 | 31.2 | 388 | 19.2 | 32.7 | 436 |  | 2020-09-18 11:12 | 44092.4669 | 19.2 | 32.7 | 436 |  | low | 2020-09-14 | B90558¦Courtroom 2¦¦Sep-18-2020 11:12
2020-09-18 11:13 | 44092.4672 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 114 |  | 0 | 11 | 45 | 377 | 21.6 | 26.3 | 409 | No | 2020-09-18 11:13 | 44092.4672 | 21.6 | 26.3 | 409 |  | low | 2020-09-14 | B14660¦114¦¦Sep-18-2020 11:12
2020-09-18 11:13 | 44092.4673 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 507 |  | 2 | 18 | 21.9 | 388 | 23.3 | 21.9 | 466 | No | 2020-09-18 11:13 | 44092.4673 | 23.3 | 21.9 | 466 |  | low | 2020-09-14 | B21128¦507¦¦Sep-18-2020 11:12
2020-09-18 11:13 | 44092.4676 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area mens washroom |  | 1 | 13.4 | 25.7 | 403 | 19.9 | 36.6 | 586 |  | 2020-09-18 11:13 | 44092.4676 | 19.9 | 36.6 | 586 |  | caution | 2020-09-14 | B20474¦Basement waiting area mens washroom¦¦Sep-18-2020 11:13
2020-09-18 11:14 | 44092.4679 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Room 301 |  | 0 | 13.8 | 27.9 | 408 |  | 27.2 | 466 |  | 2020-09-18 11:14 | 44092.4679 |  | 27.2 | 466 |  | low | 2020-09-14 | B20367¦Room 301¦¦Sep-18-2020 11:13
2020-09-18 11:14 | 44092.4679 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NE hall |  | 0 | 14 | 38 | 430 | 21 | 50 | 580 |  | 2020-09-18 11:14 | 44092.4679 | 21 | 50 | 580 |  |  | 2020-09-14 | B25548¦NE hall¦¦Sep-18-2020 11:13
2020-09-18 11:14 | 44092.4681 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room waiting room/entrance - right side |  | 1 | 18.1 | 29 | 385 | 22.3 | 25.8 | 407 |  | 2020-09-18 11:14 | 44092.4681 | 22.3 | 25.8 | 407 |  | low | 2020-09-14 | B70277¦Court room waiting room/entrance - right side¦¦Sep-18-2020 11:14
2020-09-18 11:14 | 44092.4682 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Private room |  | 0 | 8 | 55 | 374 | 22.1 | 42.3 | 418 | No | 2020-09-18 11:14 | 44092.4682 | 22.1 | 42.3 | 418 |  |  | 2020-09-14 | B20489¦Private room ¦¦Sep-18-2020 11:14
2020-09-18 11:14 | 44092.4684 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 408 |  | 2 | 18 | 21.9 | 388 | 23.9 | 20.4 | 534 | No | 2020-09-18 11:14 | 44092.4684 | 23.9 | 20.4 | 534 |  | low | 2020-09-14 | B21128¦408¦¦Sep-18-2020 11:14
2020-09-18 11:15 | 44092.4686 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 4 |  | 1 | 9 | 51 | 392 | 22.4 | 34.4 | 422 |  | 2020-09-18 11:15 | 44092.4686 | 22.4 | 34.4 | 422 |  | low | 2020-09-14 | B20494¦Courtroom 4¦¦Sep-18-2020 11:14
2020-09-18 11:15 | 44092.4687 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 104 |  | 0 | 11 | 45 | 377 | 21.6 | 33.5 | 413 | No | 2020-09-18 11:15 | 44092.4687 | 21.6 | 33.5 | 413 |  | low | 2020-09-14 | B14660¦104¦¦Sep-18-2020 11:14
2020-09-18 11:15 | 44092.4689 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 2 |  | 0 | 13.8 | 27.9 | 408 | 21.1 | 28.1 | 442 |  | 2020-09-18 11:15 | 44092.4689 | 21.1 | 28.1 | 442 |  | low | 2020-09-14 | B20367¦Courtroom 2¦¦Sep-18-2020 11:15
2020-09-18 11:15 | 44092.469 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room Waiting room/ entrance - left side |  | 1 | 18.1 | 29 | 385 | 22.6 | 25.2 | 405 |  | 2020-09-18 11:15 | 44092.469 | 22.6 | 25.2 | 405 |  | low | 2020-09-14 | B70277¦Court room Waiting room/ entrance - left side¦¦Sep-18-2020 11:15
2020-09-18 11:15 | 44092.469 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | E hall |  | 0 | 14 | 38 | 430 | 22 | 48 | 620 |  | 2020-09-18 11:15 | 44092.469 | 22 | 48 | 620 |  |  | 2020-09-14 | B25548¦E hall¦¦Sep-18-2020 11:15
2020-09-18 11:16 | 44092.4692 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom3 |  | 1 | 13.4 | 25.7 | 403 | 19.8 | 36.5 | 585 |  | 2020-09-18 11:16 | 44092.4692 | 19.8 | 36.5 | 585 |  | caution | 2020-09-14 | B20474¦Waiting area courtroom3¦¦Sep-18-2020 11:15
2020-09-18 11:17 | 44092.4699 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - facing judge, back right |  | 2 | 18.1 | 29 | 385 | 22.7 | 25 | 405 |  | 2020-09-18 11:17 | 44092.4699 | 22.7 | 25 | 405 |  | low | 2020-09-14 | B70277¦Court room - facing judge, back right¦¦Sep-18-2020 11:16
2020-09-18 11:17 | 44092.4699 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 101 |  | 0 | 11 | 45 | 377 | 21.7 | 40.4 | 407 | No | 2020-09-18 11:17 | 44092.4699 | 21.7 | 40.4 | 407 |  |  | 2020-09-14 | B14660¦101¦¦Sep-18-2020 11:16
2020-09-18 11:17 | 44092.4699 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway se |  | 3 | 8.4 | 54.9 | 371 | 23.5 | 36 | 484 |  | 2020-09-18 11:17 | 44092.4699 | 23.5 | 36 | 484 |  | caution | 2020-09-14 | B20494¦Third floor hallway se¦¦Sep-18-2020 11:16
2020-09-18 11:17 | 44092.4701 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office a |  | 0 | 13.8 | 27.9 | 408 | 21 | 31.5 | 432 |  | 2020-09-18 11:17 | 44092.4701 | 21 | 31.5 | 432 |  | low | 2020-09-14 | B20367¦Office a¦¦Sep-18-2020 11:16
2020-09-18 11:17 | 44092.4701 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Court room 3 |  | 1 | 14.2 | 31.2 | 388 | 21.1 | 31 | 440 |  | 2020-09-18 11:17 | 44092.4701 | 21.1 | 31 | 440 |  | low | 2020-09-14 | B90558¦Court room 3¦¦Sep-18-2020 11:17
2020-09-18 11:17 | 44092.4703 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | SE hall |  | 0 | 14 | 38 | 430 | 23 | 46 | 610 |  | 2020-09-18 11:17 | 44092.4703 | 23 | 46 | 610 |  |  | 2020-09-14 | B25548¦SE hall¦¦Sep-18-2020 11:17
2020-09-18 11:17 | 44092.4703 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Court room 1 judge's desk |  | 0 | 8 | 55 | 374 | 22.5 | 41.7 | 415 | No | 2020-09-18 11:17 | 44092.4703 | 22.5 | 41.7 | 415 |  |  | 2020-09-14 | B20489¦Court room 1 judge's desk ¦¦Sep-18-2020 11:17
2020-09-18 11:18 | 44092.4705 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - facing judge, Back left |  | 2 | 18.1 | 29 | 385 | 22.7 | 25 | 403 |  | 2020-09-18 11:18 | 44092.4705 | 22.7 | 25 | 403 |  | low | 2020-09-14 | B70277¦Court room - facing judge, Back left¦¦Sep-18-2020 11:17
2020-09-18 11:18 | 44092.4706 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 414 |  | 2 | 18 | 21.9 | 388 | 23 | 20.7 | 473 | No | 2020-09-18 11:18 | 44092.4706 | 23 | 20.7 | 473 |  | low | 2020-09-14 | B21128¦414¦¦Sep-18-2020 11:17
2020-09-18 11:18 | 44092.4709 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Interview room 2 |  | 1 | 9 | 51 | 392 | 22.5 | 34.6 | 426 |  | 2020-09-18 11:18 | 44092.4709 | 22.5 | 34.6 | 426 |  | low | 2020-09-14 | B20494¦Interview room 2¦¦Sep-18-2020 11:18
2020-09-18 11:19 | 44092.4713 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area inside dbl doors |  | 1 | 13.4 | 25.7 | 403 | 20 | 35.6 | 602 |  | 2020-09-18 11:19 | 44092.4713 | 20 | 35.6 | 602 |  | caution | 2020-09-14 | B20474¦Basement waiting area inside dbl doors¦¦Sep-18-2020 11:18
2020-09-18 11:19 | 44092.4713 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office b |  | 0 | 13.8 | 27.9 | 408 | 21.2 | 29.6 | 446 |  | 2020-09-18 11:19 | 44092.4713 | 21.2 | 29.6 | 446 |  | low | 2020-09-14 | B20367¦Office b¦¦Sep-18-2020 11:18
2020-09-18 11:19 | 44092.4713 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - facing judge, Middle left |  | 2 | 18.1 | 29 | 401 | 22.6 | 25 | 397 |  | 2020-09-18 11:19 | 44092.4713 | 22.6 | 25 | 397 |  | low | 2020-09-14 | B70277¦Court room - facing judge, Middle left¦¦Sep-18-2020 11:18
2020-09-18 11:19 | 44092.4714 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | SW hall |  | 0 | 14 | 38 | 430 | 23 | 46 | 585 |  | 2020-09-18 11:19 | 44092.4714 | 23 | 46 | 585 |  |  | 2020-09-14 | B25548¦SW hall¦¦Sep-18-2020 11:18
2020-09-18 11:19 | 44092.4716 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway nw |  | 1 | 8.4 | 54.9 | 371 | 23.1 | 36.5 | 449 |  | 2020-09-18 11:19 | 44092.4716 | 23.1 | 36.5 | 449 |  | caution | 2020-09-14 | B20494¦Third floor hallway nw¦¦Sep-18-2020 11:19
2020-09-18 11:19 | 44092.4717 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 413 |  | 3 | 18 | 21.9 | 388 | 22.6 | 21.4 | 451 | No | 2020-09-18 11:19 | 44092.4717 | 22.6 | 21.4 | 451 |  | low | 2020-09-14 | B21128¦413¦¦Sep-18-2020 11:19
2020-09-18 11:19 | 44092.4717 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office c |  | 0 | 13.8 | 27.9 | 408 | 21.4 | 28.5 | 448 |  | 2020-09-18 11:19 | 44092.4717 | 21.4 | 28.5 | 448 |  | low | 2020-09-14 | B20367¦Office c¦¦Sep-18-2020 11:19
2020-09-18 11:19 | 44092.4718 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice Letourneau office |  | 0 | 13.2 | 31.2 | 388 | 21.1 | 35.7 | 443 |  | 2020-09-18 11:19 | 44092.4718 | 21.1 | 35.7 | 443 |  | caution | 2020-09-14 | B90558¦Justice Letourneau office¦¦Sep-18-2020 11:19
2020-09-18 11:20 | 44092.4719 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Court room 1 gallery |  | 0 | 8 | 55 | 374 | 22.7 | 41.4 | 415 | No | 2020-09-18 11:20 | 44092.4719 | 22.7 | 41.4 | 415 |  |  | 2020-09-14 | B20489¦Court room 1 gallery ¦¦Sep-18-2020 11:19
2020-09-18 11:20 | 44092.472 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - facing judge, Middle right |  | 2 | 18.1 | 29 | 385 | 22.5 | 25.2 | 391 |  | 2020-09-18 11:20 | 44092.472 | 22.5 | 25.2 | 391 |  | low | 2020-09-14 | B70277¦Court room - facing judge, Middle right¦¦Sep-18-2020 11:19
2020-09-18 11:20 | 44092.4722 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 134 |  | 0 | 11 | 45 | 377 | 22.6 | 35.8 | 430 | 0 | 2020-09-18 11:20 | 44092.4722 | 22.6 | 35.8 | 430 |  | caution | 2020-09-14 | B14660¦134¦¦Sep-18-2020 11:20
2020-09-18 11:21 | 44092.4727 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 3 |  | 3 | 13.8 | 27.9 | 408 |  |  |  | No access | 2020-09-18 11:21 | 44092.4727 | [5 empty] | 2020-09-14 | B20367¦Courtroom 3¦¦Sep-18-2020 11:20
2020-09-18 11:21 | 44092.4728 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - judges desk, left side |  | 2 | 18.1 | 29 | 385 | 22.6 | 35.2 | 394 |  | 2020-09-18 11:21 | 44092.4728 | 22.6 | 35.2 | 394 |  | caution | 2020-09-14 | B70277¦Court room - judges desk, left side¦¦Sep-18-2020 11:20
2020-09-18 11:21 | 44092.4729 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice Wheeler office |  | 0 | 13.2 | 31.2 | 388 | 20.8 | 35.4 | 446 |  | 2020-09-18 11:21 | 44092.4729 | 20.8 | 35.4 | 446 |  | caution | 2020-09-14 | B90558¦Justice Wheeler office¦¦Sep-18-2020 11:20
2020-09-18 11:21 | 44092.473 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Robing corridor |  | 1 | 13.4 | 25.7 | 403 | 19.5 | 46.2 | 580 |  | 2020-09-18 11:21 | 44092.473 | 19.5 | 46.2 | 580 |  |  | 2020-09-14 | B20474¦Robing corridor¦¦Sep-18-2020 11:21
2020-09-18 11:22 | 44092.4734 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Interview room 1 |  | 1 | 9 | 51 | 392 | 22.3 | 34.3 | 455 |  | 2020-09-18 11:22 | 44092.4734 | 22.3 | 34.3 | 455 |  | low | 2020-09-14 | B20494¦Interview room 1¦¦Sep-18-2020 11:21
2020-09-18 11:22 | 44092.4734 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 3 |  | 0 | 13.8 | 27.9 | 408 | 21.8 | 30.1 | 461 |  | 2020-09-18 11:22 | 44092.4734 | 21.8 | 30.1 | 461 |  | low | 2020-09-14 | B20367¦Waiting room 3¦¦Sep-18-2020 11:21
2020-09-18 11:22 | 44092.4735 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | Center Hall |  | 0 | 14 | 38 | 430 | 22 | 45 | 600 |  | 2020-09-18 11:22 | 44092.4735 | 22 | 45 | 600 |  |  | 2020-09-14 | B25548¦Center Hall¦¦Sep-18-2020 11:21
2020-09-18 11:22 | 44092.4736 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Court room - judges desk, Right side/ centre |  | 2 | 18.1 | 29 | 385 | 22.6 | 25.3 | 394 |  | 2020-09-18 11:22 | 44092.4736 | 22.6 | 25.3 | 394 |  | low | 2020-09-14 | B70277¦Court room - judges desk, Right side/ centre¦¦Sep-18-2020 11:21
2020-09-18 11:22 | 44092.4737 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 136 |  | 3 | 11 | 45 | 377 | 23.7 | 33.4 | 470 | No | 2020-09-18 11:22 | 44092.4737 | 23.7 | 33.4 | 470 |  | low | 2020-09-14 | B14660¦136¦¦Sep-18-2020 11:22
2020-09-18 11:22 | 44092.4737 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 412 |  | 3 | 18 | 21.9 | 388 | 22.3 | 18.1 | 446 | No | 2020-09-18 11:22 | 44092.4737 | 22.3 | 18.1 | 446 |  | low | 2020-09-14 | B21128¦412¦¦Sep-18-2020 11:22
2020-09-18 11:22 | 44092.4738 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 3rd floor hallway south |  | 0 | 8 | 55 | 374 | 22.6 | 39.8 | 471 | No | 2020-09-18 11:22 | 44092.4738 | 22.6 | 39.8 | 471 |  | caution | 2020-09-14 | B20489¦3rd floor hallway south ¦¦Sep-18-2020 11:22
2020-09-18 11:22 | 44092.4739 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway |  | 1 | 8.4 | 54.9 | 371 | 24.1 | 33.6 | 442 |  | 2020-09-18 11:22 | 44092.4739 | 24.1 | 33.6 | 442 |  | low | 2020-09-14 | B20494¦Third floor hallway ¦¦Sep-18-2020 11:22
2020-09-18 11:23 | 44092.4742 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice O'Brien office |  | 0 | 13.2 | 31.2 | 388 | 20 | 37.3 | 468 |  | 2020-09-18 11:23 | 44092.4742 | 20 | 37.3 | 468 |  | caution | 2020-09-14 | B90558¦Justice O'Brien office¦¦Sep-18-2020 11:22
2020-09-18 11:23 | 44092.4742 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Interview room 402 |  | 0 | 13.8 | 27.9 | 408 | 22.5 | 29.3 | 485 |  | 2020-09-18 11:23 | 44092.4742 | 22.5 | 29.3 | 485 |  | low | 2020-09-14 | B20367¦Interview room 402¦¦Sep-18-2020 11:22
2020-09-18 11:23 | 44092.4743 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - witness stand |  | 2 | 18.1 | 29 | 385 | 22.7 | 25.2 | 399 |  | 2020-09-18 11:23 | 44092.4743 | 22.7 | 25.2 | 399 |  | low | 2020-09-14 | B70277¦Courtroom - witness stand¦¦Sep-18-2020 11:23
2020-09-18 11:23 | 44092.4746 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 411 |  | 5 | 18 | 21.9 | 388 | 22.6 | 19.9 | 455 | No | 2020-09-18 11:23 | 44092.4746 | 22.6 | 19.9 | 455 |  | low | 2020-09-14 | B21128¦411¦¦Sep-18-2020 11:23
2020-09-18 11:23 | 44092.4746 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Bottom stairs foyer |  | 1 | 13.4 | 25.7 | 403 | 19.9 | 35.6 | 614 |  | 2020-09-18 11:23 | 44092.4746 | 19.9 | 35.6 | 614 |  | caution | 2020-09-14 | B20474¦Bottom stairs foyer¦¦Sep-18-2020 11:23
2020-09-18 11:24 | 44092.4747 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-E wall |  | 0 | 14 | 38 | 430 | 23 | 45 | 650 |  | 2020-09-18 11:24 | 44092.4747 | 23 | 45 | 650 |  |  | 2020-09-14 | B25548¦1-E wall¦¦Sep-18-2020 11:23
2020-09-18 11:24 | 44092.4749 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Interview room 402b |  | 0 | 13.8 | 27.9 | 408 | 22.8 | 29.1 | 483 |  | 2020-09-18 11:24 | 44092.4749 | 22.8 | 29.1 | 483 |  | low | 2020-09-14 | B20367¦Interview room 402b ¦¦Sep-18-2020 11:23
2020-09-18 11:24 | 44092.4752 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Main entrance |  | 1 | 12.4 | 36.5 | 409 | 18.6 | 45.1 | 409 |  | 2020-09-18 11:24 | 44092.4752 | 18.6 | 45.1 | 409 |  |  | 2020-09-14 | B11228¦Main entrance¦¦Sep-18-2020 11:24
2020-09-18 11:25 | 44092.4754 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 144 |  | 0 | 11 | 45 | 377 | 23.9 | 32.7 | 443 | No | 2020-09-18 11:25 | 44092.4754 | 23.9 | 32.7 | 443 |  | low | 2020-09-14 | B14660¦144¦¦Sep-18-2020 11:24
2020-09-18 11:25 | 44092.4755 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 410 |  | 2 | 18 | 21.9 | 388 | 22.6 | 18.5 | 460 | No | 2020-09-18 11:25 | 44092.4755 | 22.6 | 18.5 | 460 |  | low | 2020-09-14 | B21128¦410¦¦Sep-18-2020 11:24
2020-09-18 11:25 | 44092.4756 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Judges chamber - front desk |  | 1 | 18.1 | 29 | 385 | 22.6 | 25.3 | 394 |  | 2020-09-18 11:25 | 44092.4756 | 22.6 | 25.3 | 394 |  | low | 2020-09-14 | B70277¦Judges chamber - front desk¦¦Sep-18-2020 11:24
2020-09-18 11:25 | 44092.4758 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | TC office |  | 1 | 13.2 | 31.2 | 388 | 21 | 36.7 | 496 |  | 2020-09-18 11:25 | 44092.4758 | 21 | 36.7 | 496 |  | caution | 2020-09-14 | B90558¦TC office¦¦Sep-18-2020 11:25
2020-09-18 11:25 | 44092.4759 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-E wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 590 |  | 2020-09-18 11:25 | 44092.4759 | 23 | 44 | 590 |  |  | 2020-09-14 | B25548¦1-E wall¦¦Sep-18-2020 11:25
2020-09-18 11:25 | 44092.4759 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 1 west |  | 3 | 8.4 | 54.9 | 371 | 23.5 | 25.3 | 398 |  | 2020-09-18 11:25 | 44092.4759 | 23.5 | 25.3 | 398 |  | low | 2020-09-14 | B20494¦Courtroom 1 west¦¦Sep-18-2020 11:25
2020-09-18 11:26 | 44092.4762 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Operations court |  | 2 | 13.8 | 27.9 | 408 | 21.7 | 29.3 | 483 |  | 2020-09-18 11:26 | 44092.4762 | 21.7 | 29.3 | 483 |  | low | 2020-09-14 | B20367¦Operations court¦¦Sep-18-2020 11:25
2020-09-18 11:26 | 44092.4762 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Judges chamber - behind desk by back door |  | 1 | 18.1 | 29 | 385 | 22.5 | 25.8 | 394 |  | 2020-09-18 11:26 | 44092.4762 | 22.5 | 25.8 | 394 |  | low | 2020-09-14 | B70277¦Judges chamber - behind desk by back door¦¦Sep-18-2020 11:25
2020-09-18 11:26 | 44092.4763 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Main office |  | 2 | 13.4 | 25.7 | 403 | 20.3 | 34.8 | 560 |  | 2020-09-18 11:26 | 44092.4763 | 20.3 | 34.8 | 560 |  | low | 2020-09-14 | B20474¦Main office¦¦Sep-18-2020 11:25
2020-09-18 11:26 | 44092.4763 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family services |  | 1 | 9 | 51 | 392 | 23 | 42.8 | 449 |  | 2020-09-18 11:26 | 44092.4763 | 23 | 42.8 | 449 |  |  | 2020-09-14 | B20494¦Family services ¦¦Sep-18-2020 11:25
2020-09-18 11:26 | 44092.4763 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 409 |  | 12 | 18 | 21.9 | 388 | 22.7 | 19.1 | 515 | No | 2020-09-18 11:26 | 44092.4763 | 22.7 | 19.1 | 515 |  | low | 2020-09-14 | B21128¦409¦¦Sep-18-2020 11:25
2020-09-18 11:26 | 44092.4765 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-E wall |  | 0 | 14 | 38 | 430 | 23 | 45 | 590 |  | 2020-09-18 11:26 | 44092.4765 | 23 | 45 | 590 |  |  | 2020-09-14 | B25548¦1-E wall¦¦Sep-18-2020 11:26
2020-09-18 11:26 | 44092.4765 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Front stairway |  | 0 | 12.4 | 36.5 | 409 | 20.3 | 40.5 | 476 |  | 2020-09-18 11:26 | 44092.4765 | 20.3 | 40.5 | 476 |  |  | 2020-09-14 | B11228¦Front stairway¦¦Sep-18-2020 11:26
2020-09-18 11:27 | 44092.4769 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Library |  | 0 | 13.2 | 31.2 | 388 | 20.6 | 33.4 | 438 |  | 2020-09-18 11:27 | 44092.4769 | 20.6 | 33.4 | 438 |  | low | 2020-09-14 | B90558¦Library¦¦Sep-18-2020 11:26
2020-09-18 11:27 | 44092.477 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation office - desk area |  | 2 | 18.1 | 29 | 385 | 22.4 | 25.9 | 394 |  | 2020-09-18 11:27 | 44092.477 | 22.4 | 25.9 | 394 |  | low | 2020-09-14 | B70277¦Mediation office - desk area¦¦Sep-18-2020 11:26
2020-09-18 11:27 | 44092.4771 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Lunch room |  | 0 | 13.8 | 27.9 | 408 | 20 | 50 | 499 |  | 2020-09-18 11:27 | 44092.4771 | 20 | 50 | 499 |  |  | 2020-09-14 | B20367¦Lunch room ¦¦Sep-18-2020 11:27
2020-09-18 11:27 | 44092.4772 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 122 |  | 0 | 11 | 45 | 377 | 24 | 32.5 | 425 | No | 2020-09-18 11:27 | 44092.4772 | 24 | 32.5 | 425 |  | low | 2020-09-14 | B14660¦122¦¦Sep-18-2020 11:27
2020-09-18 11:27 | 44092.4773 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 595 |  | 2020-09-18 11:27 | 44092.4773 | 23 | 44 | 595 |  |  | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 11:27
2020-09-18 11:28 | 44092.4774 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 400 |  | 3 | 18 | 21.9 | 388 | 22.8 | 22.1 | 445 | No | 2020-09-18 11:28 | 44092.4774 | 22.8 | 22.1 | 445 |  | low | 2020-09-14 | B21128¦400¦¦Sep-18-2020 11:27
2020-09-18 11:28 | 44092.4776 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Lunch room |  | 0 | 13.8 | 27.9 | 408 | 20 | 50 | 529 |  | 2020-09-18 11:28 | 44092.4776 | 20 | 50 | 529 |  |  | 2020-09-14 | B90631¦Lunch room ¦¦Sep-18-2020 11:27
2020-09-18 11:28 | 44092.4778 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Large courtroom benches |  | 0 | 12.4 | 36.5 | 409 | 20.8 | 40 | 433 |  | 2020-09-18 11:28 | 44092.4778 | 20.8 | 40 | 433 |  | caution | 2020-09-14 | B11228¦Large courtroom benches¦¦Sep-18-2020 11:28
2020-09-18 11:28 | 44092.4778 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation office - printer area |  | 2 | 18.1 | 29 | 385 | 22.4 | 25.8 | 397 |  | 2020-09-18 11:28 | 44092.4778 | 22.4 | 25.8 | 397 |  | low | 2020-09-14 | B70277¦Mediation office - printer area¦¦Sep-18-2020 11:28
2020-09-18 11:28 | 44092.4779 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area main office |  | 1 | 13.4 | 25.7 | 403 | 20.5 | 34.5 | 564 |  | 2020-09-18 11:28 | 44092.4779 | 20.5 | 34.5 | 564 |  | low | 2020-09-14 | B20474¦Waiting area main office¦¦Sep-18-2020 11:28
2020-09-18 11:29 | 44092.4781 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 1 east |  | 3 | 8.4 | 54.9 | 371 | 22.6 | 26.4 | 400 |  | 2020-09-18 11:29 | 44092.4781 | 22.6 | 26.4 | 400 |  | low | 2020-09-14 | B20494¦Courtroom 1 east¦¦Sep-18-2020 11:28
2020-09-18 11:29 | 44092.4782 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom a |  | 0 | 16.2 | 32.2 | 395 | 19.5 | 33.5 | 413 |  | 2020-09-18 11:29 | 44092.4782 | 19.5 | 33.5 | 413 |  | low | 2020-09-14 | Pearso¦Ballroom a ¦¦Sep-18-2020 11:28
2020-09-18 11:29 | 44092.4784 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Lunch/ kitchen room - centre counter |  | 2 | 18.1 | 29 | 385 | 22.4 | 25.8 | 397 |  | 2020-09-18 11:29 | 44092.4784 | 22.4 | 25.8 | 397 |  | low | 2020-09-14 | B70277¦Lunch/ kitchen room - centre counter¦¦Sep-18-2020 11:28
2020-09-18 11:29 | 44092.4784 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 600 |  | 2020-09-18 11:29 | 44092.4784 | 23 | 44 | 600 |  |  | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 11:28
2020-09-18 11:29 | 44092.4786 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 105 |  | 0 | 11 | 45 | 377 | 24 | 30.1 | 422 | No | 2020-09-18 11:29 | 44092.4786 | 24 | 30.1 | 422 |  | low | 2020-09-14 | B14660¦105¦¦Sep-18-2020 11:29
2020-09-18 11:30 | 44092.4789 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Fire pump |  | 1 | 9 | 51 | 392 | 23.6 | 41.8 | 441 |  | 2020-09-18 11:30 | 44092.4789 | 23.6 | 41.8 | 441 |  |  | 2020-09-14 | B20494¦Fire pump¦¦Sep-18-2020 11:29
2020-09-18 11:30 | 44092.479 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom a 2 |  | 0 | 16.2 | 32.2 | 32.2 | 20.8 | 30.1 | 412 |  | 2020-09-18 11:30 | 44092.479 | 20.8 | 30.1 | 412 |  | low | 2020-09-14 | Pearso¦Ballroom a 2 ¦¦Sep-18-2020 11:29
2020-09-18 11:30 | 44092.4791 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 14 | 38 | 430 | 23 | 43 | 630 |  | 2020-09-18 11:30 | 44092.4791 | 23 | 43 | 630 |  |  | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 11:29
2020-09-18 11:30 | 44092.4791 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 401 |  | 6 | 18 | 21.9 | 388 | 22.9 | 19 | 440 | No | 2020-09-18 11:30 | 44092.4791 | 22.9 | 19 | 440 |  | low | 2020-09-14 | B21128¦401¦¦Sep-18-2020 11:29
2020-09-18 11:30 | 44092.4792 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Large courtroom judges stand |  | 0 | 12.4 | 36.5 | 409 | 20.8 | 38.7 | 422 |  | 2020-09-18 11:30 | 44092.4792 | 20.8 | 38.7 | 422 |  | caution | 2020-09-14 | B11228¦Large courtroom judges stand¦¦Sep-18-2020 11:29
2020-09-18 11:30 | 44092.4794 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #2 |  | 1 | 13.4 | 25.7 | 403 | 20.3 | 33.9 | 557 |  | 2020-09-18 11:30 | 44092.4794 | 20.3 | 33.9 | 557 |  | low | 2020-09-14 | B20474¦Courtroom #2¦¦Sep-18-2020 11:30
2020-09-18 11:31 | 44092.4796 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom 1 |  | 14 | 13.2 | 31.2 | 388 | 20.8 | 33.2 | 534 |  | 2020-09-18 11:31 | 44092.4796 | 20.8 | 33.2 | 534 |  | low | 2020-09-14 | B90558¦Courtroom 1¦¦Sep-18-2020 11:30
2020-09-18 11:31 | 44092.4797 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 610 |  | 2020-09-18 11:31 | 44092.4797 | 23 | 44 | 610 |  |  | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 11:30
2020-09-18 11:31 | 44092.4797 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 106 |  | 0 | 11 | 45 | 377 | 23.8 | 27.7 | 430 | No | 2020-09-18 11:31 | 44092.4797 | 23.8 | 27.7 | 430 |  | low | 2020-09-14 | B14660¦106¦¦Sep-18-2020 11:30
2020-09-18 11:31 | 44092.4798 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom b |  | 0 | 16.2 | 32.2 | 395 | 20.5 | 27.2 | 412 |  | 2020-09-18 11:31 | 44092.4798 | 20.5 | 27.2 | 412 |  | low | 2020-09-14 | Pearso¦Ballroom b ¦¦Sep-18-2020 11:30
2020-09-18 11:31 | 44092.4801 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 402 |  | 6 | 18 | 21.9 | 388 | 23 | 19.3 | 418 | No | 2020-09-18 11:31 | 44092.4801 | 23 | 19.3 | 418 |  | low | 2020-09-14 | B21128¦402¦¦Sep-18-2020 11:31
2020-09-18 11:31 | 44092.4801 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Case management |  | 5 | 13.8 | 27.9 | 408 | 21.4 | 47.2 | 1011 |  | 2020-09-18 11:31 | 44092.4801 | 21.4 | 47.2 | 1011 |  |  | 2020-09-14 | B90631¦Case management ¦¦Sep-18-2020 11:31
2020-09-18 11:32 | 44092.4805 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Rear meeting room |  | 0 | 12.4 | 36.5 | 409 | 21 | 40.1 | 419 |  | 2020-09-18 11:32 | 44092.4805 | 21 | 40.1 | 419 |  |  | 2020-09-14 | B11228¦Rear meeting room¦¦Sep-18-2020 11:31
2020-09-18 11:32 | 44092.4806 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 590 |  | 2020-09-18 11:32 | 44092.4806 | 23 | 44 | 590 |  |  | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 11:32
2020-09-18 11:32 | 44092.4807 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Waiting area 2 floor |  | 1 | 13.2 | 31.2 | 388 | 20.3 | 32.5 | 443 |  | 2020-09-18 11:32 | 44092.4807 | 20.3 | 32.5 | 443 |  | low | 2020-09-14 | B90558¦Waiting area 2 floor¦¦Sep-18-2020 11:32
2020-09-18 11:32 | 44092.4808 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Crown office 1 |  | 0 | 13.8 | 27.9 | 408 | 22.7 | 46.3 | 751 |  | 2020-09-18 11:32 | 44092.4808 | 22.7 | 46.3 | 751 |  |  | 2020-09-14 | B90631¦Crown office 1¦¦Sep-18-2020 11:32
2020-09-18 11:32 | 44092.4809 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Crown attorneys office |  | 5 | 18 | 21.9 | 388 | 23 | 19.6 | 423 | No | 2020-09-18 11:32 | 44092.4809 | 23 | 19.6 | 423 |  | low | 2020-09-14 | B21128¦Crown attorneys office ¦¦Sep-18-2020 11:32
2020-09-18 11:33 | 44092.481 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom b 2 |  | 0 | 16.2 | 33.2 | 395 | 19.6 | 28.7 | 407 |  | 2020-09-18 11:33 | 44092.481 | 19.6 | 28.7 | 407 |  | low | 2020-09-14 | Pearso¦Ballroom b 2 ¦¦Sep-18-2020 11:32
2020-09-18 11:33 | 44092.4811 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 111 |  | 0 | 11 | 45 | 377 | 23.5 | 33.6 | 440 | No | 2020-09-18 11:33 | 44092.4811 | 23.5 | 33.6 | 440 |  | low | 2020-09-14 | B14660¦111¦¦Sep-18-2020 11:32
2020-09-18 11:33 | 44092.4812 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #3 |  | 2 | 13.4 | 25.7 | 403 | 20.7 | 35.7 | 601 |  | 2020-09-18 11:33 | 44092.4812 | 20.7 | 35.7 | 601 |  | caution | 2020-09-14 | B20474¦Courtroom #3¦¦Sep-18-2020 11:32
2020-09-18 11:33 | 44092.4812 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - kitchen entrance area |  | 2 | 18.1 | 29 | 385 | 22.6 | 26.6 | 459 |  | 2020-09-18 11:33 | 44092.4812 | 22.6 | 26.6 | 459 |  | low | 2020-09-14 | B70277¦Mediation room - kitchen entrance area¦¦Sep-18-2020 11:32
2020-09-18 11:33 | 44092.4814 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 14 | 38 | 430 | 23 | 43 | 585 |  | 2020-09-18 11:33 | 44092.4814 | 23 | 43 | 585 |  |  | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 11:33
2020-09-18 11:34 | 44092.4817 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom c |  | 0 | 16.2 | 32.2 | 395 | 20.1 | 28.7 | 405 |  | 2020-09-18 11:34 | 44092.4817 | 20.1 | 28.7 | 405 |  | low | 2020-09-14 | Pearso¦Ballroom c ¦¦Sep-18-2020 11:33
2020-09-18 11:34 | 44092.4817 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Administration office |  | 1 | 13.8 | 27.9 | 408 | 23 | 46 | 737 |  | 2020-09-18 11:34 | 44092.4817 | 23 | 46 | 737 |  |  | 2020-09-14 | B90631¦Administration office ¦¦Sep-18-2020 11:33
2020-09-18 11:34 | 44092.4819 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation Room - centre table |  | 2 | 18.1 | 29 | 385 | 22.7 | 25.9 | 432 |  | 2020-09-18 11:34 | 44092.4819 | 22.7 | 25.9 | 432 |  | low | 2020-09-14 | B70277¦Mediation Room - centre table¦¦Sep-18-2020 11:33
2020-09-18 11:34 | 44092.482 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Judges office |  | 0 | 12.4 | 36.5 | 409 | 21.1 | 38.5 | 424 |  | 2020-09-18 11:34 | 44092.482 | 21.1 | 38.5 | 424 |  | caution | 2020-09-14 | B11228¦Judges office¦¦Sep-18-2020 11:34
2020-09-18 11:35 | 44092.4823 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-W wall |  | 0 | 14 | 38 | 430 | 23 | 43 | 605 |  | 2020-09-18 11:35 | 44092.4823 | 23 | 43 | 605 |  |  | 2020-09-14 | B25548¦1-W wall¦¦Sep-18-2020 11:34
2020-09-18 11:35 | 44092.4824 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Crown office 2 |  | 0 | 13.8 | 27.9 | 408 | 23.1 | 43 | 706 |  | 2020-09-18 11:35 | 44092.4824 | 23.1 | 43 | 706 |  |  | 2020-09-14 | B90631¦Crown office 2¦¦Sep-18-2020 11:34
2020-09-18 11:35 | 44092.4824 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 1st floor hall by elevator |  | 1 | 9 | 51 | 392 | 23.7 | 37.8 | 468 |  | 2020-09-18 11:35 | 44092.4824 | 23.7 | 37.8 | 468 |  | caution | 2020-09-14 | B20494¦1st floor hall by elevator ¦¦Sep-18-2020 11:34
2020-09-18 11:35 | 44092.4826 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - hallway entrance area |  | 2 | 18.1 | 29 | 385 | 22.7 | 26 | 431 |  | 2020-09-18 11:35 | 44092.4826 | 22.7 | 26 | 431 |  | low | 2020-09-14 | B70277¦Mediation room - hallway entrance area¦¦Sep-18-2020 11:34
2020-09-18 11:35 | 44092.4829 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | OPP office |  | 1 | 21 | 16 | 407 | 22 | 25 | 582 |  | 2020-09-18 11:35 | 44092.4829 | 22 | 25 | 582 |  | low | 2020-09-14 | B70235¦OPP office ¦¦Sep-18-2020 11:35
2020-09-18 11:35 | 44092.4829 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom c 2 |  | 0 | 16.2 | 32.2 | 395 | 20 | 28.6 | 404 |  | 2020-09-18 11:35 | 44092.4829 | 20 | 28.6 | 404 |  | low | 2020-09-14 | Pearso¦Ballroom c 2¦¦Sep-18-2020 11:35
2020-09-18 11:35 | 44092.483 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #1 |  | 2 | 13.4 | 25.7 | 403 | 20.3 | 34.4 | 584 |  | 2020-09-18 11:35 | 44092.483 | 20.3 | 34.4 | 584 |  | low | 2020-09-14 | B20474¦Courtroom #1¦¦Sep-18-2020 11:35
2020-09-18 11:36 | 44092.4831 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 203 |  | 0 | 11 | 45 | 377 | 23.1 | 28.7 | 427 | No | 2020-09-18 11:36 | 44092.4831 | 23.1 | 28.7 | 427 |  | low | 2020-09-14 | B14660¦203¦¦Sep-18-2020 11:35
2020-09-18 11:36 | 44092.4831 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Side hallway |  | 0 | 12.4 | 36.5 | 409 | 22.1 | 43.4 | 478 |  | 2020-09-18 11:36 | 44092.4831 | 22.1 | 43.4 | 478 |  |  | 2020-09-14 | B11228¦Side hallway¦¦Sep-18-2020 11:35
2020-09-18 11:36 | 44092.4833 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-W wall |  | 0 | 14 | 38 | 430 | 22 | 44 | 580 |  | 2020-09-18 11:36 | 44092.4833 | 22 | 44 | 580 |  |  | 2020-09-14 | B25548¦1-W wall¦¦Sep-18-2020 11:35
2020-09-18 11:36 | 44092.4836 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Vwap waiting room |  | 0 | 13.8 | 27.9 | 408 | 21.5 | 43.3 | 465 |  | 2020-09-18 11:36 | 44092.4836 | 21.5 | 43.3 | 465 |  |  | 2020-09-14 | B90631¦Vwap waiting room ¦¦Sep-18-2020 11:36
2020-09-18 11:37 | 44092.4839 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-W wall |  | 0 | 14 | 38 | 430 | 22 | 44 | 590 |  | 2020-09-18 11:37 | 44092.4839 | 22 | 44 | 590 |  |  | 2020-09-14 | B25548¦1-W wall¦¦Sep-18-2020 11:36
2020-09-18 11:37 | 44092.4842 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Rear stairway |  | 0 | 12.4 | 36.5 | 409 | 22.7 | 38.1 | 443 |  | 2020-09-18 11:37 | 44092.4842 | 22.7 | 38.1 | 443 |  | caution | 2020-09-14 | B11228¦Rear stairway¦¦Sep-18-2020 11:37
2020-09-18 11:37 | 44092.4843 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Judges chamber foyers |  | 0 | 13.8 | 27.9 | 408 | 31.7 | 45 | 526 |  | 2020-09-18 11:37 | 44092.4843 | 31.7 | 45 | 526 | high |  | 2020-09-14 | B90631¦Judges chamber foyers ¦¦Sep-18-2020 11:37
2020-09-18 11:37 | 44092.4843 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom d |  | 0 | 16.2 | 32.2 | 395 | 20.7 | 28 | 404 |  | 2020-09-18 11:37 | 44092.4843 | 20.7 | 28 | 404 |  | low | 2020-09-14 | Pearso¦Ballroom d ¦¦Sep-18-2020 11:37
2020-09-18 11:38 | 44092.4844 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office E |  | 4 | 21 | 16 | 407 | 23 | 25 | 557 |  | 2020-09-18 11:38 | 44092.4844 | 23 | 25 | 557 |  | low | 2020-09-14 | B70235¦Main office E ¦¦Sep-18-2020 11:37
2020-09-18 11:38 | 44092.4845 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | S foyer |  | 0 | 14 | 38 | 430 | 22 | 45 | 610 |  | 2020-09-18 11:38 | 44092.4845 | 22 | 45 | 610 |  |  | 2020-09-14 | B25548¦S foyer¦¦Sep-18-2020 11:37
2020-09-18 11:38 | 44092.4846 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 waiting area |  | 1 | 18 | 18 | 380 | 24 | 18 | 383 |  | 2020-09-18 11:38 | 44092.4846 | 24 | 18 | 383 |  | low | 2020-09-14 | B20772¦H9 waiting area ¦¦Sep-18-2020 11:37
2020-09-18 11:38 | 44092.4847 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom1 |  | 1 | 13.4 | 25.7 | 403 | 19.8 | 35.6 | 665 |  | 2020-09-18 11:38 | 44092.4847 | 19.8 | 35.6 | 665 |  | caution | 2020-09-14 | B20474¦Waiting area courtroom1¦¦Sep-18-2020 11:38
2020-09-18 11:38 | 44092.4848 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Duty Council office - desk area |  | 1 | 18.1 | 29 | 385 | 22.8 | 26 | 404 |  | 2020-09-18 11:38 | 44092.4848 | 22.8 | 26 | 404 |  | low | 2020-09-14 | B70277¦Duty Council office - desk area¦¦Sep-18-2020 11:38
2020-09-18 11:38 | 44092.4849 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Judges chamber |  | 0 | 13.8 | 27.9 | 408 | 21.6 | 45 | 499 |  | 2020-09-18 11:38 | 44092.4849 | 21.6 | 45 | 499 |  |  | 2020-09-14 | B90631¦Judges chamber ¦¦Sep-18-2020 11:38
2020-09-18 11:38 | 44092.4849 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom d 2 |  | 0 | 16.2 | 32.2 | 395 | 20.2 | 28.6 | 411 |  | 2020-09-18 11:38 | 44092.4849 | 20.2 | 28.6 | 411 |  | low | 2020-09-14 | Pearso¦Ballroom d 2¦¦Sep-18-2020 11:38
2020-09-18 11:39 | 44092.4852 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 3 gallery |  | 0 | 12 | 37 | 392 | 20.7 | 33.8 | 566 | No | 2020-09-18 11:39 | 44092.4852 | 20.7 | 33.8 | 566 |  | low | 2020-09-14 | B20151¦Court room 3 gallery ¦¦Sep-18-2020 11:38
2020-09-18 11:39 | 44092.4853 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 rear lef |  | 1 | 18 | 18 | 380 | 24 | 19 | 376 |  | 2020-09-18 11:39 | 44092.4853 | 24 | 19 | 376 |  | low | 2020-09-14 | B20772¦H9 rear lef¦¦Sep-18-2020 11:38
2020-09-18 11:39 | 44092.4854 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office C |  | 4 | 21 | 16 | 407 | 23 | 23 | 536 |  | 2020-09-18 11:39 | 44092.4854 | 23 | 23 | 536 |  | low | 2020-09-14 | B70235¦Main office C ¦¦Sep-18-2020 11:38
2020-09-18 11:39 | 44092.4855 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom e |  | 0 | 16.2 | 32.2 | 395 | 20 | 26.9 | 409 |  | 2020-09-18 11:39 | 44092.4855 | 20 | 26.9 | 409 |  | low | 2020-09-14 | Pearso¦Ballroom e ¦¦Sep-18-2020 11:39
2020-09-18 11:39 | 44092.4856 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | N foyer |  | 0 | 14 | 38 | 430 | 22 | 45 | 590 |  | 2020-09-18 11:39 | 44092.4856 | 22 | 45 | 590 |  |  | 2020-09-14 | B25548¦N foyer¦¦Sep-18-2020 11:39
2020-09-18 11:39 | 44092.4856 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom 4 |  | 0 | 13.8 | 27.9 | 408 | 22 | 46 | 554 |  | 2020-09-18 11:39 | 44092.4856 | 22 | 46 | 554 |  |  | 2020-09-14 | B90631¦Courtroom 4¦¦Sep-18-2020 11:39
2020-09-18 11:39 | 44092.4856 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Duty council office - back right, seating area |  | 1 | 18.1 | 29 | 385 | 22.9 | 25.8 | 395 |  | 2020-09-18 11:39 | 44092.4856 | 22.9 | 25.8 | 395 |  | low | 2020-09-14 | B70277¦Duty council office - back right, seating area¦¦Sep-18-2020 11:39
2020-09-18 11:40 | 44092.486 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 213 |  | 0 | 11 | 45 | 377 | 23 | 28.7 | 448 | No | 2020-09-18 11:40 | 44092.486 | 23 | 28.7 | 448 |  | low | 2020-09-14 | B14660¦213¦¦Sep-18-2020 11:39
2020-09-18 11:40 | 44092.486 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Outside small courtroom |  | 0 | 12.4 | 36.5 | 409 | 22.3 | 37 | 457 |  | 2020-09-18 11:40 | 44092.486 | 22.3 | 37 | 457 |  | caution | 2020-09-14 | B11228¦Outside small courtroom¦¦Sep-18-2020 11:39
2020-09-18 11:40 | 44092.486 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 rear right |  | 1 | 18 | 18 | 380 | 24 | 19 | 377 |  | 2020-09-18 11:40 | 44092.486 | 24 | 19 | 377 |  | low | 2020-09-14 | B20772¦H9 rear right¦¦Sep-18-2020 11:39
2020-09-18 11:40 | 44092.4862 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom 4 waiting room |  | 0 | 13.8 | 27.9 | 408 | 21.7 | 42 | 586 |  | 2020-09-18 11:40 | 44092.4862 | 21.7 | 42 | 586 |  |  | 2020-09-14 | B90631¦Courtroom 4 waiting room ¦¦Sep-18-2020 11:40
2020-09-18 11:40 | 44092.4862 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom e 2 |  | 0 | 16.2 | 32.2 | 395 | 19.6 | 27.9 | 408 |  | 2020-09-18 11:40 | 44092.4862 | 19.6 | 27.9 | 408 |  | low | 2020-09-14 | Pearso¦Ballroom e 2 ¦¦Sep-18-2020 11:40
2020-09-18 11:41 | 44092.4865 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office E |  | 4 | 21 | 16 | 407 | 23 | 22 | 518 |  | 2020-09-18 11:41 | 44092.4865 | 23 | 22 | 518 |  | low | 2020-09-14 | B70235¦Main office E ¦¦Sep-18-2020 11:40
2020-09-18 11:41 | 44092.4865 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney waiting room |  | 3 | 9 | 51 | 392 | 23.8 | 42.2 | 691 |  | 2020-09-18 11:41 | 44092.4865 | 23.8 | 42.2 | 691 |  |  | 2020-09-14 | B20494¦Crown attorney waiting room¦¦Sep-18-2020 11:40
2020-09-18 11:41 | 44092.4865 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Upper landing stairway |  | 1 | 13.4 | 25.7 | 403 | 19.8 | 34.8 | 645 |  | 2020-09-18 11:41 | 44092.4865 | 19.8 | 34.8 | 645 |  | low | 2020-09-14 | B20474¦Upper landing stairway ¦¦Sep-18-2020 11:40
2020-09-18 11:41 | 44092.4867 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 209 |  | 0 | 11 | 45 | 377 | 23 | 28.5 | 426 | No | 2020-09-18 11:41 | 44092.4867 | 23 | 28.5 | 426 |  | low | 2020-09-14 | B14660¦209¦¦Sep-18-2020 11:40
2020-09-18 11:41 | 44092.4868 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 dependant |  | 1 | 18 | 18 | 380 | 24 | 20 | 377 |  | 2020-09-18 11:41 | 44092.4868 | 24 | 20 | 377 |  | low | 2020-09-14 | B20772¦H9 dependant¦¦Sep-18-2020 11:41
2020-09-18 11:41 | 44092.487 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside of door “302” |  | 1 | 18.1 | 29 | 385 | 22.6 | 25.7 | 419 |  | 2020-09-18 11:41 | 44092.487 | 22.6 | 25.7 | 419 |  | low | 2020-09-14 | B70277¦Hallway - outside of door “302”¦¦Sep-18-2020 11:41
2020-09-18 11:41 | 44092.4871 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 14 | 38 | 430 | 22 | 45 | 590 |  | 2020-09-18 11:41 | 44092.4871 | 22 | 45 | 590 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 11:41
2020-09-18 11:41 | 44092.4871 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office W |  | 4 | 21 | 16 | 407 | 23 | 22 | 518 |  | 2020-09-18 11:41 | 44092.4871 | 23 | 22 | 518 |  | low | 2020-09-14 | B70235¦Main office W ¦¦Sep-18-2020 11:41
2020-09-18 11:41 | 44092.4872 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Small courtroom rear |  | 0 | 12.4 | 36.5 | 409 | 21.6 | 42.6 | 446 |  | 2020-09-18 11:42 | 44092.4872 | 21.6 | 42.6 | 446 |  |  | 2020-09-14 | B11228¦Small courtroom rear¦¦Sep-18-2020 11:41
2020-09-18 11:42 | 44092.4873 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 3 judge desk |  | 2 | 12 | 37 | 392 | 21.7 | 35.4 | 490 | No | 2020-09-18 11:42 | 44092.4873 | 21.7 | 35.4 | 490 |  | caution | 2020-09-14 | B20151¦Court room 3 judge desk ¦¦Sep-18-2020 11:41
2020-09-18 11:42 | 44092.4876 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom A chairs |  | 0 | 13.8 | 33 | 413 | 21.2 | 25.6 | 421 |  | 2020-09-18 11:42 | 44092.4876 | 21.2 | 25.6 | 421 |  | low | 2020-09-14 | B20603¦Courtroom A chairs ¦¦Sep-18-2020 11:42
2020-09-18 11:42 | 44092.4876 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 plaintiff |  | 1 | 18 | 18 | 380 | 23 | 20 | 378 |  | 2020-09-18 11:42 | 44092.4876 | 23 | 20 | 378 |  | low | 2020-09-14 | B20772¦H9 plaintiff¦¦Sep-18-2020 11:42
2020-09-18 11:43 | 44092.4879 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside of duty council office |  | 1 | 18.1 | 29 | 385 | 22.3 | 25.8 | 418 |  | 2020-09-18 11:43 | 44092.4879 | 22.3 | 25.8 | 418 |  | low | 2020-09-14 | B70277¦Hallway - outside of duty council office¦¦Sep-18-2020 11:42
2020-09-18 11:43 | 44092.4882 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 judge |  | 1 | 18 | 18 | 380 | 23 | 21 | 378 |  | 2020-09-18 11:43 | 44092.4882 | 23 | 21 | 378 |  | low | 2020-09-14 | B20772¦H9 judge¦¦Sep-18-2020 11:42
2020-09-18 11:43 | 44092.4882 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 210a |  | 1 | 11 | 45 | 377 | 23.2 | 27.6 | 416 | No | 2020-09-18 11:43 | 44092.4882 | 23.2 | 27.6 | 416 |  | low | 2020-09-14 | B14660¦210a¦¦Sep-18-2020 11:43
2020-09-18 11:43 | 44092.4883 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 14 | 38 | 430 | 22 | 45 | 570 |  | 2020-09-18 11:43 | 44092.4883 | 22 | 45 | 570 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 11:43
2020-09-18 11:43 | 44092.4884 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Trial office |  | 0 | 21 | 16 | 407 | 23 | 24 | 501 |  | 2020-09-18 11:43 | 44092.4884 | 23 | 24 | 501 |  | low | 2020-09-14 | B70235¦Trial office ¦¦Sep-18-2020 11:43
2020-09-18 11:43 | 44092.4885 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom A bench |  | 0 | 13.8 | 33 | 413 | 21.6 | 24.7 | 429 |  | 2020-09-18 11:43 | 44092.4885 | 21.6 | 24.7 | 429 |  | low | 2020-09-14 | B20603¦Courtroom A bench ¦¦Sep-18-2020 11:43
2020-09-18 11:43 | 44092.4885 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom4 corridor |  | 1 | 13.4 | 25.7 | 403 | 19.7 | 36.4 | 607 |  | 2020-09-18 11:43 | 44092.4885 | 19.7 | 36.4 | 607 |  | caution | 2020-09-14 | B20474¦Courtroom4 corridor¦¦Sep-18-2020 11:43
2020-09-18 11:44 | 44092.4886 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Small courtroom judges stand |  | 0 | 12.4 | 36.5 | 409 | 20.2 | 42.1 | 442 |  | 2020-09-18 11:44 | 44092.4886 | 20.2 | 42.1 | 442 |  |  | 2020-09-14 | B11228¦Small courtroom judges stand¦¦Sep-18-2020 11:43
2020-09-18 11:44 | 44092.4888 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - elevator lobby |  | 1 | 18.1 | 29 | 385 | 22.5 | 25.5 | 421 |  | 2020-09-18 11:44 | 44092.4888 | 22.5 | 25.5 | 421 |  | low | 2020-09-14 | B70277¦Hallway - elevator lobby¦¦Sep-18-2020 11:43
2020-09-18 11:44 | 44092.4889 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Front Lobby |  | 2 | 15 | 26.7 | 388 | 18.4 | 40 | 449 |  | 2020-09-18 11:44 | 44092.4889 | 18.4 | 40 | 449 |  | caution | 2020-09-14 | B20550¦Front Lobby¦¦Sep-18-2020 11:44
2020-09-18 11:44 | 44092.4889 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney printer room |  | 1 | 9 | 51 | 392 | 23.1 | 43.8 | 516 |  | 2020-09-18 11:44 | 44092.4889 | 23.1 | 43.8 | 516 |  |  | 2020-09-14 | B20494¦Crown attorney printer room¦¦Sep-18-2020 11:44
2020-09-18 11:44 | 44092.4889 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 206 |  | 0 | 11 | 45 | 377 | 22.8 | 27.6 | 415 | No | 2020-09-18 11:44 | 44092.4889 | 22.8 | 27.6 | 415 |  | low | 2020-09-14 | B14660¦206¦¦Sep-18-2020 11:44
2020-09-18 11:44 | 44092.4891 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom f |  | 0 | 16.2 | 32.2 | 395 | 20.7 | 27.9 | 406 |  | 2020-09-18 11:44 | 44092.4891 | 20.7 | 27.9 | 406 |  | low | 2020-09-14 | Pearso¦Ballroom f¦¦Sep-18-2020 11:44
2020-09-18 11:45 | 44092.4894 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 gallery |  | 0 | 12 | 37 | 392 | 21.7 | 31.2 | 601 | No | 2020-09-18 11:45 | 44092.4894 | 21.7 | 31.2 | 601 |  | low | 2020-09-14 | B20151¦Court room 2 gallery ¦¦Sep-18-2020 11:44
2020-09-18 11:45 | 44092.4895 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 14 | 38 | 430 | 22 | 45 | 590 |  | 2020-09-18 11:45 | 44092.4895 | 22 | 45 | 590 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 11:44
2020-09-18 11:45 | 44092.4897 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside of public washrooms |  | 1 | 18.1 | 29 | 385 | 22.5 | 25.5 | 420 |  | 2020-09-18 11:45 | 44092.4897 | 22.5 | 25.5 | 420 |  | low | 2020-09-14 | B70277¦Hallway - outside of public washrooms¦¦Sep-18-2020 11:45
2020-09-18 11:45 | 44092.4898 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom B chairs |  | 0 | 13.8 | 33 | 413 | 21.7 | 26.1 | 431 |  | 2020-09-18 11:45 | 44092.4898 | 21.7 | 26.1 | 431 |  | low | 2020-09-14 | B20603¦Courtroom B chairs ¦¦Sep-18-2020 11:45
2020-09-18 11:46 | 44092.49 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 14 | 38 | 430 | 22 | 45 | 590 |  | 2020-09-18 11:46 | 44092.49 | 22 | 45 | 590 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 11:45
2020-09-18 11:46 | 44092.49 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Ballroom f 2 |  | 0 | 16.2 | 32.2 | 395 | 20.6 | 27.2 | 404 |  | 2020-09-18 11:46 | 44092.49 | 20.6 | 27.2 | 404 |  | low | 2020-09-14 | Pearso¦Ballroom f 2¦¦Sep-18-2020 11:45
2020-09-18 11:46 | 44092.4903 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Library |  | 0 | 12.4 | 36.5 | 409 | 20.7 | 41.6 | 447 |  | 2020-09-18 11:46 | 44092.4903 | 20.7 | 41.6 | 447 |  |  | 2020-09-14 | B11228¦Library¦¦Sep-18-2020 11:45
2020-09-18 11:46 | 44092.4904 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jennifer Mumby office |  | 0 | 21 | 16 | 407 | 23 | 23 | 487 |  | 2020-09-18 11:46 | 44092.4904 | 23 | 23 | 487 |  | low | 2020-09-14 | B70235¦Jennifer Mumby office ¦¦Sep-18-2020 11:46
2020-09-18 11:46 | 44092.4905 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 14 | 38 | 430 | 23 | 45 | 590 |  | 2020-09-18 11:46 | 44092.4905 | 23 | 45 | 590 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 11:46
2020-09-18 11:46 | 44092.4906 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom B bench |  | 0 | 13.8 | 33 | 413 | 21.8 | 25.8 | 426 |  | 2020-09-18 11:46 | 44092.4906 | 21.8 | 25.8 | 426 |  | low | 2020-09-14 | B20603¦Courtroom B bench ¦¦Sep-18-2020 11:46
2020-09-18 11:47 | 44092.4907 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 judge |  | 1 | 18 | 18 | 380 | 22 | 21 | 376 |  | 2020-09-18 11:47 | 44092.4907 | 22 | 21 | 376 |  | low | 2020-09-14 | B20772¦H15 judge ¦¦Sep-18-2020 11:46
2020-09-18 11:47 | 44092.491 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Policeroom 1 |  | 0 | 16.2 | 32.2 | 395 | 21.1 | 27.7 | 406 |  | 2020-09-18 11:47 | 44092.491 | 21.1 | 27.7 | 406 |  | low | 2020-09-14 | Pearso¦Policeroom 1 ¦¦Sep-18-2020 11:47
2020-09-18 11:47 | 44092.4911 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | 3rd Floor Stairwell |  | 1 | 18.1 | 29 | 385 | 23.3 | 25.9 | 477 |  | 2020-09-18 11:47 | 44092.4911 | 23.3 | 25.9 | 477 |  | low | 2020-09-14 | B70277¦3rd Floor Stairwell¦¦Sep-18-2020 11:47
2020-09-18 11:47 | 44092.4912 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Courtroom 1 |  | 1 | 15 | 26.7 | 388 | 22.8 | 29 | 444 |  | 2020-09-18 11:47 | 44092.4912 | 22.8 | 29 | 444 |  | low | 2020-09-14 | B20550¦Courtroom 1¦¦Sep-18-2020 11:47
2020-09-18 11:47 | 44092.4913 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 plaintiff |  | 1 | 18 | 18 | 380 | 21 | 22 | 378 |  | 2020-09-18 11:47 | 44092.4913 | 21 | 22 | 378 |  | low | 2020-09-14 | B20772¦H15 plaintiff ¦¦Sep-18-2020 11:47
2020-09-18 11:48 | 44092.4914 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Admin office |  | 1 | 12.4 | 36.5 | 409 | 21.1 | 43.5 | 500 |  | 2020-09-18 11:48 | 44092.4914 | 21.1 | 43.5 | 500 |  |  | 2020-09-14 | B11228¦Admin office¦¦Sep-18-2020 11:47
2020-09-18 11:48 | 44092.4914 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom D |  | 1 | 16.7 | 25.3 | 406 | 19.8 | 60.3 | 459 | No | 2020-09-18 11:48 | 44092.4914 | 19.8 | 60.3 | 459 |  | caution | 2020-09-14 | B20478¦Courtroom D¦¦Sep-18-2020 11:47
2020-09-18 11:48 | 44092.4915 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Stuart Konyer office |  | 0 | 21 | 16 | 407 | 23 | 24 | 470 |  | 2020-09-18 11:48 | 44092.4915 | 23 | 24 | 470 |  | low | 2020-09-14 | B70235¦Stuart Konyer office ¦¦Sep-18-2020 11:47
2020-09-18 11:48 | 44092.4915 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center |  | 0 | 13.8 | 33 | 413 | 21.8 | 24.8 | 428 |  | 2020-09-18 11:48 | 44092.4915 | 21.8 | 24.8 | 428 |  | low | 2020-09-14 | B20603¦Prep center ¦¦Sep-18-2020 11:47
2020-09-18 11:48 | 44092.4915 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom2 2nd door |  | 1 | 13.4 | 25.7 | 403 | 19.5 | 37 | 586 | courtroom #4 in session | 2020-09-18 11:48 | 44092.4915 | 19.5 | 37 | 586 |  | caution | 2020-09-14 | B20474¦Waiting area courtroom2 2nd door¦¦Sep-18-2020 11:47
2020-09-18 11:48 | 44092.4916 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 14 | 38 | 430 | 22 | 45 | 585 |  | 2020-09-18 11:48 | 44092.4916 | 22 | 45 | 585 |  |  | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 11:47
2020-09-18 11:48 | 44092.4917 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 judge desk |  | 3 | 12 | 37 | 392 | 22.2 | 30.9 | 620 | No | 2020-09-18 11:48 | 44092.4917 | 22.2 | 30.9 | 620 |  | low | 2020-09-14 | B20151¦Court room 2 judge desk ¦¦Sep-18-2020 11:48
2020-09-18 11:48 | 44092.4919 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Policeroom 2 |  | 0 | 16.2 | 32.2 | 395 | 21 | 27.3 | 404 |  | 2020-09-18 11:48 | 44092.4919 | 21 | 27.3 | 404 |  | low | 2020-09-14 | Pearso¦Policeroom 2 ¦¦Sep-18-2020 11:48
2020-09-18 11:48 | 44092.4919 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 303 |  | 0 | 11 | 45 | 377 | 22.7 | 30.9 | 431 | No | 2020-09-18 11:48 | 44092.4919 | 22.7 | 30.9 | 431 |  | low | 2020-09-14 | B14660¦303¦¦Sep-18-2020 11:48
2020-09-18 11:49 | 44092.4921 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 defendant |  | 1 | 18 | 18 | 380 | 21 | 23 | 377 |  | 2020-09-18 11:49 | 44092.4921 | 21 | 23 | 377 |  | low | 2020-09-14 | B20772¦H15 defendant¦¦Sep-18-2020 11:48
2020-09-18 11:49 | 44092.4921 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Inside elevator on 3rd Floor |  | 1 | 18.1 | 29 | 385 | 24.5 | 26.1 | 480 |  | 2020-09-18 11:49 | 44092.4921 | 24.5 | 26.1 | 480 |  | low | 2020-09-14 | B70277¦Inside elevator on 3rd Floor¦¦Sep-18-2020 11:48
2020-09-18 11:49 | 44092.4922 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom B |  | 1 | 16.7 | 25.3 | 406 | 21.1 | 37.8 | 448 | No | 2020-09-18 11:49 | 44092.4922 | 21.1 | 37.8 | 448 |  | caution | 2020-09-14 | B20478¦Courtroom B¦¦Sep-18-2020 11:48
2020-09-18 11:49 | 44092.4924 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Lunch room |  | 0 | 21 | 16 | 407 | 23 | 24 | 475 |  | 2020-09-18 11:49 | 44092.4924 | 23 | 24 | 475 |  | low | 2020-09-14 | B70235¦Lunch room ¦¦Sep-18-2020 11:49
2020-09-18 11:49 | 44092.4925 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Courtroom 2 |  | 1 | 15 | 26.7 | 388 | 23.1 | 27.5 | 434 |  | 2020-09-18 11:49 | 44092.4925 | 23.1 | 27.5 | 434 |  | low | 2020-09-14 | B20550¦Courtroom 2¦¦Sep-18-2020 11:49
2020-09-18 11:49 | 44092.4927 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 14 | 38 | 430 | 23 | 45 | 630 |  | 2020-09-18 11:49 | 44092.4927 | 23 | 45 | 630 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 11:49
2020-09-18 11:50 | 44092.4928 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Policeroom 3 |  | 0 | 16.2 | 32.2 | 395 | 20.9 | 26.9 | 406 |  | 2020-09-18 11:50 | 44092.4928 | 20.9 | 26.9 | 406 |  | low | 2020-09-14 | Pearso¦Policeroom 3 ¦¦Sep-18-2020 11:49
2020-09-18 11:50 | 44092.4929 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center 2 |  | 0 | 13.8 | 33 | 413 | 21.9 | 24.8 | 437 |  | 2020-09-18 11:50 | 44092.4929 | 21.9 | 24.8 | 437 |  | low | 2020-09-14 | B20603¦Prep center 2 ¦¦Sep-18-2020 11:49
2020-09-18 11:50 | 44092.493 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney office |  | 3 | 9 | 51 | 392 | 22.7 | 46.3 | 548 |  | 2020-09-18 11:50 | 44092.493 | 22.7 | 46.3 | 548 |  |  | 2020-09-14 | B20494¦Crown attorney office¦¦Sep-18-2020 11:49
2020-09-18 11:50 | 44092.493 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 rear right |  | 1 | 18 | 18 | 380 | 21 | 23 | 382 |  | 2020-09-18 11:50 | 44092.493 | 21 | 23 | 382 |  | low | 2020-09-14 | B20772¦H15 rear right ¦¦Sep-18-2020 11:49
2020-09-18 11:50 | 44092.4931 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 302 |  | 3 | 11 | 45 | 377 | 22.4 | 29.3 | 460 | No | 2020-09-18 11:50 | 44092.4931 | 22.4 | 29.3 | 460 |  | low | 2020-09-14 | B14660¦302¦¦Sep-18-2020 11:50
2020-09-18 11:50 | 44092.4931 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | 1st Floor front door lobby |  | 4 | 18.1 | 29 | 385 | 23.7 | 25.9 | 612 |  | 2020-09-18 11:50 | 44092.4931 | 23.7 | 25.9 | 612 |  | low | 2020-09-14 | B70277¦1st Floor front door lobby¦¦Sep-18-2020 11:50
2020-09-18 11:50 | 44092.4932 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court support office |  | 0 | 21 | 16 | 407 | 23 | 27 | 547 |  | 2020-09-18 11:50 | 44092.4932 | 23 | 27 | 547 |  | low | 2020-09-14 | B70235¦Court support office ¦¦Sep-18-2020 11:50
2020-09-18 11:50 | 44092.4932 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom2 1st door |  | 1 | 13.4 | 25.7 | 403 | 19.5 | 37 | 627 |  | 2020-09-18 11:50 | 44092.4932 | 19.5 | 37 | 627 |  | caution | 2020-09-14 | B20474¦Waiting area courtroom2 1st door¦¦Sep-18-2020 11:50
2020-09-18 11:50 | 44092.4934 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 14 | 38 | 430 | 23 | 45 | 605 |  | 2020-09-18 11:50 | 44092.4934 | 23 | 45 | 605 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 11:50
2020-09-18 11:50 | 44092.4934 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Policeroom 4 |  | 0 | 16.2 | 32.2 | 395 | 21 | 27.1 | 404 |  | 2020-09-18 11:50 | 44092.4934 | 21 | 27.1 | 404 |  | low | 2020-09-14 | Pearso¦Policeroom 4¦¦Sep-18-2020 11:50
2020-09-18 11:51 | 44092.4934 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney library |  | 1 | 9 | 51 | 392 | 23.1 | 44.5 | 574 |  | 2020-09-18 11:51 | 44092.4934 | 23.1 | 44.5 | 574 |  |  | 2020-09-14 | B20494¦Crown attorney library¦¦Sep-18-2020 11:50
2020-09-18 11:51 | 44092.4936 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom C |  | 1 | 16.7 | 25.3 | 406 | 22.2 | 33.2 | 464 | No | 2020-09-18 11:51 | 44092.4936 | 22.2 | 33.2 | 464 |  | low | 2020-09-14 | B20478¦Courtroom C¦¦Sep-18-2020 11:50
2020-09-18 11:51 | 44092.4937 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center 3 |  | 0 | 13.8 | 33 | 413 |  | 22 | 24.8 |  | 2020-09-18 11:51 | 44092.4937 |  | 22 | 24.8 |  | low | 2020-09-14 | B20603¦Prep center 3¦¦Sep-18-2020 11:50
2020-09-18 11:51 | 44092.4941 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 1 |  | 0 | 16.2 | 32.2 | 395 | 21.5 | 26.7 | 409 |  | 2020-09-18 11:51 | 44092.4941 | 21.5 | 26.7 | 409 |  | low | 2020-09-14 | Pearso¦Lobby 1¦¦Sep-18-2020 11:51
2020-09-18 11:52 | 44092.4941 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Crown staff office |  | 0 | 21 | 16 | 407 | 23 | 24 | 533 |  | 2020-09-18 11:52 | 44092.4941 | 23 | 24 | 533 |  | low | 2020-09-14 | B70235¦Crown staff office ¦¦Sep-18-2020 11:51
2020-09-18 11:52 | 44092.4942 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 rear left |  | 1 | 18 | 18 | 380 | 21 | 24 | 383 |  | 2020-09-18 11:52 | 44092.4942 | 21 | 24 | 383 |  | low | 2020-09-14 | B20772¦H15 rear left¦¦Sep-18-2020 11:51
2020-09-18 11:52 | 44092.4944 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom A |  | 0 | 16.7 | 25.3 | 406 | 22.6 | 27.1 | 423 | No | 2020-09-18 11:52 | 44092.4944 | 22.6 | 27.1 | 423 |  | low | 2020-09-14 | B20478¦Courtroom A¦¦Sep-18-2020 11:51
2020-09-18 11:52 | 44092.4944 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 590 |  | 2020-09-18 11:52 | 44092.4944 | 23 | 44 | 590 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 11:51
2020-09-18 11:52 | 44092.4946 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 waiting area |  | 0 | 12 | 37 | 392 | 21.6 | 30 | 532 | No | 2020-09-18 11:52 | 44092.4946 | 21.6 | 30 | 532 |  | low | 2020-09-14 | B20151¦Court room 2 waiting area ¦¦Sep-18-2020 11:52
2020-09-18 11:52 | 44092.4947 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 301b |  | 0 | 11 | 45 | 377 | 22.9 | 33.3 | 411 | No | 2020-09-18 11:52 | 44092.4947 | 22.9 | 33.3 | 411 |  | low | 2020-09-14 | B14660¦301b¦¦Sep-18-2020 11:52
2020-09-18 11:52 | 44092.4947 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center office 1 |  | 0 | 13.8 | 33 | 413 | 22.1 | 23.8 | 439 |  | 2020-09-18 11:52 | 44092.4947 | 22.1 | 23.8 | 439 |  | low | 2020-09-14 | B20603¦Prep center office 1¦¦Sep-18-2020 11:52
2020-09-18 11:52 | 44092.4948 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 waiting area |  | 1 | 18 | 18 | 380 | 21 | 26 | 378 |  | 2020-09-18 11:52 | 44092.4948 | 21 | 26 | 378 |  | low | 2020-09-14 | B20772¦H15 waiting area¦¦Sep-18-2020 11:52
2020-09-18 11:53 | 44092.4949 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 2 |  | 0 | 16.2 | 32.2 | 395 | 21.8 | 26.9 | 411 |  | 2020-09-18 11:53 | 44092.4949 | 21.8 | 26.9 | 411 |  | low | 2020-09-14 | Pearso¦Lobby 2¦¦Sep-18-2020 11:52
2020-09-18 11:53 | 44092.495 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 620 |  | 2020-09-18 11:53 | 44092.495 | 23 | 44 | 620 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 11:52
2020-09-18 11:53 | 44092.495 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Lower landing of stairway |  | 1 | 13.4 | 25.7 | 403 | 19.6 | 36 | 638 |  | 2020-09-18 11:53 | 44092.495 | 19.6 | 36 | 638 |  | caution | 2020-09-14 | B20474¦Lower landing of stairway¦¦Sep-18-2020 11:52
2020-09-18 11:53 | 44092.4952 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Justice Swartz office |  | 0 | 15 | 26.7 | 388 | 23.2 | 28.5 | 441 |  | 2020-09-18 11:53 | 44092.4952 | 23.2 | 28.5 | 441 |  | low | 2020-09-14 | B20550¦Justice Swartz office¦¦Sep-18-2020 11:53
2020-09-18 11:53 | 44092.4952 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | rm14 JUDGE |  | 1 | 17.6 | 22 | 410 | 22 | 26 | 440 |  | 2020-09-18 11:53 | 44092.4952 | 22 | 26 | 440 |  | low | 2020-09-14 | B70740¦rm14 JUDGE¦¦Sep-18-2020 11:53
2020-09-18 11:53 | 44092.4953 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Common area beside courtroom A |  | 0 | 16.7 | 25.3 | 406 | 22.3 | 30.3 | 432 | No | 2020-09-18 11:53 | 44092.4953 | 22.3 | 30.3 | 432 |  | low | 2020-09-14 | B20478¦Common area beside courtroom A¦¦Sep-18-2020 11:53
2020-09-18 11:54 | 44092.4956 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center office 610 |  | 0 | 13.8 | 22.9 | 438 | 22.2 | 22.9 | 428 |  | 2020-09-18 11:54 | 44092.4956 | 22.2 | 22.9 | 428 |  | low | 2020-09-14 | B20603¦Prep center office 610¦¦Sep-18-2020 11:53
2020-09-18 11:54 | 44092.4956 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 14 |  | 0 | 17.6 | 22 | 410 | 22 | 26 | 440 |  | 2020-09-18 11:54 | 44092.4956 | 22 | 26 | 440 |  | low | 2020-09-14 | B70740¦14¦¦Sep-18-2020 11:53
2020-09-18 11:54 | 44092.4958 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 605 |  | 2020-09-18 11:54 | 44092.4958 | 23 | 44 | 605 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 11:53
2020-09-18 11:54 | 44092.4959 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 3 |  | 0 | 16.2 | 32.2 | 395 | 22.2 | 26.2 | 408 |  | 2020-09-18 11:54 | 44092.4959 | 22.2 | 26.2 | 408 |  | low | 2020-09-14 | Pearso¦Lobby 3¦¦Sep-18-2020 11:54
2020-09-18 11:54 | 44092.4962 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | SEATING 14 |  | 0 | 17.6 | 22 | 410 | 21.7 | 26 | 430 |  | 2020-09-18 11:54 | 44092.4962 | 21.7 | 26 | 430 |  | low | 2020-09-14 | B70740¦SEATING 14¦¦Sep-18-2020 11:54
2020-09-18 11:55 | 44092.4962 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Law Library |  | 0 | 16.7 | 25.3 | 406 | 22.8 | 31.8 | 420 | No | 2020-09-18 11:55 | 44092.4962 | 22.8 | 31.8 | 420 |  | low | 2020-09-14 | B20478¦Law Library¦¦Sep-18-2020 11:54
2020-09-18 11:55 | 44092.4964 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Office |  | 1 | 16.2 | 32.2 | 395 | 22 | 26.2 | 410 |  | 2020-09-18 11:55 | 44092.4964 | 22 | 26.2 | 410 |  | low | 2020-09-14 | Pearso¦Office¦¦Sep-18-2020 11:54
2020-09-18 11:55 | 44092.4964 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 301a |  | 0 | 11 | 45 | 377 | 23.3 | 31.1 | 406 | No | 2020-09-18 11:55 | 44092.4964 | 23.3 | 31.1 | 406 |  | low | 2020-09-14 | B14660¦301a¦¦Sep-18-2020 11:54
2020-09-18 11:55 | 44092.4964 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 14 | 38 | 430 | 23 | 45 | 620 |  | 2020-09-18 11:55 | 44092.4964 | 23 | 45 | 620 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 11:54
2020-09-18 11:55 | 44092.4965 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Front desk |  | 2 | 13.4 | 25.7 | 403 | 19.7 | 36.8 | 642 |  | 2020-09-18 11:55 | 44092.4965 | 19.7 | 36.8 | 642 |  | caution | 2020-09-14 | B20474¦Front desk¦¦Sep-18-2020 11:54
2020-09-18 11:55 | 44092.4965 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center office 618 |  | 0 | 13.8 | 33 | 413 | 22.2 | 24.2 | 425 |  | 2020-09-18 11:55 | 44092.4965 | 22.2 | 24.2 | 425 |  | low | 2020-09-14 | B20603¦Prep center office 618¦¦Sep-18-2020 11:54
2020-09-18 11:55 | 44092.4967 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Waiting area small |  | 0 | 15 | 26.7 | 388 | 23.6 | 23.7 | 439 |  | 2020-09-18 11:55 | 44092.4967 | 23.6 | 23.7 | 439 |  | low | 2020-09-14 | B20550¦Waiting area small¦¦Sep-18-2020 11:55
2020-09-18 11:55 | 44092.4967 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | FRONT HRPS |  | 0 | 17.6 | 22 | 410 | 22 | 26 | 430 |  | 2020-09-18 11:55 | 44092.4967 | 22 | 26 | 430 |  | low | 2020-09-14 | B70740¦FRONT HRPS¦¦Sep-18-2020 11:55
2020-09-18 11:56 | 44092.4971 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | east stairwell |  | 0 | 16.7 | 25.3 | 406 | 23.8 | 28.1 | 543 | No | 2020-09-18 11:56 | 44092.4971 | 23.8 | 28.1 | 543 |  | low | 2020-09-14 | B20478¦east stairwell¦¦Sep-18-2020 11:55
2020-09-18 11:56 | 44092.4971 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-W wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 620 |  | 2020-09-18 11:56 | 44092.4971 | 23 | 44 | 620 |  |  | 2020-09-14 | B25548¦2-W wall¦¦Sep-18-2020 11:55
2020-09-18 11:56 | 44092.4973 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 301a |  | 0 | 11 | 45 | 377 | 23.3 | 31.1 | 406 | No | 2020-09-18 11:56 | 44092.4973 | 23.3 | 31.1 | 406 |  | low | 2020-09-14 | B14660¦301a¦¦Sep-18-2020 11:56
2020-09-18 11:56 | 44092.4973 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN WR CORR |  | 0 | 17.6 | 22 | 410 | 22.3 | 26 | 440 |  | 2020-09-18 11:56 | 44092.4973 | 22.3 | 26 | 440 |  | low | 2020-09-14 | B70740¦MAIN WR CORR¦¦Sep-18-2020 11:56
2020-09-18 11:57 | 44092.4977 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Peterborough police |  | 3 | 21 | 16 | 407 | 23 | 25 | 552 |  | 2020-09-18 11:57 | 44092.4977 | 23 | 25 | 552 |  | low | 2020-09-14 | B70235¦Peterborough police ¦¦Sep-18-2020 11:56
2020-09-18 11:57 | 44092.4978 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | Crown Attorney |  | 0 | 11 | 45 | 377 | 23.1 | 30.7 | 409 | No | 2020-09-18 11:57 | 44092.4978 | 23.1 | 30.7 | 409 |  | low | 2020-09-14 | B14660¦Crown Attorney¦¦Sep-18-2020 11:56
2020-09-18 11:57 | 44092.4979 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 13 |  | 0 | 17.6 | 22 | 410 | 22.6 | 29 | 465 |  | 2020-09-18 11:57 | 44092.4979 | 22.6 | 29 | 465 |  | low | 2020-09-14 | B70740¦13¦¦Sep-18-2020 11:56
2020-09-18 11:57 | 44092.4979 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-W wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 620 |  | 2020-09-18 11:57 | 44092.4979 | 23 | 44 | 620 |  |  | 2020-09-14 | B25548¦2-W wall¦¦Sep-18-2020 11:56
2020-09-18 11:57 | 44092.4979 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Trial office |  | 2 | 13.4 | 25.7 | 403 | 20.1 | 35.2 | 585 |  | 2020-09-18 11:57 | 44092.4979 | 20.1 | 35.2 | 585 |  | caution | 2020-09-14 | B20474¦Trial office¦¦Sep-18-2020 11:57
2020-09-18 11:57 | 44092.498 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Waiting area big |  | 0 | 15 | 26.7 | 388 | 23.7 | 24.9 | 429 |  | 2020-09-18 11:57 | 44092.498 | 23.7 | 24.9 | 429 |  | low | 2020-09-14 | B20550¦Waiting area big¦¦Sep-18-2020 11:57
2020-09-18 11:57 | 44092.498 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 647 |  | 0 | 13.8 | 24 | 424 | 22.3 | 24.2 | 424 |  | 2020-09-18 11:57 | 44092.498 | 22.3 | 24.2 | 424 |  | low | 2020-09-14 | B20603¦Office 647¦¦Sep-18-2020 11:57
2020-09-18 11:57 | 44092.4981 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Cell block |  | 2 | 9 | 51 | 392 | 22.8 | 39.3 | 516 |  | 2020-09-18 11:57 | 44092.4981 | 22.8 | 39.3 | 516 |  | caution | 2020-09-14 | B20494¦Cell block¦¦Sep-18-2020 11:57
2020-09-18 11:57 | 44092.4982 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Main floor common area |  | 2 | 16.7 | 25.3 | 406 | 23.7 | 31.9 | 493 | No | 2020-09-18 11:57 | 44092.4982 | 23.7 | 31.9 | 493 |  | low | 2020-09-14 | B20478¦Main floor common area¦¦Sep-18-2020 11:57
2020-09-18 11:57 | 44092.4982 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview Room 4 |  | 0 | 21 | 16 | 407 | 22 | 24 | 520 |  | 2020-09-18 11:57 | 44092.4982 | 22 | 24 | 520 |  | low | 2020-09-14 | B70235¦Interview Room 4¦¦Sep-18-2020 11:57
2020-09-18 11:57 | 44092.4982 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 rear right |  | 1 | 18 | 18 | 380 | 22 | 22 | 371 |  | 2020-09-18 11:57 | 44092.4982 | 22 | 22 | 371 |  | low | 2020-09-14 | B20772¦H12 rear right ¦¦Sep-18-2020 11:57
2020-09-18 11:58 | 44092.4984 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-W wall |  | 0 | 14 | 38 | 430 | 23 | 45 | 620 |  | 2020-09-18 11:58 | 44092.4984 | 23 | 45 | 620 |  |  | 2020-09-14 | B25548¦2-W wall¦¦Sep-18-2020 11:57
2020-09-18 11:58 | 44092.4985 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | SEATIN 13 |  | 2 | 17.6 | 22 | 410 | 23.4 | 25 | 490 |  | 2020-09-18 11:58 | 44092.4985 | 23.4 | 25 | 490 |  | low | 2020-09-14 | B70740¦SEATIN 13¦¦Sep-18-2020 11:57
2020-09-18 11:58 | 44092.4989 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 1 gallery |  | 2 | 12 | 37 | 392 | 21.7 | 23.1 | 459 | No | 2020-09-18 11:58 | 44092.4989 | 21.7 | 23.1 | 459 |  | low | 2020-09-14 | B20151¦Court room 1 gallery ¦¦Sep-18-2020 11:58
2020-09-18 11:58 | 44092.4989 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 rear left |  | 1 | 18 | 18 | 380 | 22 | 23 | 368 |  | 2020-09-18 11:58 | 44092.4989 | 22 | 23 | 368 |  | low | 2020-09-14 | B20772¦H12 rear left ¦¦Sep-18-2020 11:58
2020-09-18 11:59 | 44092.499 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 2 |  | 0 | 13.8 | 33 | 413 | 22.4 | 23 | 430 |  | 2020-09-18 11:59 | 44092.499 | 22.4 | 23 | 430 |  | low | 2020-09-14 | B20603¦Office 2¦¦Sep-18-2020 11:58
2020-09-18 11:59 | 44092.499 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 12 |  | 0 | 17.6 | 22 | 410 | 23.5 | 29 | 630 |  | 2020-09-18 11:59 | 44092.499 | 23.5 | 29 | 630 |  | low | 2020-09-14 | B70740¦12¦¦Sep-18-2020 11:58
2020-09-18 11:59 | 44092.4991 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 judge |  | 0 | 21 | 16 | 407 | 22 | 22 | 421 |  | 2020-09-18 11:59 | 44092.4991 | 22 | 22 | 421 |  | low | 2020-09-14 | B70235¦Court #4 judge ¦¦Sep-18-2020 11:58
2020-09-18 11:59 | 44092.4991 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Corridor at admin offices |  | 0 | 16.7 | 25.3 | 406 | 24.1 | 31.1 | 492 | No | 2020-09-18 11:59 | 44092.4991 | 24.1 | 31.1 | 492 |  | low | 2020-09-14 | B20478¦Corridor at admin offices¦¦Sep-18-2020 11:58
2020-09-18 11:59 | 44092.4992 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 14 | 38 | 430 | 23 | 46 | 670 |  | 2020-09-18 11:59 | 44092.4992 | 23 | 46 | 670 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 11:58
2020-09-18 11:59 | 44092.4995 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Security desk |  | 0 | 15 | 26.7 | 388 | 23.6 | 26.1 | 442 |  | 2020-09-18 11:59 | 44092.4995 | 23.6 | 26.1 | 442 |  | low | 2020-09-14 | B20550¦Security desk¦¦Sep-18-2020 11:59
2020-09-18 11:59 | 44092.4995 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | SEATING 12 |  | 4 | 17.6 | 22 | 410 | 23 | 25 | 550 |  | 2020-09-18 11:59 | 44092.4995 | 23 | 25 | 550 |  | low | 2020-09-14 | B70740¦SEATING 12¦¦Sep-18-2020 11:59
2020-09-18 11:59 | 44092.4996 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 defendant |  | 1 | 18 | 18 | 380 | 22 | 22 | 368 |  | 2020-09-18 11:59 | 44092.4996 | 22 | 22 | 368 |  | low | 2020-09-14 | B20772¦H12 defendant¦¦Sep-18-2020 11:59
2020-09-18 12:00 | 44092.4997 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 306 |  | 0 | 11 | 45 | 377 | 22.8 | 30.9 | 404 | No | 2020-09-18 12:00 | 44092.4997 | 22.8 | 30.9 | 404 |  | low | 2020-09-14 | B14660¦306¦¦Sep-18-2020 11:59
2020-09-18 12:00 | 44092.4998 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 lawyer |  | 0 | 21 | 16 | 407 | 22 | 22 | 427 |  | 2020-09-18 12:00 | 44092.4998 | 22 | 22 | 427 |  | low | 2020-09-14 | B70235¦Court #4 lawyer ¦¦Sep-18-2020 11:59
2020-09-18 12:00 | 44092.4999 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 3 |  | 0 | 13.8 | 33 | 413 | 22.3 | 22.9 | 423 |  | 2020-09-18 12:00 | 44092.4999 | 22.3 | 22.9 | 423 |  | low | 2020-09-14 | B20603¦Office 3¦¦Sep-18-2020 11:59
2020-09-18 12:00 | 44092.5 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | 2nd floor common area |  | 0 | 16.7 | 25.3 | 406 | 23.5 | 33.6 | 513 | No | 2020-09-18 12:00 | 44092.5 | 23.5 | 33.6 | 513 |  | low | 2020-09-14 | B20478¦2nd floor common area¦¦Sep-18-2020 11:59
2020-09-18 12:00 | 44092.5 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Main floor at stairway |  | 1 | 13.4 | 25.7 | 403 | 20 | 35.8 | 633 |  | 2020-09-18 12:00 | 44092.5 | 20 | 35.8 | 633 |  | caution | 2020-09-14 | B20474¦Main floor at stairway¦¦Sep-18-2020 12:00
2020-09-18 12:00 | 44092.5001 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 620 |  | 2020-09-18 12:00 | 44092.5001 | 23 | 44 | 620 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 12:00
2020-09-18 12:01 | 44092.5004 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | POLICE WAIING RM |  | 0 | 17.6 | 22 | 410 | 22.7 | 27 | 530 |  | 2020-09-18 12:01 | 44092.5004 | 22.7 | 27 | 530 |  | low | 2020-09-14 | B70740¦POLICE WAIING RM¦¦Sep-18-2020 12:00
2020-09-18 12:01 | 44092.5006 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Administrative office |  | 2 | 15 | 26.7 | 388 | 23.7 | 24.4 | 445 |  | 2020-09-18 12:01 | 44092.5006 | 23.7 | 24.4 | 445 |  | low | 2020-09-14 | B20550¦Administrative office¦¦Sep-18-2020 12:00
2020-09-18 12:01 | 44092.5007 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 4 |  | 0 | 13.8 | 33 | 413 | 22.2 | 23.4 | 423 |  | 2020-09-18 12:01 | 44092.5007 | 22.2 | 23.4 | 423 |  | low | 2020-09-14 | B20603¦Office 4 ¦¦Sep-18-2020 12:01
2020-09-18 12:01 | 44092.5009 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 11 |  | 2 | 17.6 | 22 | 410 | 22.7 | 31 | 530 |  | 2020-09-18 12:01 | 44092.5009 | 22.7 | 31 | 530 |  | low | 2020-09-14 | B70740¦11¦¦Sep-18-2020 12:01
2020-09-18 12:01 | 44092.5009 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 605 |  | 2020-09-18 12:01 | 44092.5009 | 23 | 44 | 605 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 12:01
2020-09-18 12:01 | 44092.501 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 vestibule |  | 0 | 21 | 16 | 407 | 22 | 24 | 474 |  | 2020-09-18 12:01 | 44092.501 | 22 | 24 | 474 |  | low | 2020-09-14 | B70235¦Court #4 vestibule ¦¦Sep-18-2020 12:01
2020-09-18 12:02 | 44092.5013 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | 2nd floor crown attorney corridor |  | 0 | 16.7 | 25.3 | 406 | 23.2 | 31.6 | 434 | No | 2020-09-18 12:02 | 44092.5013 | 23.2 | 31.6 | 434 |  | low | 2020-09-14 | B20478¦2nd floor crown attorney corridor¦¦Sep-18-2020 12:01
2020-09-18 12:02 | 44092.5016 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN AREA |  | 3 | 17.6 | 22 | 410 | 22.6 | 26 | 540 |  | 2020-09-18 12:02 | 44092.5016 | 22.6 | 26 | 540 |  | low | 2020-09-14 | B70740¦MAIN AREA¦¦Sep-18-2020 12:02
2020-09-18 12:02 | 44092.5016 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 5 |  | 0 | 13.8 | 33 | 413 | 22.2 | 22.7 | 426 |  | 2020-09-18 12:02 | 44092.5016 | 22.2 | 22.7 | 426 |  | low | 2020-09-14 | B20603¦Office 5¦¦Sep-18-2020 12:02
2020-09-18 12:03 | 44092.502 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN OFFICE |  | 3 | 17.6 | 22 | 410 | 22.7 | 29 | 540 |  | 2020-09-18 12:03 | 44092.502 | 22.7 | 29 | 540 |  | low | 2020-09-14 | B70740¦MAIN OFFICE¦¦Sep-18-2020 12:02
2020-09-18 12:03 | 44092.5021 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Judicial office corridor |  | 0 | 16.7 | 25.3 | 406 | 23.1 | 31.8 | 446 | No | 2020-09-18 12:03 | 44092.5021 | 23.1 | 31.8 | 446 |  | low | 2020-09-14 | B20478¦Judicial office corridor¦¦Sep-18-2020 12:03
2020-09-18 12:03 | 44092.5023 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 vestibule |  | 0 | 21 | 16 | 407 | 22 | 25 | 478 |  | 2020-09-18 12:03 | 44092.5023 | 22 | 25 | 478 |  | low | 2020-09-14 | B70235¦Court #4 vestibule ¦¦Sep-18-2020 12:03
2020-09-18 12:04 | 44092.5024 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin Office |  | 4 | 12 | 37 | 392 | 22.5 | 29.2 | 603 | No | 2020-09-18 12:04 | 44092.5024 | 22.5 | 29.2 | 603 |  | low | 2020-09-14 | B20151¦Admin Office ¦¦Sep-18-2020 12:03
2020-09-18 12:04 | 44092.5026 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 605 |  | 2020-09-18 12:04 | 44092.5026 | 23 | 44 | 605 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 12:03
2020-09-18 12:04 | 44092.5027 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | JUSTICE BALDWIN |  | 1 | 17.6 | 22 | 410 | 21.9 | 31 | 530 |  | 2020-09-18 12:04 | 44092.5027 | 21.9 | 31 | 530 |  | low | 2020-09-14 | B70740¦JUSTICE BALDWIN¦¦Sep-18-2020 12:03
2020-09-18 12:04 | 44092.5031 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Basement witness protection corridor |  | 0 | 16.7 | 25.3 | 406 | 22.6 | 27.5 | 440 | No | 2020-09-18 12:04 | 44092.5031 | 22.6 | 27.5 | 440 |  | low | 2020-09-14 | B20478¦Basement witness protection corridor¦¦Sep-18-2020 12:04
2020-09-18 12:05 | 44092.5032 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | entryway |  | 2 | 14.6 | 41.2 | 380 | 17.5 | 45.2 | 479 |  | 2020-09-18 12:05 | 44092.5032 | 17.5 | 45.2 | 479 |  |  | 2020-09-14 | B20390¦entryway¦¦Sep-18-2020 12:04
2020-09-18 12:05 | 44092.5033 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview room 3 |  | 0 | 21 | 16 | 407 | 22 | 25 | 506 |  | 2020-09-18 12:05 | 44092.5033 | 22 | 25 | 506 |  | low | 2020-09-14 | B70235¦Interview room 3¦¦Sep-18-2020 12:04
2020-09-18 12:05 | 44092.5033 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | JUSTICE BROWN |  | 1 | 17.6 | 22 | 410 | 22.5 | 30 | 530 |  | 2020-09-18 12:05 | 44092.5033 | 22.5 | 30 | 530 |  | low | 2020-09-14 | B70740¦JUSTICE BROWN¦¦Sep-18-2020 12:04
2020-09-18 12:05 | 44092.5033 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 14 | 38 | 430 | 23 | 45 | 605 |  | 2020-09-18 12:05 | 44092.5033 | 23 | 45 | 605 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 12:04
2020-09-18 12:06 | 44092.5038 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Basement corridor middle |  | 0 | 16.7 | 25.3 | 406 | 22.1 | 32.3 | 459 | No | 2020-09-18 12:06 | 44092.5038 | 22.1 | 32.3 | 459 |  | low | 2020-09-14 | B20478¦Basement corridor middle¦¦Sep-18-2020 12:05
2020-09-18 12:06 | 44092.5039 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 judge |  | 1 | 18 | 18 | 380 | 22 | 22 | 377 |  | 2020-09-18 12:06 | 44092.5039 | 22 | 22 | 377 |  | low | 2020-09-14 | B20772¦H12 judge ¦¦Sep-18-2020 12:05
2020-09-18 12:06 | 44092.5041 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 West |  | 0 | 14.4 | 45 | 400 | 21 | 36.9 | 447 |  | 2020-09-18 12:06 | 44092.5041 | 21 | 36.9 | 447 |  | caution | 2020-09-14 | B10577¦Courtroom 3 West ¦¦Sep-18-2020 12:05
2020-09-18 12:06 | 44092.5043 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 600 |  | 2020-09-18 12:06 | 44092.5043 | 23 | 44 | 600 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 12:06
2020-09-18 12:06 | 44092.5044 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 626 |  | 0 | 13.8 | 33 | 413 | 22.3 | 22.7 | 439 |  | 2020-09-18 12:06 | 44092.5044 | 22.3 | 22.7 | 439 |  | low | 2020-09-14 | B20603¦Office 626¦¦Sep-18-2020 12:06
2020-09-18 12:06 | 44092.5045 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview Room 2 |  | 0 | 21 | 16 | 407 | 22 | 25 | 515 |  | 2020-09-18 12:06 | 44092.5045 | 22 | 25 | 515 |  | low | 2020-09-14 | B70235¦Interview Room 2¦¦Sep-18-2020 12:06
2020-09-18 12:07 | 44092.5048 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin supervisor room |  | 1 | 12 | 37 | 392 | 22.3 | 32.4 | 662 | No | 2020-09-18 12:07 | 44092.5048 | 22.3 | 32.4 | 662 |  | low | 2020-09-14 | B20151¦Admin supervisor room ¦¦Sep-18-2020 12:06
2020-09-18 12:07 | 44092.5048 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | basement corridor prisoner holding cell |  | 0 | 16.7 | 25.3 | 406 | 21.7 | 42.8 | 478 | No | 2020-09-18 12:07 | 44092.5048 | 21.7 | 42.8 | 478 |  |  | 2020-09-14 | B20478¦basement corridor prisoner holding cell¦¦Sep-18-2020 12:06
2020-09-18 12:07 | 44092.505 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | First floor waiting area |  | 4 | 14.6 | 41.2 | 380 | 19.3 | 42.8 | 434 |  | 2020-09-18 12:07 | 44092.505 | 19.3 | 42.8 | 434 |  |  | 2020-09-14 | B20390¦First floor waiting area¦¦Sep-18-2020 12:07
2020-09-18 12:07 | 44092.5051 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Front lobby |  | 5 | 23 | 20 | 407 | 22 | 23 | 480 |  | 2020-09-18 12:07 | 44092.5051 | 22 | 23 | 480 |  | low | 2020-09-14 | B19570¦Front lobby ¦¦Sep-18-2020 12:07
2020-09-18 12:07 | 44092.5052 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-E wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 630 |  | 2020-09-18 12:07 | 44092.5052 | 23 | 44 | 630 |  |  | 2020-09-14 | B25548¦2-E wall¦¦Sep-18-2020 12:07
2020-09-18 12:08 | 44092.5053 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 judge |  | 0 | 21 | 16 | 407 | 23 | 23 | 497 |  | 2020-09-18 12:08 | 44092.5053 | 23 | 23 | 497 |  | low | 2020-09-14 | B70235¦Court #2 judge ¦¦Sep-18-2020 12:07
2020-09-18 12:08 | 44092.5057 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 10 |  | 0 | 13.8 | 33 | 413 | 22 | 22.3 | 430 |  | 2020-09-18 12:08 | 44092.5057 | 22 | 22.3 | 430 |  | low | 2020-09-14 | B20603¦Office 10¦¦Sep-18-2020 12:08
2020-09-18 12:08 | 44092.5058 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 2 |  | 2 | 14.6 | 41.2 | 380 | 19.9 | 42.8 | 443 |  | 2020-09-18 12:08 | 44092.5058 | 19.9 | 42.8 | 443 |  |  | 2020-09-14 | B20390¦Outside courtroom 2¦¦Sep-18-2020 12:08
2020-09-18 12:09 | 44092.506 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-E wall |  | 0 | 14 | 38 | 430 | 23 | 44 | 610 |  | 2020-09-18 12:09 | 44092.506 | 23 | 44 | 610 |  |  | 2020-09-14 | B25548¦2-E wall¦¦Sep-18-2020 12:08
2020-09-18 12:09 | 44092.5061 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 lawyer |  | 0 | 21 | 16 | 407 | 23 | 23 | 489 |  | 2020-09-18 12:09 | 44092.5061 | 23 | 23 | 489 |  | low | 2020-09-14 | B70235¦Court #2 lawyer ¦¦Sep-18-2020 12:08
2020-09-18 12:09 | 44092.5061 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Administration office east |  | 1 | 17 | 32 | 421 | 22 | 34 | 588 |  | 2020-09-18 12:09 | 44092.5061 | 22 | 34 | 588 |  | low | 2020-09-14 | B25479¦Administration office east ¦¦Sep-18-2020 12:08
2020-09-18 12:09 | 44092.5065 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Security area |  | 2 | 15 | 27.2 | 390 | 17.3 | 39.2 | 492 |  | 2020-09-18 12:09 | 44092.5065 | 17.3 | 39.2 | 492 |  | caution | 2020-09-14 | B17477¦Security area¦¦Sep-18-2020 12:09
2020-09-18 12:10 | 44092.5066 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 3 |  | 2 | 14.6 | 41.2 | 380 | 20.2 | 41 | 439 |  | 2020-09-18 12:10 | 44092.5066 | 20.2 | 41 | 439 |  |  | 2020-09-14 | B20390¦Outside courtroom 3¦¦Sep-18-2020 12:09
2020-09-18 12:10 | 44092.5067 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Administration office west |  | 1 | 17 | 32 | 421 | 23 | 36 | 603 |  | 2020-09-18 12:10 | 44092.5067 | 23 | 36 | 603 |  | caution | 2020-09-14 | B25479¦Administration office west ¦¦Sep-18-2020 12:09
2020-09-18 12:10 | 44092.5069 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 vestibule |  | 0 | 21 | 16 | 407 | 23 | 23 | 511 |  | 2020-09-18 12:10 | 44092.5069 | 23 | 23 | 511 |  | low | 2020-09-14 | B70235¦Court #2 vestibule ¦¦Sep-18-2020 12:09
2020-09-18 12:10 | 44092.507 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin file room |  | 3 | 12 | 37 | 392 | 22.5 | 31.2 | 638 | No | 2020-09-18 12:10 | 44092.507 | 22.5 | 31.2 | 638 |  | low | 2020-09-14 | B20151¦Admin file room ¦¦Sep-18-2020 12:10
2020-09-18 12:10 | 44092.5071 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-E wall |  | 0 | 14 | 38 | 430 | 23 | 43 | 610 |  | 2020-09-18 12:10 | 44092.5071 | 23 | 43 | 610 |  |  | 2020-09-14 | B25548¦2-E wall¦¦Sep-18-2020 12:10
2020-09-18 12:11 | 44092.5074 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL3 waiting area N |  | 0 | 15 | 27.2 | 390 | 18.9 | 35.3 | 475 |  | 2020-09-18 12:11 | 44092.5074 | 18.9 | 35.3 | 475 |  | caution | 2020-09-14 | B17477¦LVL3 waiting area N¦¦Sep-18-2020 12:10
2020-09-18 12:11 | 44092.5074 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space |  | 0 | 13.8 | 33 | 413 | 21.6 | 23.2 | 430 |  | 2020-09-18 12:11 | 44092.5074 | 21.6 | 23.2 | 430 |  | low | 2020-09-14 | B20603¦Office space ¦¦Sep-18-2020 12:10
2020-09-18 12:11 | 44092.5076 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Supervisors office |  | 1 | 17 | 32 | 421 | 23 | 31 | 612 |  | 2020-09-18 12:11 | 44092.5076 | 23 | 31 | 612 |  | low | 2020-09-14 | B25479¦Supervisors office ¦¦Sep-18-2020 12:11
2020-09-18 12:11 | 44092.508 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | First floor vending machines |  | 1 | 14.6 | 41.2 | 380 | 21.2 | 42.2 | 435 |  | 2020-09-18 12:11 | 44092.508 | 21.2 | 42.2 | 435 |  |  | 2020-09-14 | B20390¦First floor vending machines¦¦Sep-18-2020 12:11
2020-09-18 12:11 | 44092.508 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Intake office |  | 0 | 17 | 32 | 421 | 23 | 32 | 560 |  | 2020-09-18 12:11 | 44092.508 | 23 | 32 | 560 |  | low | 2020-09-14 | B25479¦Intake office ¦¦Sep-18-2020 12:11
2020-09-18 12:12 | 44092.508 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Duty Counsel room |  | 0 | 21 | 16 | 407 | 23 | 24 | 530 |  | 2020-09-18 12:12 | 44092.508 | 23 | 24 | 530 |  | low | 2020-09-14 | B70235¦Duty Counsel room ¦¦Sep-18-2020 12:11
2020-09-18 12:12 | 44092.5081 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL3 waiting area S |  | 0 | 15 | 27.2 | 390 | 20 | 31.4 | 444 |  | 2020-09-18 12:12 | 44092.5081 | 20 | 31.4 | 444 |  | low | 2020-09-14 | B17477¦LVL3 waiting area S¦¦Sep-18-2020 12:11
2020-09-18 12:12 | 44092.5082 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | Mediation room |  | 0 | 14 | 38 | 430 | 23 | 43 | 585 |  | 2020-09-18 12:12 | 44092.5082 | 23 | 43 | 585 |  |  | 2020-09-14 | B25548¦Mediation room¦¦Sep-18-2020 12:11
2020-09-18 12:12 | 44092.5083 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space 2 |  | 0 | 13.8 | 33 | 413 | 21.6 | 24 | 433 |  | 2020-09-18 12:12 | 44092.5083 | 21.6 | 24 | 433 |  | low | 2020-09-14 | B20603¦Office space 2 ¦¦Sep-18-2020 12:11
2020-09-18 12:12 | 44092.5083 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Poa office |  | 5 | 21 | 20 | 407 | 22 | 30 | 515 |  | 2020-09-18 12:12 | 44092.5083 | 22 | 30 | 515 |  | low | 2020-09-14 | B19570¦Poa office¦¦Sep-18-2020 12:11
2020-09-18 12:12 | 44092.5086 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Lunchroom |  | 1 | 17 | 32 | 421 | 23 | 32 | 600 |  | 2020-09-18 12:12 | 44092.5086 | 23 | 32 | 600 |  | low | 2020-09-14 | B25479¦Lunchroom ¦¦Sep-18-2020 12:12
2020-09-18 12:13 | 44092.5088 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 5 |  | 2 | 23 | 20 | 407 | 22 | 27 | 466 |  | 2020-09-18 12:13 | 44092.5088 | 22 | 27 | 466 |  | low | 2020-09-14 | B19570¦Court 5¦¦Sep-18-2020 12:12
2020-09-18 12:13 | 44092.5089 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell, first floor |  | 1 | 14.6 | 41.2 | 380 | 21.5 | 40.3 | 417 |  | 2020-09-18 12:13 | 44092.5089 | 21.5 | 40.3 | 417 |  |  | 2020-09-14 | B20390¦Main stairwell, first floor¦¦Sep-18-2020 12:12
2020-09-18 12:13 | 44092.5091 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space 3 |  | 0 | 13.8 | 33 | 413 | 21.6 | 23.3 | 437 |  | 2020-09-18 12:13 | 44092.5091 | 21.6 | 23.3 | 437 |  | low | 2020-09-14 | B20603¦Office space 3 ¦¦Sep-18-2020 12:13
2020-09-18 12:13 | 44092.5091 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Court room 300 waiting area |  | 0 | 15 | 27.2 | 390 | 21.1 | 27.7 | 419 |  | 2020-09-18 12:13 | 44092.5091 | 21.1 | 27.7 | 419 |  | low | 2020-09-14 | B17477¦Court room 300 waiting area¦¦Sep-18-2020 12:13
2020-09-18 12:13 | 44092.5092 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 judge |  | 1 | 21 | 16 | 407 | 23 | 21 | 561 |  | 2020-09-18 12:13 | 44092.5092 | 23 | 21 | 561 |  | low | 2020-09-14 | B70235¦Court #1 judge ¦¦Sep-18-2020 12:13
2020-09-18 12:13 | 44092.5093 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 3 |  | 4 | 17 | 32 | 421 | 23 | 29 | 587 |  | 2020-09-18 12:13 | 44092.5093 | 23 | 29 | 587 |  | low | 2020-09-14 | B25479¦Courtroom 3¦¦Sep-18-2020 12:13
2020-09-18 12:14 | 44092.5096 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 4 |  | 2 | 23 | 20 | 407 | 21 | 29 | 430 |  | 2020-09-18 12:14 | 44092.5096 | 21 | 29 | 430 |  | low | 2020-09-14 | B19570¦Court 4¦¦Sep-18-2020 12:13
2020-09-18 12:14 | 44092.5098 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 2 |  | 3 | 17 | 32 | 421 | 22 | 26 | 575 |  | 2020-09-18 12:14 | 44092.5098 | 22 | 26 | 575 |  | low | 2020-09-14 | B25479¦Courtroom 2¦¦Sep-18-2020 12:14
2020-09-18 12:14 | 44092.5098 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell, second floor |  | 1 | 14.6 | 41.2 | 380 | 21.6 | 40.1 | 410 |  | 2020-09-18 12:14 | 44092.5098 | 21.6 | 40.1 | 410 |  |  | 2020-09-14 | B20390¦Main stairwell, second floor¦¦Sep-18-2020 12:14
2020-09-18 12:14 | 44092.51 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 3 |  | 2 | 23 | 20 | 407 | 21 | 29 | 429 |  | 2020-09-18 12:14 | 44092.51 | 21 | 29 | 429 |  | low | 2020-09-14 | B19570¦Court 3¦¦Sep-18-2020 12:14
2020-09-18 12:15 | 44092.5101 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space 4 |  | 0 | 13.8 | 33 | 413 | 21.7 | 23.1 | 435 |  | 2020-09-18 12:15 | 44092.5101 | 21.7 | 23.1 | 435 |  | low | 2020-09-14 | B20603¦Office space 4 ¦¦Sep-18-2020 12:14
2020-09-18 12:15 | 44092.5103 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 lawyer |  | 1 | 21 | 16 | 407 | 23 | 21 | 568 |  | 2020-09-18 12:15 | 44092.5103 | 23 | 21 | 568 |  | low | 2020-09-14 | B70235¦Court #1 lawyer ¦¦Sep-18-2020 12:14
2020-09-18 12:15 | 44092.5103 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 1 |  | 0 | 17 | 32 | 421 | 22 | 25 | 558 |  | 2020-09-18 12:15 | 44092.5103 | 22 | 25 | 558 |  | low | 2020-09-14 | B25479¦Courtroom 1¦¦Sep-18-2020 12:14
2020-09-18 12:15 | 44092.5104 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 retiring room |  | 1 | 18 | 18 | 380 | 22 | 25 | 373 |  | 2020-09-18 12:15 | 44092.5104 | 22 | 25 | 373 |  | low | 2020-09-14 | B20772¦H12 retiring room ¦¦Sep-18-2020 12:14
2020-09-18 12:15 | 44092.5105 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 1 |  | 2 | 23 | 20 | 407 | 21 | 29 | 431 |  | 2020-09-18 12:15 | 44092.5105 | 21 | 29 | 431 |  | low | 2020-09-14 | B19570¦Court 1¦¦Sep-18-2020 12:15
2020-09-18 12:15 | 44092.5107 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Second floor waiting area |  | 3 | 14.6 | 41.2 | 380 | 22 | 35.3 | 398 |  | 2020-09-18 12:15 | 44092.5107 | 22 | 35.3 | 398 |  | caution | 2020-09-14 | B20390¦Second floor waiting area¦¦Sep-18-2020 12:15
2020-09-18 12:16 | 44092.5108 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Court room 300 W |  | 0 | 15 | 27.2 | 390 | 21.7 | 28.5 | 445 |  | 2020-09-18 12:16 | 44092.5108 | 21.7 | 28.5 | 445 |  | low | 2020-09-14 | B17477¦Court room 300 W¦¦Sep-18-2020 12:15
2020-09-18 12:16 | 44092.5109 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin waiting area |  | 1 | 12 | 37 | 392 | 22 | 24.8 | 489 | No | 2020-09-18 12:16 | 44092.5109 | 22 | 24.8 | 489 |  | low | 2020-09-14 | B20151¦Admin waiting area ¦¦Sep-18-2020 12:15
2020-09-18 12:16 | 44092.5109 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space 5 |  | 0 | 13.8 | 33 | 413 | 21.8 | 22.9 | 437 |  | 2020-09-18 12:16 | 44092.5109 | 21.8 | 22.9 | 437 |  | low | 2020-09-14 | B20603¦Office space 5 ¦¦Sep-18-2020 12:15
2020-09-18 12:16 | 44092.5111 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 2 |  | 2 | 23 | 20 | 407 | 21 | 25 | 433 |  | 2020-09-18 12:16 | 44092.5111 | 21 | 25 | 433 |  | low | 2020-09-14 | B19570¦Court 2¦¦Sep-18-2020 12:16
2020-09-18 12:16 | 44092.5112 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 4 |  | 0 | 17 | 32 | 421 | 22 | 23 | 545 |  | 2020-09-18 12:16 | 44092.5112 | 22 | 23 | 545 |  | low | 2020-09-14 | B25479¦Courtroom 4¦¦Sep-18-2020 12:16
2020-09-18 12:16 | 44092.5114 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 vestibule |  | 0 | 21 | 16 | 407 | 23 | 25 | 672 |  | 2020-09-18 12:16 | 44092.5114 | 23 | 25 | 672 |  | low | 2020-09-14 | B70235¦Court #1 vestibule ¦¦Sep-18-2020 12:16
2020-09-18 12:17 | 44092.5115 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Court room 300 E |  | 0 | 15 | 27.2 | 390 | 21.8 | 28.3 | 404 |  | 2020-09-18 12:17 | 44092.5115 | 21.8 | 28.3 | 404 |  | low | 2020-09-14 | B17477¦Court room 300 E¦¦Sep-18-2020 12:16
2020-09-18 12:17 | 44092.5116 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Law library hall s |  | 1 | 23 | 20 | 407 | 21 | 26 | 397 |  | 2020-09-18 12:17 | 44092.5116 | 21 | 26 | 397 |  | low | 2020-09-14 | B19570¦Law library hall s ¦¦Sep-18-2020 12:16
2020-09-18 12:17 | 44092.5116 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Jury room waiting area |  | 1 | 14.6 | 41.2 | 380 | 22.1 | 38.4 | 394 |  | 2020-09-18 12:17 | 44092.5116 | 22.1 | 38.4 | 394 |  | caution | 2020-09-14 | B20390¦Jury room waiting area¦¦Sep-18-2020 12:16
2020-09-18 12:17 | 44092.5117 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space 6 |  | 1 | 13.8 | 33 | 413 | 22.1 | 22.7 | 448 |  | 2020-09-18 12:17 | 44092.5117 | 22.1 | 22.7 | 448 |  | low | 2020-09-14 | B20603¦Office space 6 ¦¦Sep-18-2020 12:16
2020-09-18 12:17 | 44092.5119 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 5 |  | 5 | 17 | 32 | 421 | 22 | 27 | 536 |  | 2020-09-18 12:17 | 44092.5119 | 22 | 27 | 536 |  | low | 2020-09-14 | B25479¦Courtroom 5¦¦Sep-18-2020 12:17
2020-09-18 12:18 | 44092.5122 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Law library hall n |  | 1 | 23 | 20 | 407 | 22 | 25 | 414 |  | 2020-09-18 12:18 | 44092.5122 | 22 | 25 | 414 |  | low | 2020-09-14 | B19570¦Law library hall n ¦¦Sep-18-2020 12:17
2020-09-18 12:18 | 44092.5123 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Library |  | 0 | 17 | 32 | 421 | 22 | 31 | 547 |  | 2020-09-18 12:18 | 44092.5123 | 22 | 31 | 547 |  | low | 2020-09-14 | B25479¦Library ¦¦Sep-18-2020 12:17
2020-09-18 12:18 | 44092.5124 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Police Sergeant office |  | 0 | 21 | 16 | 407 | 23 | 24 | 591 |  | 2020-09-18 12:18 | 44092.5124 | 23 | 24 | 591 |  | low | 2020-09-14 | B70235¦Police Sergeant office ¦¦Sep-18-2020 12:17
2020-09-18 12:18 | 44092.5125 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside museum |  | 1 | 14.6 | 41.2 | 380 | 21.9 | 38.1 | 405 |  | 2020-09-18 12:18 | 44092.5125 | 21.9 | 38.1 | 405 |  | caution | 2020-09-14 | B20390¦Outside museum¦¦Sep-18-2020 12:17
2020-09-18 12:18 | 44092.5126 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | TC office |  | 1 | 17 | 32 | 421 | 23 | 30 | 553 |  | 2020-09-18 12:18 | 44092.5126 | 23 | 30 | 553 |  | low | 2020-09-14 | B25479¦TC office ¦¦Sep-18-2020 12:18
2020-09-18 12:18 | 44092.5126 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 259 |  | 1 | 23 | 20 | 407 | 22 | 23 | 412 |  | 2020-09-18 12:18 | 44092.5126 | 22 | 23 | 412 |  | low | 2020-09-14 | B19570¦259¦¦Sep-18-2020 12:18
2020-09-18 12:18 | 44092.5127 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Reception |  | 2 | 13.8 | 33 | 413 | 21.8 | 22.7 | 470 |  | 2020-09-18 12:18 | 44092.5127 | 21.8 | 22.7 | 470 |  | low | 2020-09-14 | B20603¦Reception ¦¦Sep-18-2020 12:18
2020-09-18 12:18 | 44092.5128 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Court services |  | 0 | 15 | 27.2 | 390 | 22.2 | 25.5 | 405 |  | 2020-09-18 12:18 | 44092.5128 | 22.2 | 25.5 | 405 |  | low | 2020-09-14 | B17477¦Court services¦¦Sep-18-2020 12:18
2020-09-18 12:19 | 44092.513 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 260 |  | 1 | 23 | 20 | 407 | 22 | 22 | 410 |  | 2020-09-18 12:19 | 44092.513 | 22 | 22 | 410 |  | low | 2020-09-14 | B19570¦260¦¦Sep-18-2020 12:18
2020-09-18 12:19 | 44092.5131 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | JP lobby |  | 0 | 17 | 32 | 421 | 23 | 29 | 554 |  | 2020-09-18 12:19 | 44092.5131 | 23 | 29 | 554 |  | low | 2020-09-14 | B25479¦JP lobby ¦¦Sep-18-2020 12:18
2020-09-18 12:19 | 44092.5134 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Reception 2 |  | 2 | 13.8 | 33 | 477 | 21.7 | 22.5 | 478 |  | 2020-09-18 12:19 | 44092.5134 | 21.7 | 22.5 | 478 |  | low | 2020-09-14 | B20603¦Reception 2¦¦Sep-18-2020 12:19
2020-09-18 12:19 | 44092.5135 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 261 |  | 1 | 23 | 20 | 407 | 22 | 22 | 413 |  | 2020-09-18 12:19 | 44092.5135 | 22 | 22 | 413 |  | low | 2020-09-14 | B19570¦261¦¦Sep-18-2020 12:19
2020-09-18 12:20 | 44092.5136 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 3 interview room |  | 0 | 15 | 27.2 | 390 | 22.3 | 24.6 | 405 |  | 2020-09-18 12:20 | 44092.5136 | 22.3 | 24.6 | 405 |  | low | 2020-09-14 | B17477¦LVL 3 interview room ¦¦Sep-18-2020 12:19
2020-09-18 12:20 | 44092.5136 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main lobby S |  | 2 | 21 | 16 | 407 | 23 | 24 | 562 |  | 2020-09-18 12:20 | 44092.5136 | 23 | 24 | 562 |  | low | 2020-09-14 | B70235¦Main lobby S¦¦Sep-18-2020 12:19
2020-09-18 12:20 | 44092.5138 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 265 |  | 1 | 23 | 20 | 407 | 22 | 22 | 408 |  | 2020-09-18 12:20 | 44092.5138 | 22 | 22 | 408 |  | low | 2020-09-14 | B19570¦265¦¦Sep-18-2020 12:19
2020-09-18 12:20 | 44092.5142 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 264 |  | 1 | 23 | 20 | 407 | 22 | 22 | 406 |  | 2020-09-18 12:20 | 44092.5142 | 22 | 22 | 406 |  | low | 2020-09-14 | B19570¦264¦¦Sep-18-2020 12:20
2020-09-18 12:21 | 44092.5144 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 2 waiting area |  | 0 | 15 | 27.2 | 390 | 22.2 | 25.3 | 409 |  | 2020-09-18 12:21 | 44092.5144 | 22.2 | 25.3 | 409 |  | low | 2020-09-14 | B17477¦LVL 2 waiting area¦¦Sep-18-2020 12:20
2020-09-18 12:21 | 44092.5145 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Reception seating |  | 0 | 13.8 | 33 | 468 | 21.8 | 22.9 | 472 |  | 2020-09-18 12:21 | 44092.5145 | 21.8 | 22.9 | 472 |  | low | 2020-09-14 | B20603¦Reception seating ¦¦Sep-18-2020 12:20
2020-09-18 12:21 | 44092.5146 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Hallway nw |  | 1 | 23 | 20 | 407 | 22 | 24 | 403 |  | 2020-09-18 12:21 | 44092.5146 | 22 | 24 | 403 |  | low | 2020-09-14 | B19570¦Hallway nw ¦¦Sep-18-2020 12:21
2020-09-18 12:21 | 44092.5149 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Main lobby south |  | 0 | 17 | 32 | 421 | 22 | 27 | 571 |  | 2020-09-18 12:21 | 44092.5149 | 22 | 27 | 571 |  | low | 2020-09-14 | B25479¦Main lobby south ¦¦Sep-18-2020 12:21
2020-09-18 12:22 | 44092.515 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main lobby C |  | 0 | 21 | 16 | 407 | 23 | 23 | 546 |  | 2020-09-18 12:22 | 44092.515 | 23 | 23 | 546 |  | low | 2020-09-14 | B70235¦Main lobby C ¦¦Sep-18-2020 12:21
2020-09-18 12:22 | 44092.515 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 5 top |  | 1 | 23 | 20 | 407 | 23 | 24 | 409 |  | 2020-09-18 12:22 | 44092.515 | 23 | 24 | 409 |  | low | 2020-09-14 | B19570¦Stairwell 5 top ¦¦Sep-18-2020 12:21
2020-09-18 12:22 | 44092.5151 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 1 waiting area N |  | 0 | 15 | 27.2 | 390 | 22.1 | 25.9 | 415 |  | 2020-09-18 12:22 | 44092.5151 | 22.1 | 25.9 | 415 |  | low | 2020-09-14 | B17477¦LVL 1 waiting area N¦¦Sep-18-2020 12:21
2020-09-18 12:22 | 44092.5153 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Reception seating 2 |  | 0 | 13.8 | 22.7 | 475 | 21.8 | 22.6 | 477 |  | 2020-09-18 12:22 | 44092.5153 | 21.8 | 22.6 | 477 |  | low | 2020-09-14 | B20603¦Reception seating 2¦¦Sep-18-2020 12:22
2020-09-18 12:22 | 44092.5154 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Main lobby north |  | 1 | 17 | 32 | 421 | 23 | 28 | 575 |  | 2020-09-18 12:22 | 44092.5154 | 23 | 28 | 575 |  | low | 2020-09-14 | B25479¦Main lobby north ¦¦Sep-18-2020 12:22
2020-09-18 12:22 | 44092.5154 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 retiring home |  | 1 | 18 | 18 | 380 | 22 | 26 | 372 |  | 2020-09-18 12:22 | 44092.5154 | 22 | 26 | 372 |  | low | 2020-09-14 | B20772¦H11 retiring home¦¦Sep-18-2020 12:22
2020-09-18 12:22 | 44092.5154 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 5 bottom |  | 1 | 23 | 20 | 407 | 23 | 26 | 420 |  | 2020-09-18 12:22 | 44092.5154 | 23 | 26 | 420 |  | low | 2020-09-14 | B19570¦Stairwell 5 bottom ¦¦Sep-18-2020 12:22
2020-09-18 12:22 | 44092.5155 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Museum |  | 1 | 14.6 | 41.2 | 380 | 21.2 | 43 | 402 |  | 2020-09-18 12:22 | 44092.5155 | 21.2 | 43 | 402 |  |  | 2020-09-14 | B20390¦Museum¦¦Sep-18-2020 12:22
2020-09-18 12:23 | 44092.5157 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main lobby N |  | 0 | 21 | 16 | 407 | 23 | 23 | 512 |  | 2020-09-18 12:23 | 44092.5157 | 23 | 23 | 512 |  | low | 2020-09-14 | B70235¦Main lobby N ¦¦Sep-18-2020 12:22
2020-09-18 12:23 | 44092.5158 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 judge |  | 1 | 18 | 18 | 380 | 22 | 23 | 368 |  | 2020-09-18 12:23 | 44092.5158 | 22 | 23 | 368 |  | low | 2020-09-14 | B20772¦H11 judge¦¦Sep-18-2020 12:22
2020-09-18 12:23 | 44092.5158 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Basement hall w |  | 1 | 23 | 20 | 407 | 23 | 26 | 430 |  | 2020-09-18 12:23 | 44092.5158 | 23 | 26 | 430 |  | low | 2020-09-14 | B19570¦Basement hall w¦¦Sep-18-2020 12:22
2020-09-18 12:23 | 44092.5159 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 1 waiting area S |  | 0 | 15 | 27.2 | 390 | 22.1 | 26.5 | 414 |  | 2020-09-18 12:23 | 44092.5159 | 22.1 | 26.5 | 414 |  | low | 2020-09-14 | B17477¦LVL 1 waiting area S¦¦Sep-18-2020 12:22
2020-09-18 12:23 | 44092.5162 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court admin hall |  | 1 | 23 | 20 | 407 | 22 | 27 | 435 |  | 2020-09-18 12:23 | 44092.5162 | 22 | 27 | 435 |  | low | 2020-09-14 | B19570¦Court admin hall ¦¦Sep-18-2020 12:23
2020-09-18 12:24 | 44092.5165 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 plaintiff |  | 1 | 18 | 18 | 380 | 22 | 23 | 367 |  | 2020-09-18 12:24 | 44092.5165 | 22 | 23 | 367 |  | low | 2020-09-14 | B20772¦H11 plaintiff¦¦Sep-18-2020 12:23
2020-09-18 12:24 | 44092.5166 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Employee entrance |  | 1 | 23 | 20 | 407 | 22 | 27 | 444 |  | 2020-09-18 12:24 | 44092.5166 | 22 | 27 | 444 |  | low | 2020-09-14 | B19570¦Employee entrance ¦¦Sep-18-2020 12:23
2020-09-18 12:24 | 44092.5167 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 6 |  | 1 | 14.6 | 41.2 | 380 | 21.6 | 39.9 | 394 |  | 2020-09-18 12:24 | 44092.5167 | 21.6 | 39.9 | 394 |  | caution | 2020-09-14 | B20390¦Outside courtroom 6¦¦Sep-18-2020 12:24
2020-09-18 12:24 | 44092.5167 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office hallway |  | 0 | 13.8 | 33 | 413 | 21.7 | 21.9 | 447 |  | 2020-09-18 12:24 | 44092.5167 | 21.7 | 21.9 | 447 |  | low | 2020-09-14 | B20603¦Office hallway ¦¦Sep-18-2020 12:24
2020-09-18 12:24 | 44092.5168 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 waiting area |  | 0 | 15 | 27.2 | 390 | 22.2 | 27.8 | 402 |  | 2020-09-18 12:24 | 44092.5168 | 22.2 | 27.8 | 402 |  | low | 2020-09-14 | B17477¦Courtroom 100 waiting area¦¦Sep-18-2020 12:24
2020-09-18 12:25 | 44092.5171 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court services office |  | 6 | 23 | 20 | 407 | 22 | 26 | 452 |  | 2020-09-18 12:25 | 44092.5171 | 22 | 26 | 452 |  | low | 2020-09-14 | B19570¦Court services office ¦¦Sep-18-2020 12:24
2020-09-18 12:25 | 44092.5175 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 defendant |  | 1 | 18 | 18 | 380 | 22 | 23 | 372 |  | 2020-09-18 12:25 | 44092.5175 | 22 | 23 | 372 |  | low | 2020-09-14 | B20772¦H11 defendant¦¦Sep-18-2020 12:25
2020-09-18 12:25 | 44092.5176 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Basement hall e |  | 1 | 23 | 20 | 407 | 22 | 28 | 447 |  | 2020-09-18 12:25 | 44092.5176 | 22 | 28 | 447 |  | low | 2020-09-14 | B19570¦Basement hall e ¦¦Sep-18-2020 12:25
2020-09-18 12:25 | 44092.5176 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Back stairwell, second floor |  | 1 | 14.6 | 41.2 | 380 | 21.6 | 42.5 | 386 |  | 2020-09-18 12:25 | 44092.5176 | 21.6 | 42.5 | 386 |  |  | 2020-09-14 | B20390¦Back stairwell, second floor¦¦Sep-18-2020 12:25
2020-09-18 12:26 | 44092.5178 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office hallway 2 |  | 0 | 13.8 | 33 | 413 | 21.9 | 22.2 | 437 |  | 2020-09-18 12:26 | 44092.5178 | 21.9 | 22.2 | 437 |  | low | 2020-09-14 | B20603¦Office hallway 2¦¦Sep-18-2020 12:25
2020-09-18 12:26 | 44092.5179 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 1 interview room 1 |  | 0 | 15 | 27.2 | 390 | 22.2 | 27.6 | 407 |  | 2020-09-18 12:26 | 44092.5179 | 22.2 | 27.6 | 407 |  | low | 2020-09-14 | B17477¦LVL 1 interview room 1¦¦Sep-18-2020 12:25
2020-09-18 12:26 | 44092.518 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 4 bottom |  | 1 | 23 | 20 | 407 | 21 | 29 | 433 |  | 2020-09-18 12:26 | 44092.518 | 21 | 29 | 433 |  | low | 2020-09-14 | B19570¦Stairwell 4 bottom¦¦Sep-18-2020 12:25
2020-09-18 12:26 | 44092.5181 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 rear right |  | 1 | 18 | 18 | 380 | 22 | 23 | 380 |  | 2020-09-18 12:26 | 44092.5181 | 22 | 23 | 380 |  | low | 2020-09-14 | B20772¦H11 rear right¦¦Sep-18-2020 12:26
2020-09-18 12:26 | 44092.5184 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 4 top |  | 1 | 23 | 20 | 407 | 21 | 29 | 429 |  | 2020-09-18 12:26 | 44092.5184 | 21 | 29 | 429 |  | low | 2020-09-14 | B19570¦Stairwell 4 top ¦¦Sep-18-2020 12:26
2020-09-18 12:27 | 44092.5186 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Between second floor washrooms |  | 1 | 14.6 | 41.2 | 380 | 21.7 | 39.9 | 389 |  | 2020-09-18 12:27 | 44092.5186 | 21.7 | 39.9 | 389 |  | caution | 2020-09-14 | B20390¦Between second floor washrooms¦¦Sep-18-2020 12:26
2020-09-18 12:27 | 44092.5187 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 251 |  | 1 | 23 | 20 | 407 | 22 | 24 | 430 |  | 2020-09-18 12:27 | 44092.5187 | 22 | 24 | 430 |  | low | 2020-09-14 | B19570¦251¦¦Sep-18-2020 12:26
2020-09-18 12:27 | 44092.5188 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 rear left |  | 1 | 18 | 18 | 380 | 22 | 23 | 381 |  | 2020-09-18 12:27 | 44092.5188 | 22 | 23 | 381 |  | low | 2020-09-14 | B20772¦H11 rear left¦¦Sep-18-2020 12:27
2020-09-18 12:27 | 44092.5188 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Printer room |  | 0 | 13.8 | 33 | 413 | 21.8 | 22 | 458 |  | 2020-09-18 12:27 | 44092.5188 | 21.8 | 22 | 458 |  | low | 2020-09-14 | B20603¦Printer room ¦¦Sep-18-2020 12:27
2020-09-18 12:27 | 44092.519 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 1 interview room 2 |  | 0 | 15 | 27.2 | 390 | 22.1 | 27.7 | 411 |  | 2020-09-18 12:27 | 44092.519 | 22.1 | 27.7 | 411 |  | low | 2020-09-14 | B17477¦LVL 1 interview room 2 ¦¦Sep-18-2020 12:27
2020-09-18 12:27 | 44092.519 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 250 |  | 1 | 23 | 20 | 407 | 22 | 24 | 423 |  | 2020-09-18 12:27 | 44092.519 | 22 | 24 | 423 |  | low | 2020-09-14 | B19570¦250¦¦Sep-18-2020 12:27
2020-09-18 12:28 | 44092.5193 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jason Mariasine office |  | 1 | 21 | 16 | 407 |  |  |  |  | 2020-09-18 12:28 | 44092.5193 | [5 empty] | 2020-09-14 | B70235¦Jason Mariasine office ¦¦Sep-18-2020 12:27
2020-09-18 12:28 | 44092.5193 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Hallway ne |  | 1 | 23 | 20 | 407 | 22 | 24 | 418 |  | 2020-09-18 12:28 | 44092.5193 | 22 | 24 | 418 |  | low | 2020-09-14 | B19570¦Hallway ne ¦¦Sep-18-2020 12:27
2020-09-18 12:28 | 44092.5196 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Printer room |  | 0 | 13.8 | 33 | 413 | 22.1 | 22.1 | 448 |  | 2020-09-18 12:28 | 44092.5196 | 22.1 | 22.1 | 448 |  | low | 2020-09-14 | B20603¦Printer room ¦¦Sep-18-2020 12:28
2020-09-18 12:28 | 44092.5197 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Duty crown hall |  | 1 | 23 | 20 | 407 | 22 | 25 | 420 |  | 2020-09-18 12:28 | 44092.5197 | 22 | 25 | 420 |  | low | 2020-09-14 | B19570¦Duty crown hall ¦¦Sep-18-2020 12:28
2020-09-18 12:29 | 44092.52 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Court attorneys waiting area |  | 1 | 14.6 | 41.2 | 380 | 22.1 | 32.1 | 394 |  | 2020-09-18 12:29 | 44092.52 | 22.1 | 32.1 | 394 |  | low | 2020-09-14 | B20390¦Court attorneys waiting area¦¦Sep-18-2020 12:28
2020-09-18 12:29 | 44092.52 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 245 |  | 1 | 23 | 20 | 407 | 22 | 22 | 416 |  | 2020-09-18 12:29 | 44092.52 | 22 | 22 | 416 |  | low | 2020-09-14 | B19570¦245¦¦Sep-18-2020 12:28
2020-09-18 12:29 | 44092.5202 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office hallway 3 |  | 0 | 13.8 | 33 | 413 | 22 | 22.5 | 444 |  | 2020-09-18 12:29 | 44092.5202 | 22 | 22.5 | 444 |  | low | 2020-09-14 | B20603¦Office hallway 3¦¦Sep-18-2020 12:29
2020-09-18 12:29 | 44092.5204 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 247 |  | 1 | 23 | 20 | 407 | 23 | 22 | 409 |  | 2020-09-18 12:29 | 44092.5204 | 23 | 22 | 409 |  | low | 2020-09-14 | B19570¦247¦¦Sep-18-2020 12:29
2020-09-18 12:30 | 44092.5206 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Court attorneys reception area |  | 1 | 14.6 | 41.2 | 380 | 22.1 | 36.8 | 396 |  | 2020-09-18 12:30 | 44092.5206 | 22.1 | 36.8 | 396 |  | caution | 2020-09-14 | B20390¦Court attorneys reception area¦¦Sep-18-2020 12:29
2020-09-18 12:30 | 44092.5207 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main entrance |  | 0 | 17.1 | 27 | 402 | 18.3 | 37.9 | 419 |  | 2020-09-18 12:30 | 44092.5207 | 18.3 | 37.9 | 419 |  | caution | 2020-09-14 | B10577¦Main entrance ¦¦Sep-18-2020 12:29
2020-09-18 12:30 | 44092.5207 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 244 |  | 1 | 23 | 20 | 407 | 23 | 21 | 406 |  | 2020-09-18 12:30 | 44092.5207 | 23 | 21 | 406 |  | low | 2020-09-14 | B19570¦244¦¦Sep-18-2020 12:29
2020-09-18 12:30 | 44092.5208 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 W |  | 0 | 15 | 27.2 | 390 | 21.9 | 27.6 | 404 |  | 2020-09-18 12:30 | 44092.5208 | 21.9 | 27.6 | 404 |  | low | 2020-09-14 | B17477¦Courtroom 100 W¦¦Sep-18-2020 12:29
2020-09-18 12:30 | 44092.5211 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office hallway 4 |  | 0 | 13.8 | 33 | 413 | 22.1 | 22.2 | 440 |  | 2020-09-18 12:30 | 44092.5211 | 22.1 | 22.2 | 440 |  | low | 2020-09-14 | B20603¦Office hallway 4¦¦Sep-18-2020 12:30
2020-09-18 12:31 | 44092.5213 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Lobby south |  | 0 | 17.1 | 27 | 402 | 21.2 | 41.3 | 595 |  | 2020-09-18 12:31 | 44092.5213 | 21.2 | 41.3 | 595 |  |  | 2020-09-14 | B10577¦Main Lobby south ¦¦Sep-18-2020 12:30
2020-09-18 12:31 | 44092.5215 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 E |  | 0 | 15 | 27.2 | 390 | 21.7 | 27.8 | 397 |  | 2020-09-18 12:31 | 44092.5215 | 21.7 | 27.8 | 397 |  | low | 2020-09-14 | B17477¦Courtroom 100 E¦¦Sep-18-2020 12:30
2020-09-18 12:31 | 44092.5217 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 5 |  | 1 | 14.6 | 41.2 | 380 | 22 | 32.3 | 396 | Court in session - courtroom 5 | 2020-09-18 12:31 | 44092.5217 | 22 | 32.3 | 396 |  | low | 2020-09-14 | B20390¦Outside courtroom 5¦¦Sep-18-2020 12:31
2020-09-18 12:31 | 44092.5218 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office hallway 5 |  | 0 | 13.8 | 33 | 413 | 22.2 | 22.3 | 438 |  | 2020-09-18 12:31 | 44092.5218 | 22.2 | 22.3 | 438 |  | low | 2020-09-14 | B20603¦Office hallway 5¦¦Sep-18-2020 12:31
2020-09-18 12:32 | 44092.5221 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Court service office |  | 2 | 17.1 | 27 | 402 | 21.3 | 40.7 | 602 |  | 2020-09-18 12:32 | 44092.5221 | 21.3 | 40.7 | 602 |  |  | 2020-09-14 | B10577¦Court service office ¦¦Sep-18-2020 12:31
2020-09-18 12:32 | 44092.5224 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H14 north judge entrance |  | 1 | 18 | 18 | 380 | 22 | 24 | 373 |  | 2020-09-18 12:32 | 44092.5224 | 22 | 24 | 373 |  | low | 2020-09-14 | B20772¦H14 north judge entrance ¦¦Sep-18-2020 12:32
2020-09-18 12:33 | 44092.5228 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H14 exit |  | 1 | 18 | 18 | 380 | 22 | 24 | 372 |  | 2020-09-18 12:33 | 44092.5228 | 22 | 24 | 372 |  | low | 2020-09-14 | B20772¦H14 exit ¦¦Sep-18-2020 12:32
2020-09-18 12:33 | 44092.523 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Witness area |  | 0 | 17.1 | 27 | 402 | 21.7 | 41.1 | 608 |  | 2020-09-18 12:33 | 44092.523 | 21.7 | 41.1 | 608 |  |  | 2020-09-14 | B10577¦Witness area ¦¦Sep-18-2020 12:33
2020-09-18 12:33 | 44092.5231 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 4 |  | 1 | 14.6 | 41.2 | 380 | 21.9 | 32.1 | 406 |  | 2020-09-18 12:33 | 44092.5231 | 21.9 | 32.1 | 406 |  | low | 2020-09-14 | B20390¦Outside courtroom 4¦¦Sep-18-2020 12:33
2020-09-18 12:34 | 44092.5236 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 South |  | 0 | 17.1 | 27 | 402 | 21.8 | 41.1 | 575 |  | 2020-09-18 12:34 | 44092.5236 | 21.8 | 41.1 | 575 |  |  | 2020-09-14 | B10577¦Courtroom 1 South ¦¦Sep-18-2020 12:33
2020-09-18 12:34 | 44092.5236 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 6th floor main hallway east |  | 0 | 13.8 | 33 | 413 | 21.2 | 22.8 | 426 |  | 2020-09-18 12:34 | 44092.5236 | 21.2 | 22.8 | 426 |  | low | 2020-09-14 | B20603¦6th floor main hallway east ¦¦Sep-18-2020 12:33
2020-09-18 12:34 | 44092.5237 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 4 waiting area S |  | 0 | 15 | 27.2 | 390 | 22.2 | 23.9 | 412 |  | 2020-09-18 12:34 | 44092.5237 | 22.2 | 23.9 | 412 |  | low | 2020-09-14 | B17477¦LVL 4 waiting area S¦¦Sep-18-2020 12:34
2020-09-18 12:35 | 44092.5241 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jennifer Broderick office |  | 1 | 21 | 16 | 407 |  |  |  | Occupied, no access | 2020-09-18 12:35 | 44092.5241 | [5 empty] | 2020-09-14 | B70235¦Jennifer Broderick office ¦¦Sep-18-2020 12:34
2020-09-18 12:35 | 44092.5242 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 east |  | 0 | 17.1 | 27 | 402 | 22.1 | 41 | 529 |  | 2020-09-18 12:35 | 44092.5242 | 22.1 | 41 | 529 |  |  | 2020-09-14 | B10577¦Courtroom 1 east¦¦Sep-18-2020 12:34
2020-09-18 12:35 | 44092.5244 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Interview room 6 |  | 1 | 14.6 | 41.2 | 380 | 22 | 38.1 | 400 |  | 2020-09-18 12:35 | 44092.5244 | 22 | 38.1 | 400 |  | caution | 2020-09-14 | B20390¦Interview room 6¦¦Sep-18-2020 12:35
2020-09-18 12:35 | 44092.5244 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 6th floor main hallway 2 |  | 0 | 13.8 | 33 | 413 | 21.1 | 23.7 | 425 |  | 2020-09-18 12:35 | 44092.5244 | 21.1 | 23.7 | 425 |  | low | 2020-09-14 | B20603¦6th floor main hallway 2 ¦¦Sep-18-2020 12:35
2020-09-18 12:35 | 44092.5246 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 4 waiting area N |  | 0 | 15 | 27.2 | 390 | 22.4 | 23.1 | 416 |  | 2020-09-18 12:35 | 44092.5246 | 22.4 | 23.1 | 416 |  | low | 2020-09-14 | B17477¦LVL 4 waiting area N¦¦Sep-18-2020 12:35
2020-09-18 12:36 | 44092.5248 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Robert Beninger office |  | 1 | 21 | 16 | 407 |  |  |  | Occupied, no access | 2020-09-18 12:36 | 44092.5248 | [5 empty] | 2020-09-14 | B70235¦Robert Beninger office ¦¦Sep-18-2020 12:35
2020-09-18 12:36 | 44092.525 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 North |  | 0 | 17.1 | 27 | 402 | 22.2 | 40.5 | 516 |  | 2020-09-18 12:36 | 44092.525 | 22.2 | 40.5 | 516 |  |  | 2020-09-14 | B10577¦Courtroom 1 North ¦¦Sep-18-2020 12:35
2020-09-18 12:37 | 44092.5255 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 waiting area |  | 0 | 15 | 27.2 | 390 | 22.4 | 24.1 | 409 |  | 2020-09-18 12:37 | 44092.5255 | 22.4 | 24.1 | 409 |  | low | 2020-09-14 | B17477¦Courtroom 400 waiting area¦¦Sep-18-2020 12:36
2020-09-18 12:37 | 44092.5256 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Interview room 8 |  | 1 | 14.6 | 41.2 | 380 | 21.9 | 30.1 | 398 |  | 2020-09-18 12:37 | 44092.5256 | 21.9 | 30.1 | 398 |  | low | 2020-09-14 | B20390¦Interview room 8¦¦Sep-18-2020 12:36
2020-09-18 12:37 | 44092.5256 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 6th floor main hallway 3 |  | 0 | 13.8 | 33 | 413 | 21.2 | 23.6 | 428 |  | 2020-09-18 12:37 | 44092.5256 | 21.2 | 23.6 | 428 |  | low | 2020-09-14 | B20603¦6th floor main hallway 3¦¦Sep-18-2020 12:36
2020-09-18 12:37 | 44092.5256 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 judge |  | 1 | 21 | 16 | 407 |  |  |  | Occupied, no access | 2020-09-18 12:37 | 44092.5256 | [5 empty] | 2020-09-14 | B70235¦Court #3 judge ¦¦Sep-18-2020 12:36
2020-09-18 12:38 | 44092.5261 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 West |  | 0 | 17.1 | 27 | 402 | 22.2 | 40.2 | 502 |  | 2020-09-18 12:38 | 44092.5261 | 22.2 | 40.2 | 502 |  |  | 2020-09-14 | B10577¦Courtroom 1 West¦¦Sep-18-2020 12:37
2020-09-18 12:38 | 44092.5263 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 4 interview room |  | 0 | 15 | 27.2 | 390 | 22.3 | 24 | 404 |  | 2020-09-18 12:38 | 44092.5263 | 22.3 | 24 | 404 |  | low | 2020-09-14 | B17477¦LVL 4 interview room ¦¦Sep-18-2020 12:37
2020-09-18 12:38 | 44092.5263 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 lawyer |  | 1 | 21 | 16 | 407 |  |  |  | Occupied, no access | 2020-09-18 12:38 | 44092.5263 | [5 empty] | 2020-09-14 | B70235¦Court #3 lawyer ¦¦Sep-18-2020 12:37
2020-09-18 12:38 | 44092.5265 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 center |  | 0 | 17.1 | 27 | 402 | 22.3 | 40.1 | 500 |  | 2020-09-18 12:38 | 44092.5265 | 22.3 | 40.1 | 500 |  |  | 2020-09-14 | B10577¦Courtroom 1 center ¦¦Sep-18-2020 12:38
2020-09-18 12:38 | 44092.5266 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 6th floor main hallway 4 |  | 0 | 13.8 | 33 | 413 | 21.5 | 23.2 | 428 |  | 2020-09-18 12:38 | 44092.5266 | 21.5 | 23.2 | 428 |  | low | 2020-09-14 | B20603¦6th floor main hallway 4¦¦Sep-18-2020 12:38
2020-09-18 12:40 | 44092.5275 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Lobby North |  | 3 | 17.1 | 27 | 402 | 22 | 40 | 529 |  | 2020-09-18 12:40 | 44092.5275 | 22 | 40 | 529 |  | caution | 2020-09-14 | B10577¦Main Lobby North ¦¦Sep-18-2020 12:39
2020-09-18 12:40 | 44092.5275 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 W |  | 0 | 15 | 27.2 | 390 | 22 | 23.3 | 404 |  | 2020-09-18 12:40 | 44092.5275 | 22 | 23.3 | 404 |  | low | 2020-09-14 | B17477¦Courtroom 400 W¦¦Sep-18-2020 12:39
2020-09-18 12:40 | 44092.528 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Stairwell |  | 0 | 17.1 | 27 | 402 | 22.2 | 41.8 | 569 |  | 2020-09-18 12:40 | 44092.528 | 22.2 | 41.8 | 569 |  |  | 2020-09-14 | B10577¦Main Stairwell ¦¦Sep-18-2020 12:40
2020-09-18 12:40 | 44092.528 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 6th floor main hallway 5 |  | 0 | 13.8 | 33 | 413 | 22 | 23.2 | 426 |  | 2020-09-18 12:40 | 44092.528 | 22 | 23.2 | 426 |  | low | 2020-09-14 | B20603¦6th floor main hallway 5¦¦Sep-18-2020 12:40
2020-09-18 12:41 | 44092.5282 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 E |  | 0 | 15 | 27.2 | 390 | 22.2 | 23.8 | 403 |  | 2020-09-18 12:41 | 44092.5282 | 22.2 | 23.8 | 403 |  | low | 2020-09-14 | B17477¦Courtroom 400 E¦¦Sep-18-2020 12:40
2020-09-18 12:41 | 44092.5286 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2 floor waiting area North |  | 0 | 17.1 | 27 | 402 | 22.2 | 43.4 | 590 |  | 2020-09-18 12:41 | 44092.5286 | 22.2 | 43.4 | 590 |  |  | 2020-09-14 | B10577¦2 floor waiting area North ¦¦Sep-18-2020 12:41
2020-09-18 12:41 | 44092.5288 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 6th floor main hallway 6 |  | 0 | 13.8 | 33 | 413 | 22.2 | 23.1 | 426 |  | 2020-09-18 12:41 | 44092.5288 | 22.2 | 23.1 | 426 |  | low | 2020-09-14 | B20603¦6th floor main hallway 6 ¦¦Sep-18-2020 12:41
2020-09-18 12:42 | 44092.5289 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Waiting area outside courtroom3 |  | 1 | 15.5 | 20.9 | 415 | 21.5 | 20.9 | 493 |  | 2020-09-18 12:42 | 44092.5289 | 21.5 | 20.9 | 493 |  | low | 2020-09-14 | B21554¦Waiting area outside courtroom3¦¦Sep-18-2020 12:41
2020-09-18 12:42 | 44092.5293 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell, third floor |  | 1 | 14.6 | 41.2 | 380 | 24.6 | 31.4 | 395 |  | 2020-09-18 12:42 | 44092.5293 | 24.6 | 31.4 | 395 |  | low | 2020-09-14 | B20390¦Main stairwell, third floor¦¦Sep-18-2020 12:42
2020-09-18 12:42 | 44092.5294 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2 floor waiting area center |  | 0 | 17.1 | 27 | 402 | 22.3 | 43.5 | 595 |  | 2020-09-18 12:42 | 44092.5294 | 22.3 | 43.5 | 595 |  |  | 2020-09-14 | B10577¦2 floor waiting area center ¦¦Sep-18-2020 12:42
2020-09-18 12:42 | 44092.5295 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 judge |  | 1 | 18 | 18 | 380 | 22 | 23 | 370 |  | 2020-09-18 12:42 | 44092.5295 | 22 | 23 | 370 |  | low | 2020-09-14 | B20772¦H13 judge¦¦Sep-18-2020 12:42
2020-09-18 12:43 | 44092.5296 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Crown attorney office |  | 0 | 15 | 27.2 | 390 | 22.2 | 25.3 | 411 |  | 2020-09-18 12:43 | 44092.5296 | 22.2 | 25.3 | 411 |  | low | 2020-09-14 | B17477¦Crown attorney office¦¦Sep-18-2020 12:42
2020-09-18 12:43 | 44092.5297 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 6th floor main hallway 7 |  | 0 | 13.8 | 33 | 413 | 22.5 | 23.9 | 426 |  | 2020-09-18 12:43 | 44092.5297 | 22.5 | 23.9 | 426 |  | low | 2020-09-14 | B20603¦6th floor main hallway 7 ¦¦Sep-18-2020 12:42
2020-09-18 12:43 | 44092.5299 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 plaintiff |  | 1 | 18 | 18 | 380 | 22 | 23 | 369 |  | 2020-09-18 12:43 | 44092.5299 | 22 | 23 | 369 |  | low | 2020-09-14 | B20772¦H13 plaintiff¦¦Sep-18-2020 12:43
2020-09-18 12:43 | 44092.5299 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2 floor waiting area south |  | 0 | 17.1 | 27 | 402 | 22.4 | 43.4 | 598 |  | 2020-09-18 12:43 | 44092.5299 | 22.4 | 43.4 | 598 |  |  | 2020-09-14 | B10577¦2 floor waiting area south ¦¦Sep-18-2020 12:43
2020-09-18 12:43 | 44092.5302 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Third floor waiting area |  | 1 | 14.6 | 41.2 | 380 | 23.9 | 29.9 | 394 |  | 2020-09-18 12:43 | 44092.5302 | 23.9 | 29.9 | 394 |  | low | 2020-09-14 | B20390¦Third floor waiting area¦¦Sep-18-2020 12:43
2020-09-18 12:44 | 44092.5304 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 defendant |  | 1 | 18 | 18 | 380 | 22 | 23 | 375 |  | 2020-09-18 12:44 | 44092.5304 | 22 | 23 | 375 |  | low | 2020-09-14 | B20772¦H13 defendant¦¦Sep-18-2020 12:43
2020-09-18 12:44 | 44092.5307 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 5 waiting area N |  | 0 | 15 | 27.2 | 390 | 22.3 | 25.5 | 409 |  | 2020-09-18 12:44 | 44092.5307 | 22.3 | 25.5 | 409 |  | low | 2020-09-14 | B17477¦LVL 5 waiting area N¦¦Sep-18-2020 12:44
2020-09-18 12:44 | 44092.5307 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Basement corridor at washrooms |  | 1 | 15.5 | 20.9 | 415 | 22.1 | 21 | 488 |  | 2020-09-18 12:44 | 44092.5307 | 22.1 | 21 | 488 |  | low | 2020-09-14 | B21554¦Basement corridor at washrooms¦¦Sep-18-2020 12:44
2020-09-18 12:44 | 44092.5308 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 West |  | 0 | 17.1 | 27 | 402 | 22.6 | 40.3 | 599 |  | 2020-09-18 12:44 | 44092.5308 | 22.6 | 40.3 | 599 |  |  | 2020-09-14 | B10577¦Courtroom 2 West¦¦Sep-18-2020 12:44
2020-09-18 12:45 | 44092.5313 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Hearing room |  | 0 | 13.8 | 33 | 413 | 22.8 | 21.7 | 422 |  | 2020-09-18 12:45 | 44092.5313 | 22.8 | 21.7 | 422 |  | low | 2020-09-14 | B20603¦Hearing room ¦¦Sep-18-2020 12:45
2020-09-18 12:45 | 44092.5315 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 5 waiting area S |  | 0 | 15 | 27.2 | 390 | 22.5 | 24.5 | 409 |  | 2020-09-18 12:45 | 44092.5315 | 22.5 | 24.5 | 409 |  | low | 2020-09-14 | B17477¦LVL 5 waiting area S¦¦Sep-18-2020 12:45
2020-09-18 12:46 | 44092.532 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Hearing room 2 |  | 0 | 13.8 | 33 | 413 | 22.8 | 21.9 | 423 |  | 2020-09-18 12:46 | 44092.532 | 22.8 | 21.9 | 423 |  | low | 2020-09-14 | B20603¦Hearing room 2¦¦Sep-18-2020 12:46
2020-09-18 12:46 | 44092.5323 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Basement corridor at exit door |  | 1 | 15.5 | 20.9 | 415 | 22.3 | 19.9 | 489 |  | 2020-09-18 12:46 | 44092.5323 | 22.3 | 19.9 | 489 |  | low | 2020-09-14 | B21554¦Basement corridor at exit door¦¦Sep-18-2020 12:46
2020-09-18 12:47 | 44092.5324 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 South |  | 0 | 17.1 | 27 | 402 | 22.7 | 38.3 | 599 |  | 2020-09-18 12:47 | 44092.5324 | 22.7 | 38.3 | 599 |  | caution | 2020-09-14 | B10577¦Courtroom 2 South¦¦Sep-18-2020 12:46
2020-09-18 12:47 | 44092.5326 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Courtroom 1 waiting area |  | 1 | 14.6 | 41.2 | 380 | 22 | 33.6 | 380 |  | 2020-09-18 12:47 | 44092.5326 | 22 | 33.6 | 380 |  | low | 2020-09-14 | B20390¦Courtroom 1 waiting area¦¦Sep-18-2020 12:47
2020-09-18 12:47 | 44092.5329 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 rear left |  | 1 | 18 | 18 | 380 | 22 | 23 | 376 |  | 2020-09-18 12:47 | 44092.5329 | 22 | 23 | 376 |  | low | 2020-09-14 | B20772¦H13 rear left¦¦Sep-18-2020 12:47
2020-09-18 12:47 | 44092.533 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 500 waiting area |  | 0 | 15 | 27.2 | 390 | 22.5 | 23.2 | 402 |  | 2020-09-18 12:47 | 44092.533 | 22.5 | 23.2 | 402 |  | low | 2020-09-14 | B17477¦Courtroom 500 waiting area¦¦Sep-18-2020 12:47
2020-09-18 12:48 | 44092.5331 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 East |  | 0 | 17.1 | 27 | 402 | 23.1 | 37.1 | 593 |  | 2020-09-18 12:48 | 44092.5331 | 23.1 | 37.1 | 593 |  | caution | 2020-09-14 | B10577¦Courtroom 3 East¦¦Sep-18-2020 12:47
2020-09-18 12:48 | 44092.5334 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Stairway landing |  | 1 | 15.5 | 20.9 | 415 | 22.5 | 20.2 | 495 |  | 2020-09-18 12:48 | 44092.5334 | 22.5 | 20.2 | 495 |  | low | 2020-09-14 | B21554¦Stairway landing¦¦Sep-18-2020 12:48
2020-09-18 12:48 | 44092.5335 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 North |  | 1 | 17.1 | 27 | 402 | 23.1 | 37 | 593 |  | 2020-09-18 12:48 | 44092.5335 | 23.1 | 37 | 593 |  | caution | 2020-09-14 | B10577¦Courtroom 1 North ¦¦Sep-18-2020 12:48
2020-09-18 12:48 | 44092.5337 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside third floor elevator |  | 1 | 14.6 | 41.2 | 380 | 22.1 | 34.5 | 393 |  | 2020-09-18 12:48 | 44092.5337 | 22.1 | 34.5 | 393 |  | low | 2020-09-14 | B20390¦Outside third floor elevator¦¦Sep-18-2020 12:48
2020-09-18 12:49 | 44092.5341 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 5 interview room 1 |  | 0 | 15 | 27.2 | 390 | 22.6 | 22.8 | 396 |  | 2020-09-18 12:49 | 44092.5341 | 22.6 | 22.8 | 396 |  | low | 2020-09-14 | B17477¦LVL 5 interview room 1¦¦Sep-18-2020 12:49
2020-09-18 12:49 | 44092.5341 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 printer |  | 1 | 18 | 18 | 380 | 22 | 24 | 374 |  | 2020-09-18 12:49 | 44092.5341 | 22 | 24 | 374 |  | low | 2020-09-14 | B20772¦H16 printer¦¦Sep-18-2020 12:49
2020-09-18 12:49 | 44092.5343 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Public seating area |  | 0 | 17.2 | 18 | 434 | 22.3 | 30.1 | 555 |  | 2020-09-18 12:49 | 44092.5343 | 22.3 | 30.1 | 555 |  | low | 2020-09-14 | B19890¦Public seating area ¦¦Sep-18-2020 12:49
2020-09-18 12:49 | 44092.5344 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 outside |  | 0 | 17.1 | 27 | 402 | 22 | 36.7 | 588 |  | 2020-09-18 12:49 | 44092.5344 | 22 | 36.7 | 588 |  | caution | 2020-09-14 | B10577¦Courtroom 3 outside¦¦Sep-18-2020 12:49
2020-09-18 12:50 | 44092.5345 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Stairwell |  | 0 | 13.8 | 33 | 413 | 19.2 | 26.2 | 413 |  | 2020-09-18 12:50 | 44092.5345 | 19.2 | 26.2 | 413 |  | low | 2020-09-14 | B20603¦Stairwell ¦¦Sep-18-2020 12:49
2020-09-18 12:50 | 44092.5346 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Elevator |  | 1 | 14.6 | 41.2 | 380 | 22.7 | 36.6 | 405 |  | 2020-09-18 12:50 | 44092.5346 | 22.7 | 36.6 | 405 |  | caution | 2020-09-14 | B20390¦Elevator ¦¦Sep-18-2020 12:49
2020-09-18 12:50 | 44092.5349 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 5 interview room 2 |  | 0 | 15 | 27.2 | 390 | 22.2 | 23.6 | 403 |  | 2020-09-18 12:50 | 44092.5349 | 22.2 | 23.6 | 403 |  | low | 2020-09-14 | B17477¦LVL 5 interview room 2 ¦¦Sep-18-2020 12:50
2020-09-18 12:50 | 44092.5351 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Legal aid office corridor |  | 2 | 15.5 | 20.9 | 415 | 21.7 | 19.2 | 459 |  | 2020-09-18 12:50 | 44092.5351 | 21.7 | 19.2 | 459 |  | low | 2020-09-14 | B21554¦Legal aid office corridor¦¦Sep-18-2020 12:50
2020-09-18 12:51 | 44092.5351 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 typer |  | 1 | 18 | 18 | 380 | 22 | 24 | 376 |  | 2020-09-18 12:51 | 44092.5351 | 22 | 24 | 376 |  | low | 2020-09-14 | B20772¦H16 typer¦¦Sep-18-2020 12:50
2020-09-18 12:51 | 44092.5354 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Stairwell 2 |  | 0 | 13.8 | 33 | 413 | 18.1 | 29.1 | 411 |  | 2020-09-18 12:51 | 44092.5354 | 18.1 | 29.1 | 411 |  | low | 2020-09-14 | B20603¦Stairwell 2¦¦Sep-18-2020 12:51
2020-09-18 12:51 | 44092.5355 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Staff area |  | 2 | 17.2 | 18 | 434 | 22.5 | 29.7 | 519 |  | 2020-09-18 12:51 | 44092.5355 | 22.5 | 29.7 | 519 |  | low | 2020-09-14 | B19890¦Staff area ¦¦Sep-18-2020 12:51
2020-09-18 12:51 | 44092.5356 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 waiting area |  | 0 | 17.1 | 27 | 402 | 21.7 | 35.2 | 550 |  | 2020-09-18 12:51 | 44092.5356 | 21.7 | 35.2 | 550 |  | caution | 2020-09-14 | B10577¦Courtroom 3 waiting area ¦¦Sep-18-2020 12:51
2020-09-18 12:52 | 44092.5358 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 plaintiff |  | 1 | 18 | 18 | 380 | 22 | 25 | 375 |  | 2020-09-18 12:52 | 44092.5358 | 22 | 25 | 375 |  | low | 2020-09-14 | B20772¦H16 plaintiff¦¦Sep-18-2020 12:51
2020-09-18 12:52 | 44092.536 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Interview room 2 |  | 0 | 17.1 | 27 | 402 | 21.6 | 34.4 | 470 |  | 2020-09-18 12:52 | 44092.536 | 21.6 | 34.4 | 470 |  | low | 2020-09-14 | B10577¦Interview room 2¦¦Sep-18-2020 12:51
2020-09-18 12:52 | 44092.536 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Stair well 3 |  | 0 | 13.8 | 33 | 413 | 17.6 | 30.4 | 412 |  | 2020-09-18 12:52 | 44092.536 | 17.6 | 30.4 | 412 |  | low | 2020-09-14 | B20603¦Stair well 3¦¦Sep-18-2020 12:51
2020-09-18 12:52 | 44092.5364 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 500 W |  | 0 | 15 | 27.2 | 390 | 22.7 | 25.8 | 400 |  | 2020-09-18 12:52 | 44092.5364 | 22.7 | 25.8 | 400 |  | low | 2020-09-14 | B17477¦Courtroom 500 W¦¦Sep-18-2020 12:52
2020-09-18 12:52 | 44092.5364 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 defendant’s |  | 1 | 18 | 18 | 380 | 22 | 25 | 370 |  | 2020-09-18 12:52 | 44092.5364 | 22 | 25 | 370 |  | low | 2020-09-14 | B20772¦H16 defendant’s ¦¦Sep-18-2020 12:52
2020-09-18 12:53 | 44092.5365 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Main entrance |  | 0 | 17.2 | 18 | 434 | 23 | 30.2 | 552 |  | 2020-09-18 12:53 | 44092.5365 | 23 | 30.2 | 552 |  | low | 2020-09-14 | B19890¦Main entrance ¦¦Sep-18-2020 12:52
2020-09-18 12:53 | 44092.5366 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 South |  | 0 | 17.1 | 27 | 402 | 21.4 | 34 | 433 |  | 2020-09-18 12:53 | 44092.5366 | 21.4 | 34 | 433 |  | low | 2020-09-14 | B10577¦Courtroom 3 South ¦¦Sep-18-2020 12:52
2020-09-18 12:53 | 44092.5371 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 500 E |  | 0 | 15 | 27.2 | 390 | 22.9 | 26.6 | 398 |  | 2020-09-18 12:53 | 44092.5371 | 22.9 | 26.6 | 398 |  | low | 2020-09-14 | B17477¦Courtroom 500 E¦¦Sep-18-2020 12:53
2020-09-18 12:53 | 44092.5371 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 East |  | 0 | 17.1 | 27 | 402 | 21.5 | 21.4 | 33.8 | 242 | 2020-09-18 12:53 | 44092.5371 | 21.5 | 21.4 | 33.8 |  | low | 2020-09-14 | B10577¦Courtroom 3 East¦¦Sep-18-2020 12:53
2020-09-18 12:54 | 44092.5373 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Main waiting area |  | 2 | 15.5 | 20.9 | 415 | 20.8 | 21.4 | 507 |  | 2020-09-18 12:54 | 44092.5373 | 20.8 | 21.4 | 507 |  | low | 2020-09-14 | B21554¦Main waiting area¦¦Sep-18-2020 12:53
2020-09-18 12:54 | 44092.5373 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Crown office |  | 1 | 17.2 | 18 | 434 | 23.2 | 30.8 | 554 |  | 2020-09-18 12:54 | 44092.5373 | 23.2 | 30.8 | 554 |  | low | 2020-09-14 | B19890¦Crown office ¦¦Sep-18-2020 12:53
2020-09-18 12:54 | 44092.5375 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Crown attorney office |  | 0 | 8 | 55 | 374 | 21.3 | 38.4 | 533 | No | 2020-09-18 12:54 | 44092.5375 | 21.3 | 38.4 | 533 |  | caution | 2020-09-14 | B20489¦Crown attorney office ¦¦Sep-18-2020 12:53
2020-09-18 12:54 | 44092.5375 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area south |  | 1 | 18 | 18 | 380 | 22 | 23 | 370 |  | 2020-09-18 12:54 | 44092.5375 | 22 | 23 | 370 |  | low | 2020-09-14 | B20772¦Courtroom waiting area south¦¦Sep-18-2020 12:54
2020-09-18 12:54 | 44092.5376 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 North |  | 0 | 17.1 | 27 | 402 | 21.4 | 33.8 | 425 |  | 2020-09-18 12:54 | 44092.5376 | 21.4 | 33.8 | 425 |  | low | 2020-09-14 | B10577¦Courtroom 3 North ¦¦Sep-18-2020 12:54
2020-09-18 12:54 | 44092.5376 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 2 nd floor SE Hall |  | 1 | 9 | 51 | 392 | 23.3 | 36.1 | 508 |  | 2020-09-18 12:54 | 44092.5376 | 23.3 | 36.1 | 508 |  | caution | 2020-09-14 | B20494¦2 nd floor SE Hall¦¦Sep-18-2020 12:54
2020-09-18 12:54 | 44092.5378 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 3 |  | 3 | 8.4 | 54.9 | 371 | 21.9 | 40.4 | 541 |  | 2020-09-18 12:54 | 44092.5378 | 21.9 | 40.4 | 541 |  |  | 2020-09-14 | B20494¦Courtroom 3¦¦Sep-18-2020 12:54
2020-09-18 12:55 | 44092.5381 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area north |  | 1 | 18 | 18 | 380 | 22 | 23 | 367 |  | 2020-09-18 12:55 | 44092.5381 | 22 | 23 | 367 |  | low | 2020-09-14 | B20772¦Courtroom waiting area north¦¦Sep-18-2020 12:54
2020-09-18 12:55 | 44092.5383 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Public seating area 2 |  | 0 | 17.2 | 18 | 434 | 22.4 | 30.3 | 527 |  | 2020-09-18 12:55 | 44092.5383 | 22.4 | 30.3 | 527 |  | low | 2020-09-14 | B19890¦Public seating area 2¦¦Sep-18-2020 12:55
2020-09-18 12:55 | 44092.5385 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 West |  | 0 | 17.1 | 27 | 402 | 21.3 | 33.7 | 424 |  | 2020-09-18 12:55 | 44092.5385 | 21.3 | 33.7 | 424 |  | low | 2020-09-14 | B10577¦Courtroom 3 West¦¦Sep-18-2020 12:55
2020-09-18 12:55 | 44092.5385 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st floor main lobby |  | 6 | 13.5 | 32 | 415 | 22.1 | 23.2 | 471 | no | 2020-09-18 12:55 | 44092.5385 | 22.1 | 23.2 | 471 |  | low | 2020-09-14 | B70496¦1st floor main lobby¦¦Sep-18-2020 12:55
2020-09-18 12:56 | 44092.5389 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Second floor hallway nw |  | 1 | 8.4 | 54.9 | 371 | 22.1 | 40.7 | 530 |  | 2020-09-18 12:56 | 44092.5389 | 22.1 | 40.7 | 530 |  |  | 2020-09-14 | B20494¦Second floor hallway nw¦¦Sep-18-2020 12:55
2020-09-18 12:56 | 44092.5391 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Front desk |  | 3 | 15.5 | 20.9 | 415 | 20.5 | 23 | 550 |  | 2020-09-18 12:56 | 44092.5391 | 20.5 | 23 | 550 |  | low | 2020-09-14 | B21554¦Front desk¦¦Sep-18-2020 12:56
2020-09-18 12:56 | 44092.5391 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Courtroom 1 |  | 0 | 17.2 | 18 | 434 | 22.4 | 26.2 | 458 |  | 2020-09-18 12:56 | 44092.5391 | 22.4 | 26.2 | 458 |  | low | 2020-09-14 | B19890¦Courtroom 1¦¦Sep-18-2020 12:56
2020-09-18 12:56 | 44092.5391 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Crown attorney waiting area |  | 0 | 8 | 55 | 374 | 21.7 | 38.7 | 548 | No | 2020-09-18 12:56 | 44092.5391 | 21.7 | 38.7 | 548 |  | caution | 2020-09-14 | B20489¦Crown attorney waiting area ¦¦Sep-18-2020 12:56
2020-09-18 12:58 | 44092.5401 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st floor hallway |  | 3 | 13.5 | 32 | 415 | 22 | 24 | 419 | no | 2020-09-18 12:58 | 44092.5401 | 22 | 24 | 419 |  | low | 2020-09-14 | B70496¦1st floor hallway¦¦Sep-18-2020 12:57
2020-09-18 12:58 | 44092.5401 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Second floor hallway sw |  | 1 | 8.4 | 54.9 | 371 | 22.3 | 42.4 | 498 |  | 2020-09-18 12:58 | 44092.5401 | 22.3 | 42.4 | 498 |  |  | 2020-09-14 | B20494¦Second floor hallway sw¦¦Sep-18-2020 12:57
2020-09-18 12:58 | 44092.5404 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Main office |  | 2 | 15.5 | 20.9 | 415 | 20.6 | 23.5 | 497 |  | 2020-09-18 12:58 | 44092.5404 | 20.6 | 23.5 | 497 |  | low | 2020-09-14 | B21554¦Main office¦¦Sep-18-2020 12:58
2020-09-18 12:58 | 44092.5405 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Courtroom 2 |  | 0 | 17.2 | 18 | 434 | 22.7 | 24.8 | 470 |  | 2020-09-18 12:58 | 44092.5405 | 22.7 | 24.8 | 470 |  | low | 2020-09-14 | B19890¦Courtroom 2¦¦Sep-18-2020 12:58
2020-09-18 12:58 | 44092.5405 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Criminal justice office |  | 2 | 9 | 51 | 392 | 23.5 | 37.8 | 535 |  | 2020-09-18 12:58 | 44092.5405 | 23.5 | 37.8 | 535 |  | caution | 2020-09-14 | B20494¦Criminal justice office¦¦Sep-18-2020 12:58
2020-09-18 12:59 | 44092.5407 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 2nd floor hallway |  | 0 | 8 | 55 | 374 | 21.8 | 36 | 445 | No | 2020-09-18 12:59 | 44092.5407 | 21.8 | 36 | 445 |  | caution | 2020-09-14 | B20489¦2nd floor hallway ¦¦Sep-18-2020 12:58
2020-09-18 12:59 | 44092.541 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom 4 waiting room |  | 0 | 13.8 | 27.9 | 408 | 21.7 | 42 | 586 |  | 2020-09-18 12:59 | 44092.541 | 21.7 | 42 | 586 |  |  | 2020-09-14 | B90631¦Courtroom 4 waiting room ¦¦Sep-18-2020 12:59
2020-09-18 12:59 | 44092.5412 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 2 |  | 0 | 9 | 51 | 392 |  |  |  | Courtroom 2 - locked | 2020-09-18 12:59 | 44092.5412 | [5 empty] | 2020-09-14 | B20494¦Courtroom 2¦¦Sep-18-2020 12:59
2020-09-18 13:00 | 44092.5416 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Stairwells |  | 0 | 17.2 | 18 | 434 | 22.1 | 30.2 | 512 |  | 2020-09-18 13:00 | 44092.5416 | 22.1 | 30.2 | 512 |  | low | 2020-09-14 | B19890¦Stairwells ¦¦Sep-18-2020 12:59
2020-09-18 13:00 | 44092.5417 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family court counter |  | 1 | 8.4 | 54.9 | 371 | 22.5 | 39.8 | 517 |  | 2020-09-18 13:00 | 44092.5417 | 22.5 | 39.8 | 517 |  | caution | 2020-09-14 | B20494¦Family court counter ¦¦Sep-18-2020 13:00
2020-09-18 13:00 | 44092.5419 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Foyers |  | 1 | 13.6 | 30.5 | 409 | 18 | 35 | 533 |  | 2020-09-18 13:00 | 44092.5419 | 18 | 35 | 533 |  | caution | 2020-09-14 | B20367¦Foyers ¦¦Sep-18-2020 13:00
2020-09-18 13:01 | 44092.5423 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Main hallway |  | 0 | 17.2 | 18 | 434 | 22.2 | 30.8 | 558 |  | 2020-09-18 13:01 | 44092.5423 | 22.2 | 30.8 | 558 |  | low | 2020-09-14 | B19890¦Main hallway ¦¦Sep-18-2020 13:00
2020-09-18 13:01 | 44092.5423 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st floor seating area |  | 1 | 13.5 | 32 | 415 | 21.8 | 25.9 | 412 | no | 2020-09-18 13:01 | 44092.5423 | 21.8 | 25.9 | 412 |  | low | 2020-09-14 | B70496¦1st floor seating area¦¦Sep-18-2020 13:00
2020-09-18 13:02 | 44092.5428 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 101 |  | 1 | 13.5 | 32 | 415 | 21.7 | 22.3 | 408 | no | 2020-09-18 13:02 | 44092.5428 | 21.7 | 22.3 | 408 |  | low | 2020-09-14 | B70496¦101¦¦Sep-18-2020 13:01
2020-09-18 13:02 | 44092.5429 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Motion office |  | 0 | 8 | 55 | 374 | 21.3 | 40.4 | 448 | No | 2020-09-18 13:02 | 44092.5429 | 21.3 | 40.4 | 448 |  |  | 2020-09-14 | B20489¦Motion office ¦¦Sep-18-2020 13:01
2020-09-18 13:02 | 44092.543 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Front lobby |  | 2 | 17.2 | 18 | 434 | 21.5 | 29.4 | 560 |  | 2020-09-18 13:02 | 44092.543 | 21.5 | 29.4 | 560 |  | low | 2020-09-14 | B19890¦Front lobby ¦¦Sep-18-2020 13:01
2020-09-18 13:02 | 44092.543 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 2 nd floor nE hall |  | 1 | 9 | 51 | 392 | 22.5 | 37.9 | 518 |  | 2020-09-18 13:02 | 44092.543 | 22.5 | 37.9 | 518 |  | caution | 2020-09-14 | B20494¦2 nd floor nE hall¦¦Sep-18-2020 13:01
2020-09-18 13:02 | 44092.5433 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Administration |  | 5 | 13.6 | 30.5 | 409 | 21.8 | 34 | 744 |  | 2020-09-18 13:02 | 44092.5433 | 21.8 | 34 | 744 |  | low | 2020-09-14 | B20367¦Administration ¦¦Sep-18-2020 13:02
2020-09-18 13:02 | 44092.5433 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 102 |  | 1 | 13.5 | 32 | 415 | 21.9 | 22 | 405 | no | 2020-09-18 13:02 | 44092.5433 | 21.9 | 22 | 405 |  | low | 2020-09-14 | B70496¦102¦¦Sep-18-2020 13:02
2020-09-18 13:03 | 44092.5437 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 102 |  | 1 | 13.5 | 32 | 415 | 22 | 21.3 | 405 | no | 2020-09-18 13:03 | 44092.5437 | 22 | 21.3 | 405 |  | low | 2020-09-14 | B70496¦102¦¦Sep-18-2020 13:02
2020-09-18 13:03 | 44092.544 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family court office |  | 3 | 8.4 | 54.9 | 371 | 23.2 | 40 | 538 |  | 2020-09-18 13:03 | 44092.544 | 23.2 | 40 | 538 |  | caution | 2020-09-14 | B20494¦Family court office¦¦Sep-18-2020 13:03
2020-09-18 13:03 | 44092.5441 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom 2 |  | 4 | 16 | 24.1 | 393 | 19.8 | 28.6 | 456 |  | 2020-09-18 13:04 | 44092.5441 | 19.8 | 28.6 | 456 |  | low | 2020-09-14 | B90558¦Courtroom 2¦¦Sep-18-2020 13:03
2020-09-18 13:04 | 44092.5442 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Administration |  | 5 | 13.6 | 30.5 | 409 | 22.5 | 31 | 652 |  | 2020-09-18 13:04 | 44092.5442 | 22.5 | 31 | 652 |  | low | 2020-09-14 | B20367¦Administration ¦¦Sep-18-2020 13:03
2020-09-18 13:04 | 44092.5447 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Main entry |  | 5 | 9 | 51 | 392 | 23 | 37.3 | 517 |  | 2020-09-18 13:04 | 44092.5447 | 23 | 37.3 | 517 |  | caution | 2020-09-14 | B20494¦Main entry¦¦Sep-18-2020 13:04
2020-09-18 13:05 | 44092.545 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | stairwell |  | 1 | 13.5 | 32 | 415 | 22.7 | 26.3 | 490 | no | 2020-09-18 13:05 | 44092.545 | 22.7 | 26.3 | 490 |  | low | 2020-09-14 | B70496¦stairwell¦¦Sep-18-2020 13:04
2020-09-18 13:05 | 44092.5453 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 1 |  | 0 | 13.6 | 30.5 | 409 | 22 | 24.9 | 465 |  | 2020-09-18 13:05 | 44092.5453 | 22 | 24.9 | 465 |  | low | 2020-09-14 | B20367¦Waiting room 1¦¦Sep-18-2020 13:05
2020-09-18 13:06 | 44092.5457 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 2nd floor elevator lobby |  | 2 | 13.5 | 32 | 415 | 23 | 25.5 | 550 | no | 2020-09-18 13:06 | 44092.5457 | 23 | 25.5 | 550 |  | low | 2020-09-14 | B70496¦2nd floor elevator lobby¦¦Sep-18-2020 13:05
2020-09-18 13:06 | 44092.5458 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Waiting area 2 floor |  | 1 | 16 | 24.1 | 393 | 21.2 | 30 | 450 |  | 2020-09-18 13:06 | 44092.5458 | 21.2 | 30 | 450 |  | low | 2020-09-14 | B90558¦Waiting area 2 floor¦¦Sep-18-2020 13:05
2020-09-18 13:06 | 44092.5461 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judges chamber Foyers |  | 0 | 13.6 | 30.5 | 409 | 22 | 31 | 469 |  | 2020-09-18 13:06 | 44092.5461 | 22 | 31 | 469 |  | low | 2020-09-14 | B20367¦Judges chamber Foyers ¦¦Sep-18-2020 13:06
2020-09-18 13:07 | 44092.5462 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family court common |  | 1 | 8.4 | 54.9 | 371 | 23.1 | 38 | 522 |  | 2020-09-18 13:07 | 44092.5462 | 23.1 | 38 | 522 |  | caution | 2020-09-14 | B20494¦Family court common ¦¦Sep-18-2020 13:06
2020-09-18 13:07 | 44092.5464 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 3rd floor hallway |  | 0 | 8 | 55 | 374 | 22.5 | 39.9 | 490 | No | 2020-09-18 13:07 | 44092.5464 | 22.5 | 39.9 | 490 |  | caution | 2020-09-14 | B20489¦3rd floor hallway ¦¦Sep-18-2020 13:06
2020-09-18 13:07 | 44092.5464 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 204 |  | 1 | 13.5 | 32 | 415 | 22 | 22.1 | 451 | no | 2020-09-18 13:07 | 44092.5464 | 22 | 22.1 | 451 |  | low | 2020-09-14 | B70496¦204¦¦Sep-18-2020 13:06
2020-09-18 13:07 | 44092.5468 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judges chamber foyers |  | 0 | 13.6 | 30.5 | 409 | 22.5 | 31 | 470 |  | 2020-09-18 13:07 | 44092.5468 | 22.5 | 31 | 470 |  | low | 2020-09-14 | B20367¦Judges chamber foyers ¦¦Sep-18-2020 13:07
2020-09-18 13:07 | 44092.5469 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 204 |  | 1 | 13.5 | 32 | 415 | 22.3 | 25.1 | 584 | no | 2020-09-18 13:08 | 44092.5469 | 22.3 | 25.1 | 584 |  | low | 2020-09-14 | B70496¦204¦¦Sep-18-2020 13:07
2020-09-18 13:08 | 44092.5471 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 4 |  | 2 | 9 | 51 | 392 | 22.7 | 33.9 | 465 |  | 2020-09-18 13:08 | 44092.5471 | 22.7 | 33.9 | 465 |  | low | 2020-09-14 | B20494¦Courtroom 4¦¦Sep-18-2020 13:07
2020-09-18 13:08 | 44092.5474 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judicial stairwell |  | 0 | 13.6 | 30.5 | 409 | 22.3 | 37 | 474 |  | 2020-09-18 13:08 | 44092.5474 | 22.3 | 37 | 474 |  | caution | 2020-09-14 | B20367¦Judicial stairwell ¦¦Sep-18-2020 13:08
2020-09-18 13:09 | 44092.548 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family court east |  | 2 | 8.4 | 54.9 | 371 | 23.1 | 39.3 | 525 |  | 2020-09-18 13:09 | 44092.548 | 23.1 | 39.3 | 525 |  | caution | 2020-09-14 | B20494¦Family court east¦¦Sep-18-2020 13:09
2020-09-18 13:09 | 44092.5481 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Jury room |  | 0 | 8 | 55 | 374 | 22.5 | 38.5 | 451 | No | 2020-09-18 13:09 | 44092.5481 | 22.5 | 38.5 | 451 |  | caution | 2020-09-14 | B20489¦Jury room ¦¦Sep-18-2020 13:09
2020-09-18 13:10 | 44092.5483 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Judges chamber courtroom 1 |  | 0 | 13.6 | 36.4 | 409 | 22 | 36 | 471 |  | 2020-09-18 13:10 | 44092.5483 | 22 | 36 | 471 |  | caution | 2020-09-14 | B20367¦Judges chamber courtroom 1¦¦Sep-18-2020 13:09
2020-09-18 13:10 | 44092.5484 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom 1 |  | 0 | 16 | 24.1 | 393 | 21.6 | 28.4 | 496 |  | 2020-09-18 13:10 | 44092.5484 | 21.6 | 28.4 | 496 |  | low | 2020-09-14 | B90558¦Courtroom 1¦¦Sep-18-2020 13:09
2020-09-18 13:11 | 44092.5494 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 1 |  | 0 | 13.6 | 30.5 | 409 | 22 | 28.5 | 434 |  | 2020-09-18 13:11 | 44092.5494 | 22 | 28.5 | 434 |  | low | 2020-09-14 | B20367¦Courtroom 1¦¦Sep-18-2020 13:11
2020-09-18 13:11 | 44092.5496 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 5 |  | 1 | 8.4 | 54.9 | 371 |  |  |  | Door locked, no access | 2020-09-18 13:11 | 44092.5496 | [5 empty] | 2020-09-14 | B20494¦Courtroom 5¦¦Sep-18-2020 13:11
2020-09-18 13:12 | 44092.5497 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 2nd floor hallway |  | 1 | 13.5 | 32 | 415 | 22.7 | 24.2 | 489 | no | 2020-09-18 13:12 | 44092.5497 | 22.7 | 24.2 | 489 |  | low | 2020-09-14 | B70496¦2nd floor hallway¦¦Sep-18-2020 13:11
2020-09-18 13:12 | 44092.5498 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Interview room 2 |  | 1 | 9 | 51 | 392 | 22.8 | 33.6 | 456 |  | 2020-09-18 13:12 | 44092.5498 | 22.8 | 33.6 | 456 |  | low | 2020-09-14 | B20494¦Interview room 2¦¦Sep-18-2020 13:11
2020-09-18 13:12 | 44092.5503 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 203 |  | 1 | 13.5 | 32 | 415 | 22.1 | 28.2 | 483 | no | 2020-09-18 13:12 | 44092.5503 | 22.1 | 28.2 | 483 |  | low | 2020-09-14 | B70496¦203¦¦Sep-18-2020 13:12
2020-09-18 13:12 | 44092.5503 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom 3 |  | 0 | 16 | 24.1 | 393 | 21.5 | 27 | 451 |  | 2020-09-18 13:12 | 44092.5503 | 21.5 | 27 | 451 |  | low | 2020-09-14 | B90558¦Courtroom 3¦¦Sep-18-2020 13:12
2020-09-18 13:13 | 44092.5508 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 202 |  | 2 | 13.5 | 32 | 415 | 22 | 23.6 | 476 | no | 2020-09-18 13:13 | 44092.5508 | 22 | 23.6 | 476 |  | low | 2020-09-14 | B70496¦202¦¦Sep-18-2020 13:13
2020-09-18 13:13 | 44092.551 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Private room |  | 0 | 8 | 55 | 374 | 22.2 | 41.5 | 434 | No | 2020-09-18 13:13 | 44092.551 | 22.2 | 41.5 | 434 |  |  | 2020-09-14 | B20489¦Private room ¦¦Sep-18-2020 13:13
2020-09-18 13:14 | 44092.5511 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway ne |  | 1 | 8.4 | 53.9 | 371 | 22.8 | 37.6 | 486 |  | 2020-09-18 13:14 | 44092.5511 | 22.8 | 37.6 | 486 |  | caution | 2020-09-14 | B20494¦Third floor hallway ne¦¦Sep-18-2020 13:13
2020-09-18 13:14 | 44092.5511 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Interview room 1 |  | 1 | 9 | 51 | 392 | 22.7 | 33 | 465 |  | 2020-09-18 13:14 | 44092.5511 | 22.7 | 33 | 465 |  | low | 2020-09-14 | B20494¦Interview room 1¦¦Sep-18-2020 13:13
2020-09-18 13:14 | 44092.5513 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 2 |  | 0 | 13.6 | 30.5 | 409 | 21.5 | 24.7 | 455 |  | 2020-09-18 13:14 | 44092.5513 | 21.5 | 24.7 | 455 |  | low | 2020-09-14 | B20367¦Waiting room 2¦¦Sep-18-2020 13:13
2020-09-18 13:14 | 44092.5513 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 201 |  | 1 | 13.5 | 32 | 415 | 21.7 | 24.3 | 461 | no | 2020-09-18 13:14 | 44092.5513 | 21.7 | 24.3 | 461 |  | low | 2020-09-14 | B70496¦201¦¦Sep-18-2020 13:13
2020-09-18 13:15 | 44092.5518 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice Letourneau office |  | 0 | 16 | 24.1 | 393 | 22.7 | 32 | 465 |  | 2020-09-18 13:15 | 44092.5518 | 22.7 | 32 | 465 |  | low | 2020-09-14 | B90558¦Justice Letourneau office¦¦Sep-18-2020 13:14
2020-09-18 13:15 | 44092.5519 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | Administration office |  | 3 | 13.5 | 32 | 415 | 21.6 | 27.6 | 525 | no | 2020-09-18 13:15 | 44092.5519 | 21.6 | 27.6 | 525 |  | low | 2020-09-14 | B70496¦Administration office¦¦Sep-18-2020 13:14
2020-09-18 13:15 | 44092.552 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | 301 |  | 0 | 13.6 | 30.5 | 409 | 21.6 | 24.7 | 446 |  | 2020-09-18 13:15 | 44092.552 | 21.6 | 24.7 | 446 |  | low | 2020-09-14 | B20367¦301¦¦Sep-18-2020 13:14
2020-09-18 13:15 | 44092.5521 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Entrance |  | 0 | 15 | 21 | 396 | 17.5 | 31.6 | 555 |  | 2020-09-18 13:15 | 44092.5521 | 17.5 | 31.6 | 555 |  | low | 2020-09-14 | B16187¦Entrance ¦¦Sep-18-2020 13:15
2020-09-18 13:15 | 44092.5524 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway se |  | 3 | 8.4 | 54.9 | 371 | 23.5 | 36.5 | 491 |  | 2020-09-18 13:15 | 44092.5524 | 23.5 | 36.5 | 491 |  | caution | 2020-09-14 | B20494¦Third floor hallway se¦¦Sep-18-2020 13:15
2020-09-18 13:16 | 44092.5527 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Court room 1 judge's desk |  | 0 | 8 | 55 | 374 | 22.6 | 40.9 | 423 | No | 2020-09-18 13:16 | 44092.5527 | 22.6 | 40.9 | 423 |  |  | 2020-09-14 | B20489¦Court room 1 judge's desk ¦¦Sep-18-2020 13:15
2020-09-18 13:16 | 44092.5527 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 4 | 15 | 21 | 396 | 20.8 | 25 | 616 |  | 2020-09-18 13:16 | 44092.5527 | 20.8 | 25 | 616 |  | low | 2020-09-14 | B16187¦Court 3¦¦Sep-18-2020 13:15
2020-09-18 13:16 | 44092.5528 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | Outside customer service entrance |  | 1 | 13.5 | 32 | 415 | 11.1 | 42 | 457 | no | 2020-09-18 13:16 | 44092.5528 | 11.1 | 42 | 457 |  |  | 2020-09-14 | B70496¦Outside customer service entrance¦¦Sep-18-2020 13:16
2020-09-18 13:16 | 44092.5529 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | Outside Customer Service Entrance |  | 1 | 11.4 | 44 | 420 | 9 | 56 | 401 | no | 2020-09-18 13:16 | 44092.5529 | 9 | 56 | 401 |  |  | 2020-09-14 | B70496¦Outside Customer Service Entrance ¦¦Sep-18-2020 13:16
2020-09-18 13:16 | 44092.5529 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice Wheeler office |  | 0 | 16 | 24.1 | 393 | 21.5 | 32 | 463 |  | 2020-09-18 13:16 | 44092.5529 | 21.5 | 32 | 463 |  | low | 2020-09-14 | B90558¦Justice Wheeler office¦¦Sep-18-2020 13:16
2020-09-18 13:16 | 44092.553 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 2 |  | 0 | 13.6 | 30.5 | 409 | 21.3 | 26.3 | 439 |  | 2020-09-18 13:16 | 44092.553 | 21.3 | 26.3 | 439 |  | low | 2020-09-14 | B20367¦Courtroom 2¦¦Sep-18-2020 13:16
2020-09-18 13:17 | 44092.5531 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 4 | 15 | 21 | 396 | 21.2 | 24.1 | 598 |  | 2020-09-18 13:16 | 44092.5531 | 21.2 | 24.1 | 598 |  | low | 2020-09-14 | B16187¦Court 3¦¦Sep-18-2020 13:16
2020-09-18 13:17 | 44092.5536 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 3 |  | 4 | 15 | 21 | 396 | 21.4 | 23.4 | 609 |  | 2020-09-18 13:17 | 44092.5536 | 21.4 | 23.4 | 609 |  | low | 2020-09-14 | B16187¦Court 3¦¦Sep-18-2020 13:17
2020-09-18 13:17 | 44092.5537 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Family services |  | 1 | 9 | 51 | 392 | 22.2 | 40.9 | 469 |  | 2020-09-18 13:17 | 44092.5537 | 22.2 | 40.9 | 469 |  |  | 2020-09-14 | B20494¦Family services ¦¦Sep-18-2020 13:17
2020-09-18 13:17 | 44092.5538 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office a |  | 0 | 13.6 | 30.5 | 409 | 21.6 | 27.8 | 433 |  | 2020-09-18 13:17 | 44092.5538 | 21.6 | 27.8 | 433 |  | low | 2020-09-14 | B20367¦Office a¦¦Sep-18-2020 13:17
2020-09-18 13:18 | 44092.554 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 4 |  | 0 | 15 | 21 | 396 | 22.2 | 21.5 | 497 |  | 2020-09-18 13:18 | 44092.554 | 22.2 | 21.5 | 497 |  | low | 2020-09-14 | B16187¦Court 4¦¦Sep-18-2020 13:17
2020-09-18 13:18 | 44092.5541 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | Court room 1 gallery |  | 0 | 8 | 55 | 374 | 22.8 | 40.6 | 419 | No | 2020-09-18 13:18 | 44092.5541 | 22.8 | 40.6 | 419 |  |  | 2020-09-14 | B20489¦Court room 1 gallery ¦¦Sep-18-2020 13:17
2020-09-18 13:18 | 44092.5543 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | TC office |  | 1 | 16 | 24.1 | 393 | 21.1 | 32.9 | 490 |  | 2020-09-18 13:18 | 44092.5543 | 21.1 | 32.9 | 490 |  | low | 2020-09-14 | B90558¦TC office¦¦Sep-18-2020 13:18
2020-09-18 13:18 | 44092.5544 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 15 | 21 | 396 | 22.4 | 21.8 | 462 |  | 2020-09-18 13:18 | 44092.5544 | 22.4 | 21.8 | 462 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 13:18
2020-09-18 13:18 | 44092.5545 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway nw |  | 1 | 8.4 | 54.9 | 371 | 22.7 | 37.2 | 458 |  | 2020-09-18 13:18 | 44092.5545 | 22.7 | 37.2 | 458 |  | caution | 2020-09-14 | B20494¦Third floor hallway nw¦¦Sep-18-2020 13:18
2020-09-18 13:19 | 44092.5547 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 3 |  | 1 | 13.6 | 30.5 | 409 | 22 | 29.7 | 451 |  | 2020-09-18 13:19 | 44092.5547 | 22 | 29.7 | 451 |  | low | 2020-09-14 | B20367¦Courtroom 3¦¦Sep-18-2020 13:18
2020-09-18 13:19 | 44092.5547 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 15 | 21 | 396 | 22.1 | 22.1 | 471 |  | 2020-09-18 13:19 | 44092.5547 | 22.1 | 22.1 | 471 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 13:18
2020-09-18 13:19 | 44092.5551 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 15 | 21 | 396 | 22.5 | 22 | 467 |  | 2020-09-18 13:19 | 44092.5551 | 22.5 | 22 | 467 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 13:19
2020-09-18 13:19 | 44092.5551 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Library |  | 0 | 16 | 24.1 | 393 | 21 | 30.2 | 436 |  | 2020-09-18 13:19 | 44092.5551 | 21 | 30.2 | 436 |  | low | 2020-09-14 | B90558¦Library¦¦Sep-18-2020 13:19
2020-09-18 13:20 | 44092.5554 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 15 | 21 | 396 | 22.3 | 20.9 | 462 |  | 2020-09-18 13:20 | 44092.5554 | 22.3 | 20.9 | 462 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 13:19
2020-09-18 13:20 | 44092.5554 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office b |  | 0 | 13.6 | 30.5 | 409 | 22.2 | 25.5 | 441 |  | 2020-09-18 13:20 | 44092.5554 | 22.2 | 25.5 | 441 |  | low | 2020-09-14 | B20367¦Office b ¦¦Sep-18-2020 13:19
2020-09-18 13:20 | 44092.5558 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 15 | 21 | 396 | 21.8 | 19 | 469 |  | 2020-09-18 13:20 | 44092.5558 | 21.8 | 19 | 469 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 13:20
2020-09-18 13:20 | 44092.5558 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 3rd floor hallway south |  | 0 | 8 | 55 | 374 | 22.6 | 39 | 474 | No | 2020-09-18 13:20 | 44092.5558 | 22.6 | 39 | 474 |  | caution | 2020-09-14 | B20489¦3rd floor hallway south ¦¦Sep-18-2020 13:20
2020-09-18 13:20 | 44092.5558 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom#1 |  | 2 | 15.5 | 20.9 | 415 | 20.7 | 26.4 | 722 |  | 2020-09-18 13:20 | 44092.5558 | 20.7 | 26.4 | 722 |  | low | 2020-09-14 | B21554¦Courtroom#1¦¦Sep-18-2020 13:20
2020-09-18 13:21 | 44092.5561 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Office c |  | 0 | 13.6 | 30.5 | 409 | 21.9 | 25 | 433 |  | 2020-09-18 13:21 | 44092.5561 | 21.9 | 25 | 433 |  | low | 2020-09-14 | B20367¦Office c¦¦Sep-18-2020 13:20
2020-09-18 13:21 | 44092.5561 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Fire pump |  | 1 | 9 | 51 | 392 | 23.3 | 41.7 | 460 |  | 2020-09-18 13:21 | 44092.5561 | 23.3 | 41.7 | 460 |  |  | 2020-09-14 | B20494¦Fire pump¦¦Sep-18-2020 13:20
2020-09-18 13:21 | 44092.5563 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 1 |  | 0 | 15 | 21 | 396 | 21.7 | 18 | 455 |  | 2020-09-18 13:21 | 44092.5563 | 21.7 | 18 | 455 |  | low | 2020-09-14 | B16187¦Court 1¦¦Sep-18-2020 13:21
2020-09-18 13:21 | 44092.5564 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice O'Brien office |  | 0 | 16 | 24.1 | 393 | 20.3 | 35.4 | 472 | Dehumidifier running set at 17 | 2020-09-18 13:21 | 44092.5564 | 20.3 | 35.4 | 472 |  | caution | 2020-09-14 | B90558¦Justice O'Brien office¦¦Sep-18-2020 13:21
2020-09-18 13:22 | 44092.5567 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 15 | 21 | 396 | 22.1 | 22.4 | 392 |  | 2020-09-18 13:22 | 44092.5567 | 22.1 | 22.4 | 392 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 13:21
2020-09-18 13:22 | 44092.5568 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 306 |  | 0 | 11 | 45 | 377 | 22.8 | 30.9 | 404 | No | 2020-09-18 13:22 | 44092.5568 | 22.8 | 30.9 | 404 |  | low | 2020-09-14 | B14660¦306¦¦Sep-18-2020 13:21
2020-09-18 13:22 | 44092.5569 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Third floor hallway sw |  | 1 | 8.4 | 54.9 | 371 | 24.7 | 32.6 | 458 |  | 2020-09-18 13:22 | 44092.5569 | 24.7 | 32.6 | 458 |  | low | 2020-09-14 | B20494¦Third floor hallway sw¦¦Sep-18-2020 13:21
2020-09-18 13:22 | 44092.557 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 15 | 21 | 396 | 22.3 | 22.4 | 559 |  | 2020-09-18 13:22 | 44092.557 | 22.3 | 22.4 | 559 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 13:22
2020-09-18 13:22 | 44092.5572 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom#2 |  | 1 | 15.5 | 20.9 | 415 | 21.1 | 21 | 450 |  | 2020-09-18 13:22 | 44092.5572 | 21.1 | 21 | 450 |  | low | 2020-09-14 | B21554¦Courtroom#2¦¦Sep-18-2020 13:22
2020-09-18 13:23 | 44092.5573 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 15 | 21 | 396 | 22.3 | 21.9 | 571 |  | 2020-09-18 13:23 | 44092.5573 | 22.3 | 21.9 | 571 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 13:22
2020-09-18 13:23 | 44092.5575 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Waiting room 3 |  | 0 | 13.6 | 30.5 | 409 | 22 | 26.8 | 440 |  | 2020-09-18 13:23 | 44092.5575 | 22 | 26.8 | 440 |  | low | 2020-09-14 | B20367¦Waiting room 3¦¦Sep-18-2020 13:22
2020-09-18 13:24 | 44092.5582 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | 402b |  | 0 | 13.6 | 30.5 | 409 | 22.5 | 27.5 | 446 |  | 2020-09-18 13:24 | 44092.5582 | 22.5 | 27.5 | 446 |  | low | 2020-09-14 | B20367¦402b¦¦Sep-18-2020 13:23
2020-09-18 13:24 | 44092.5583 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | OPP |  | 0 | 15 | 21 | 396 | 22.4 | 22.1 | 555 |  | 2020-09-18 13:24 | 44092.5583 | 22.4 | 22.1 | 555 |  | low | 2020-09-14 | B16187¦OPP¦¦Sep-18-2020 13:23
2020-09-18 13:24 | 44092.5584 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Administrative office |  | 2 | 16 | 24.1 | 393 | 21 | 29.3 | 455 |  | 2020-09-18 13:24 | 44092.5584 | 21 | 29.3 | 455 |  | low | 2020-09-14 | B90558¦Administrative office¦¦Sep-18-2020 13:24
2020-09-18 13:25 | 44092.5589 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom #3 |  | 5 | 15.5 | 20.9 | 415 | 21.9 | 29 | 700 |  | 2020-09-18 13:25 | 44092.5589 | 21.9 | 29 | 700 |  | low | 2020-09-14 | B21554¦Courtroom #3¦¦Sep-18-2020 13:24
2020-09-18 13:25 | 44092.5589 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | OPP |  | 0 | 15 | 21 | 396 | 22.5 | 20.5 | 529 |  | 2020-09-18 13:25 | 44092.5589 | 22.5 | 20.5 | 529 |  | low | 2020-09-14 | B16187¦OPP¦¦Sep-18-2020 13:24
2020-09-18 13:25 | 44092.559 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | 402a |  | 0 | 13.6 | 30.5 | 409 | 22.6 | 26.5 | 449 |  | 2020-09-18 13:25 | 44092.559 | 22.6 | 26.5 | 449 |  | low | 2020-09-14 | B20367¦402a¦¦Sep-18-2020 13:24
2020-09-18 13:25 | 44092.5593 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 1 east |  | 1 | 8.4 | 54.9 | 371 | 22.4 | 25.2 | 386 |  | 2020-09-18 13:25 | 44092.5593 | 22.4 | 25.2 | 386 |  | low | 2020-09-14 | B20494¦Courtroom 1 east¦¦Sep-18-2020 13:25
2020-09-18 13:25 | 44092.5593 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Crown attorney |  | 0 | 15 | 21 | 396 | 22.2 | 20.3 | 485 |  | 2020-09-18 13:25 | 44092.5593 | 22.2 | 20.3 | 485 |  | low | 2020-09-14 | B16187¦Crown attorney ¦¦Sep-18-2020 13:25
2020-09-18 13:26 | 44092.5595 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney office |  | 2 | 9 | 51 | 392 | 22.8 | 44.2 | 525 |  | 2020-09-18 13:26 | 44092.5595 | 22.8 | 44.2 | 525 |  |  | 2020-09-14 | B20494¦Crown attorney office ¦¦Sep-18-2020 13:25
2020-09-18 13:26 | 44092.5595 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Front lobby |  | 2 | 17.8 | 17.7 | 437 | 18.2 | 38.1 | 495 |  | 2020-09-18 13:26 | 44092.5595 | 18.2 | 38.1 | 495 |  | caution | 2020-09-14 | B25477¦Front lobby ¦¦Sep-18-2020 13:25
2020-09-18 13:26 | 44092.5597 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 2 |  | 0 | 15 | 21 | 396 | 22.5 | 20.6 | 475 |  | 2020-09-18 13:26 | 44092.5597 | 22.5 | 20.6 | 475 |  | low | 2020-09-14 | B16187¦Court 2¦¦Sep-18-2020 13:26
2020-09-18 13:27 | 44092.5601 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Court 2 |  | 0 | 15 | 21 | 396 | 21.9 | 19.3 | 463 |  | 2020-09-18 13:27 | 44092.5601 | 21.9 | 19.3 | 463 |  | low | 2020-09-14 | B16187¦Court 2¦¦Sep-18-2020 13:26
2020-09-18 13:27 | 44092.5602 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney library |  | 1 | 9 | 51 | 392 | 22.8 | 43.5 | 513 |  | 2020-09-18 13:27 | 44092.5602 | 22.8 | 43.5 | 513 |  |  | 2020-09-14 | B20494¦Crown attorney library¦¦Sep-18-2020 13:26
2020-09-18 13:27 | 44092.5606 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 15 | 21 | 396 | 21.2 | 20.7 | 460 |  | 2020-09-18 13:27 | 44092.5606 | 21.2 | 20.7 | 460 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 13:27
2020-09-18 13:27 | 44092.5607 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | HR |  | 2 | 17.8 | 17.7 | 437 | 20 | 33.7 | 501 |  | 2020-09-18 13:27 | 44092.5607 | 20 | 33.7 | 501 |  | low | 2020-09-14 | B25477¦HR¦¦Sep-18-2020 13:27
2020-09-18 13:28 | 44092.5609 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 15 | 21 | 396 | 22.4 | 27 | 505 |  | 2020-09-18 13:28 | 44092.5609 | 22.4 | 27 | 505 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 13:27
2020-09-18 13:28 | 44092.561 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney printer room |  | 2 | 9 | 51 | 392 | 22.8 | 44.6 | 525 |  | 2020-09-18 13:28 | 44092.561 | 22.8 | 44.6 | 525 |  |  | 2020-09-14 | B20494¦Crown attorney printer room¦¦Sep-18-2020 13:27
2020-09-18 13:28 | 44092.5612 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 15 | 21 | 396 | 22.5 | 26.3 | 557 |  | 2020-09-18 13:28 | 44092.5612 | 22.5 | 26.3 | 557 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 13:28
2020-09-18 13:28 | 44092.5613 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | 1st Floor front door lobby |  | 4 | 18.1 | 29 | 385 | 23.7 | 25.9 | 612 |  | 2020-09-18 13:28 | 44092.5613 | 23.7 | 25.9 | 612 |  | low | 2020-09-14 | B70277¦1st Floor front door lobby¦¦Sep-18-2020 13:28
2020-09-18 13:29 | 44092.5616 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Cell waiting area |  | 0 | 15 | 21 | 396 | 21.8 | 22.2 | 501 |  | 2020-09-18 13:29 | 44092.5616 | 21.8 | 22.2 | 501 |  | low | 2020-09-14 | B16187¦Cell waiting area ¦¦Sep-18-2020 13:28
2020-09-18 13:29 | 44092.5619 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Basement hallway |  | 0 | 15 | 21 | 396 | 21.7 | 26.3 | 483 |  | 2020-09-18 13:29 | 44092.5619 | 21.7 | 26.3 | 483 |  | low | 2020-09-14 | B16187¦Basement hallway ¦¦Sep-18-2020 13:29
2020-09-18 13:29 | 44092.5619 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 1 west |  | 1 | 8.4 | 54.9 | 371 | 22.6 | 25.2 | 377 |  | 2020-09-18 13:29 | 44092.5619 | 22.6 | 25.2 | 377 |  | low | 2020-09-14 | B20494¦Courtroom 1 west¦¦Sep-18-2020 13:29
2020-09-18 13:30 | 44092.5622 | AINSWORTH | B16187 | B16187 - 3 Dominion St - Bracebridge | Common |  | 0 | 15 | 21 | 396 | 21.8 | 29.3 | 490 |  | 2020-09-18 13:30 | 44092.5622 | 21.8 | 29.3 | 490 |  | low | 2020-09-14 | B16187¦Common ¦¦Sep-18-2020 13:29
2020-09-18 13:30 | 44092.5623 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | 1st Floor front door lobby |  | 2 | 14.6 | 21 | 371 | 19.6 | 34.8 | 690 |  | 2020-09-18 13:30 | 44092.5623 | 19.6 | 34.8 | 690 |  | low | 2020-09-14 | B70277¦1st Floor front door lobby¦¦Sep-18-2020 13:29
2020-09-18 13:31 | 44092.5634 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Courtroom 1 west |  | 1 | 8.4 | 54.9 | 371 | 22.6 | 25.2 | 377 |  | 2020-09-18 13:31 | 44092.5634 | 22.6 | 25.2 | 377 |  | low | 2020-09-14 | B20494¦Courtroom 1 west¦¦Sep-18-2020 13:31
2020-09-18 13:32 | 44092.5637 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Crown attorney waiting room |  | 1 | 9 | 51 | 392 | 23.4 | 40.5 | 494 |  | 2020-09-18 13:32 | 44092.5637 | 23.4 | 40.5 | 494 |  |  | 2020-09-14 | B20494¦Crown attorney waiting room ¦¦Sep-18-2020 13:31
2020-09-18 13:32 | 44092.564 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | ED office |  | 4 | 17.8 | 17.7 | 437 | 21.7 | 29.3 | 534 |  | 2020-09-18 13:32 | 44092.564 | 21.7 | 29.3 | 534 |  | low | 2020-09-14 | B25477¦ED office ¦¦Sep-18-2020 13:32
2020-09-18 13:32 | 44092.564 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Inside elevator 3rd floor |  | 1 | 14.6 | 21 | 371 | 20.7 | 31.4 | 490 |  | 2020-09-18 13:32 | 44092.564 | 20.7 | 31.4 | 490 |  | low | 2020-09-14 | B70277¦Inside elevator 3rd floor¦¦Sep-18-2020 13:32
2020-09-18 13:33 | 44092.5648 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Courtroom 5 |  | 1 | 13.6 | 30.5 | 409 |  |  |  | No access | 2020-09-18 13:33 | 44092.5648 | [5 empty] | 2020-09-14 | B20367¦Courtroom 5¦¦Sep-18-2020 13:33
2020-09-18 13:33 | 44092.5649 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | 1 st floor hall by elevator |  | 1 | 9 | 51 | 392 | 23.6 | 37.3 | 470 |  | 2020-09-18 13:33 | 44092.5649 | 23.6 | 37.3 | 470 |  | caution | 2020-09-14 | B20494¦1 st floor hall by elevator ¦¦Sep-18-2020 13:33
2020-09-18 13:34 | 44092.5654 | AINSWORTH | B20367 | B20367 - 207 Cayley St - Walkerton | Court operations |  | 2 | 13.6 | 30.5 | 409 | 21.3 | 26 | 506 |  | 2020-09-18 13:34 | 44092.5654 | 21.3 | 26 | 506 |  | low | 2020-09-14 | B20367¦Court operations ¦¦Sep-18-2020 13:34
2020-09-18 13:34 | 44092.5655 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 128 |  | 0 | 14 | 25 | 375 | 17.5 | 31.5 | 379 | No | 2020-09-18 13:34 | 44092.5655 | 17.5 | 31.5 | 379 |  | low | 2020-09-14 | B14660¦128¦¦Sep-18-2020 13:34
2020-09-18 13:36 | 44092.5664 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Lunch room |  | 0 | 13.6 | 30.5 | 409 | 20 | 49.4 | 581 |  | 2020-09-18 13:36 | 44092.5664 | 20 | 49.4 | 581 |  |  | 2020-09-14 | B90631¦Lunch room ¦¦Sep-18-2020 13:35
2020-09-18 13:36 | 44092.5668 | AINSWORTH | B20494 | B20494 - 415 Hunter St - Woodstock | Cell block |  | 1 | 9 | 51 | 392 | 22.8 | 37.9 | 457 |  | 2020-09-18 13:36 | 44092.5668 | 22.8 | 37.9 | 457 |  | caution | 2020-09-14 | B20494¦Cell block¦¦Sep-18-2020 13:36
2020-09-18 13:37 | 44092.5672 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom waiting room - right side |  | 1 | 14.6 | 21 | 371 | 22.6 | 23.7 | 394 |  | 2020-09-18 13:37 | 44092.5672 | 22.6 | 23.7 | 394 |  | low | 2020-09-14 | B70277¦Courtroom waiting room - right side¦¦Sep-18-2020 13:36
2020-09-18 13:38 | 44092.5678 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Case management |  | 2 | 13.6 | 30.5 | 409 | 20.9 | 44.5 | 804 |  | 2020-09-18 13:38 | 44092.5678 | 20.9 | 44.5 | 804 |  |  | 2020-09-14 | B90631¦Case management ¦¦Sep-18-2020 13:37
2020-09-18 13:38 | 44092.5678 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom waiting room - left side |  | 1 | 14.6 | 21 | 371 | 22.7 | 23.6 | 394 |  | 2020-09-18 13:38 | 44092.5678 | 22.7 | 23.6 | 394 |  | low | 2020-09-14 | B70277¦Courtroom waiting room - left side¦¦Sep-18-2020 13:37
2020-09-18 13:38 | 44092.5684 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Front Lobby |  | 2 | 15.4 | 26.2 | 385 | 22.6 | 23.2 | 423 |  | 2020-09-18 13:38 | 44092.5684 | 22.6 | 23.2 | 423 |  | low | 2020-09-14 | B20550¦Front Lobby¦¦Sep-18-2020 13:38
2020-09-18 13:39 | 44092.5686 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 001 |  | 0 | 14 | 25 | 375 | 20.4 | 38.2 | 412 | No | 2020-09-18 13:39 | 44092.5686 | 20.4 | 38.2 | 412 |  | caution | 2020-09-14 | B14660¦001¦¦Sep-18-2020 13:38
2020-09-18 13:39 | 44092.5686 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Crown office 1 |  | 0 | 13.6 | 30.5 | 409 | 22 | 48 | 690 |  | 2020-09-18 13:39 | 44092.5686 | 22 | 48 | 690 |  |  | 2020-09-14 | B90631¦Crown office 1¦¦Sep-18-2020 13:38
2020-09-18 13:39 | 44092.5688 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - facing the judge, back right |  | 2 | 14.6 | 21 | 371 | 22.6 | 23.3 | 393 |  | 2020-09-18 13:39 | 44092.5688 | 22.6 | 23.3 | 393 |  | low | 2020-09-14 | B70277¦Courtroom - facing the judge, back right¦¦Sep-18-2020 13:39
2020-09-18 13:40 | 44092.5694 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Administration office |  | 1 | 13.6 | 30.5 | 409 | 22.6 | 45.2 | 671 |  | 2020-09-18 13:40 | 44092.5694 | 22.6 | 45.2 | 671 |  |  | 2020-09-14 | B90631¦Administration office ¦¦Sep-18-2020 13:39
2020-09-18 13:40 | 44092.5695 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Security desk |  | 0 | 15.4 | 26.2 | 385 | 23.1 | 23.5 | 423 |  | 2020-09-18 13:40 | 44092.5695 | 23.1 | 23.5 | 423 |  | low | 2020-09-14 | B20550¦Security desk¦¦Sep-18-2020 13:40
2020-09-18 13:40 | 44092.5698 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - facing the judge, Back left |  | 2 | 14.6 | 21 | 371 | 22.5 | 23.5 | 398 |  | 2020-09-18 13:40 | 44092.5698 | 22.5 | 23.5 | 398 |  | low | 2020-09-14 | B70277¦Courtroom - facing the judge, Back left¦¦Sep-18-2020 13:40
2020-09-18 13:41 | 44092.57 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Crown office 2 |  | 0 | 13.6 | 30.5 | 409 | 22.7 | 43.8 | 662 |  | 2020-09-18 13:41 | 44092.57 | 22.7 | 43.8 | 662 |  |  | 2020-09-14 | B90631¦Crown office 2¦¦Sep-18-2020 13:40
2020-09-18 13:42 | 44092.5707 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Waiting area big |  | 0 | 15.4 | 26.2 | 385 | 23.2 | 22.8 | 414 |  | 2020-09-18 13:42 | 44092.5707 | 23.2 | 22.8 | 414 |  | low | 2020-09-14 | B20550¦Waiting area big¦¦Sep-18-2020 13:41
2020-09-18 13:42 | 44092.5708 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Admin office |  | 4 | 17.8 | 17.7 | 437 | 22.3 | 28.7 | 497 |  | 2020-09-18 13:42 | 44092.5708 | 22.3 | 28.7 | 497 |  | low | 2020-09-14 | B25477¦Admin office¦¦Sep-18-2020 13:42
2020-09-18 13:42 | 44092.571 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 028 |  | 0 | 14 | 25 | 375 | 21.4 | 31.6 | 403 | No | 2020-09-18 13:42 | 44092.571 | 21.4 | 31.6 | 403 |  | low | 2020-09-14 | B14660¦028¦¦Sep-18-2020 13:42
2020-09-18 13:43 | 44092.5713 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Vwap waiting room |  | 0 | 13.6 | 30.5 | 409 | 21.5 | 43 | 505 |  | 2020-09-18 13:43 | 44092.5713 | 21.5 | 43 | 505 |  |  | 2020-09-14 | B90631¦Vwap waiting room ¦¦Sep-18-2020 13:42
2020-09-18 13:43 | 44092.5718 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Judges chamber foyers |  | 0 | 13.6 | 30.5 | 409 | 21.8 | 45 | 511 |  | 2020-09-18 13:43 | 44092.5718 | 21.8 | 45 | 511 |  |  | 2020-09-14 | B90631¦Judges chamber foyers ¦¦Sep-18-2020 13:43
2020-09-18 13:44 | 44092.5719 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Waiting area small |  | 0 | 15.4 | 26.2 | 385 | 23 | 20.3 | 411 |  | 2020-09-18 13:44 | 44092.5719 | 23 | 20.3 | 411 |  | low | 2020-09-14 | B20550¦Waiting area small¦¦Sep-18-2020 13:43
2020-09-18 13:44 | 44092.5724 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - facing the judge, Left middle |  | 2 | 14.6 | 21 | 371 | 22.3 | 23.7 | 403 |  | 2020-09-18 13:44 | 44092.5724 | 22.3 | 23.7 | 403 |  | low | 2020-09-14 | B70277¦Courtroom - facing the judge, Left middle¦¦Sep-18-2020 13:44
2020-09-18 13:45 | 44092.5726 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Financial office |  | 4 | 17.8 | 17.7 | 437 | 21.8 | 26.7 | 497 |  | 2020-09-18 13:45 | 44092.5726 | 21.8 | 26.7 | 497 |  | low | 2020-09-14 | B25477¦Financial office ¦¦Sep-18-2020 13:44
2020-09-18 13:45 | 44092.5727 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Judges chamber |  | 0 | 13.6 | 30.5 | 409 | 21 | 45 | 515 |  | 2020-09-18 13:45 | 44092.5727 | 21 | 45 | 515 |  |  | 2020-09-14 | B90631¦Judges chamber ¦¦Sep-18-2020 13:44
2020-09-18 13:45 | 44092.5732 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 019 |  | 0 | 14 | 25 | 375 | 22.5 | 30.5 | 417 | No | 2020-09-18 13:45 | 44092.5732 | 22.5 | 30.5 | 417 |  | low | 2020-09-14 | B14660¦019¦¦Sep-18-2020 13:45
2020-09-18 13:46 | 44092.5735 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom 4 |  | 0 | 13.6 | 30.5 | 409 | 22 | 47 | 585 |  | 2020-09-18 13:46 | 44092.5735 | 22 | 47 | 585 |  |  | 2020-09-14 | B90631¦Courtroom 4¦¦Sep-18-2020 13:45
2020-09-18 13:46 | 44092.5736 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Courtroom 1 |  | 1 | 15.4 | 26.2 | 385 | 23.7 | 22.4 | 412 |  | 2020-09-18 13:46 | 44092.5736 | 23.7 | 22.4 | 412 |  | low | 2020-09-14 | B20550¦Courtroom 1¦¦Sep-18-2020 13:45
2020-09-18 13:46 | 44092.5738 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 019 |  | 0 | 14 | 25 | 375 | 22.5 | 30.5 | 417 | No | 2020-09-18 13:46 | 44092.5738 | 22.5 | 30.5 | 417 |  | low | 2020-09-14 | B14660¦019¦¦Sep-18-2020 13:46
2020-09-18 13:47 | 44092.5741 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Courtroom |  | 4 | 17.8 | 17.7 | 437 | 21.5 | 27.5 | 466 |  | 2020-09-18 13:47 | 44092.5741 | 21.5 | 27.5 | 466 |  | low | 2020-09-14 | B25477¦Courtroom ¦¦Sep-18-2020 13:46
2020-09-18 13:47 | 44092.5744 | AINSWORTH | B90631 | B90631 - 215 Cayley St - Walkerton | Courtroom 4 waiting room |  | 0 | 13.6 | 30.5 | 409 | 21.3 | 42.6 | 643 |  | 2020-09-18 13:47 | 44092.5744 | 21.3 | 42.6 | 643 |  |  | 2020-09-14 | B90631¦Courtroom 4 waiting room ¦¦Sep-18-2020 13:47
2020-09-18 13:47 | 44092.5747 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - facing the judge, Middle right |  | 2 | 14.6 | 21 | 371 | 22.5 | 23.7 | 393 |  | 2020-09-18 13:48 | 44092.5747 | 22.5 | 23.7 | 393 |  | low | 2020-09-14 | B70277¦Courtroom - facing the judge, Middle right¦¦Sep-18-2020 13:47
2020-09-18 13:48 | 44092.5749 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Emergency services |  | 2 | 17.8 | 17.7 | 437 | 21.7 | 26.6 | 509 |  | 2020-09-18 13:48 | 44092.5749 | 21.7 | 26.6 | 509 |  | low | 2020-09-14 | B25477¦Emergency services ¦¦Sep-18-2020 13:47
2020-09-18 13:48 | 44092.575 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Courtroom 2 |  | 1 | 15.4 | 26.2 | 385 | 25 | 21 | 414 |  | 2020-09-18 13:48 | 44092.575 | 25 | 21 | 414 |  | low | 2020-09-14 | B20550¦Courtroom 2¦¦Sep-18-2020 13:48
2020-09-18 13:49 | 44092.5757 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Mezzanine |  | 0 | 17.8 | 17.7 | 437 | 21.9 | 26.7 | 518 |  | 2020-09-18 13:49 | 44092.5757 | 21.9 | 26.7 | 518 |  | low | 2020-09-14 | B25477¦Mezzanine ¦¦Sep-18-2020 13:49
2020-09-18 13:50 | 44092.5763 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Board room |  | 3 | 17.8 | 17.7 | 437 | 22 | 25.2 | 500 |  | 2020-09-18 13:50 | 44092.5763 | 22 | 25.2 | 500 |  | low | 2020-09-14 | B25477¦Board room ¦¦Sep-18-2020 13:49
2020-09-18 13:50 | 44092.5764 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Justice Swartz office |  | 0 | 15.4 | 26.2 | 385 | 23.8 | 22.9 | 415 |  | 2020-09-18 13:50 | 44092.5764 | 23.8 | 22.9 | 415 |  | low | 2020-09-14 | B20550¦Justice Swartz office¦¦Sep-18-2020 13:50
2020-09-18 13:50 | 44092.5766 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 011 |  | 0 | 14 | 25 | 375 | 22.6 | 33.1 | 426 | No | 2020-09-18 13:50 | 44092.5766 | 22.6 | 33.1 | 426 |  | low | 2020-09-14 | B14660¦011¦¦Sep-18-2020 13:50
2020-09-18 13:51 | 44092.5768 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE STAFF ROOM |  | 2 | 16 | 23 | 416 | 20 | 39 | 480 |  | 2020-09-18 13:51 | 44092.5768 | 20 | 39 | 480 |  | caution | 2020-09-14 | B20022¦JUDGE STAFF ROOM¦¦Sep-18-2020 13:50
2020-09-18 13:51 | 44092.5768 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - facing the judge, Judges desk left side |  | 2 | 14.6 | 21 | 371 | 22.7 | 23.3 | 399 |  | 2020-09-18 13:51 | 44092.5768 | 22.7 | 23.3 | 399 |  | low | 2020-09-14 | B70277¦Courtroom - facing the judge, Judges desk left side¦¦Sep-18-2020 13:50
2020-09-18 13:51 | 44092.5773 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE CORKERY |  | 2 | 16 | 23 | 416 | 20 | 40 | 450 |  | 2020-09-18 13:51 | 44092.5773 | 20 | 40 | 450 |  | caution | 2020-09-14 | B20022¦JUDGE CORKERY¦¦Sep-18-2020 13:51
2020-09-18 13:52 | 44092.5775 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Library |  | 0 | 17.8 | 17.7 | 437 | 21.9 | 25.9 | 485 |  | 2020-09-18 13:52 | 44092.5775 | 21.9 | 25.9 | 485 |  | low | 2020-09-14 | B25477¦Library ¦¦Sep-18-2020 13:51
2020-09-18 13:52 | 44092.5775 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Crown attorneys office |  | 5 | 18 | 21.9 | 388 | 23 | 19.6 | 423 | No | 2020-09-18 13:52 | 44092.5775 | 23 | 19.6 | 423 |  | low | 2020-09-14 | B21128¦Crown attorneys office ¦¦Sep-18-2020 13:51
2020-09-18 13:52 | 44092.5777 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | VISITING JUDGE |  | 2 | 16 | 23 | 416 | 21 | 43 | 416 |  | 2020-09-18 13:52 | 44092.5777 | 21 | 43 | 416 |  |  | 2020-09-14 | B20022¦VISITING JUDGE¦¦Sep-18-2020 13:51
2020-09-18 13:52 | 44092.5781 | AINSWORTH | B20550 | B20550 - 469 Montreal St - Kingston | Administrative office |  | 1 | 15.4 | 26.2 | 385 | 23.7 | 21.2 | 414 |  | 2020-09-18 13:52 | 44092.5781 | 23.7 | 21.2 | 414 |  | low | 2020-09-14 | B20550¦Administrative office¦¦Sep-18-2020 13:52
2020-09-18 13:53 | 44092.5781 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE INGRAM |  | 2 | 16 | 23 | 416 | 21 | 40.5 | 439 |  | 2020-09-18 13:53 | 44092.5781 | 21 | 40.5 | 439 |  |  | 2020-09-14 | B20022¦JUDGE INGRAM¦¦Sep-18-2020 13:52
2020-09-18 13:53 | 44092.5786 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE MCLEOD |  | 2 | 16 | 23 | 416 | 21 | 45 | 447 |  | 2020-09-18 13:53 | 44092.5786 | 21 | 45 | 447 |  |  | 2020-09-14 | B20022¦JUDGE MCLEOD¦¦Sep-18-2020 13:53
2020-09-18 13:53 | 44092.5788 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 118 |  | 0 | 14 | 25 | 375 | 22.8 | 24.7 | 393 | No | 2020-09-18 13:53 | 44092.5788 | 22.8 | 24.7 | 393 |  | low | 2020-09-14 | B14660¦118¦¦Sep-18-2020 13:53
2020-09-18 13:54 | 44092.579 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - facing the judge, Judges desk right side/centre |  | 2 | 14.6 | 21 | 371 | 22.5 | 23.5 | 405 |  | 2020-09-18 13:54 | 44092.579 | 22.5 | 23.5 | 405 |  | low | 2020-09-14 | B70277¦Courtroom - facing the judge, Judges desk right side/centre¦¦Sep-18-2020 13:53
2020-09-18 13:54 | 44092.579 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 JUDGE |  | 2 | 16 | 23 | 416 | 21 | 40 | 455 |  | 2020-09-18 13:54 | 44092.579 | 21 | 40 | 455 |  | caution | 2020-09-14 | B20022¦COURT 3 JUDGE¦¦Sep-18-2020 13:53
2020-09-18 13:54 | 44092.5792 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Main entrance |  | 0 | 17.8 | 17.7 | 437 | 21.6 | 27.1 | 496 |  | 2020-09-18 13:54 | 44092.5792 | 21.6 | 27.1 | 496 |  | low | 2020-09-14 | B25477¦Main entrance ¦¦Sep-18-2020 13:53
2020-09-18 13:54 | 44092.5794 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 LAWYER |  | 2 | 16 | 23 | 416 | 20.7 | 39 | 436 |  | 2020-09-18 13:54 | 44092.5794 | 20.7 | 39 | 436 |  | caution | 2020-09-14 | B20022¦COURT 3 LAWYER¦¦Sep-18-2020 13:54
2020-09-18 13:55 | 44092.5801 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | ADVICE COUNSEL |  | 2 | 16 | 23 | 416 | 20.6 | 34 | 426 |  | 2020-09-18 13:55 | 44092.5801 | 20.6 | 34 | 426 |  | low | 2020-09-14 | B20022¦ADVICE COUNSEL¦¦Sep-18-2020 13:55
2020-09-18 13:56 | 44092.5803 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Front door entrance |  | 9 | 18.3 | 24.2 | 388 | 21.5 | 21.9 | 446 | No | 2020-09-18 13:56 | 44092.5803 | 21.5 | 21.9 | 446 |  | low | 2020-09-14 | B21128¦Front door entrance ¦¦Sep-18-2020 13:55
2020-09-18 13:56 | 44092.5803 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 115 |  | 0 | 14 | 25 | 375 | 23.2 | 29.7 | 411 | No | 2020-09-18 13:56 | 44092.5803 | 23.2 | 29.7 | 411 |  | low | 2020-09-14 | B14660¦115¦¦Sep-18-2020 13:55
2020-09-18 13:56 | 44092.5805 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Courtroom - Witness stand |  | 2 | 14.6 | 21 | 371 | 22.6 | 23.6 | 408 |  | 2020-09-18 13:56 | 44092.5805 | 22.6 | 23.6 | 408 |  | low | 2020-09-14 | B70277¦Courtroom - Witness stand¦¦Sep-18-2020 13:55
2020-09-18 13:56 | 44092.5807 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 WAITING AREA |  | 2 | 16 | 23 | 416 | 20.7 | 32.7 | 423 |  | 2020-09-18 13:56 | 44092.5807 | 20.7 | 32.7 | 423 |  | low | 2020-09-14 | B20022¦COURT 3 WAITING AREA¦¦Sep-18-2020 13:56
2020-09-18 13:56 | 44092.5807 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 3 gallery |  | 0 | 12 | 37 | 392 | 21.2 | 28.7 | 474 | No | 2020-09-18 13:56 | 44092.5807 | 21.2 | 28.7 | 474 |  | low | 2020-09-14 | B20151¦Court room 3 gallery ¦¦Sep-18-2020 13:56
2020-09-18 13:57 | 44092.5811 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 403 |  | 7 | 18.3 | 24.2 | 388 | 22.2 | 18.8 | 446 | No | 2020-09-18 13:57 | 44092.5811 | 22.2 | 18.8 | 446 |  | low | 2020-09-14 | B21128¦403¦¦Sep-18-2020 13:56
2020-09-18 13:57 | 44092.5812 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT OFFICE LOBBY |  | 2 | 16 | 23 | 407 | 19.5 | 36 | 534 |  | 2020-09-18 13:57 | 44092.5812 | 19.5 | 36 | 534 |  | caution | 2020-09-14 | B20022¦COURT OFFICE LOBBY¦¦Sep-18-2020 13:56
2020-09-18 13:58 | 44092.5816 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT OFFICE |  | 3 | 16 | 23 | 416 | 21.5 | 38 | 604 |  | 2020-09-18 13:58 | 44092.5816 | 21.5 | 38 | 604 |  | caution | 2020-09-14 | B20022¦COURT OFFICE¦¦Sep-18-2020 13:57
2020-09-18 13:58 | 44092.5816 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | OPP office |  | 2 | 21 | 18 | 404 | 22 | 25 | 554 |  | 2020-09-18 13:58 | 44092.5816 | 22 | 25 | 554 |  | low | 2020-09-14 | B70235¦OPP office ¦¦Sep-18-2020 13:57
2020-09-18 13:58 | 44092.5821 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | MEDIATION ROOM |  | 1 | 16 | 23 | 416 | 21.6 | 38 | 627 |  | 2020-09-18 13:58 | 44092.5821 | 21.6 | 38 | 627 |  | caution | 2020-09-14 | B20022¦MEDIATION ROOM¦¦Sep-18-2020 13:58
2020-09-18 13:58 | 44092.5822 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Judges chamber - desk area |  | 2 | 14.6 | 21 | 371 | 22.6 | 24.1 | 411 |  | 2020-09-18 13:58 | 44092.5822 | 22.6 | 24.1 | 411 |  | low | 2020-09-14 | B70277¦Judges chamber - desk area¦¦Sep-18-2020 13:58
2020-09-18 13:59 | 44092.5825 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | OFFICER ROOM |  | 1 | 16 | 23 | 416 | 21 | 38 | 566 |  | 2020-09-18 13:59 | 44092.5825 | 21 | 38 | 566 |  | caution | 2020-09-14 | B20022¦OFFICER ROOM¦¦Sep-18-2020 13:58
2020-09-18 13:59 | 44092.5827 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | N.W hallway entrance |  | 2 | 18.3 | 24.2 | 388 | 23.6 | 19.6 | 535 | No | 2020-09-18 13:59 | 44092.5827 | 23.6 | 19.6 | 535 |  | low | 2020-09-14 | B21128¦N.W hallway entrance ¦¦Sep-18-2020 13:59
2020-09-18 13:59 | 44092.5829 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 1 FLOOR LOBBY |  | 5 | 16 | 23 | 416 | 18 | 38 | 460 |  | 2020-09-18 13:59 | 44092.5829 | 18 | 38 | 460 |  | caution | 2020-09-14 | B20022¦1 FLOOR LOBBY¦¦Sep-18-2020 13:59
2020-09-18 14:00 | 44092.583 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office E |  | 2 | 21 | 18 | 404 | 23 | 23 | 515 |  | 2020-09-18 14:00 | 44092.583 | 23 | 23 | 515 |  | low | 2020-09-14 | B70235¦Main office E ¦¦Sep-18-2020 13:59
2020-09-18 14:00 | 44092.5831 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 3 judge desk |  | 2 | 12 | 37 | 392 | 21.7 | 28.4 | 486 | No | 2020-09-18 14:00 | 44092.5831 | 21.7 | 28.4 | 486 |  | low | 2020-09-14 | B20151¦Court room 3 judge desk ¦¦Sep-18-2020 13:59
2020-09-18 14:00 | 44092.5832 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Judges chamber - behind the desk, beside back door |  | 2 | 14.6 | 21 | 371 | 22.7 | 24.5 | 400 |  | 2020-09-18 14:00 | 44092.5832 | 22.7 | 24.5 | 400 |  | low | 2020-09-14 | B70277¦Judges chamber - behind the desk, beside back door¦¦Sep-18-2020 13:59
2020-09-18 14:00 | 44092.5836 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 107 |  | 2 | 14 | 25 | 375 | 20.2 | 28.8 | 428 | No | 2020-09-18 14:00 | 44092.5836 | 20.2 | 28.8 | 428 |  | low | 2020-09-14 | B14660¦107¦¦Sep-18-2020 14:00
2020-09-18 14:01 | 44092.5838 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office C |  | 2 | 21 | 18 | 404 | 23 | 22 | 488 |  | 2020-09-18 14:01 | 44092.5838 | 23 | 22 | 488 |  | low | 2020-09-14 | B70235¦Main office C ¦¦Sep-18-2020 14:00
2020-09-18 14:01 | 44092.5842 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation office - desk area |  | 2 | 14.6 | 21 | 371 | 22.7 | 24 | 396 |  | 2020-09-18 14:01 | 44092.5842 | 22.7 | 24 | 396 |  | low | 2020-09-14 | B70277¦Mediation office - desk area¦¦Sep-18-2020 14:01
2020-09-18 14:02 | 44092.5847 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 405 |  | 3 | 18.3 | 24.2 | 388 | 23.4 | 17.9 | 407 | No | 2020-09-18 14:02 | 44092.5847 | 23.4 | 17.9 | 407 |  | low | 2020-09-14 | B21128¦405¦¦Sep-18-2020 14:01
2020-09-18 14:02 | 44092.5848 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 113 |  | 0 | 14 | 25 | 375 | 21.1 | 28.9 | 410 | No | 2020-09-18 14:02 | 44092.5848 | 21.1 | 28.9 | 410 |  | low | 2020-09-14 | B14660¦113¦¦Sep-18-2020 14:02
2020-09-18 14:02 | 44092.5851 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office W |  | 2 | 21 | 18 | 404 | 23 | 21 | 479 |  | 2020-09-18 14:02 | 44092.5851 | 23 | 21 | 479 |  | low | 2020-09-14 | B70235¦Main office W¦¦Sep-18-2020 14:02
2020-09-18 14:03 | 44092.5854 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Main office |  | 6 | 14.7 | 30.6 | 387 | 20.4 | 35.6 | 606 |  | 2020-09-18 14:03 | 44092.5854 | 20.4 | 35.6 | 606 |  | caution | 2020-09-14 | B21554¦Main office¦¦Sep-18-2020 14:02
2020-09-18 14:03 | 44092.5856 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 406 |  | 6 | 18.3 | 24.2 | 388 | 23.2 | 19.2 | 474 | No | 2020-09-18 14:03 | 44092.5856 | 23.2 | 19.2 | 474 |  | low | 2020-09-14 | B21128¦406¦¦Sep-18-2020 14:03
2020-09-18 14:03 | 44092.5856 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation office - printer area |  | 2 | 14.6 | 21 | 371 | 22.8 | 24.1 | 400 |  | 2020-09-18 14:03 | 44092.5856 | 22.8 | 24.1 | 400 |  | low | 2020-09-14 | B70277¦Mediation office - printer area¦¦Sep-18-2020 14:03
2020-09-18 14:04 | 44092.586 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Trial office |  | 0 | 21 | 18 | 404 | 23 | 23 | 482 |  | 2020-09-18 14:04 | 44092.586 | 23 | 23 | 482 |  | low | 2020-09-14 | B70235¦Trial office ¦¦Sep-18-2020 14:03
2020-09-18 14:04 | 44092.5864 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom a |  | 0 | 21 | 21 | 367 | 23.2 | 24.9 | 412 |  | 2020-09-18 14:04 | 44092.5864 | 23.2 | 24.9 | 412 |  | low | 2020-09-14 | Pearso¦Courtroom a¦¦Sep-18-2020 14:04
2020-09-18 14:05 | 44092.5865 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Lunch/kitchen room - centre counter |  | 1 | 14.6 | 21 | 371 | 22.8 | 23.8 | 404 |  | 2020-09-18 14:05 | 44092.5865 | 22.8 | 23.8 | 404 |  | low | 2020-09-14 | B70277¦Lunch/kitchen room - centre counter¦¦Sep-18-2020 14:04
2020-09-18 14:05 | 44092.5867 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 407 |  | 2 | 18.3 | 24.2 | 388 | 23.7 | 20 | 451 | No | 2020-09-18 14:05 | 44092.5867 | 23.7 | 20 | 451 |  | low | 2020-09-14 | B21128¦407¦¦Sep-18-2020 14:04
2020-09-18 14:05 | 44092.5868 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 114 |  | 0 | 14 | 25 | 375 | 21.5 | 29.6 | 397 | No | 2020-09-18 14:05 | 44092.5868 | 21.5 | 29.6 | 397 |  | low | 2020-09-14 | B14660¦114¦¦Sep-18-2020 14:04
2020-09-18 14:05 | 44092.5869 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jennifer Mumby office |  | 0 | 21 | 18 | 404 | 22 | 21 | 463 |  | 2020-09-18 14:05 | 44092.5869 | 22 | 21 | 463 |  | low | 2020-09-14 | B70235¦Jennifer Mumby office ¦¦Sep-18-2020 14:05
2020-09-18 14:06 | 44092.5872 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - kitchen entrance area |  | 1 | 14.6 | 21 | 371 | 22.8 | 23.5 | 408 |  | 2020-09-18 14:06 | 44092.5872 | 22.8 | 23.5 | 408 |  | low | 2020-09-14 | B70277¦Mediation room - kitchen entrance area¦¦Sep-18-2020 14:05
2020-09-18 14:06 | 44092.5872 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 1 gallery |  | 2 | 12 | 37 | 392 | 22 | 23.7 | 472 | No | 2020-09-18 14:06 | 44092.5872 | 22 | 23.7 | 472 |  | low | 2020-09-14 | B20151¦Court room 1 gallery ¦¦Sep-18-2020 14:05
2020-09-18 14:06 | 44092.5874 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #2 |  | 3 | 14.7 | 30.6 | 387 | 21 | 34.3 | 640 |  | 2020-09-18 14:06 | 44092.5874 | 21 | 34.3 | 640 |  | low | 2020-09-14 | B20474¦Courtroom #2¦¦Sep-18-2020 14:05
2020-09-18 14:06 | 44092.5874 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom a back |  | 0 | 20.5 | 20.9 | 367 | 23.8 | 20.7 | 412 |  | 2020-09-18 14:06 | 44092.5874 | 23.8 | 20.7 | 412 |  | low | 2020-09-14 | Pearso¦Courtroom a back¦¦Sep-18-2020 14:05
2020-09-18 14:06 | 44092.5877 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 408 |  | 2 | 18.3 | 24.2 | 388 | 24.2 | 19 | 456 |  | 2020-09-18 14:06 | 44092.5877 | 24.2 | 19 | 456 |  | low | 2020-09-14 | B21128¦408¦¦Sep-18-2020 14:06
2020-09-18 14:06 | 44092.5877 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jennifer Broderick office |  | 0 | 21 | 18 | 404 | 22 | 23 | 457 |  | 2020-09-18 14:06 | 44092.5877 | 22 | 23 | 457 |  | low | 2020-09-14 | B70235¦Jennifer Broderick office ¦¦Sep-18-2020 14:06
2020-09-18 14:06 | 44092.5878 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Main lobby north |  | 0 | 16 | 33 | 411 | 23 | 29 | 577 |  | 2020-09-18 14:06 | 44092.5878 | 23 | 29 | 577 |  | low | 2020-09-14 | B25479¦Main lobby north ¦¦Sep-18-2020 14:06
2020-09-18 14:07 | 44092.5879 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - centre table |  | 1 | 14.6 | 21 | 371 | 22.8 | 23.6 | 405 |  | 2020-09-18 14:07 | 44092.5879 | 22.8 | 23.6 | 405 |  | low | 2020-09-14 | B70277¦Mediation room - centre table¦¦Sep-18-2020 14:06
2020-09-18 14:07 | 44092.5884 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Main lobby south |  | 5 | 16 | 33 | 411 | 22 | 27 | 575 |  | 2020-09-18 14:07 | 44092.5884 | 22 | 27 | 575 |  | low | 2020-09-14 | B25479¦Main lobby south ¦¦Sep-18-2020 14:07
2020-09-18 14:07 | 44092.5884 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 414 |  | 2 | 18.3 | 24.2 | 388 | 23.5 | 19.4 | 431 |  | 2020-09-18 14:07 | 44092.5884 | 23.5 | 19.4 | 431 |  | low | 2020-09-14 | B21128¦414¦¦Sep-18-2020 14:07
2020-09-18 14:08 | 44092.5886 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Security area |  | 1 | 19.5 | 22 | 393 | 21 | 28.2 | 535 |  | 2020-09-18 14:08 | 44092.5886 | 21 | 28.2 | 535 |  | low | 2020-09-14 | B17477¦Security area¦¦Sep-18-2020 14:07
2020-09-18 14:08 | 44092.5887 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom b |  | 0 | 20.5 | 20.9 | 367 | 23.8 | 18 | 399 |  | 2020-09-18 14:08 | 44092.5887 | 23.8 | 18 | 399 |  | low | 2020-09-14 | Pearso¦Courtroom b¦¦Sep-18-2020 14:07
2020-09-18 14:08 | 44092.5888 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 104 |  | 0 | 14 | 25 | 375 | 21.1 | 33 | 419 | No | 2020-09-18 14:08 | 44092.5888 | 21.1 | 33 | 419 |  | low | 2020-09-14 | B14660¦104¦¦Sep-18-2020 14:07
2020-09-18 14:08 | 44092.5889 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 413 |  | 2 | 18.3 | 24.2 | 388 | 23.5 | 22.7 | 539 |  | 2020-09-18 14:08 | 44092.5889 | 23.5 | 22.7 | 539 |  | low | 2020-09-14 | B21128¦413¦¦Sep-18-2020 14:07
2020-09-18 14:08 | 44092.589 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #1 |  | 2 | 14.7 | 30.6 | 387 | 20.8 | 33.7 | 615 |  | 2020-09-18 14:08 | 44092.589 | 20.8 | 33.7 | 615 |  | low | 2020-09-14 | B20474¦Courtroom #1¦¦Sep-18-2020 14:08
2020-09-18 14:08 | 44092.589 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Mediation room - hallway entrance area |  | 1 | 14.6 | 21 | 371 | 22.9 | 23.9 | 405 |  | 2020-09-18 14:08 | 44092.589 | 22.9 | 23.9 | 405 |  | low | 2020-09-14 | B70277¦Mediation room - hallway entrance area¦¦Sep-18-2020 14:08
2020-09-18 14:08 | 44092.5891 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Stuart Konyer office |  | 0 | 21 | 18 | 404 | 22 | 23 | 465 |  | 2020-09-18 14:08 | 44092.5891 | 22 | 23 | 465 |  | low | 2020-09-14 | B70235¦Stuart Konyer office ¦¦Sep-18-2020 14:08
2020-09-18 14:08 | 44092.5891 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom A chairs |  | 0 | 15.5 | 30.2 | 422 | 21.6 | 22.8 | 419 |  | 2020-09-18 14:08 | 44092.5891 | 21.6 | 22.8 | 419 |  | low | 2020-09-14 | B20603¦Courtroom A chairs ¦¦Sep-18-2020 14:08
2020-09-18 14:08 | 44092.5892 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 gallery |  | 0 | 12 | 37 | 392 | 21.9 | 30.4 | 559 | No | 2020-09-18 14:08 | 44092.5892 | 21.9 | 30.4 | 559 |  | low | 2020-09-14 | B20151¦Court room 2 gallery ¦¦Sep-18-2020 14:08
2020-09-18 14:09 | 44092.5894 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Administration office east |  | 3 | 16 | 33 | 411 | 23 | 30 | 619 |  | 2020-09-18 14:09 | 44092.5894 | 23 | 30 | 619 |  | low | 2020-09-14 | B25479¦Administration office east ¦¦Sep-18-2020 14:08
2020-09-18 14:09 | 44092.5896 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL3 waiting area N |  | 0 | 19.5 | 22 | 393 | 21.5 | 26.2 | 472 |  | 2020-09-18 14:09 | 44092.5896 | 21.5 | 26.2 | 472 |  | low | 2020-09-14 | B17477¦LVL3 waiting area N¦¦Sep-18-2020 14:08
2020-09-18 14:09 | 44092.5898 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom b back |  | 0 | 20.5 | 20.9 | 367 | 23.2 | 19.2 | 392 |  | 2020-09-18 14:09 | 44092.5898 | 23.2 | 19.2 | 392 |  | low | 2020-09-14 | Pearso¦Courtroom b back¦¦Sep-18-2020 14:09
2020-09-18 14:09 | 44092.5898 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Duty council office - desk area |  | 1 | 14.6 | 21 | 371 | 23 | 23.6 | 405 |  | 2020-09-18 14:09 | 44092.5898 | 23 | 23.6 | 405 |  | low | 2020-09-14 | B70277¦Duty council office - desk area¦¦Sep-18-2020 14:09
2020-09-18 14:09 | 44092.5899 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 412 |  | 2 | 18.3 | 24.2 | 388 | 23.1 | 18.1 | 434 | No | 2020-09-18 14:09 | 44092.5899 | 23.1 | 18.1 | 434 |  | low | 2020-09-14 | B21128¦412¦¦Sep-18-2020 14:09
2020-09-18 14:09 | 44092.5899 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom A bench |  | 0 | 15.5 | 30.2 | 422 | 21.8 | 22.6 | 421 |  | 2020-09-18 14:09 | 44092.5899 | 21.8 | 22.6 | 421 |  | low | 2020-09-14 | B20603¦Courtroom A bench ¦¦Sep-18-2020 14:09
2020-09-18 14:10 | 44092.5899 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Administration office west |  | 3 | 16 | 33 | 411 | 23 | 32 | 643 |  | 2020-09-18 14:10 | 44092.5899 | 23 | 32 | 643 |  | low | 2020-09-14 | B25479¦Administration office west ¦¦Sep-18-2020 14:09
2020-09-18 14:10 | 44092.5902 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 3 waiting area S |  | 0 | 19.5 | 22 | 393 | 21.7 | 24.6 | 455 |  | 2020-09-18 14:10 | 44092.5902 | 21.7 | 24.6 | 455 |  | low | 2020-09-14 | B17477¦LVL 3 waiting area S¦¦Sep-18-2020 14:09
2020-09-18 14:10 | 44092.5902 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Lunch room |  | 0 | 21 | 18 | 404 | 22 | 23 | 464 |  | 2020-09-18 14:10 | 44092.5902 | 22 | 23 | 464 |  | low | 2020-09-14 | B70235¦Lunch room ¦¦Sep-18-2020 14:09
2020-09-18 14:10 | 44092.5904 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 101 |  | 0 | 14 | 25 | 375 | 21.6 | 39.7 | 399 | No | 2020-09-18 14:10 | 44092.5904 | 21.6 | 39.7 | 399 |  | caution | 2020-09-14 | B14660¦101¦¦Sep-18-2020 14:10
2020-09-18 14:10 | 44092.5905 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Intake office |  | 0 | 16 | 33 | 411 | 23 | 31 | 635 |  | 2020-09-18 14:10 | 44092.5905 | 23 | 31 | 635 |  | low | 2020-09-14 | B25479¦Intake office ¦¦Sep-18-2020 14:10
2020-09-18 14:11 | 44092.5907 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 411 |  | 5 | 18.3 | 24.2 | 388 | 22.8 | 20.2 | 414 |  | 2020-09-18 14:11 | 44092.5907 | 22.8 | 20.2 | 414 |  | low | 2020-09-14 | B21128¦411¦¦Sep-18-2020 14:10
2020-09-18 14:11 | 44092.5907 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Duty council office - back right, seating area |  | 1 | 14.6 | 21 | 371 | 23.1 | 23.8 | 404 |  | 2020-09-18 14:11 | 44092.5907 | 23.1 | 23.8 | 404 |  | low | 2020-09-14 | B70277¦Duty council office - back right, seating area¦¦Sep-18-2020 14:10
2020-09-18 14:11 | 44092.5909 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Main hallway |  | 0 | 16 | 33 | 411 | 23 | 30 | 624 |  | 2020-09-18 14:11 | 44092.5909 | 23 | 30 | 624 |  | low | 2020-09-14 | B25479¦Main hallway ¦¦Sep-18-2020 14:10
2020-09-18 14:11 | 44092.591 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom c |  | 0 | 20.5 | 20.9 | 367 | 23.1 | 20.8 | 391 |  | 2020-09-18 14:11 | 44092.591 | 23.1 | 20.8 | 391 |  | low | 2020-09-14 | Pearso¦Courtroom c¦¦Sep-18-2020 14:10
2020-09-18 14:11 | 44092.591 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom B chairs |  | 0 | 15.5 | 30.2 | 422 | 21.6 | 23.9 | 428 |  | 2020-09-18 14:11 | 44092.591 | 21.6 | 23.9 | 428 |  | low | 2020-09-14 | B20603¦Courtroom B chairs ¦¦Sep-18-2020 14:11
2020-09-18 14:11 | 44092.5911 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 waiting area |  | 3 | 19.5 | 22 | 393 | 22 | 22.6 | 424 |  | 2020-09-18 14:11 | 44092.5911 | 22 | 22.6 | 424 |  | low | 2020-09-14 | B17477¦Courtroom 300 waiting area¦¦Sep-18-2020 14:11
2020-09-18 14:11 | 44092.5912 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court Support office |  | 0 | 21 | 18 | 404 | 22 | 25 | 470 |  | 2020-09-18 14:11 | 44092.5912 | 22 | 25 | 470 |  | low | 2020-09-14 | B70235¦Court Support office ¦¦Sep-18-2020 14:11
2020-09-18 14:12 | 44092.5914 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Lunchroom |  | 0 | 16 | 33 | 411 | 23 | 33 | 623 |  | 2020-09-18 14:12 | 44092.5914 | 23 | 33 | 623 |  | low | 2020-09-14 | B25479¦Lunchroom ¦¦Sep-18-2020 14:11
2020-09-18 14:12 | 44092.5916 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside of door “302” |  | 1 | 14.6 | 21 | 371 | 23 | 22.6 | 415 |  | 2020-09-18 14:12 | 44092.5916 | 23 | 22.6 | 415 |  | low | 2020-09-14 | B70277¦Hallway - outside of door “302”¦¦Sep-18-2020 14:11
2020-09-18 14:12 | 44092.5917 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR LUNCH ROOM |  | 2 | 16 | 23 | 416 | 21.8 | 30.9 | 494 |  | 2020-09-18 14:12 | 44092.5917 | 21.8 | 30.9 | 494 |  | low | 2020-09-14 | B20022¦2 FLOOR LUNCH ROOM¦¦Sep-18-2020 14:12
2020-09-18 14:12 | 44092.5919 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom Bench |  | 0 | 15.5 | 30.2 | 422 | 21.6 | 24.5 | 427 |  | 2020-09-18 14:12 | 44092.5919 | 21.6 | 24.5 | 427 |  | low | 2020-09-14 | B20603¦Courtroom Bench¦¦Sep-18-2020 14:12
2020-09-18 14:13 | 44092.592 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 W |  | 0 | 19.5 | 22 | 393 | 22.2 | 23.2 | 402 |  | 2020-09-18 14:13 | 44092.592 | 22.2 | 23.2 | 402 |  | low | 2020-09-14 | B17477¦Courtroom 300 W¦¦Sep-18-2020 14:12
2020-09-18 14:13 | 44092.5922 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 410 |  | 2 | 18.3 | 24.2 | 388 | 22.1 | 18.8 | 413 | No | 2020-09-18 14:13 | 44092.5922 | 22.1 | 18.8 | 413 |  | low | 2020-09-14 | B21128¦410¦¦Sep-18-2020 14:12
2020-09-18 14:13 | 44092.5923 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 2 JUDGE |  | 2 | 16 | 23 | 416 | 21.8 | 29.9 | 440 |  | 2020-09-18 14:13 | 44092.5923 | 21.8 | 29.9 | 440 |  | low | 2020-09-14 | B20022¦COURT 2 JUDGE¦¦Sep-18-2020 14:12
2020-09-18 14:13 | 44092.5927 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 134 |  | 0 | 14 | 25 | 375 | 22.6 | 34.4 | 391 | No | 2020-09-18 14:13 | 44092.5927 | 22.6 | 34.4 | 391 |  | low | 2020-09-14 | B14660¦134¦¦Sep-18-2020 14:13
2020-09-18 14:14 | 44092.5927 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 E |  | 0 | 19.5 | 22 | 393 | 22.2 | 23.9 | 398 |  | 2020-09-18 14:13 | 44092.5927 | 22.2 | 23.9 | 398 |  | low | 2020-09-14 | B17477¦Courtroom 300 E¦¦Sep-18-2020 14:13
2020-09-18 14:14 | 44092.5927 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom c back |  | 0 | 20.5 | 20.9 | 366 | 22.8 | 20.6 | 391 |  | 2020-09-18 14:14 | 44092.5927 | 22.8 | 20.6 | 391 |  | low | 2020-09-14 | Pearso¦Courtroom c back¦¦Sep-18-2020 14:13
2020-09-18 14:14 | 44092.5927 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 judge desk |  | 1 | 12 | 37 | 392 | 22.6 | 30.2 | 581 | No | 2020-09-18 14:14 | 44092.5927 | 22.6 | 30.2 | 581 |  | low | 2020-09-14 | B20151¦Court room 2 judge desk ¦¦Sep-18-2020 14:13
2020-09-18 14:14 | 44092.5928 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Crown staff office |  | 2 | 21 | 18 | 404 | 22 | 24 | 537 |  | 2020-09-18 14:14 | 44092.5928 | 22 | 24 | 537 |  | low | 2020-09-14 | B70235¦Crown staff office ¦¦Sep-18-2020 14:13
2020-09-18 14:14 | 44092.5928 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 2 LAWYER |  | 2 | 16 | 23 | 416 | 21.3 | 29.7 | 434 |  | 2020-09-18 14:14 | 44092.5928 | 21.3 | 29.7 | 434 |  | low | 2020-09-14 | B20022¦COURT 2 LAWYER¦¦Sep-18-2020 14:13
2020-09-18 14:14 | 44092.5929 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center |  | 0 | 15.5 | 30.2 | 422 | 21.6 | 23.1 | 425 |  | 2020-09-18 14:14 | 44092.5929 | 21.6 | 23.1 | 425 |  | low | 2020-09-14 | B20603¦Prep center ¦¦Sep-18-2020 14:13
2020-09-18 14:14 | 44092.5929 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | robing corridor |  | 1 | 14.7 | 30.6 | 387 | 21.6 | 39.6 | 603 |  | 2020-09-18 14:14 | 44092.5929 | 21.6 | 39.6 | 603 |  | caution | 2020-09-14 | B20474¦robing corridor¦¦Sep-18-2020 14:13
2020-09-18 14:14 | 44092.5929 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - outside of duty council office |  | 1 | 14.6 | 21 | 371 | 22.6 | 23.3 | 410 |  | 2020-09-18 14:14 | 44092.5929 | 22.6 | 23.3 | 410 |  | low | 2020-09-14 | B70277¦Hallway - outside of duty council office¦¦Sep-18-2020 14:13
2020-09-18 14:14 | 44092.5933 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 JUDGE |  | 3 | 16 | 23 | 416 | 21.6 | 36 | 434 |  | 2020-09-18 14:14 | 44092.5933 | 21.6 | 36 | 434 |  | caution | 2020-09-14 | B20022¦COURT 1 JUDGE¦¦Sep-18-2020 14:14
2020-09-18 14:15 | 44092.5936 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center 2 |  | 0 | 15.5 | 30.2 | 422 | 21.7 | 22.8 | 433 |  | 2020-09-18 14:15 | 44092.5936 | 21.7 | 22.8 | 433 |  | low | 2020-09-14 | B20603¦Prep center 2¦¦Sep-18-2020 14:14
2020-09-18 14:15 | 44092.5937 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - Elevator lobby |  | 1 | 14.6 | 21 | 371 | 22.5 | 22.7 | 411 |  | 2020-09-18 14:15 | 44092.5937 | 22.5 | 22.7 | 411 |  | low | 2020-09-14 | B70277¦Hallway - Elevator lobby¦¦Sep-18-2020 14:14
2020-09-18 14:15 | 44092.5938 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 410 |  | 2 | 18.3 | 24.2 | 388 | 22.2 | 18.4 | 404 | No | 2020-09-18 14:15 | 44092.5938 | 22.2 | 18.4 | 404 |  | low | 2020-09-14 | B21128¦410¦¦Sep-18-2020 14:15
2020-09-18 14:15 | 44092.5939 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 RIGHT SIDE |  | 3 | 16 | 23 | 416 | 22.2 | 35.7 | 544 |  | 2020-09-18 14:15 | 44092.5939 | 22.2 | 35.7 | 544 |  | caution | 2020-09-14 | B20022¦COURT 1 RIGHT SIDE¦¦Sep-18-2020 14:15
2020-09-18 14:16 | 44092.5941 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom d |  | 0 | 20.5 | 20.9 | 367 | 23.7 | 19.7 | 389 |  | 2020-09-18 14:16 | 44092.5941 | 23.7 | 19.7 | 389 |  | low | 2020-09-14 | Pearso¦Courtroom d¦¦Sep-18-2020 14:15
2020-09-18 14:16 | 44092.5942 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 3 |  | 3 | 16 | 33 | 411 | 23 | 29 | 601 |  | 2020-09-18 14:16 | 44092.5942 | 23 | 29 | 601 |  | low | 2020-09-14 | B25479¦Courtroom 3¦¦Sep-18-2020 14:15
2020-09-18 14:16 | 44092.5943 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 136 |  | 3 | 14 | 25 | 375 | 23.5 | 31.2 | 440 | No | 2020-09-18 14:16 | 44092.5943 | 23.5 | 31.2 | 440 |  | low | 2020-09-14 | B14660¦136¦¦Sep-18-2020 14:15
2020-09-18 14:16 | 44092.5944 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 LEFT SIDE |  | 3 | 16 | 23 | 416 | 22.2 | 34.6 | 507 |  | 2020-09-18 14:16 | 44092.5944 | 22.2 | 34.6 | 507 |  | low | 2020-09-14 | B20022¦COURT 1 LEFT SIDE¦¦Sep-18-2020 14:15
2020-09-18 14:16 | 44092.5944 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center 3 |  | 0 | 15.5 | 30.2 | 422 | 21.9 | 23 | 433 |  | 2020-09-18 14:16 | 44092.5944 | 21.9 | 23 | 433 |  | low | 2020-09-14 | B20603¦Prep center 3¦¦Sep-18-2020 14:15
2020-09-18 14:16 | 44092.5944 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Court services |  | 3 | 19.5 | 22 | 393 | 22.6 | 22.6 | 426 |  | 2020-09-18 14:16 | 44092.5944 | 22.6 | 22.6 | 426 |  | low | 2020-09-14 | B17477¦Court services¦¦Sep-18-2020 14:15
2020-09-18 14:16 | 44092.5945 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Peterborough Police |  | 3 | 21 | 18 | 404 | 22 | 25 | 594 |  | 2020-09-18 14:16 | 44092.5945 | 22 | 25 | 594 |  | low | 2020-09-14 | B70235¦Peterborough Police ¦¦Sep-18-2020 14:16
2020-09-18 14:16 | 44092.5945 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | Hallway - Outside of wahsrooms |  | 1 | 14.6 | 21 | 371 | 22.5 | 22.8 | 418 |  | 2020-09-18 14:16 | 44092.5945 | 22.5 | 22.8 | 418 |  | low | 2020-09-14 | B70277¦Hallway - Outside of wahsrooms¦¦Sep-18-2020 14:16
2020-09-18 14:16 | 44092.5947 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 2 |  | 0 | 16 | 33 | 411 | 22 | 26 | 509 |  | 2020-09-18 14:16 | 44092.5947 | 22 | 26 | 509 |  | low | 2020-09-14 | B25479¦Courtroom 2¦¦Sep-18-2020 14:16
2020-09-18 14:16 | 44092.5947 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JURY ROOM |  | 3 | 16 | 23 | 416 | 22.2 | 33 | 458 |  | 2020-09-18 14:16 | 44092.5947 | 22.2 | 33 | 458 |  | low | 2020-09-14 | B20022¦JURY ROOM¦¦Sep-18-2020 14:16
2020-09-18 14:17 | 44092.5948 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 409 |  | 9 | 18.3 | 24.2 | 388 | 22.3 | 20.3 | 418 | No | 2020-09-18 14:17 | 44092.5948 | 22.3 | 20.3 | 418 |  | low | 2020-09-14 | B21128¦409¦¦Sep-18-2020 14:16
2020-09-18 14:17 | 44092.595 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area at mens washroom |  | 1 | 14.7 | 30.6 | 387 | 20.8 | 34.2 | 614 |  | 2020-09-18 14:17 | 44092.595 | 20.8 | 34.2 | 614 |  | low | 2020-09-14 | B20474¦Basement waiting area at mens washroom¦¦Sep-18-2020 14:16
2020-09-18 14:17 | 44092.5951 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 1 |  | 2 | 16 | 33 | 411 | 22 | 26 | 526 |  | 2020-09-18 14:17 | 44092.5951 | 22 | 26 | 526 |  | low | 2020-09-14 | B25479¦Courtroom 1¦¦Sep-18-2020 14:16
2020-09-18 14:17 | 44092.5952 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 3 interview room |  | 0 | 19.5 | 22 | 393 | 22.6 | 21.8 | 441 |  | 2020-09-18 14:17 | 44092.5952 | 22.6 | 21.8 | 441 |  | low | 2020-09-14 | B17477¦LVL 3 interview room¦¦Sep-18-2020 14:17
2020-09-18 14:17 | 44092.5952 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR LEFT MEETING |  | 1 | 16 | 23 | 416 | 22.1 | 36.5 | 561 |  | 2020-09-18 14:17 | 44092.5952 | 22.1 | 36.5 | 561 |  | caution | 2020-09-14 | B20022¦2 FLOOR LEFT MEETING¦¦Sep-18-2020 14:17
2020-09-18 14:17 | 44092.5952 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom d back |  | 0 | 20.5 | 20.9 | 367 | 23.1 | 19.9 | 389 |  | 2020-09-18 14:17 | 44092.5952 | 23.1 | 19.9 | 389 |  | low | 2020-09-14 | Pearso¦Courtroom d back¦¦Sep-18-2020 14:17
2020-09-18 14:17 | 44092.5953 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center office 1 |  | 0 | 15.5 | 30.2 | 422 | 21.9 | 22 | 434 |  | 2020-09-18 14:17 | 44092.5953 | 21.9 | 22 | 434 |  | low | 2020-09-14 | B20603¦Prep center office 1¦¦Sep-18-2020 14:17
2020-09-18 14:17 | 44092.5953 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 vestibule |  | 0 | 21 | 18 | 404 | 22 | 22 | 505 |  | 2020-09-18 14:17 | 44092.5953 | 22 | 22 | 505 |  | low | 2020-09-14 | B70235¦Court #4 vestibule ¦¦Sep-18-2020 14:17
2020-09-18 14:18 | 44092.5956 | AINSWORTH | B70277 | B70277 - 34 Simcoe St - Barrie | 3rd Floor Stairwell |  | 1 | 14.6 | 21 | 371 | 23 | 24.6 | 465 |  | 2020-09-18 14:18 | 44092.5956 | 23 | 24.6 | 465 |  | low | 2020-09-14 | B70277¦3rd Floor Stairwell¦¦Sep-18-2020 14:17
2020-09-18 14:18 | 44092.5956 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NW hall |  | 0 | 15 | 30 | 425 | 21 | 46 | 575 |  | 2020-09-18 14:18 | 44092.5956 | 21 | 46 | 575 |  |  | 2020-09-14 | B25548¦NW hall¦¦Sep-18-2020 14:17
2020-09-18 14:18 | 44092.5956 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR RIGHT MEETING |  | 1 | 16 | 23 | 416 | 22.2 | 36.5 | 517 |  | 2020-09-18 14:18 | 44092.5956 | 22.2 | 36.5 | 517 |  | caution | 2020-09-14 | B20022¦2 FLOOR RIGHT MEETING¦¦Sep-18-2020 14:17
2020-09-18 14:18 | 44092.5959 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 4 |  | 0 | 16 | 33 | 411 | 22 | 27 | 575 |  | 2020-09-18 14:18 | 44092.5959 | 22 | 27 | 575 |  | low | 2020-09-14 | B25479¦Courtroom 4¦¦Sep-18-2020 14:18
2020-09-18 14:18 | 44092.596 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 400 |  | 4 | 18.3 | 24.2 | 388 | 22.8 | 19.8 | 434 | No | 2020-09-18 14:18 | 44092.596 | 22.8 | 19.8 | 434 |  | low | 2020-09-14 | B21128¦400¦¦Sep-18-2020 14:18
2020-09-18 14:18 | 44092.596 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 2 waiting area |  | 0 | 19.5 | 22 | 393 | 22.2 | 22.8 | 427 |  | 2020-09-18 14:18 | 44092.596 | 22.2 | 22.8 | 427 |  | low | 2020-09-14 | B17477¦LVL 2 waiting area¦¦Sep-18-2020 14:18
2020-09-18 14:18 | 44092.596 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 144 |  | 0 | 14 | 25 | 375 | 24.1 | 30.2 | 418 | No | 2020-09-18 14:18 | 44092.596 | 24.1 | 30.2 | 418 |  | low | 2020-09-14 | B14660¦144¦¦Sep-18-2020 14:18
2020-09-18 14:18 | 44092.5961 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 1 FLOOR MAIN HALL |  | 2 | 16 | 23 | 416 | 22 | 31 | 508 |  | 2020-09-18 14:18 | 44092.5961 | 22 | 31 | 508 |  | low | 2020-09-14 | B20022¦1 FLOOR MAIN HALL¦¦Sep-18-2020 14:18
2020-09-18 14:19 | 44092.5962 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center office 610 |  | 0 | 15.5 | 30.2 | 422 | 22 | 21.6 | 427 |  | 2020-09-18 14:19 | 44092.5962 | 22 | 21.6 | 427 |  | low | 2020-09-14 | B20603¦Prep center office 610¦¦Sep-18-2020 14:18
2020-09-18 14:19 | 44092.5964 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 5 |  | 4 | 16 | 33 | 411 | 22 | 28 | 542 |  | 2020-09-18 14:19 | 44092.5964 | 22 | 28 | 542 |  | low | 2020-09-14 | B25479¦Courtroom 5¦¦Sep-18-2020 14:18
2020-09-18 14:19 | 44092.5965 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom d back |  | 0 | 20.5 | 20.9 | 367 | 23.1 | 19.9 | 389 |  | 2020-09-18 14:19 | 44092.5965 | 23.1 | 19.9 | 389 |  | low | 2020-09-14 | Pearso¦Courtroom d back¦¦Sep-18-2020 14:18
2020-09-18 14:19 | 44092.5966 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview Room 4 |  | 0 | 21 | 18 | 404 | 22 | 22 | 509 |  | 2020-09-18 14:19 | 44092.5966 | 22 | 22 | 509 |  | low | 2020-09-14 | B70235¦Interview Room 4¦¦Sep-18-2020 14:19
2020-09-18 14:19 | 44092.5966 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Court room 2 waiting area |  | 0 | 12 | 37 | 392 | 22.4 | 31.5 | 506 | No | 2020-09-18 14:19 | 44092.5966 | 22.4 | 31.5 | 506 |  | low | 2020-09-14 | B20151¦Court room 2 waiting area ¦¦Sep-18-2020 14:19
2020-09-18 14:19 | 44092.5967 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | SOUTH WING ENTERANCE |  | 2 | 16 | 23 | 416 | 22.7 | 27.8 | 493 |  | 2020-09-18 14:19 | 44092.5967 | 22.7 | 27.8 | 493 |  | low | 2020-09-14 | B20022¦SOUTH WING ENTERANCE¦¦Sep-18-2020 14:19
2020-09-18 14:19 | 44092.5967 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 1 waiting area N |  | 0 | 19.5 | 22 | 393 | 22.2 | 23.2 | 419 |  | 2020-09-18 14:19 | 44092.5967 | 22.2 | 23.2 | 419 |  | low | 2020-09-14 | B17477¦LVL 1 waiting area N¦¦Sep-18-2020 14:19
2020-09-18 14:19 | 44092.5967 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Library |  | 0 | 16 | 33 | 411 | 22 | 31 | 534 |  | 2020-09-18 14:19 | 44092.5967 | 22 | 31 | 534 |  | low | 2020-09-14 | B25479¦Library ¦¦Sep-18-2020 14:19
2020-09-18 14:20 | 44092.5969 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 401 |  | 9 | 18.3 | 24.2 | 388 | 23.1 | 20.2 | 442 | No | 2020-09-18 14:20 | 44092.5969 | 23.1 | 20.2 | 442 |  | low | 2020-09-14 | B21128¦401¦¦Sep-18-2020 14:19
2020-09-18 14:20 | 44092.597 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Tc office |  | 1 | 16 | 33 | 411 | 23 | 30 | 542 |  | 2020-09-18 14:20 | 44092.597 | 23 | 30 | 542 |  | low | 2020-09-14 | B25479¦Tc office ¦¦Sep-18-2020 14:19
2020-09-18 14:20 | 44092.5971 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom e |  | 0 | 20.5 | 20.9 | 367 | 22.2 | 19.9 | 389 |  | 2020-09-18 14:20 | 44092.5971 | 22.2 | 19.9 | 389 |  | low | 2020-09-14 | Pearso¦Courtroom e¦¦Sep-18-2020 14:19
2020-09-18 14:20 | 44092.5972 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 122 |  | 0 | 14 | 25 | 375 | 24.1 | 28.1 | 424 | No | 2020-09-18 14:20 | 44092.5972 | 24.1 | 28.1 | 424 |  | low | 2020-09-14 | B14660¦122¦¦Sep-18-2020 14:20
2020-09-18 14:20 | 44092.5973 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 1 waiting area S |  | 0 | 19.5 | 22 | 393 | 22.3 | 23.9 | 416 |  | 2020-09-18 14:20 | 44092.5973 | 22.3 | 23.9 | 416 |  | low | 2020-09-14 | B17477¦LVL 1 waiting area S¦¦Sep-18-2020 14:20
2020-09-18 14:20 | 44092.5973 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center office 618 |  | 0 | 15.5 | 30.2 | 422 | 22.1 | 22.5 | 428 |  | 2020-09-18 14:20 | 44092.5973 | 22.1 | 22.5 | 428 |  | low | 2020-09-14 | B20603¦Prep center office 618¦¦Sep-18-2020 14:20
2020-09-18 14:20 | 44092.5975 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Jp lobby |  | 0 | 16 | 33 | 411 | 23 | 30 | 555 |  | 2020-09-18 14:20 | 44092.5975 | 23 | 30 | 555 |  | low | 2020-09-14 | B25479¦Jp lobby ¦¦Sep-18-2020 14:20
2020-09-18 14:21 | 44092.5976 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 1 FLOOR HALLWAY, BOTTOM OF COURT 2 |  | 2 | 16 | 23 | 416 | 20.8 | 32 | 420 | ADDED ROOM* | 2020-09-18 14:20 | 44092.5976 | 20.8 | 32 | 420 |  | low | 2020-09-14 | B20022¦1 FLOOR HALLWAY, BOTTOM OF COURT 2¦¦Sep-18-2020 14:20
2020-09-18 14:21 | 44092.5978 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | 402 |  | 6 | 18.3 | 24.2 | 388 | 23 | 18.3 | 437 | No | 2020-09-18 14:21 | 44092.5978 | 23 | 18.3 | 437 |  | low | 2020-09-14 | B21128¦402¦¦Sep-18-2020 14:20
2020-09-18 14:21 | 44092.5978 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 vestibule |  | 0 | 21 | 18 | 404 | 22 | 23 | 471 |  | 2020-09-18 14:21 | 44092.5978 | 22 | 23 | 471 |  | low | 2020-09-14 | B70235¦Court #3 vestibule ¦¦Sep-18-2020 14:20
2020-09-18 14:21 | 44092.5979 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 waiting area |  | 0 | 19.5 | 22 | 393 | 22.3 | 24.9 | 403 |  | 2020-09-18 14:21 | 44092.5979 | 22.3 | 24.9 | 403 |  | low | 2020-09-14 | B17477¦Courtroom 100 waiting area¦¦Sep-18-2020 14:21
2020-09-18 14:21 | 44092.598 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom e |  | 0 | 20.5 | 20.9 | 367 | 22.2 | 19 | 389 |  | 2020-09-18 14:21 | 44092.598 | 22.2 | 19 | 389 |  | low | 2020-09-14 | Pearso¦Courtroom e¦¦Sep-18-2020 14:21
2020-09-18 14:21 | 44092.5981 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Front lobby |  | 4 | 23 | 21 | 390 | 22 | 24 | 445 |  | 2020-09-18 14:21 | 44092.5981 | 22 | 24 | 445 |  | low | 2020-09-14 | B19570¦Front lobby ¦¦Sep-18-2020 14:21
2020-09-18 14:21 | 44092.5981 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | TOP STAIRS OUTSIDE COURT 2 |  | 2 | 16 | 23 | 416 | 21.7 | 35.6 | 557 | ADDED ROOM* | 2020-09-18 14:21 | 44092.5981 | 21.7 | 35.6 | 557 |  | caution | 2020-09-14 | B20022¦TOP STAIRS OUTSIDE COURT 2¦¦Sep-18-2020 14:21
2020-09-18 14:21 | 44092.5981 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NE hall |  | 0 | 15 | 30 | 425 | 22 | 47 | 780 |  | 2020-09-18 14:21 | 44092.5981 | 22 | 47 | 780 |  |  | 2020-09-14 | B25548¦NE hall¦¦Sep-18-2020 14:21
2020-09-18 14:22 | 44092.5984 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 647 |  | 0 | 15.5 | 30.2 | 422 | 22 | 22.9 | 422 |  | 2020-09-18 14:22 | 44092.5984 | 22 | 22.9 | 422 |  | low | 2020-09-14 | B20603¦Office 647¦¦Sep-18-2020 14:21
2020-09-18 14:22 | 44092.5985 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Crown attorneys office |  | 2 | 18.3 | 24.2 | 388 | 23 | 18.9 | 420 | No | 2020-09-18 14:22 | 44092.5985 | 23 | 18.9 | 420 |  | low | 2020-09-14 | B21128¦Crown attorneys office ¦¦Sep-18-2020 14:21
2020-09-18 14:22 | 44092.5986 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 1 interview room 1 |  | 0 | 19.5 | 22 | 393 | 22.3 | 25.6 | 397 |  | 2020-09-18 14:22 | 44092.5986 | 22.3 | 25.6 | 397 |  | low | 2020-09-14 | B17477¦LVL 1 interview room 1¦¦Sep-18-2020 14:22
2020-09-18 14:22 | 44092.5987 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | TOP STAIRS SOUTH ENTRANCE |  | 2 | 16 | 23 | 416 | 22.6 | 30.4 | 464 | ADDED ROOM* | 2020-09-18 14:22 | 44092.5987 | 22.6 | 30.4 | 464 |  | low | 2020-09-14 | B20022¦TOP STAIRS SOUTH ENTRANCE¦¦Sep-18-2020 14:22
2020-09-18 14:22 | 44092.5987 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview Room 3 |  | 0 | 21 | 18 | 404 | 23 | 23 | 510 |  | 2020-09-18 14:22 | 44092.5987 | 23 | 23 | 510 |  | low | 2020-09-14 | B70235¦Interview Room 3¦¦Sep-18-2020 14:22
2020-09-18 14:22 | 44092.5988 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 105 |  | 0 | 14 | 25 | 375 | 24 | 27.7 | 421 | No | 2020-09-18 14:22 | 44092.5988 | 24 | 27.7 | 421 |  | low | 2020-09-14 | B14660¦105¦¦Sep-18-2020 14:22
2020-09-18 14:23 | 44092.5992 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom e back |  | 0 | 20.5 | 20.9 | 367 | 21.9 | 19.9 | 391 |  | 2020-09-18 14:23 | 44092.5992 | 21.9 | 19.9 | 391 |  | low | 2020-09-14 | Pearso¦Courtroom e back¦¦Sep-18-2020 14:22
2020-09-18 14:23 | 44092.5994 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 1 interview room 2 |  | 0 | 19.5 | 22 | 393 | 22 | 25.6 | 396 |  | 2020-09-18 14:23 | 44092.5994 | 22 | 25.6 | 396 |  | low | 2020-09-14 | B17477¦LVL 1 interview room 2¦¦Sep-18-2020 14:23
2020-09-18 14:23 | 44092.5994 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin office area |  | 4 | 16 | 37 | 392 | 22.2 | 30.9 | 588 | No | 2020-09-18 14:23 | 44092.5994 | 22.2 | 30.9 | 588 |  | low | 2020-09-14 | B20151¦Admin office area ¦¦Sep-18-2020 14:23
2020-09-18 14:23 | 44092.5996 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Hallway nw |  | 1 | 23 | 21 | 390 | 23 | 22 | 406 |  | 2020-09-18 14:23 | 44092.5996 | 23 | 22 | 406 |  | low | 2020-09-14 | B19570¦Hallway nw ¦¦Sep-18-2020 14:23
2020-09-18 14:23 | 44092.5996 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | E hall |  | 0 | 15 | 30 | 425 | 24 | 42 | 730 |  | 2020-09-18 14:23 | 44092.5996 | 24 | 42 | 730 |  |  | 2020-09-14 | B25548¦E hall¦¦Sep-18-2020 14:23
2020-09-18 14:23 | 44092.5996 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area for courtroom3 |  | 1 | 14.7 | 30.6 | 387 | 20.5 | 33.5 | 617 |  | 2020-09-18 14:23 | 44092.5996 | 20.5 | 33.5 | 617 |  | low | 2020-09-14 | B20474¦Waiting area for courtroom3¦¦Sep-18-2020 14:23
2020-09-18 14:24 | 44092.5997 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 106 |  | 0 | 14 | 25 | 375 | 23.7 | 24.5 | 429 | No | 2020-09-18 14:24 | 44092.5997 | 23.7 | 24.5 | 429 |  | low | 2020-09-14 | B14660¦106¦¦Sep-18-2020 14:23
2020-09-18 14:24 | 44092.5998 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 2 |  | 0 | 15.5 | 30.2 | 422 | 22.2 | 21.6 | 423 |  | 2020-09-18 14:24 | 44092.5998 | 22.2 | 21.6 | 423 |  | low | 2020-09-14 | B20603¦Office 2¦¦Sep-18-2020 14:23
2020-09-18 14:24 | 44092.5999 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 259 |  | 1 | 23 | 21 | 390 | 23 | 21 | 407 |  | 2020-09-18 14:24 | 44092.5999 | 23 | 21 | 407 |  | low | 2020-09-14 | B19570¦259¦¦Sep-18-2020 14:23
2020-09-18 14:24 | 44092.6 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Interview Room 2 |  | 0 | 21 | 18 | 404 | 23 | 23 | 517 |  | 2020-09-18 14:24 | 44092.6 | 23 | 23 | 517 |  | low | 2020-09-14 | B70235¦Interview Room 2¦¦Sep-18-2020 14:23
2020-09-18 14:24 | 44092.6 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom f |  | 0 | 20.5 | 20.9 | 367 | 22.8 | 20.4 | 390 |  | 2020-09-18 14:24 | 44092.6 | 22.8 | 20.4 | 390 |  | low | 2020-09-14 | Pearso¦Courtroom f¦¦Sep-18-2020 14:24
2020-09-18 14:24 | 44092.6003 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 265 |  | 1 | 23 | 21 | 390 | 23 | 21 | 409 |  | 2020-09-18 14:24 | 44092.6003 | 23 | 21 | 409 |  | low | 2020-09-14 | B19570¦265¦¦Sep-18-2020 14:24
2020-09-18 14:25 | 44092.6007 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 264 |  | 1 | 23 | 21 | 390 | 23 | 20 | 406 |  | 2020-09-18 14:25 | 44092.6007 | 23 | 20 | 406 |  | low | 2020-09-14 | B19570¦264¦¦Sep-18-2020 14:25
2020-09-18 14:25 | 44092.6008 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | SE hall |  | 0 | 15 | 30 | 425 | 28 | 33 | 600 |  | 2020-09-18 14:25 | 44092.6008 | 28 | 33 | 600 | high | low | 2020-09-14 | B25548¦SE hall¦¦Sep-18-2020 14:25
2020-09-18 14:25 | 44092.6008 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 3 |  | 0 | 15.5 | 30.2 | 422 | 22.1 | 21.5 | 423 |  | 2020-09-18 14:25 | 44092.6008 | 22.1 | 21.5 | 423 |  | low | 2020-09-14 | B20603¦Office 3 ¦¦Sep-18-2020 14:25
2020-09-18 14:25 | 44092.6009 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 judge |  | 0 | 21 | 18 | 404 | 23 | 22 | 462 |  | 2020-09-18 14:25 | 44092.6009 | 23 | 22 | 462 |  | low | 2020-09-14 | B70235¦Court #2 judge ¦¦Sep-18-2020 14:25
2020-09-18 14:26 | 44092.601 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom f back |  | 0 | 20.5 | 20.9 | 367 | 22.4 | 20.6 | 394 |  | 2020-09-18 14:26 | 44092.601 | 22.4 | 20.6 | 394 |  | low | 2020-09-14 | Pearso¦Courtroom f back¦¦Sep-18-2020 14:25
2020-09-18 14:26 | 44092.6011 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 261 |  | 1 | 23 | 21 | 390 | 23 | 20 | 403 |  | 2020-09-18 14:26 | 44092.6011 | 23 | 20 | 403 |  | low | 2020-09-14 | B19570¦261¦¦Sep-18-2020 14:25
2020-09-18 14:26 | 44092.6015 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 260 |  | 1 | 23 | 21 | 390 | 23 | 21 | 398 |  | 2020-09-18 14:26 | 44092.6015 | 23 | 21 | 398 |  | low | 2020-09-14 | B19570¦260¦¦Sep-18-2020 14:26
2020-09-18 14:26 | 44092.6016 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | SW hall |  | 0 | 15 | 30 | 425 | 27 | 33 | 600 |  | 2020-09-18 14:26 | 44092.6016 | 27 | 33 | 600 | caution | low | 2020-09-14 | B25548¦SW hall¦¦Sep-18-2020 14:26
2020-09-18 14:26 | 44092.6017 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 4 |  | 0 | 15.5 | 30.2 | 422 | 21.9 | 21.8 | 422 |  | 2020-09-18 14:26 | 44092.6017 | 21.9 | 21.8 | 422 |  | low | 2020-09-14 | B20603¦Office 4 ¦¦Sep-18-2020 14:26
2020-09-18 14:27 | 44092.6018 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin supervisor room |  | 0 | 12 | 37 | 392 | 22.3 | 32.9 | 610 | No | 2020-09-18 14:27 | 44092.6018 | 22.3 | 32.9 | 610 |  | low | 2020-09-14 | B20151¦Admin supervisor room ¦¦Sep-18-2020 14:26
2020-09-18 14:27 | 44092.602 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Police room 1 |  | 0 | 20.5 | 20.9 | 367 | 22.5 | 21.7 | 397 |  | 2020-09-18 14:27 | 44092.602 | 22.5 | 21.7 | 397 |  | low | 2020-09-14 | Pearso¦Police room 1¦¦Sep-18-2020 14:26
2020-09-18 14:27 | 44092.602 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 West |  | 0 | 17.1 | 27 | 402 | 21.3 | 33.7 | 424 |  | 2020-09-18 14:27 | 44092.602 | 21.3 | 33.7 | 424 |  | low | 2020-09-14 | B10577¦Courtroom 3 West¦¦Sep-18-2020 14:26
2020-09-18 14:27 | 44092.602 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 111 |  | 0 | 14 | 25 | 375 | 23.3 | 28.7 | 444 | No | 2020-09-18 14:27 | 44092.602 | 23.3 | 28.7 | 444 |  | low | 2020-09-14 | B14660¦111¦¦Sep-18-2020 14:26
2020-09-18 14:27 | 44092.6021 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 lawyer |  | 0 | 21 | 18 | 404 | 23 | 22 | 461 |  | 2020-09-18 14:27 | 44092.6021 | 23 | 22 | 461 |  | low | 2020-09-14 | B70235¦Court #2 lawyer ¦¦Sep-18-2020 14:27
2020-09-18 14:27 | 44092.6021 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Law library hall s |  | 1 | 23 | 21 | 390 | 22 | 23 | 392 |  | 2020-09-18 14:27 | 44092.6021 | 22 | 23 | 392 |  | low | 2020-09-14 | B19570¦Law library hall s¦¦Sep-18-2020 14:27
2020-09-18 14:28 | 44092.6025 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 4 waiting room S |  | 2 | 19.5 | 22 | 393 | 22.3 | 23.3 | 416 | Courtroom 100 occupied | 2020-09-18 14:28 | 44092.6025 | 22.3 | 23.3 | 416 |  | low | 2020-09-14 | B17477¦LVL 4 waiting room S¦¦Sep-18-2020 14:27
2020-09-18 14:28 | 44092.6026 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Law library hall n |  | 1 | 23 | 21 | 390 | 22 | 24 | 399 |  | 2020-09-18 14:28 | 44092.6026 | 22 | 24 | 399 |  | low | 2020-09-14 | B19570¦Law library hall n¦¦Sep-18-2020 14:27
2020-09-18 14:28 | 44092.6026 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | Center hall |  | 0 | 15 | 30 | 425 | 25 | 36 | 620 |  | 2020-09-18 14:28 | 44092.6026 | 25 | 36 | 620 |  | caution | 2020-09-14 | B25548¦Center hall¦¦Sep-18-2020 14:27
2020-09-18 14:28 | 44092.6027 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main entrance |  | 0 | 17.8 | 20.4 | 397 | 18.4 | 30.2 | 400 |  | 2020-09-18 14:28 | 44092.6027 | 18.4 | 30.2 | 400 |  | low | 2020-09-14 | B10577¦Main entrance ¦¦Sep-18-2020 14:27
2020-09-18 14:28 | 44092.6029 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Police room 2 |  | 0 | 20.5 | 20.9 | 367 | 22.4 | 21.8 | 402 |  | 2020-09-18 14:28 | 44092.6029 | 22.4 | 21.8 | 402 |  | low | 2020-09-14 | Pearso¦Police room 2¦¦Sep-18-2020 14:28
2020-09-18 14:28 | 44092.6031 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #2 vestibule |  | 0 | 21 | 18 | 404 | 23 | 22 | 475 |  | 2020-09-18 14:28 | 44092.6031 | 23 | 22 | 475 |  | low | 2020-09-14 | B70235¦Court #2 vestibule ¦¦Sep-18-2020 14:28
2020-09-18 14:28 | 44092.6031 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 5 top |  | 1 | 23 | 21 | 390 | 22 | 23 | 439 |  | 2020-09-18 14:28 | 44092.6031 | 22 | 23 | 439 |  | low | 2020-09-14 | B19570¦Stairwell 5 top ¦¦Sep-18-2020 14:28
2020-09-18 14:29 | 44092.6032 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 5 |  | 0 | 15.5 | 30.2 | 422 | 22 | 21.4 | 422 |  | 2020-09-18 14:29 | 44092.6032 | 22 | 21.4 | 422 |  | low | 2020-09-14 | B20603¦Office 5 ¦¦Sep-18-2020 14:28
2020-09-18 14:29 | 44092.6033 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Lobby south |  | 1 | 17.8 | 20.4 | 397 | 20.4 | 39.3 | 519 |  | 2020-09-18 14:29 | 44092.6033 | 20.4 | 39.3 | 519 |  | caution | 2020-09-14 | B10577¦Main Lobby south ¦¦Sep-18-2020 14:28
2020-09-18 14:29 | 44092.6035 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 5 bottom |  | 1 | 23 | 21 | 390 | 22 | 26 | 416 |  | 2020-09-18 14:29 | 44092.6035 | 22 | 26 | 416 |  | low | 2020-09-14 | B19570¦Stairwell 5 bottom ¦¦Sep-18-2020 14:29
2020-09-18 14:29 | 44092.6036 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 4 waiting room N |  | 0 | 19.5 | 22 | 393 | 22.5 | 21.5 | 412 |  | 2020-09-18 14:29 | 44092.6036 | 22.5 | 21.5 | 412 |  | low | 2020-09-14 | B17477¦LVL 4 waiting room N¦¦Sep-18-2020 14:29
2020-09-18 14:29 | 44092.6037 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-E wall |  | 0 | 15 | 30 | 425 | 25 | 37 | 600 |  | 2020-09-18 14:29 | 44092.6037 | 25 | 37 | 600 |  | caution | 2020-09-14 | B25548¦1-E wall¦¦Sep-18-2020 14:29
2020-09-18 14:29 | 44092.6037 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 203 |  | 0 | 14 | 25 | 375 | 23 | 27.7 | 423 | No | 2020-09-18 14:29 | 44092.6037 | 23 | 27.7 | 423 |  | low | 2020-09-14 | B14660¦203¦¦Sep-18-2020 14:29
2020-09-18 14:30 | 44092.6039 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Court service office |  | 2 | 17.8 | 20.4 | 397 | 21.8 | 27.9 | 519 |  | 2020-09-18 14:30 | 44092.6039 | 21.8 | 27.9 | 519 |  | low | 2020-09-14 | B10577¦Court service office ¦¦Sep-18-2020 14:29
2020-09-18 14:30 | 44092.6039 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Basement hall w |  | 1 | 23 | 21 | 390 | 22 | 27 | 424 |  | 2020-09-18 14:30 | 44092.6039 | 22 | 27 | 424 |  | low | 2020-09-14 | B19570¦Basement hall w¦¦Sep-18-2020 14:29
2020-09-18 14:30 | 44092.6039 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Police room 3 |  | 0 | 20.5 | 20.9 | 367 | 22.3 | 21.8 | 404 |  | 2020-09-18 14:30 | 44092.6039 | 22.3 | 21.8 | 404 |  | low | 2020-09-14 | Pearso¦Police room 3¦¦Sep-18-2020 14:29
2020-09-18 14:30 | 44092.604 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Duty Counsel room |  | 0 | 21 | 18 | 404 | 23 | 23 | 503 |  | 2020-09-18 14:30 | 44092.604 | 23 | 23 | 503 |  | low | 2020-09-14 | B70235¦Duty Counsel room ¦¦Sep-18-2020 14:29
2020-09-18 14:30 | 44092.6042 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basement waiting area inside dbl doors |  | 1 | 14.7 | 30.6 | 387 | 20.7 | 33.5 | 622 |  | 2020-09-18 14:30 | 44092.6042 | 20.7 | 33.5 | 622 |  | low | 2020-09-14 | B20474¦Basement waiting area inside dbl doors¦¦Sep-18-2020 14:30
2020-09-18 14:30 | 44092.6043 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 641 |  | 0 | 15.5 | 30.2 | 422 | 21.7 | 22.1 | 421 |  | 2020-09-18 14:30 | 44092.6043 | 21.7 | 22.1 | 421 |  | low | 2020-09-14 | B20603¦Office 641¦¦Sep-18-2020 14:30
2020-09-18 14:30 | 44092.6043 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court admin hall |  | 1 | 23 | 21 | 390 | 22 | 25 | 425 |  | 2020-09-18 14:30 | 44092.6043 | 22 | 25 | 425 |  | low | 2020-09-14 | B19570¦Court admin hall ¦¦Sep-18-2020 14:30
2020-09-18 14:30 | 44092.6045 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Witness area |  | 0 | 17.8 | 20.4 | 397 | 21.1 | 38.6 | 590 |  | 2020-09-18 14:30 | 44092.6045 | 21.1 | 38.6 | 590 |  | caution | 2020-09-14 | B10577¦Witness area ¦¦Sep-18-2020 14:30
2020-09-18 14:31 | 44092.6045 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 waiting area |  | 0 | 19.5 | 22 | 393 | 22.6 | 22.4 | 404 |  | 2020-09-18 14:31 | 44092.6045 | 22.6 | 22.4 | 404 |  | low | 2020-09-14 | B17477¦Courtroom 400 waiting area¦¦Sep-18-2020 14:30
2020-09-18 14:31 | 44092.6047 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-E wall |  | 0 | 15 | 30 | 425 | 25 | 38 | 595 |  | 2020-09-18 14:31 | 44092.6047 | 25 | 38 | 595 |  | caution | 2020-09-14 | B25548¦1-E wall¦¦Sep-18-2020 14:30
2020-09-18 14:31 | 44092.6047 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Employee entrance |  | 1 | 23 | 21 | 390 | 22 | 26 | 422 |  | 2020-09-18 14:31 | 44092.6047 | 22 | 26 | 422 |  | low | 2020-09-14 | B19570¦Employee entrance¦¦Sep-18-2020 14:30
2020-09-18 14:31 | 44092.6048 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Police room 4 |  | 0 | 20.5 | 20.9 | 367 | 22.2 | 22 | 407 |  | 2020-09-18 14:31 | 44092.6048 | 22.2 | 22 | 407 |  | low | 2020-09-14 | Pearso¦Police room 4¦¦Sep-18-2020 14:30
2020-09-18 14:31 | 44092.605 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 south |  | 0 | 17.8 | 20.4 | 397 | 21.7 | 38 | 519 |  | 2020-09-18 14:31 | 44092.605 | 21.7 | 38 | 519 |  | caution | 2020-09-14 | B10577¦Courtroom 1 south ¦¦Sep-18-2020 14:31
2020-09-18 14:31 | 44092.605 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 213 |  | 0 | 14 | 25 | 375 | 22.8 | 27.6 | 453 | No | 2020-09-18 14:31 | 44092.605 | 22.8 | 27.6 | 453 |  | low | 2020-09-14 | B14660¦213¦¦Sep-18-2020 14:31
2020-09-18 14:32 | 44092.6052 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin file room |  | 0 | 12 | 37 | 392 | 22.9 | 27.8 | 543 | No | 2020-09-18 14:32 | 44092.6052 | 22.9 | 27.8 | 543 |  | low | 2020-09-14 | B20151¦Admin file room ¦¦Sep-18-2020 14:31
2020-09-18 14:32 | 44092.6052 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 4 interview room |  | 0 | 19.5 | 22 | 393 | 22.4 | 22 | 402 |  | 2020-09-18 14:32 | 44092.6052 | 22.4 | 22 | 402 |  | low | 2020-09-14 | B17477¦LVL 4 interview room ¦¦Sep-18-2020 14:31
2020-09-18 14:32 | 44092.6053 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-E wall |  | 0 | 15 | 30 | 425 | 25 | 37 | 590 |  | 2020-09-18 14:32 | 44092.6053 | 25 | 37 | 590 |  | caution | 2020-09-14 | B25548¦1-E wall¦¦Sep-18-2020 14:31
2020-09-18 14:32 | 44092.6054 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 7 |  | 0 | 15.5 | 30.2 | 422 | 21.9 | 22.6 | 428 |  | 2020-09-18 14:32 | 44092.6054 | 21.9 | 22.6 | 428 |  | low | 2020-09-14 | B20603¦Office 7 ¦¦Sep-18-2020 14:31
2020-09-18 14:32 | 44092.6054 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Police Sergeant office |  | 1 | 21 | 18 | 404 | 23 | 24 | 599 |  | 2020-09-18 14:32 | 44092.6054 | 23 | 24 | 599 |  | low | 2020-09-14 | B70235¦Police Sergeant office ¦¦Sep-18-2020 14:31
2020-09-18 14:32 | 44092.6057 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 1 |  | 0 | 20.5 | 20.9 | 367 | 23.3 | 20.4 | 408 |  | 2020-09-18 14:32 | 44092.6057 | 23.3 | 20.4 | 408 |  | low | 2020-09-14 | Pearso¦Lobby 1¦¦Sep-18-2020 14:32
2020-09-18 14:32 | 44092.6059 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 East |  | 0 | 17.8 | 20.4 | 397 | 21.5 | 37.4 | 503 |  | 2020-09-18 14:32 | 44092.6059 | 21.5 | 37.4 | 503 |  | caution | 2020-09-14 | B10577¦Courtroom 1 East ¦¦Sep-18-2020 14:32
2020-09-18 14:33 | 44092.6061 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 15 | 30 | 425 | 26 | 37 | 590 |  | 2020-09-18 14:33 | 44092.6061 | 26 | 37 | 590 | caution | caution | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 14:32
2020-09-18 14:33 | 44092.6063 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 W |  | 0 | 19.5 | 22 | 393 | 22.1 | 21.5 | 399 |  | 2020-09-18 14:33 | 44092.6063 | 22.1 | 21.5 | 399 |  | low | 2020-09-14 | B17477¦Courtroom 400 W¦¦Sep-18-2020 14:33
2020-09-18 14:33 | 44092.6064 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 judge |  | 1 | 21 | 18 | 404 | 23 | 19 | 503 |  | 2020-09-18 14:33 | 44092.6064 | 23 | 19 | 503 |  | low | 2020-09-14 | B70235¦Court #1 judge ¦¦Sep-18-2020 14:33
2020-09-18 14:34 | 44092.6066 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 2 |  | 0 | 20.5 | 20.9 | 367 | 24.3 | 19.3 | 399 |  | 2020-09-18 14:34 | 44092.6066 | 24.3 | 19.3 | 399 |  | low | 2020-09-14 | Pearso¦Lobby 2¦¦Sep-18-2020 14:33
2020-09-18 14:34 | 44092.6067 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 North |  | 0 | 17.8 | 20.4 | 397 | 21.6 |  | 497 |  | 2020-09-18 14:34 | 44092.6067 | 21.6 |  | 497 |  |  | 2020-09-14 | B10577¦Courtroom 1 North ¦¦Sep-18-2020 14:33
2020-09-18 14:34 | 44092.6068 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 626 |  | 0 | 15.5 | 30.2 | 422 | 22.1 | 22.4 | 447 |  | 2020-09-18 14:34 | 44092.6068 | 22.1 | 22.4 | 447 |  | low | 2020-09-14 | B20603¦Office 626¦¦Sep-18-2020 14:33
2020-09-18 14:34 | 44092.6068 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 15 | 30 | 425 | 26 | 37 | 590 |  | 2020-09-18 14:34 | 44092.6068 | 26 | 37 | 590 | caution | caution | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 14:33
2020-09-18 14:34 | 44092.607 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 400 E |  | 0 | 19.5 | 22 | 393 | 22.2 | 22.6 | 397 |  | 2020-09-18 14:34 | 44092.607 | 22.2 | 22.6 | 397 |  | low | 2020-09-14 | B17477¦Courtroom 400 E¦¦Sep-18-2020 14:34
2020-09-18 14:35 | 44092.6075 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 15 | 30 | 425 | 26 | 35 | 585 |  | 2020-09-18 14:35 | 44092.6075 | 26 | 35 | 585 | caution | caution | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 14:34
2020-09-18 14:35 | 44092.6075 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 West |  | 0 | 17.8 | 20.4 | 397 | 21.4 | 39.2 | 493 |  | 2020-09-18 14:35 | 44092.6075 | 21.4 | 39.2 | 493 |  | caution | 2020-09-14 | B10577¦Courtroom 1 West ¦¦Sep-18-2020 14:34
2020-09-18 14:35 | 44092.6075 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 lawyer |  | 1 | 21 | 18 | 404 | 23 | 20 | 500 |  | 2020-09-18 14:35 | 44092.6075 | 23 | 20 | 500 |  | low | 2020-09-14 | B70235¦Court #1 lawyer ¦¦Sep-18-2020 14:34
2020-09-18 14:35 | 44092.6076 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court services office |  | 4 | 23 | 21 | 390 | 22 | 22 | 422 |  | 2020-09-18 14:35 | 44092.6076 | 22 | 22 | 422 |  | low | 2020-09-14 | B19570¦Court services office ¦¦Sep-18-2020 14:34
2020-09-18 14:35 | 44092.6076 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 210A |  | 3 | 14 | 25 | 375 | 23.3 | 26.3 | 445 | No | 2020-09-18 14:35 | 44092.6076 | 23.3 | 26.3 | 445 |  | low | 2020-09-14 | B14660¦210A¦¦Sep-18-2020 14:34
2020-09-18 14:35 | 44092.6077 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 3 |  | 0 | 20.5 | 20.9 | 367 | 24.5 | 19.5 | 391 |  | 2020-09-18 14:35 | 44092.6077 | 24.5 | 19.5 | 391 |  | low | 2020-09-14 | Pearso¦Lobby 3¦¦Sep-18-2020 14:35
2020-09-18 14:35 | 44092.6079 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | 612 |  | 0 | 15.5 | 30.2 | 422 | 21.9 | 21.7 | 448 |  | 2020-09-18 14:35 | 44092.6079 | 21.9 | 21.7 | 448 |  | low | 2020-09-14 | B20603¦612¦¦Sep-18-2020 14:35
2020-09-18 14:35 | 44092.6079 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 Center |  | 0 | 17.8 | 20.4 | 397 | 21.3 | 39.8 | 494 |  | 2020-09-18 14:35 | 44092.6079 | 21.3 | 39.8 | 494 |  | caution | 2020-09-14 | B10577¦Courtroom 1 Center ¦¦Sep-18-2020 14:35
2020-09-18 14:35 | 44092.6079 | AINSWORTH | B20151 | B20151 - 100 St. Patrick St - Stratford | Admin waiting area |  | 0 | 12 | 37 | 392 | 22.3 | 24.4 | 462 | No | 2020-09-18 14:35 | 44092.6079 | 22.3 | 24.4 | 462 |  | low | 2020-09-14 | B20151¦Admin waiting area ¦¦Sep-18-2020 14:35
2020-09-18 14:36 | 44092.608 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Crown attorney office |  | 0 | 19.5 | 22 | 393 | 22.1 | 23 | 403 |  | 2020-09-18 14:36 | 44092.608 | 22.1 | 23 | 403 |  | low | 2020-09-14 | B17477¦Crown attorney office¦¦Sep-18-2020 14:35
2020-09-18 14:36 | 44092.6081 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 15 | 30 | 425 | 26 | 35 | 590 |  | 2020-09-18 14:36 | 44092.6081 | 26 | 35 | 590 | caution | caution | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 14:35
2020-09-18 14:36 | 44092.6082 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Poa office |  | 5 | 23 | 21 | 390 | 22 | 29 | 472 |  | 2020-09-18 14:36 | 44092.6082 | 22 | 29 | 472 |  | low | 2020-09-14 | B19570¦Poa office¦¦Sep-18-2020 14:35
2020-09-18 14:36 | 44092.6083 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #1 vestibule |  | 0 | 21 | 18 | 404 | 23 | 25 | 780 |  | 2020-09-18 14:36 | 44092.6083 | 23 | 25 | 780 |  | low | 2020-09-14 | B70235¦Court #1 vestibule ¦¦Sep-18-2020 14:35
2020-09-18 14:37 | 44092.6087 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 15 | 30 | 425 | 26 | 35 | 600 |  | 2020-09-18 14:37 | 44092.6087 | 26 | 35 | 600 | caution | caution | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 14:36
2020-09-18 14:37 | 44092.6087 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 206 |  | 2 | 14 | 25 | 375 | 22.6 | 26 | 427 | No | 2020-09-18 14:37 | 44092.6087 | 22.6 | 26 | 427 |  | low | 2020-09-14 | B14660¦206¦¦Sep-18-2020 14:36
2020-09-18 14:37 | 44092.6088 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Office |  | 1 | 20.5 | 20.9 | 367 | 23.4 | 21.6 | 405 |  | 2020-09-18 14:37 | 44092.6088 | 23.4 | 21.6 | 405 |  | low | 2020-09-14 | Pearso¦Office¦¦Sep-18-2020 14:36
2020-09-18 14:37 | 44092.6088 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 5 |  | 2 | 23 | 21 | 390 | 23 | 27 | 428 |  | 2020-09-18 14:37 | 44092.6088 | 23 | 27 | 428 |  | low | 2020-09-14 | B19570¦Court 5¦¦Sep-18-2020 14:36
2020-09-18 14:37 | 44092.6088 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 5 waiting area N |  | 0 | 19.5 | 22 | 393 | 22.3 | 23.3 | 403 |  | 2020-09-18 14:37 | 44092.6088 | 22.3 | 23.3 | 403 |  | low | 2020-09-14 | B17477¦LVL 5 waiting area N¦¦Sep-18-2020 14:36
2020-09-18 14:37 | 44092.6088 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 10 |  | 0 | 15.5 | 30.2 | 422 | 22 | 21.9 | 438 |  | 2020-09-18 14:37 | 44092.6088 | 22 | 21.9 | 438 |  | low | 2020-09-14 | B20603¦Office 10 ¦¦Sep-18-2020 14:36
2020-09-18 14:37 | 44092.6093 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 5 waiting area S |  | 0 | 19.5 | 22 | 393 | 22.5 | 24.4 | 407 |  | 2020-09-18 14:37 | 44092.6093 | 22.5 | 24.4 | 407 |  | low | 2020-09-14 | B17477¦LVL 5 waiting area S¦¦Sep-18-2020 14:37
2020-09-18 14:38 | 44092.6095 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 4 |  | 4 | 23 | 21 | 390 | 21 | 28 | 428 |  | 2020-09-18 14:38 | 44092.6095 | 21 | 28 | 428 |  | low | 2020-09-14 | B19570¦Court 4¦¦Sep-18-2020 14:37
2020-09-18 14:38 | 44092.6096 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-S wall |  | 0 | 15 | 30 | 425 | 26 | 35 | 580 |  | 2020-09-18 14:38 | 44092.6096 | 26 | 35 | 580 | caution | caution | 2020-09-14 | B25548¦1-S wall¦¦Sep-18-2020 14:37
2020-09-18 14:38 | 44092.6099 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 3 |  | 2 | 23 | 21 | 390 | 21 | 29 | 417 |  | 2020-09-18 14:38 | 44092.6099 | 21 | 29 | 417 |  | low | 2020-09-14 | B19570¦Court 3¦¦Sep-18-2020 14:38
2020-09-18 14:38 | 44092.61 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space |  | 0 | 15.5 | 30.2 | 422 | 21.7 | 22 | 434 |  | 2020-09-18 14:38 | 44092.61 | 21.7 | 22 | 434 |  | low | 2020-09-14 | B20603¦Office space ¦¦Sep-18-2020 14:38
2020-09-18 14:39 | 44092.6102 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 500 waiting area |  | 0 | 19.5 | 22 | 393 | 22.6 | 23 | 403 |  | 2020-09-18 14:39 | 44092.6102 | 22.6 | 23 | 403 |  | low | 2020-09-14 | B17477¦Courtroom 500 waiting area¦¦Sep-18-2020 14:38
2020-09-18 14:39 | 44092.6104 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-W wall |  | 0 | 15 | 30 | 425 | 25 | 36 | 620 |  | 2020-09-18 14:39 | 44092.6104 | 25 | 36 | 620 |  | caution | 2020-09-14 | B25548¦1-W wall¦¦Sep-18-2020 14:38
2020-09-18 14:39 | 44092.6104 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 1 |  | 2 | 23 | 21 | 390 | 21 | 28 | 416 |  | 2020-09-18 14:39 | 44092.6104 | 21 | 28 | 416 |  | low | 2020-09-14 | B19570¦Court 1¦¦Sep-18-2020 14:38
2020-09-18 14:39 | 44092.6104 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main lobby S |  | 2 | 21 | 18 | 404 | 24 | 22 | 548 |  | 2020-09-18 14:39 | 44092.6104 | 24 | 22 | 548 |  | low | 2020-09-14 | B70235¦Main lobby S ¦¦Sep-18-2020 14:39
2020-09-18 14:40 | 44092.6108 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 5 interview room 1 |  | 0 | 19.5 | 22 | 393 | 22.6 | 21.4 | 394 |  | 2020-09-18 14:40 | 44092.6108 | 22.6 | 21.4 | 394 |  | low | 2020-09-14 | B17477¦LVL 5 interview room 1¦¦Sep-18-2020 14:39
2020-09-18 14:40 | 44092.6109 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Court 2 |  | 2 | 23 | 21 | 390 | 22 | 25 | 424 |  | 2020-09-18 14:40 | 44092.6109 | 22 | 25 | 424 |  | low | 2020-09-14 | B19570¦Court 2¦¦Sep-18-2020 14:39
2020-09-18 14:40 | 44092.6111 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space 2 |  | 0 | 15.5 | 30.2 | 422 | 21.7 | 22 | 442 |  | 2020-09-18 14:40 | 44092.6111 | 21.7 | 22 | 442 |  | low | 2020-09-14 | B20603¦Office space 2¦¦Sep-18-2020 14:39
2020-09-18 14:40 | 44092.6112 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-W wall |  | 0 | 15 | 30 | 425 | 24 | 37 | 600 |  | 2020-09-18 14:40 | 44092.6112 | 24 | 37 | 600 |  | caution | 2020-09-14 | B25548¦1-W wall¦¦Sep-18-2020 14:40
2020-09-18 14:40 | 44092.6112 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 209 |  | 0 | 14 | 25 | 375 | 23 | 29 | 526 | No | 2020-09-18 14:40 | 44092.6112 | 23 | 29 | 526 |  | low | 2020-09-14 | B14660¦209¦¦Sep-18-2020 14:40
2020-09-18 14:41 | 44092.6116 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main lobby C |  | 4 | 21 | 18 | 404 | 23 | 22 | 537 |  | 2020-09-18 14:41 | 44092.6116 | 23 | 22 | 537 |  | low | 2020-09-14 | B70235¦Main lobby C¦¦Sep-18-2020 14:40
2020-09-18 14:41 | 44092.6116 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 5 interview room 2 |  | 0 | 19.5 | 22 | 393 | 22.5 | 21.7 | 396 |  | 2020-09-18 14:41 | 44092.6116 | 22.5 | 21.7 | 396 |  | low | 2020-09-14 | B17477¦LVL 5 interview room 2¦¦Sep-18-2020 14:40
2020-09-18 14:41 | 44092.6118 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-W wall |  | 0 | 15 | 30 | 425 | 25 | 37 | 600 |  | 2020-09-18 14:41 | 44092.6118 | 25 | 37 | 600 |  | caution | 2020-09-14 | B25548¦1-W wall¦¦Sep-18-2020 14:41
2020-09-18 14:41 | 44092.6119 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space 3 |  | 0 | 15.5 | 30.2 | 422 | 21.6 | 21.9 | 438 |  | 2020-09-18 14:41 | 44092.6119 | 21.6 | 21.9 | 438 |  | low | 2020-09-14 | B20603¦Office space 3 ¦¦Sep-18-2020 14:41
2020-09-18 14:41 | 44092.612 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Basement hall e |  | 1 | 23 | 21 | 390 | 22 | 26 | 412 |  | 2020-09-18 14:41 | 44092.612 | 22 | 26 | 412 |  | low | 2020-09-14 | B19570¦Basement hall e ¦¦Sep-18-2020 14:41
2020-09-18 14:42 | 44092.6124 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Lobby North |  | 2 | 17.8 | 20.4 | 397 | 21.9 | 38.8 | 636 |  | 2020-09-18 14:42 | 44092.6124 | 21.9 | 38.8 | 636 |  | caution | 2020-09-14 | B10577¦Main Lobby North ¦¦Sep-18-2020 14:41
2020-09-18 14:42 | 44092.6125 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | S foyer |  | 0 | 15 | 30 | 425 | 24 | 38 | 620 |  | 2020-09-18 14:42 | 44092.6125 | 24 | 38 | 620 |  | caution | 2020-09-14 | B25548¦S foyer¦¦Sep-18-2020 14:42
2020-09-18 14:42 | 44092.6125 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 4 bottom |  | 1 | 23 | 21 | 390 | 21 | 27 | 415 |  | 2020-09-18 14:42 | 44092.6125 | 21 | 27 | 415 |  | low | 2020-09-14 | B19570¦Stairwell 4 bottom¦¦Sep-18-2020 14:42
2020-09-18 14:42 | 44092.6128 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main lobby N |  | 2 | 21 | 18 | 404 | 23 | 21 | 522 |  | 2020-09-18 14:42 | 44092.6128 | 23 | 21 | 522 |  | low | 2020-09-14 | B70235¦Main lobby N¦¦Sep-18-2020 14:42
2020-09-18 14:42 | 44092.6128 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space 4 |  | 0 | 15.5 | 30.2 | 422 | 21.7 | 22.1 | 448 |  | 2020-09-18 14:42 | 44092.6128 | 21.7 | 22.1 | 448 |  | low | 2020-09-14 | B20603¦Office space 4 ¦¦Sep-18-2020 14:42
2020-09-18 14:43 | 44092.613 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Main Stairwell |  | 0 | 17.8 | 20.4 | 397 | 21.7 | 40.9 | 560 |  | 2020-09-18 14:43 | 44092.613 | 21.7 | 40.9 | 560 |  |  | 2020-09-14 | B10577¦Main Stairwell ¦¦Sep-18-2020 14:42
2020-09-18 14:43 | 44092.6131 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Stairwell 4 top |  | 1 | 23 | 21 | 390 | 21 | 28 | 418 |  | 2020-09-18 14:43 | 44092.6131 | 21 | 28 | 418 |  | low | 2020-09-14 | B19570¦Stairwell 4 top ¦¦Sep-18-2020 14:42
2020-09-18 14:43 | 44092.6132 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 500 W |  | 0 | 19.5 | 22 | 393 | 22.6 | 25.2 | 371 |  | 2020-09-18 14:43 | 44092.6132 | 22.6 | 25.2 | 371 |  | low | 2020-09-14 | B17477¦Courtroom 500 W¦¦Sep-18-2020 14:43
2020-09-18 14:43 | 44092.6134 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | N foyer |  | 0 | 15 | 30 | 425 | 24 | 39 | 590 |  | 2020-09-18 14:43 | 44092.6134 | 24 | 39 | 590 |  | caution | 2020-09-14 | B25548¦N foyer¦¦Sep-18-2020 14:43
2020-09-18 14:43 | 44092.6135 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 251 |  | 1 | 23 | 21 | 390 | 22 | 25 | 441 |  | 2020-09-18 14:43 | 44092.6135 | 22 | 25 | 441 |  | low | 2020-09-14 | B19570¦251¦¦Sep-18-2020 14:43
2020-09-18 14:43 | 44092.6135 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2 floor waiting area North |  | 0 | 17.8 | 20.4 | 397 | 22.1 | 41.6 | 606 |  | 2020-09-18 14:43 | 44092.6135 | 22.1 | 41.6 | 606 |  |  | 2020-09-14 | B10577¦2 floor waiting area North ¦¦Sep-18-2020 14:43
2020-09-18 14:44 | 44092.6136 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 303 |  | 0 | 14 | 25 | 375 | 22.8 | 30.5 | 420 | No | 2020-09-18 14:44 | 44092.6136 | 22.8 | 30.5 | 420 |  | low | 2020-09-14 | B14660¦303¦¦Sep-18-2020 14:43
2020-09-18 14:44 | 44092.6137 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Front lobby |  | 1 | 18 | 14.5 | 424 | 18.8 | 22.7 | 498 |  | 2020-09-18 14:44 | 44092.6137 | 18.8 | 22.7 | 498 |  | low | 2020-09-14 | B19890¦Front lobby ¦¦Sep-18-2020 14:43
2020-09-18 14:44 | 44092.6137 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space 5 |  | 0 | 15.5 | 30.2 | 422 | 22 | 22 | 456 |  | 2020-09-18 14:44 | 44092.6137 | 22 | 22 | 456 |  | low | 2020-09-14 | B20603¦Office space 5 ¦¦Sep-18-2020 14:43
2020-09-18 14:44 | 44092.6138 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 250 |  | 1 | 23 | 21 | 390 | 22 | 23 | 471 |  | 2020-09-18 14:44 | 44092.6138 | 22 | 23 | 471 |  | low | 2020-09-14 | B19570¦250¦¦Sep-18-2020 14:43
2020-09-18 14:44 | 44092.6139 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 500 E |  | 0 | 19.5 | 22 | 393 | 22.8 | 23.7 | 370 |  | 2020-09-18 14:44 | 44092.6139 | 22.8 | 23.7 | 370 |  | low | 2020-09-14 | B17477¦Courtroom 500 E¦¦Sep-18-2020 14:44
2020-09-18 14:44 | 44092.6141 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2 floor waiting area center |  | 0 | 17.8 | 20.4 | 397 | 22 | 41.5 | 603 |  | 2020-09-18 14:44 | 44092.6141 | 22 | 41.5 | 603 |  |  | 2020-09-14 | B10577¦2 floor waiting area center ¦¦Sep-18-2020 14:44
2020-09-18 14:45 | 44092.6143 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Public seating area |  | 0 | 18 | 14.5 | 424 | 20.2 | 29.8 | 597 |  | 2020-09-18 14:45 | 44092.6143 | 20.2 | 29.8 | 597 |  | low | 2020-09-14 | B19890¦Public seating area ¦¦Sep-18-2020 14:44
2020-09-18 14:45 | 44092.6144 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 15 | 30 | 425 | 24 | 40 | 585 |  | 2020-09-18 14:45 | 44092.6144 | 24 | 40 | 585 |  | caution | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 14:44
2020-09-18 14:45 | 44092.6146 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office space 6 |  | 1 | 15.5 | 30.2 | 422 | 22.2 | 21.2 | 457 |  | 2020-09-18 14:45 | 44092.6146 | 22.2 | 21.2 | 457 |  | low | 2020-09-14 | B20603¦Office space 6 ¦¦Sep-18-2020 14:44
2020-09-18 14:45 | 44092.6148 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | 2 floor waiting area south |  | 0 | 17.8 | 20.4 | 397 | 22.1 | 41.4 | 606 |  | 2020-09-18 14:45 | 44092.6148 | 22.1 | 41.4 | 606 |  |  | 2020-09-14 | B10577¦2 floor waiting area south ¦¦Sep-18-2020 14:45
2020-09-18 14:45 | 44092.6149 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 302 |  | 3 | 14 | 25 | 375 | 22.6 | 26.7 | 438 | No | 2020-09-18 14:45 | 44092.6149 | 22.6 | 26.7 | 438 |  | low | 2020-09-14 | B14660¦302¦¦Sep-18-2020 14:45
2020-09-18 14:46 | 44092.615 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Main entrance |  | 0 | 18 | 14.5 | 424 | 21.3 | 30.4 | 577 |  | 2020-09-18 14:46 | 44092.615 | 21.3 | 30.4 | 577 |  | low | 2020-09-14 | B19890¦Main entrance ¦¦Sep-18-2020 14:45
2020-09-18 14:46 | 44092.6152 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 15 | 30 | 425 | 24 | 39 | 580 |  | 2020-09-18 14:46 | 44092.6152 | 24 | 39 | 580 |  | caution | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 14:45
2020-09-18 14:46 | 44092.6155 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Reception |  | 2 | 15.5 | 30.2 | 422 | 21.9 | 21.5 | 460 |  | 2020-09-18 14:46 | 44092.6155 | 21.9 | 21.5 | 460 |  | low | 2020-09-14 | B20603¦Reception ¦¦Sep-18-2020 14:46
2020-09-18 14:47 | 44092.6157 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 West |  | 0 | 17.8 | 20.4 | 397 | 22.4 | 36.1 | 580 |  | 2020-09-18 14:47 | 44092.6157 | 22.4 | 36.1 | 580 |  | caution | 2020-09-14 | B10577¦Courtroom 2 West ¦¦Sep-18-2020 14:46
2020-09-18 14:47 | 44092.6158 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Staff area |  | 2 | 18 | 14.5 | 424 | 22 | 29.5 | 556 |  | 2020-09-18 14:47 | 44092.6158 | 22 | 29.5 | 556 |  | low | 2020-09-14 | B19890¦Staff area ¦¦Sep-18-2020 14:46
2020-09-18 14:47 | 44092.616 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 15 | 30 | 425 | 24 | 39 | 580 |  | 2020-09-18 14:47 | 44092.616 | 24 | 39 | 580 |  | caution | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 14:47
2020-09-18 14:47 | 44092.6162 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 250 |  | 1 | 23 | 21 | 390 | 22 | 23 | 433 |  | 2020-09-18 14:47 | 44092.6162 | 22 | 23 | 433 |  | low | 2020-09-14 | B19570¦250¦¦Sep-18-2020 14:47
2020-09-18 14:47 | 44092.6162 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Reception 2 |  | 2 | 15.5 | 30.2 | 422 | 21.7 | 21.7 | 476 |  | 2020-09-18 14:47 | 44092.6162 | 21.7 | 21.7 | 476 |  | low | 2020-09-14 | B20603¦Reception 2 ¦¦Sep-18-2020 14:47
2020-09-18 14:48 | 44092.6165 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom D |  | 1 | 16 | 25.2 | 406 | 21.2 | 41.8 | 450 | No | 2020-09-18 14:48 | 44092.6165 | 21.2 | 41.8 | 450 |  |  | 2020-09-14 | B20478¦Courtroom D¦¦Sep-18-2020 14:47
2020-09-18 14:48 | 44092.6166 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 15 | 30 | 425 | 24 | 39 | 590 |  | 2020-09-18 14:48 | 44092.6166 | 24 | 39 | 590 |  | caution | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 14:47
2020-09-18 14:48 | 44092.6167 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 2 south |  | 0 | 17.8 | 20.4 | 397 | 23.4 | 35.1 | 599 |  | 2020-09-18 14:48 | 44092.6167 | 23.4 | 35.1 | 599 |  | caution | 2020-09-14 | B10577¦Courtroom 2 south¦¦Sep-18-2020 14:47
2020-09-18 14:48 | 44092.6167 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Hallway ne |  | 1 | 23 | 21 | 390 | 23 | 22 | 423 |  | 2020-09-18 14:48 | 44092.6167 | 23 | 22 | 423 |  | low | 2020-09-14 | B19570¦Hallway ne ¦¦Sep-18-2020 14:48
2020-09-18 14:48 | 44092.6169 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Crown office |  | 1 | 18 | 14.5 | 424 | 22.4 | 26.3 | 517 |  | 2020-09-18 14:48 | 44092.6169 | 22.4 | 26.3 | 517 |  | low | 2020-09-14 | B19890¦Crown office ¦¦Sep-18-2020 14:48
2020-09-18 14:49 | 44092.6171 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | Duty crown hall |  | 1 | 23 | 21 | 390 | 22 | 23 | 423 |  | 2020-09-18 14:49 | 44092.6171 | 22 | 23 | 423 |  | low | 2020-09-14 | B19570¦Duty crown hall ¦¦Sep-18-2020 14:48
2020-09-18 14:49 | 44092.6171 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 15 | 30 | 425 | 24 | 38 | 610 |  | 2020-09-18 14:49 | 44092.6171 | 24 | 38 | 610 |  | caution | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 14:48
2020-09-18 14:49 | 44092.6172 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 East |  | 1 | 17.8 | 20.4 | 397 | 22.2 | 34.9 | 579 |  | 2020-09-18 14:49 | 44092.6172 | 22.2 | 34.9 | 579 |  | low | 2020-09-14 | B10577¦Courtroom 1 East¦¦Sep-18-2020 14:48
2020-09-18 14:49 | 44092.6174 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 245 |  | 1 | 23 | 21 | 390 | 22 | 22 | 433 |  | 2020-09-18 14:49 | 44092.6174 | 22 | 22 | 433 |  | low | 2020-09-14 | B19570¦245¦¦Sep-18-2020 14:49
2020-09-18 14:49 | 44092.6176 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Main entrance |  | 2 | 16 | 24.5 | 409 | 19.7 | 33.5 | 467 |  | 2020-09-18 14:49 | 44092.6176 | 19.7 | 33.5 | 467 |  | low | 2020-09-14 | B11228¦Main entrance¦¦Sep-18-2020 14:49
2020-09-18 14:49 | 44092.6177 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Reception seating area |  | 0 | 15.5 | 30.2 | 422 | 21.8 | 21.6 | 466 |  | 2020-09-18 14:49 | 44092.6177 | 21.8 | 21.6 | 466 |  | low | 2020-09-14 | B20603¦Reception seating area ¦¦Sep-18-2020 14:49
2020-09-18 14:49 | 44092.6177 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom B |  | 1 | 16 | 25.2 | 406 | 22.2 | 31.1 | 442 | No | 2020-09-18 14:49 | 44092.6177 | 22.2 | 31.1 | 442 |  | low | 2020-09-14 | B20478¦Courtroom B¦¦Sep-18-2020 14:49
2020-09-18 14:50 | 44092.6179 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 1-N wall |  | 0 | 15 | 30 | 425 | 24 | 38 | 595 |  | 2020-09-18 14:50 | 44092.6179 | 24 | 38 | 595 |  | caution | 2020-09-14 | B25548¦1-N wall¦¦Sep-18-2020 14:49
2020-09-18 14:50 | 44092.6179 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 1 North |  | 0 | 17.8 | 20.4 | 397 | 23.7 | 35.2 | 584 |  | 2020-09-18 14:50 | 44092.6179 | 23.7 | 35.2 | 584 |  | caution | 2020-09-14 | B10577¦Courtroom 1 North ¦¦Sep-18-2020 14:49
2020-09-18 14:50 | 44092.6182 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 301b |  | 0 | 14 | 25 | 375 | 23.2 | 32.2 | 405 | No | 2020-09-18 14:50 | 44092.6182 | 23.2 | 32.2 | 405 |  | low | 2020-09-14 | B14660¦301b¦¦Sep-18-2020 14:50
2020-09-18 14:50 | 44092.6184 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 247 |  | 1 | 23 | 21 | 390 | 23 | 23 | 430 |  | 2020-09-18 14:50 | 44092.6184 | 23 | 23 | 430 |  | low | 2020-09-14 | B19570¦247¦¦Sep-18-2020 14:50
2020-09-18 14:51 | 44092.6186 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 outside |  | 0 | 17.8 | 20.4 | 397 | 21.6 | 33.2 | 545 |  | 2020-09-18 14:51 | 44092.6186 | 21.6 | 33.2 | 545 |  | low | 2020-09-14 | B10577¦Courtroom 3 outside ¦¦Sep-18-2020 14:50
2020-09-18 14:51 | 44092.6186 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Front stairway |  | 0 | 16 | 24.5 | 409 | 20.5 | 31.7 | 433 |  | 2020-09-18 14:51 | 44092.6186 | 20.5 | 31.7 | 433 |  | low | 2020-09-14 | B11228¦Front stairway¦¦Sep-18-2020 14:50
2020-09-18 14:51 | 44092.6188 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom C |  | 1 | 16 | 25.2 | 406 | 22.3 | 25.6 | 437 | No | 2020-09-18 14:51 | 44092.6188 | 22.3 | 25.6 | 437 |  | low | 2020-09-14 | B20478¦Courtroom C¦¦Sep-18-2020 14:51
2020-09-18 14:51 | 44092.6188 | AINSWORTH | B19570 | B19570 - 860 William St - Cobourg | 244 |  | 1 | 23 | 21 | 390 | 23 | 20 | 420 |  | 2020-09-18 14:51 | 44092.6188 | 23 | 20 | 420 |  | low | 2020-09-14 | B19570¦244¦¦Sep-18-2020 14:51
2020-09-18 14:51 | 44092.6188 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office hallway |  | 0 | 15.5 | 30.2 | 422 | 22 | 21.5 | 452 |  | 2020-09-18 14:51 | 44092.6188 | 22 | 21.5 | 452 |  | low | 2020-09-14 | B20603¦Office hallway ¦¦Sep-18-2020 14:51
2020-09-18 14:52 | 44092.6191 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 15 | 30 | 425 | 24 | 40 | 580 |  | 2020-09-18 14:52 | 44092.6191 | 24 | 40 | 580 |  | caution | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 14:51
2020-09-18 14:52 | 44092.6192 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 waiting area |  | 0 | 17.8 | 20.4 | 397 | 21.7 | 33.1 | 504 |  | 2020-09-18 14:52 | 44092.6192 | 21.7 | 33.1 | 504 |  | low | 2020-09-14 | B10577¦Courtroom 3 waiting area ¦¦Sep-18-2020 14:51
2020-09-18 14:52 | 44092.6194 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office hallway 2 |  | 0 | 15.5 | 30.2 | 422 | 22.1 | 21.8 | 448 |  | 2020-09-18 14:52 | 44092.6194 | 22.1 | 21.8 | 448 |  | low | 2020-09-14 | B20603¦Office hallway 2¦¦Sep-18-2020 14:51
2020-09-18 14:52 | 44092.6198 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Interview room |  | 0 | 17.8 | 20.4 | 397 | 21.4 | 32.1 | 449 |  | 2020-09-18 14:52 | 44092.6198 | 21.4 | 32.1 | 449 |  | low | 2020-09-14 | B10577¦Interview room ¦¦Sep-18-2020 14:52
2020-09-18 14:53 | 44092.6198 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Large courtroom benches |  | 0 | 16 | 24.5 | 409 | 21 | 31.4 | 421 |  | 2020-09-18 14:53 | 44092.6198 | 21 | 31.4 | 421 |  | low | 2020-09-14 | B11228¦Large courtroom benches¦¦Sep-18-2020 14:52
2020-09-18 14:53 | 44092.62 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 15 | 30 | 425 | 24 | 40 | 585 |  | 2020-09-18 14:53 | 44092.62 | 24 | 40 | 585 |  | caution | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 14:52
2020-09-18 14:53 | 44092.6202 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Printer room |  | 0 | 15.5 | 30.2 | 422 | 22 | 21.5 | 459 |  | 2020-09-18 14:53 | 44092.6202 | 22 | 21.5 | 459 |  | low | 2020-09-14 | B20603¦Printer room ¦¦Sep-18-2020 14:53
2020-09-18 14:54 | 44092.6205 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom A |  | 1 | 16 | 25.2 | 406 | 22.4 | 23.7 | 414 | No | 2020-09-18 14:54 | 44092.6205 | 22.4 | 23.7 | 414 |  | low | 2020-09-14 | B20478¦Courtroom A¦¦Sep-18-2020 14:53
2020-09-18 14:54 | 44092.6207 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 15 | 30 | 425 | 23 | 40 | 585 |  | 2020-09-18 14:54 | 44092.6207 | 23 | 40 | 585 |  | caution | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 14:53
2020-09-18 14:54 | 44092.6208 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 South |  | 0 | 17.8 | 20.4 | 397 | 21.3 | 31.4 | 423 |  | 2020-09-18 14:54 | 44092.6208 | 21.3 | 31.4 | 423 |  | low | 2020-09-14 | B10577¦Courtroom 3 South¦¦Sep-18-2020 14:53
2020-09-18 14:54 | 44092.6211 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Large courtroom judges stand |  | 0 | 16 | 24.5 | 409 | 21.2 | 31.7 | 417 |  | 2020-09-18 14:54 | 44092.6211 | 21.2 | 31.7 | 417 |  | low | 2020-09-14 | B11228¦Large courtroom judges stand¦¦Sep-18-2020 14:54
2020-09-18 14:54 | 44092.6211 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Printer room |  | 0 | 15.5 | 30.2 | 422 | 22.2 | 21.4 | 448 |  | 2020-09-18 14:54 | 44092.6211 | 22.2 | 21.4 | 448 |  | low | 2020-09-14 | B20603¦Printer room ¦¦Sep-18-2020 14:54
2020-09-18 14:55 | 44092.6214 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 15 | 30 | 425 | 23 | 41 | 590 |  | 2020-09-18 14:55 | 44092.6214 | 23 | 41 | 590 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 14:54
2020-09-18 14:55 | 44092.6214 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 East |  | 0 | 17.8 | 20.4 | 397 | 21.3 | 30.8 | 423 |  | 2020-09-18 14:55 | 44092.6214 | 21.3 | 30.8 | 423 |  | low | 2020-09-14 | B10577¦Courtroom 3 East¦¦Sep-18-2020 14:54
2020-09-18 14:55 | 44092.6214 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 301a |  | 0 | 14 | 25 | 375 | 24.7 | 28.8 | 399 | No | 2020-09-18 14:55 | 44092.6214 | 24.7 | 28.8 | 399 |  | low | 2020-09-14 | B14660¦301a¦¦Sep-18-2020 14:54
2020-09-18 14:55 | 44092.6218 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Common room beside courtroom A |  | 0 | 16 | 25.2 | 406 | 23.3 | 23.5 | 447 | No | 2020-09-18 14:55 | 44092.6218 | 23.3 | 23.5 | 447 |  | low | 2020-09-14 | B20478¦Common room beside courtroom A¦¦Sep-18-2020 14:55
2020-09-18 14:56 | 44092.6219 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 North |  | 0 | 17.8 | 20.4 | 397 | 21.3 | 31.1 | 420 |  | 2020-09-18 14:55 | 44092.6219 | 21.3 | 31.1 | 420 |  | low | 2020-09-14 | B10577¦Courtroom 3 North¦¦Sep-18-2020 14:55
2020-09-18 14:56 | 44092.622 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 15 | 30 | 425 | 23 | 41 | 610 |  | 2020-09-18 14:56 | 44092.622 | 23 | 41 | 610 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 14:55
2020-09-18 14:56 | 44092.622 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Rear meeting room |  | 0 | 16 | 24.5 | 409 | 20.8 | 35.3 | 425 |  | 2020-09-18 14:56 | 44092.622 | 20.8 | 35.3 | 425 |  | caution | 2020-09-14 | B11228¦Rear meeting room¦¦Sep-18-2020 14:55
2020-09-18 14:56 | 44092.6222 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office hallway 3 |  | 0 | 15.5 | 30.2 | 449 | 22.3 | 21.3 | 451 |  | 2020-09-18 14:56 | 44092.6222 | 22.3 | 21.3 | 451 |  | low | 2020-09-14 | B20603¦Office hallway 3 ¦¦Sep-18-2020 14:55
2020-09-18 14:57 | 44092.6226 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Law library |  | 0 | 16 | 25.2 | 406 | 23.2 | 27.7 | 430 | No | 2020-09-18 14:57 | 44092.6226 | 23.2 | 27.7 | 430 |  | low | 2020-09-14 | B20478¦Law library¦¦Sep-18-2020 14:56
2020-09-18 14:57 | 44092.6226 | AINSWORTH | B10577 | B10577 - 55 Munsee St N - Cayuga | Courtroom 3 West |  | 0 | 17.8 | 20.4 | 397 | 21.2 | 31.8 | 414 |  | 2020-09-18 14:57 | 44092.6226 | 21.2 | 31.8 | 414 |  | low | 2020-09-14 | B10577¦Courtroom 3 West¦¦Sep-18-2020 14:56
2020-09-18 14:57 | 44092.6226 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-S wall |  | 0 | 15 | 30 | 425 | 23 | 41 | 605 |  | 2020-09-18 14:57 | 44092.6226 | 23 | 41 | 605 |  |  | 2020-09-14 | B25548¦2-S wall¦¦Sep-18-2020 14:56
2020-09-18 14:57 | 44092.6231 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office hallway 4 |  | 0 | 15.5 | 30.2 | 422 | 22.2 | 21.6 | 443 |  | 2020-09-18 14:57 | 44092.6231 | 22.2 | 21.6 | 443 |  | low | 2020-09-14 | B20603¦Office hallway 4¦¦Sep-18-2020 14:57
2020-09-18 14:58 | 44092.6234 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Judges office |  | 0 | 16 | 24.5 | 409 | 20.4 | 34.6 | 420 |  | 2020-09-18 14:58 | 44092.6234 | 20.4 | 34.6 | 420 |  | low | 2020-09-14 | B11228¦Judges office¦¦Sep-18-2020 14:57
2020-09-18 14:58 | 44092.6235 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-W wall |  | 0 | 15 | 30 | 425 | 23 | 41 | 620 |  | 2020-09-18 14:58 | 44092.6235 | 23 | 41 | 620 |  |  | 2020-09-14 | B25548¦2-W wall¦¦Sep-18-2020 14:57
2020-09-18 14:58 | 44092.6235 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | East stairwell |  | 0 | 16 | 25.2 | 406 | 23.6 | 26.5 | 515 | No | 2020-09-18 14:58 | 44092.6235 | 23.6 | 26.5 | 515 |  | low | 2020-09-14 | B20478¦East stairwell¦¦Sep-18-2020 14:57
2020-09-18 14:58 | 44092.6238 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | Crown Attorney |  | 0 | 14 | 25 | 375 | 23.8 | 28.6 | 398 | Jp | 2020-09-18 14:58 | 44092.6238 | 23.8 | 28.6 | 398 |  | low | 2020-09-14 | B14660¦Crown Attorney¦¦Sep-18-2020 14:58
2020-09-18 14:59 | 44092.624 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office hallway 5 |  | 0 | 15.5 | 30.2 | 422 | 22.3 | 21.7 | 444 |  | 2020-09-18 14:59 | 44092.624 | 22.3 | 21.7 | 444 |  | low | 2020-09-14 | B20603¦Office hallway 5¦¦Sep-18-2020 14:58
2020-09-18 14:59 | 44092.6241 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-W wall |  | 0 | 15 | 30 | 425 | 23 | 40 | 610 |  | 2020-09-18 14:59 | 44092.6241 | 23 | 40 | 610 |  | caution | 2020-09-14 | B25548¦2-W wall¦¦Sep-18-2020 14:58
2020-09-18 14:59 | 44092.6243 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Main floor common area |  | 4 | 16 | 25.2 | 406 | 19.7 | 32.9 | 444 | No | 2020-09-18 14:59 | 44092.6243 | 19.7 | 32.9 | 444 |  | low | 2020-09-14 | B20478¦Main floor common area¦¦Sep-18-2020 14:59
2020-09-18 14:59 | 44092.6244 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Side hallway |  | 0 | 16 | 24.5 | 409 | 21.2 | 36.3 | 481 |  | 2020-09-18 14:59 | 44092.6244 | 21.2 | 36.3 | 481 |  | caution | 2020-09-14 | B11228¦Side hallway¦¦Sep-18-2020 14:59
2020-09-18 15:00 | 44092.6249 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-W wall |  | 0 | 15 | 30 | 425 | 23 | 41 | 600 |  | 2020-09-18 15:00 | 44092.6249 | 23 | 41 | 600 |  |  | 2020-09-14 | B25548¦2-W wall¦¦Sep-18-2020 14:59
2020-09-18 15:00 | 44092.6253 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jason Mariasine office |  | 1 | 21 | 18 | 404 |  |  |  | Occupied, no access | 2020-09-18 15:00 | 44092.6253 | [5 empty] | 2020-09-14 | B70235¦Jason Mariasine office ¦¦Sep-18-2020 15:00
2020-09-18 15:01 | 44092.6255 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Public seating area 2 |  | 0 | 18 | 14.5 | 424 | 22.5 | 27.6 | 507 |  | 2020-09-18 15:01 | 44092.6255 | 22.5 | 27.6 | 507 |  | low | 2020-09-14 | B19890¦Public seating area 2¦¦Sep-18-2020 15:00
2020-09-18 15:01 | 44092.6255 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Rear stairway |  | 0 | 16 | 24.5 | 409 | 23.2 | 36.6 | 441 |  | 2020-09-18 15:01 | 44092.6255 | 23.2 | 36.6 | 441 |  | caution | 2020-09-14 | B11228¦Rear stairway¦¦Sep-18-2020 15:00
2020-09-18 15:01 | 44092.6256 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 15 | 30 | 426 | 23 | 41 | 605 |  | 2020-09-18 15:01 | 44092.6256 | 23 | 41 | 605 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 15:00
2020-09-18 15:01 | 44092.626 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Robert Beninger office |  | 1 | 21 | 18 | 404 |  |  |  | Occupied, no access | 2020-09-18 15:01 | 44092.626 | [5 empty] | 2020-09-14 | B70235¦Robert Beninger office ¦¦Sep-18-2020 15:01
2020-09-18 15:01 | 44092.626 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | corridor at admin offices |  | 0 | 16 | 25.2 | 406 | 21.1 | 30.5 | 455 | No | 2020-09-18 15:01 | 44092.626 | 21.1 | 30.5 | 455 |  | low | 2020-09-14 | B20478¦corridor at admin offices¦¦Sep-18-2020 15:01
2020-09-18 15:01 | 44092.626 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 11 |  | 1 | 15.5 | 30.2 | 422 | 22.3 | 22.1 | 448 |  | 2020-09-18 15:01 | 44092.626 | 22.3 | 22.1 | 448 |  | low | 2020-09-14 | B20603¦Office 11¦¦Sep-18-2020 15:01
2020-09-18 15:02 | 44092.6261 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 306 |  | 0 | 14 | 25 | 375 | 23.2 | 30.2 | 395 | No | 2020-09-18 15:02 | 44092.6261 | 23.2 | 30.2 | 395 |  | low | 2020-09-14 | B14660¦306¦¦Sep-18-2020 15:01
2020-09-18 15:02 | 44092.6262 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | entryway |  | 2 | 16.1 | 27.3 | 383 | 19 | 31.2 | 505 |  | 2020-09-18 15:02 | 44092.6262 | 19 | 31.2 | 505 |  | low | 2020-09-14 | B20390¦entryway¦¦Sep-18-2020 15:01
2020-09-18 15:02 | 44092.6262 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Courtroom 1 |  | 2 | 18 | 22.4 | 486 | 22.5 | 25 | 481 |  | 2020-09-18 15:02 | 44092.6262 | 22.5 | 25 | 481 |  | low | 2020-09-14 | B19890¦Courtroom 1¦¦Sep-18-2020 15:01
2020-09-18 15:02 | 44092.6263 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 15 | 30 | 425 | 23 | 41 | 635 |  | 2020-09-18 15:02 | 44092.6263 | 23 | 41 | 635 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 15:01
2020-09-18 15:02 | 44092.6266 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 judge |  | 1 | 21 | 18 | 404 |  |  |  | Occupied, no access | 2020-09-18 15:02 | 44092.6266 | [5 empty] | 2020-09-14 | B70235¦Court #4 judge ¦¦Sep-18-2020 15:02
2020-09-18 15:02 | 44092.6266 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Outside small courtroom |  | 0 | 16 | 24.5 | 409 | 22.3 | 32.3 | 437 |  | 2020-09-18 15:02 | 44092.6266 | 22.3 | 32.3 | 437 |  | low | 2020-09-14 | B11228¦Outside small courtroom¦¦Sep-18-2020 15:02
2020-09-18 15:03 | 44092.627 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | 2nd floor common area |  | 0 | 16 | 25.2 | 406 | 22.5 | 31.3 | 475 | No | 2020-09-18 15:03 | 44092.627 | 22.5 | 31.3 | 475 |  | low | 2020-09-14 | B20478¦2nd floor common area¦¦Sep-18-2020 15:02
2020-09-18 15:03 | 44092.6271 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 15 | 30 | 425 | 23 | 41 | 640 |  | 2020-09-18 15:03 | 44092.6271 | 23 | 41 | 640 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 15:03
2020-09-18 15:03 | 44092.6273 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 lawyer |  | 1 | 21 | 18 | 404 |  |  |  | Occupied, no access | 2020-09-18 15:03 | 44092.6273 | [5 empty] | 2020-09-14 | B70235¦Court #4 lawyer ¦¦Sep-18-2020 15:03
2020-09-18 15:03 | 44092.6273 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | First floor waiting area |  | 5 | 16.1 | 27.3 | 383 | 20 | 36.1 | 501 |  | 2020-09-18 15:03 | 44092.6273 | 20 | 36.1 | 501 |  | caution | 2020-09-14 | B20390¦First floor waiting area¦¦Sep-18-2020 15:03
2020-09-18 15:04 | 44092.6274 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Main hallway |  | 0 | 15.5 | 30.2 | 422 | 21.6 | 21.8 | 425 |  | 2020-09-18 15:04 | 44092.6274 | 21.6 | 21.8 | 425 |  | low | 2020-09-14 | B20603¦Main hallway ¦¦Sep-18-2020 15:03
2020-09-18 15:04 | 44092.6276 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Courtroom 2 |  | 0 | 18 | 14.5 | 424 | 22.4 | 24.6 | 472 |  | 2020-09-18 15:04 | 44092.6276 | 22.4 | 24.6 | 472 |  | low | 2020-09-14 | B19890¦Courtroom 2¦¦Sep-18-2020 15:03
2020-09-18 15:04 | 44092.6278 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 15 | 30 | 425 | 23 | 41 | 620 |  | 2020-09-18 15:04 | 44092.6278 | 23 | 41 | 620 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 15:04
2020-09-18 15:04 | 44092.6278 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Small courtroom rear |  | 0 | 16 | 24.5 | 409 | 19.8 | 35.4 | 446 |  | 2020-09-18 15:04 | 44092.6278 | 19.8 | 35.4 | 446 |  | caution | 2020-09-14 | B11228¦Small courtroom rear¦¦Sep-18-2020 15:04
2020-09-18 15:04 | 44092.6278 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 lawyer |  | 1 | 21 | 18 | 404 |  |  |  | Occupied, no access | 2020-09-18 15:04 | 44092.6278 | [5 empty] | 2020-09-14 | B70235¦Court #3 lawyer ¦¦Sep-18-2020 15:04
2020-09-18 15:04 | 44092.6279 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | 2nd floor crown attorney corridor |  | 0 | 16 | 25.2 | 406 | 23 | 30 | 431 | No | 2020-09-18 15:04 | 44092.6279 | 23 | 30 | 431 |  | low | 2020-09-14 | B20478¦2nd floor crown attorney corridor¦¦Sep-18-2020 15:04
2020-09-18 15:05 | 44092.6284 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 2 |  | 2 | 16.1 | 27.3 | 383 | 20.5 | 36.6 | 503 |  | 2020-09-18 15:05 | 44092.6284 | 20.5 | 36.6 | 503 |  | caution | 2020-09-14 | B20390¦Outside courtroom 2¦¦Sep-18-2020 15:04
2020-09-18 15:05 | 44092.6284 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 15 | 30 | 425 | 23 | 42 | 600 |  | 2020-09-18 15:05 | 44092.6284 | 23 | 42 | 600 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 15:04
2020-09-18 15:05 | 44092.6284 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 judge |  | 1 | 21 | 18 | 404 |  |  |  | Occupied, no access | 2020-09-18 15:05 | 44092.6284 | [5 empty] | 2020-09-14 | B70235¦Court #3 judge ¦¦Sep-18-2020 15:04
2020-09-18 15:05 | 44092.6285 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Main hallway 2 |  | 0 | 15.5 | 30.2 | 422 | 21.4 | 22 | 431 |  | 2020-09-18 15:05 | 44092.6285 | 21.4 | 22 | 431 |  | low | 2020-09-14 | B20603¦Main hallway 2¦¦Sep-18-2020 15:04
2020-09-18 15:05 | 44092.6287 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Stairwell |  | 0 | 18 | 14.5 | 424 | 21.9 | 29.4 | 525 |  | 2020-09-18 15:05 | 44092.6287 | 21.9 | 29.4 | 525 |  | low | 2020-09-14 | B19890¦Stairwell¦¦Sep-18-2020 15:05
2020-09-18 15:06 | 44092.6289 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Judicial office corridor |  | 0 | 16 | 25.2 | 406 | 23.2 | 30.3 | 430 | No | 2020-09-18 15:06 | 44092.6289 | 23.2 | 30.3 | 430 |  | low | 2020-09-14 | B20478¦Judicial office corridor¦¦Sep-18-2020 15:05
2020-09-18 15:06 | 44092.629 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Library |  | 0 | 16 | 24.5 | 409 | 19.6 | 40.3 | 427 |  | 2020-09-18 15:06 | 44092.629 | 19.6 | 40.3 | 427 |  |  | 2020-09-14 | B11228¦Library¦¦Sep-18-2020 15:05
2020-09-18 15:06 | 44092.6292 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Main hallway 3 |  | 0 | 15.5 | 30.2 | 422 | 21.6 | 22 | 430 |  | 2020-09-18 15:06 | 44092.6292 | 21.6 | 22 | 430 |  | low | 2020-09-14 | B20603¦Main hallway 3 ¦¦Sep-18-2020 15:06
2020-09-18 15:06 | 44092.6293 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-N wall |  | 0 | 15 | 30 | 425 | 23 | 42 | 595 |  | 2020-09-18 15:06 | 44092.6293 | 23 | 42 | 595 |  |  | 2020-09-14 | B25548¦2-N wall¦¦Sep-18-2020 15:06
2020-09-18 15:06 | 44092.6294 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 3 |  | 2 | 16.1 | 27.3 | 383 | 20.7 | 36.2 | 496 |  | 2020-09-18 15:06 | 44092.6294 | 20.7 | 36.2 | 496 |  | caution | 2020-09-14 | B20390¦Outside courtroom 3¦¦Sep-18-2020 15:06
2020-09-18 15:06 | 44092.6295 | AINSWORTH | B19890 | B19890 - 41 Dundas St W - Napanee | Main hallway |  | 0 | 18 | 14.5 | 424 | 22.1 | 30.1 | 565 |  | 2020-09-18 15:06 | 44092.6295 | 22.1 | 30.1 | 565 |  | low | 2020-09-14 | B19890¦Main hallway ¦¦Sep-18-2020 15:06
2020-09-18 15:07 | 44092.63 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Main hallway 4 |  | 0 | 15.5 | 30.2 | 422 | 21.9 | 22 | 429 |  | 2020-09-18 15:07 | 44092.63 | 21.9 | 22 | 429 |  | low | 2020-09-14 | B20603¦Main hallway 4 ¦¦Sep-18-2020 15:07
2020-09-18 15:07 | 44092.63 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-E wall |  | 0 | 15 | 30 | 425 | 23 | 41 | 595 |  | 2020-09-18 15:07 | 44092.63 | 23 | 41 | 595 |  |  | 2020-09-14 | B25548¦2-E wall¦¦Sep-18-2020 15:07
2020-09-18 15:07 | 44092.63 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Bottom stairs foyer |  | 1 | 14.7 | 30.6 | 387 | 20.1 | 34.6 | 623 |  | 2020-09-18 15:07 | 44092.63 | 20.1 | 34.6 | 623 |  | low | 2020-09-14 | B20474¦Bottom stairs foyer¦¦Sep-18-2020 15:07
2020-09-18 15:07 | 44092.63 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Basement witness protection corridor |  | 0 | 16 | 25.2 | 406 | 22.7 | 23.1 | 418 | No | 2020-09-18 15:07 | 44092.63 | 22.7 | 23.1 | 418 |  | low | 2020-09-14 | B20478¦Basement witness protection corridor¦¦Sep-18-2020 15:07
2020-09-18 15:08 | 44092.6303 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Small courtroom judges stand |  | 0 | 16 | 24.5 | 409 | 19.2 | 39.5 | 430 |  | 2020-09-18 15:08 | 44092.6303 | 19.2 | 39.5 | 430 |  | caution | 2020-09-14 | B11228¦Small courtroom judges stand¦¦Sep-18-2020 15:07
2020-09-18 15:08 | 44092.6305 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Civil/small claims waiting area |  | 2 | 16.1 | 27.3 | 383 | 21.2 | 44.7 | 491 |  | 2020-09-18 15:08 | 44092.6305 | 21.2 | 44.7 | 491 |  |  | 2020-09-14 | B20390¦Civil/small claims waiting area¦¦Sep-18-2020 15:07
2020-09-18 15:08 | 44092.6306 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-E wall |  | 0 | 15 | 30 | 425 | 23 | 42 | 605 |  | 2020-09-18 15:08 | 44092.6306 | 23 | 42 | 605 |  |  | 2020-09-14 | B25548¦2-E wall¦¦Sep-18-2020 15:08
2020-09-18 15:08 | 44092.6308 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Main hallway 5 |  | 0 | 15.5 | 30.2 | 422 | 22.2 | 22 | 428 |  | 2020-09-18 15:08 | 44092.6308 | 22.2 | 22 | 428 |  | low | 2020-09-14 | B20603¦Main hallway 5 ¦¦Sep-18-2020 15:08
2020-09-18 15:08 | 44092.6308 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st Floor main lobby |  | 7 | 11.1 | 31.7 | 400 | 17.1 | 36.5 | 452 | no | 2020-09-18 15:08 | 44092.6308 | 17.1 | 36.5 | 452 |  | caution | 2020-09-14 | B70496¦1st Floor main lobby¦¦Sep-18-2020 15:08
2020-09-18 15:09 | 44092.6311 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Basement corridor middle |  | 0 | 16 | 25.2 | 406 | 22.2 | 26.4 | 426 | No | 2020-09-18 15:09 | 44092.6311 | 22.2 | 26.4 | 426 |  | low | 2020-09-14 | B20478¦Basement corridor middle¦¦Sep-18-2020 15:08
2020-09-18 15:09 | 44092.6311 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | 2-E wall |  | 0 | 15 | 30 | 425 | 23 | 41 | 610 |  | 2020-09-18 15:09 | 44092.6311 | 23 | 41 | 610 |  |  | 2020-09-14 | B25548¦2-E wall¦¦Sep-18-2020 15:08
2020-09-18 15:09 | 44092.6313 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Finance services waiting area |  | 1 | 16.1 | 27.3 | 383 | 21.5 | 43 | 496 |  | 2020-09-18 15:09 | 44092.6313 | 21.5 | 43 | 496 |  |  | 2020-09-14 | B20390¦Finance services waiting area¦¦Sep-18-2020 15:09
2020-09-18 15:09 | 44092.6313 | AINSWORTH | B11228 | B11228 - 44 Union St - Picton | Admin office |  | 1 | 16 | 24.5 | 409 | 20.4 | 39.7 | 468 |  | 2020-09-18 15:09 | 44092.6313 | 20.4 | 39.7 | 468 |  | caution | 2020-09-14 | B11228¦Admin office¦¦Sep-18-2020 15:09
2020-09-18 15:10 | 44092.6317 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Lower landing of stairway |  | 1 | 14.7 | 30.6 | 387 | 19.8 | 34.9 | 619 |  | 2020-09-18 15:10 | 44092.6317 | 19.8 | 34.9 | 619 |  | low | 2020-09-14 | B20474¦Lower landing of stairway¦¦Sep-18-2020 15:09
2020-09-18 15:10 | 44092.6317 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Main hallway 6 |  | 0 | 15.5 | 30.2 | 422 | 22.5 | 22.3 | 435 |  | 2020-09-18 15:10 | 44092.6317 | 22.5 | 22.3 | 435 |  | low | 2020-09-14 | B20603¦Main hallway 6¦¦Sep-18-2020 15:09
2020-09-18 15:10 | 44092.6321 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st floor hall |  | 1 | 11.1 | 31.7 | 400 | 20.2 | 27.5 | 484 | no | 2020-09-18 15:10 | 44092.6321 | 20.2 | 27.5 | 484 |  | low | 2020-09-14 | B70496¦1st floor hall¦¦Sep-18-2020 15:10
2020-09-18 15:10 | 44092.6321 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Family services waiting area |  | 2 | 16.1 | 27.3 | 383 | 21.5 | 43.3 | 504 |  | 2020-09-18 15:10 | 44092.6321 | 21.5 | 43.3 | 504 |  |  | 2020-09-14 | B20390¦Family services waiting area¦¦Sep-18-2020 15:10
2020-09-18 15:10 | 44092.6321 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Basement prisoner holding corridor |  | 0 | 16 | 25.2 | 406 | 21.7 | 39.4 | 441 | No | 2020-09-18 15:10 | 44092.6321 | 21.7 | 39.4 | 441 |  | caution | 2020-09-14 | B20478¦Basement prisoner holding corridor¦¦Sep-18-2020 15:10
2020-09-18 15:11 | 44092.6326 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Main hallway 7 |  | 0 | 15.5 | 30.2 | 422 | 22.7 | 21.8 | 428 |  | 2020-09-18 15:11 | 44092.6326 | 22.7 | 21.8 | 428 |  | low | 2020-09-14 | B20603¦Main hallway 7¦¦Sep-18-2020 15:10
2020-09-18 15:11 | 44092.6328 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 1st floor seating area |  | 1 | 11.1 | 31.7 | 400 | 20.2 | 27.5 | 460 | no | 2020-09-18 15:11 | 44092.6328 | 20.2 | 27.5 | 460 |  | low | 2020-09-14 | B70496¦1st floor seating area¦¦Sep-18-2020 15:11
2020-09-18 15:11 | 44092.633 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | Meditation |  | 0 | 15 | 30 | 425 | 24 | 42 | 590 |  | 2020-09-18 15:11 | 44092.633 | 24 | 42 | 590 |  |  | 2020-09-14 | B25548¦Meditation¦¦Sep-18-2020 15:11
2020-09-18 15:12 | 44092.6333 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Main floor at stairway |  | 1 | 14.7 | 30.6 | 387 | 19.8 | 35.2 | 619 |  | 2020-09-18 15:12 | 44092.6333 | 19.8 | 35.2 | 619 |  | caution | 2020-09-14 | B20474¦Main floor at stairway¦¦Sep-18-2020 15:11
2020-09-18 15:12 | 44092.6333 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell, first floor |  | 1 | 16.1 | 27.3 | 383 | 21.6 | 34.4 | 417 |  | 2020-09-18 15:12 | 44092.6333 | 21.6 | 34.4 | 417 |  | low | 2020-09-14 | B20390¦Main stairwell, first floor¦¦Sep-18-2020 15:12
2020-09-18 15:13 | 44092.6342 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Hearing room |  | 0 | 15.5 | 30.2 | 422 | 23 | 19.3 | 431 |  | 2020-09-18 15:13 | 44092.6342 | 23 | 19.3 | 431 |  | low | 2020-09-14 | B20603¦Hearing room ¦¦Sep-18-2020 15:13
2020-09-18 15:13 | 44092.6343 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 101 |  | 1 | 11.1 | 31.7 | 400 | 20.2 | 26 | 412 | no | 2020-09-18 15:13 | 44092.6343 | 20.2 | 26 | 412 |  | low | 2020-09-14 | B70496¦101¦¦Sep-18-2020 15:13
2020-09-18 15:13 | 44092.6343 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell, second floor |  | 1 | 16.1 | 27.3 | 383 | 22 | 34.1 | 421 |  | 2020-09-18 15:13 | 44092.6343 | 22 | 34.1 | 421 |  | low | 2020-09-14 | B20390¦Main stairwell, second floor ¦¦Sep-18-2020 15:13
2020-09-18 15:14 | 44092.6347 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 102 |  | 1 | 11.1 | 31.7 | 400 | 20.8 | 23.6 | 413 | no | 2020-09-18 15:14 | 44092.6347 | 20.8 | 23.6 | 413 |  | low | 2020-09-14 | B70496¦102¦¦Sep-18-2020 15:14
2020-09-18 15:14 | 44092.6348 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Hearing room 2 |  | 0 | 15.5 | 30.2 | 422 | 23 | 19.4 | 425 |  | 2020-09-18 15:14 | 44092.6348 | 23 | 19.4 | 425 |  | low | 2020-09-14 | B20603¦Hearing room 2¦¦Sep-18-2020 15:14
2020-09-18 15:15 | 44092.6351 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Second floor waiting area |  | 1 | 16.1 | 27.3 | 383 | 22.3 | 28.6 | 408 |  | 2020-09-18 15:15 | 44092.6351 | 22.3 | 28.6 | 408 |  | low | 2020-09-14 | B20390¦Second floor waiting area ¦¦Sep-18-2020 15:14
2020-09-18 15:15 | 44092.6351 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom4 corridor |  | 1 | 14.7 | 30.6 | 387 | 19.8 | 36.9 | 575 |  | 2020-09-18 15:15 | 44092.6351 | 19.8 | 36.9 | 575 |  | caution | 2020-09-14 | B20474¦Courtroom4 corridor¦¦Sep-18-2020 15:14
2020-09-18 15:15 | 44092.6353 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 102 |  | 1 | 11.1 | 31.7 | 400 | 21.2 | 22.8 | 413 | no | 2020-09-18 15:15 | 44092.6353 | 21.2 | 22.8 | 413 |  | low | 2020-09-14 | B70496¦102¦¦Sep-18-2020 15:14
2020-09-18 15:16 | 44092.636 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Jury room waiting area |  | 1 | 16.1 | 27.3 | 383 | 22.4 | 32.3 | 399 |  | 2020-09-18 15:16 | 44092.636 | 22.4 | 32.3 | 399 |  | low | 2020-09-14 | B20390¦Jury room waiting area¦¦Sep-18-2020 15:15
2020-09-18 15:16 | 44092.6364 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Stairwell |  | 0 | 15.5 | 30.2 | 422 | 20 | 25.3 | 425 |  | 2020-09-18 15:16 | 44092.6364 | 20 | 25.3 | 425 |  | low | 2020-09-14 | B20603¦Stairwell ¦¦Sep-18-2020 15:16
2020-09-18 15:18 | 44092.6372 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Stair well 2 |  | 0 | 15.5 | 30.2 | 422 | 19 | 27.6 | 426 |  | 2020-09-18 15:18 | 44092.6372 | 19 | 27.6 | 426 |  | low | 2020-09-14 | B20603¦Stair well 2¦¦Sep-18-2020 15:17
2020-09-18 15:18 | 44092.6372 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom2 2nd door |  | 1 | 14.7 | 30.6 | 387 | 20 | 36.6 | 559 |  | 2020-09-18 15:18 | 44092.6372 | 20 | 36.6 | 559 |  | caution | 2020-09-14 | B20474¦Waiting area courtroom2 2nd door¦¦Sep-18-2020 15:17
2020-09-18 15:18 | 44092.6375 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside museum |  | 1 | 16.1 | 27.3 | 383 | 22.1 | 32.2 | 410 |  | 2020-09-18 15:18 | 44092.6375 | 22.1 | 32.2 | 410 |  | low | 2020-09-14 | B20390¦Outside museum¦¦Sep-18-2020 15:18
2020-09-18 15:19 | 44092.638 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Stairwell 3 |  | 0 | 15.5 | 30.2 | 422 | 18 | 29.3 | 420 |  | 2020-09-18 15:19 | 44092.638 | 18 | 29.3 | 420 |  | low | 2020-09-14 | B20603¦Stairwell 3¦¦Sep-18-2020 15:18
2020-09-18 15:19 | 44092.6382 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Museum |  | 1 | 16.1 | 27.3 | 383 | 21.7 | 36.6 | 394 |  | 2020-09-18 15:19 | 44092.6382 | 21.7 | 36.6 | 394 |  | caution | 2020-09-14 | B20390¦Museum ¦¦Sep-18-2020 15:19
2020-09-18 15:20 | 44092.6391 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom2 1st door |  | 1 | 14.7 | 30.6 | 387 | 19.9 | 35.3 | 603 |  | 2020-09-18 15:20 | 44092.6391 | 19.9 | 35.3 | 603 |  | caution | 2020-09-14 | B20474¦Waiting area courtroom2 1st door¦¦Sep-18-2020 15:20
2020-09-18 15:21 | 44092.6395 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 6 |  | 1 | 16.1 | 27.3 | 383 | 22.1 | 33.2 | 384 | courtroom 6 in use | 2020-09-18 15:21 | 44092.6395 | 22.1 | 33.2 | 384 |  | low | 2020-09-14 | B20390¦Outside courtroom 6¦¦Sep-18-2020 15:20
2020-09-18 15:22 | 44092.6402 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Main entrance |  | 0 | 20.2 | 13 | 457 | 21 | 21 | 491 |  | 2020-09-18 15:22 | 44092.6402 | 21 | 21 | 491 |  | low | 2020-09-14 | B25477¦Main entrance ¦¦Sep-18-2020 15:21
2020-09-18 15:22 | 44092.6404 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Back stairwell, second floor |  | 1 | 16.1 | 27.3 | 383 | 21.8 | 36.6 | 382 |  | 2020-09-18 15:22 | 44092.6404 | 21.8 | 36.6 | 382 |  | caution | 2020-09-14 | B20390¦Back stairwell, second floor¦¦Sep-18-2020 15:22
2020-09-18 15:22 | 44092.6405 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Front desk |  | 4 | 14.7 | 30.6 | 387 | 19.8 | 34.7 | 608 |  | 2020-09-18 15:22 | 44092.6405 | 19.8 | 34.7 | 608 |  | low | 2020-09-14 | B20474¦Front desk¦¦Sep-18-2020 15:22
2020-09-18 15:23 | 44092.641 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Front lobby |  | 2 | 20.2 | 13 | 457 | 21.8 | 25 | 512 |  | 2020-09-18 15:23 | 44092.641 | 21.8 | 25 | 512 |  | low | 2020-09-14 | B25477¦Front lobby ¦¦Sep-18-2020 15:23
2020-09-18 15:23 | 44092.641 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | stairwell |  | 1 | 11.1 | 31.7 | 400 | 23.4 | 24.6 | 466 | no | 2020-09-18 15:23 | 44092.641 | 23.4 | 24.6 | 466 |  | low | 2020-09-14 | B70496¦stairwell¦¦Sep-18-2020 15:23
2020-09-18 15:24 | 44092.6415 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Between second floor washrooms |  | 1 | 16.1 | 27.3 | 383 | 21.8 | 34 | 405 |  | 2020-09-18 15:24 | 44092.6415 | 21.8 | 34 | 405 |  | low | 2020-09-14 | B20390¦Between second floor washrooms¦¦Sep-18-2020 15:23
2020-09-18 15:24 | 44092.6416 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 2nd floor elevator lobby |  | 2 | 11.1 | 31.7 | 400 | 23.1 | 24.5 | 484 | no | 2020-09-18 15:24 | 44092.6416 | 23.1 | 24.5 | 484 |  | low | 2020-09-14 | B70496¦2nd floor elevator lobby¦¦Sep-18-2020 15:23
2020-09-18 15:24 | 44092.6418 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | HR |  | 2 | 20.2 | 13 | 457 | 21.7 | 24 | 512 |  | 2020-09-18 15:24 | 44092.6418 | 21.7 | 24 | 512 |  | low | 2020-09-14 | B25477¦HR¦¦Sep-18-2020 15:24
2020-09-18 15:25 | 44092.6426 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | ED office |  | 2 | 20.2 | 13 | 457 | 22 | 25.1 | 522 |  | 2020-09-18 15:25 | 44092.6426 | 22 | 25.1 | 522 |  | low | 2020-09-14 | B25477¦ED office ¦¦Sep-18-2020 15:25
2020-09-18 15:26 | 44092.6428 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Crown attoreys waiting area |  | 1 | 16.1 | 27.3 | 383 | 22.2 | 26.2 | 393 |  | 2020-09-18 15:26 | 44092.6428 | 22.2 | 26.2 | 393 |  | low | 2020-09-14 | B20390¦Crown attoreys waiting area¦¦Sep-18-2020 15:25
2020-09-18 15:27 | 44092.6434 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom #4 |  | 4 | 14.7 | 30.6 | 387 | 21.1 | 34.2 | 578 |  | 2020-09-18 15:27 | 44092.6434 | 21.1 | 34.2 | 578 |  | low | 2020-09-14 | B20474¦Courtroom #4¦¦Sep-18-2020 15:26
2020-09-18 15:27 | 44092.6436 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Crown attorneys reception area |  | 1 | 16.1 | 27.3 | 383 | 22.1 | 32 | 396 |  | 2020-09-18 15:27 | 44092.6436 | 22.1 | 32 | 396 |  | low | 2020-09-14 | B20390¦Crown attorneys reception area¦¦Sep-18-2020 15:26
2020-09-18 15:27 | 44092.6439 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Admin office |  | 2 | 20.2 | 13 | 457 | 22.2 | 26.9 | 538 |  | 2020-09-18 15:27 | 44092.6439 | 22.2 | 26.9 | 538 |  | low | 2020-09-14 | B25477¦Admin office ¦¦Sep-18-2020 15:27
2020-09-18 15:28 | 44092.6446 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Financial services |  | 4 | 20.2 | 13 | 457 | 22.2 | 26.6 | 530 |  | 2020-09-18 15:28 | 44092.6446 | 22.2 | 26.6 | 530 |  | low | 2020-09-14 | B25477¦Financial services ¦¦Sep-18-2020 15:28
2020-09-18 15:29 | 44092.645 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Trial office |  | 2 | 14.7 | 30.6 | 387 | 21.2 | 33.2 | 593 |  | 2020-09-18 15:29 | 44092.645 | 21.2 | 33.2 | 593 |  | low | 2020-09-14 | B20474¦Trial office¦¦Sep-18-2020 15:28
2020-09-18 15:29 | 44092.645 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 4 |  | 1 | 16.1 | 27.3 | 383 | 21.8 | 26.6 | 401 | Courtroom 4 locked | 2020-09-18 15:29 | 44092.645 | 21.8 | 26.6 | 401 |  | low | 2020-09-14 | B20390¦Outside courtroom 4¦¦Sep-18-2020 15:28
2020-09-18 15:29 | 44092.6455 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Courtroom |  | 3 | 20.2 | 13 | 457 | 21.8 | 25 | 485 |  | 2020-09-18 15:29 | 44092.6455 | 21.8 | 25 | 485 |  | low | 2020-09-14 | B25477¦Courtroom ¦¦Sep-18-2020 15:29
2020-09-18 15:31 | 44092.6462 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside courtroom 5 |  | 1 | 16.1 | 27.3 | 383 | 22 | 25.9 | 395 | Courtroom 5 locked | 2020-09-18 15:31 | 44092.6462 | 22 | 25.9 | 395 |  | low | 2020-09-14 | B20390¦Outside courtroom 5¦¦Sep-18-2020 15:30
2020-09-18 15:31 | 44092.6463 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Emergency services |  | 3 | 20.2 | 13 | 457 | 22.1 | 24.6 | 477 |  | 2020-09-18 15:31 | 44092.6463 | 22.1 | 24.6 | 477 |  | low | 2020-09-14 | B25477¦Emergency services ¦¦Sep-18-2020 15:30
2020-09-18 15:31 | 44092.6469 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Mezzanine |  | 0 | 20.2 | 13 | 457 | 22.2 | 25.1 | 521 |  | 2020-09-18 15:31 | 44092.6469 | 22.2 | 25.1 | 521 |  | low | 2020-09-14 | B25477¦Mezzanine ¦¦Sep-18-2020 15:31
2020-09-18 15:32 | 44092.6473 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area main office |  | 1 | 14.7 | 30.6 | 387 | 20.7 | 34.5 | 609 |  | 2020-09-18 15:32 | 44092.6473 | 20.7 | 34.5 | 609 |  | low | 2020-09-14 | B20474¦Waiting area main office¦¦Sep-18-2020 15:32
2020-09-18 15:32 | 44092.6475 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Main stairwell, third floor |  | 1 | 16.1 | 27.3 | 383 | 23 | 31.4 | 417 |  | 2020-09-18 15:32 | 44092.6475 | 23 | 31.4 | 417 |  | low | 2020-09-14 | B20390¦Main stairwell, third floor ¦¦Sep-18-2020 15:32
2020-09-18 15:33 | 44092.6478 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Library |  | 0 | 20.2 | 13 | 457 | 22.1 | 23.6 | 470 |  | 2020-09-18 15:33 | 44092.6478 | 22.1 | 23.6 | 470 |  | low | 2020-09-14 | B25477¦Library ¦¦Sep-18-2020 15:32
2020-09-18 15:33 | 44092.6483 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 204 |  | 1 | 11.1 | 31.7 | 400 | 21.4 | 23.3 | 470 | no | 2020-09-18 15:33 | 44092.6483 | 21.4 | 23.3 | 470 |  | low | 2020-09-14 | B70496¦204¦¦Sep-18-2020 15:33
2020-09-18 15:34 | 44092.6484 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Third floor waiting area |  | 1 | 16.1 | 27.3 | 383 | 23 | 28.2 | 414 |  | 2020-09-18 15:34 | 44092.6484 | 23 | 28.2 | 414 |  | low | 2020-09-14 | B20390¦Third floor waiting area¦¦Sep-18-2020 15:33
2020-09-18 15:34 | 44092.6486 | AINSWORTH | B25477 | B25477 - 97 Thomas St E - Napanee | Board room |  | 0 | 20.2 | 13 | 457 | 22.8 | 23.8 | 471 |  | 2020-09-18 15:34 | 44092.6486 | 22.8 | 23.8 | 471 |  | low | 2020-09-14 | B25477¦Board room ¦¦Sep-18-2020 15:33
2020-09-18 15:34 | 44092.6487 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 204 |  | 1 | 11.1 | 31.7 | 400 | 21.4 | 25 | 552 | no | 2020-09-18 15:34 | 44092.6487 | 21.4 | 25 | 552 |  | low | 2020-09-14 | B70496¦204¦¦Sep-18-2020 15:34
2020-09-18 15:35 | 44092.6493 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #3 judge |  | 1 | 21 | 18 | 404 |  |  |  | Occupied, no access | 2020-09-18 15:35 | 44092.6493 | [5 empty] | 2020-09-14 | B70235¦Court #3 judge ¦¦Sep-18-2020 15:34
2020-09-18 15:35 | 44092.6495 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | courtroom 1 waiting area |  | 1 | 16.1 | 27.3 | 383 | 22.5 | 28.4 | 395 | Courtroom 1 in use | 2020-09-18 15:35 | 44092.6495 | 22.5 | 28.4 | 395 |  | low | 2020-09-14 | B20390¦courtroom 1 waiting area¦¦Sep-18-2020 15:35
2020-09-18 15:35 | 44092.6495 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Upper landing on stairway |  | 1 | 14.7 | 33.7 | 618 | 20.1 | 34 | 630 |  | 2020-09-18 15:35 | 44092.6495 | 20.1 | 34 | 630 |  | low | 2020-09-14 | B20474¦Upper landing on stairway¦¦Sep-18-2020 15:35
2020-09-18 15:36 | 44092.6497 | AINSWORTH | B21128 | B21128 - 1911 Eglinton Ave E - Scarborough | Crown attorneys office |  | 2 | 18.3 | 24.2 | 388 | 23 | 18.9 | 420 | No | 2020-09-18 15:36 | 44092.6497 | 23 | 18.9 | 420 |  | low | 2020-09-14 | B21128¦Crown attorneys office ¦¦Sep-18-2020 15:35
2020-09-18 15:37 | 44092.6505 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 2nd floor hallway |  | 2 | 11.1 | 31.7 | 400 | 22.5 | 24.4 | 471 | no | 2020-09-18 15:37 | 44092.6505 | 22.5 | 24.4 | 471 |  | low | 2020-09-14 | B70496¦2nd floor hallway¦¦Sep-18-2020 15:36
2020-09-18 15:37 | 44092.651 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 203 |  | 1 | 11.1 | 31.7 | 400 | 21.1 | 29.5 | 478 | no | 2020-09-18 15:37 | 44092.651 | 21.1 | 29.5 | 478 |  | low | 2020-09-14 | B70496¦203¦¦Sep-18-2020 15:37
2020-09-18 15:38 | 44092.6511 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Outside third floor elevator |  | 1 | 16.1 | 27.3 | 383 | 22.4 | 30.3 | 406 |  | 2020-09-18 15:38 | 44092.6511 | 22.4 | 30.3 | 406 |  | low | 2020-09-14 | B20390¦Outside third floor elevator¦¦Sep-18-2020 15:37
2020-09-18 15:38 | 44092.6512 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Office |  | 1 | 21.1 | 17.3 | 363 | 21.9 | 23.2 | 411 |  | 2020-09-18 15:38 | 44092.6512 | 21.9 | 23.2 | 411 |  | low | 2020-09-14 | Pearso¦Office¦¦Sep-18-2020 15:37
2020-09-18 15:38 | 44092.6515 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 202 |  | 4 | 11.1 | 31.7 | 400 | 21.5 | 24.4 | 460 | no | 2020-09-18 15:38 | 44092.6515 | 21.5 | 24.4 | 460 |  | low | 2020-09-14 | B70496¦202¦¦Sep-18-2020 15:38
2020-09-18 15:39 | 44092.6519 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Waiting area courtroom1 |  | 1 | 14.7 | 30.6 | 387 | 19.8 | 35.2 | 634 |  | 2020-09-18 15:39 | 44092.6519 | 19.8 | 35.2 | 634 |  | caution | 2020-09-14 | B20474¦Waiting area courtroom1¦¦Sep-18-2020 15:38
2020-09-18 15:39 | 44092.652 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom a |  | 0 | 21.1 | 17.3 | 363 | 23.1 | 20.7 | 387 |  | 2020-09-18 15:39 | 44092.652 | 23.1 | 20.7 | 387 |  | low | 2020-09-14 | Pearso¦Courtroom a¦¦Sep-18-2020 15:38
2020-09-18 15:40 | 44092.6525 | AINSWORTH | B20390 | B20390 - 102 East Main St - Welland | Elevator |  | 1 | 16.1 | 27.3 | 383 | 23.1 | 31.1 | 408 |  | 2020-09-18 15:40 | 44092.6525 | 23.1 | 31.1 | 408 |  | low | 2020-09-14 | B20390¦Elevator ¦¦Sep-18-2020 15:39
2020-09-18 15:40 | 44092.6526 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom a back |  | 0 | 21.1 | 17.3 | 363 | 22.7 | 20.6 | 382 |  | 2020-09-18 15:40 | 44092.6526 | 22.7 | 20.6 | 382 |  | low | 2020-09-14 | Pearso¦Courtroom a back¦¦Sep-18-2020 15:39
2020-09-18 15:40 | 44092.6528 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 waiting area |  | 1 | 25 | 14 | 356 | 22 | 23 | 364 |  | 2020-09-18 15:40 | 44092.6528 | 22 | 23 | 364 |  | low | 2020-09-14 | B20772¦H9 waiting area ¦¦Sep-18-2020 15:40
2020-09-18 15:41 | 44092.6536 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 rear left |  | 1 | 25 | 14 | 356 | 22 | 23 | 363 |  | 2020-09-18 15:41 | 44092.6536 | 22 | 23 | 363 |  | low | 2020-09-14 | B20772¦H9 rear left¦¦Sep-18-2020 15:41
2020-09-18 15:42 | 44092.654 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom b |  | 0 | 21.1 | 17.3 | 363 | 22.5 | 20.1 | 377 |  | 2020-09-18 15:42 | 44092.654 | 22.5 | 20.1 | 377 |  | low | 2020-09-14 | Pearso¦Courtroom b¦¦Sep-18-2020 15:41
2020-09-18 15:42 | 44092.6543 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 rear right |  | 1 | 25 | 14 | 356 | 22 | 23 | 363 |  | 2020-09-18 15:42 | 44092.6543 | 22 | 23 | 363 |  | low | 2020-09-14 | B20772¦H9 rear right ¦¦Sep-18-2020 15:42
2020-09-18 15:43 | 44092.6547 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom b back |  | 0 | 21.1 | 17.3 | 376 | 22.7 | 20.1 | 376 |  | 2020-09-18 15:43 | 44092.6547 | 22.7 | 20.1 | 376 |  | low | 2020-09-14 | Pearso¦Courtroom b back¦¦Sep-18-2020 15:42
2020-09-18 15:43 | 44092.6549 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 defendant |  | 1 | 25 | 14 | 356 | 22 | 23 | 364 |  | 2020-09-18 15:43 | 44092.6549 | 22 | 23 | 364 |  | low | 2020-09-14 | B20772¦H9 defendant ¦¦Sep-18-2020 15:43
2020-09-18 15:44 | 44092.6553 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom c |  | 0 | 21.1 | 17.3 | 363 | 22.7 | 20.4 | 376 |  | 2020-09-18 15:44 | 44092.6553 | 22.7 | 20.4 | 376 |  | low | 2020-09-14 | Pearso¦Courtroom c¦¦Sep-18-2020 15:43
2020-09-18 15:44 | 44092.6556 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 plaintiff |  | 1 | 25 | 14 | 356 | 22 | 23 | 365 |  | 2020-09-18 15:44 | 44092.6556 | 22 | 23 | 365 |  | low | 2020-09-14 | B20772¦H9 plaintiff ¦¦Sep-18-2020 15:44
2020-09-18 15:45 | 44092.6563 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 judge |  | 1 | 25 | 14 | 365 | 22 | 23 | 365 |  | 2020-09-18 15:45 | 44092.6563 | 22 | 23 | 365 |  | low | 2020-09-14 | B20772¦H9 judge¦¦Sep-18-2020 15:45
2020-09-18 15:45 | 44092.6566 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom c back |  | 0 | 21.1 | 17.3 | 363 | 23.2 | 19.9 | 375 |  | 2020-09-18 15:45 | 44092.6566 | 23.2 | 19.9 | 375 |  | low | 2020-09-14 | Pearso¦Courtroom c back¦¦Sep-18-2020 15:45
2020-09-18 15:47 | 44092.6575 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom d |  | 0 | 21.1 | 17.3 | 363 | 23 | 19.8 | 369 |  | 2020-09-18 15:47 | 44092.6575 | 23 | 19.8 | 369 |  | low | 2020-09-14 | Pearso¦Courtroom d¦¦Sep-18-2020 15:46
2020-09-18 15:48 | 44092.6583 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom d back |  | 0 | 21.1 | 17.3 | 363 | 23.1 | 19.5 | 372 |  | 2020-09-18 15:48 | 44092.6583 | 23.1 | 19.5 | 372 |  | low | 2020-09-14 | Pearso¦Courtroom d back¦¦Sep-18-2020 15:48
2020-09-18 15:49 | 44092.659 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom e |  | 0 | 21.1 | 17.3 | 363 | 22.5 | 18.5 | 367 |  | 2020-09-18 15:49 | 44092.659 | 22.5 | 18.5 | 367 |  | low | 2020-09-14 | Pearso¦Courtroom e¦¦Sep-18-2020 15:49
2020-09-18 15:49 | 44092.6591 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 judge |  | 1 | 25 | 14 | 356 | 21 | 23 | 363 |  | 2020-09-18 15:49 | 44092.6591 | 21 | 23 | 363 |  | low | 2020-09-14 | B20772¦H15 judge ¦¦Sep-18-2020 15:49
2020-09-18 15:50 | 44092.6597 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom e back |  | 0 | 21.1 | 17.3 | 363 | 22.5 | 19.2 | 364 |  | 2020-09-18 15:50 | 44092.6597 | 22.5 | 19.2 | 364 |  | low | 2020-09-14 | Pearso¦Courtroom e back¦¦Sep-18-2020 15:50
2020-09-18 15:50 | 44092.6601 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 plaintiff’s |  | 1 | 25 | 14 | 356 | 21 | 23 | 363 |  | 2020-09-18 15:50 | 44092.6601 | 21 | 23 | 363 |  | low | 2020-09-14 | B20772¦H15 plaintiff’s ¦¦Sep-18-2020 15:50
2020-09-18 15:51 | 44092.6606 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom f |  | 0 | 21.1 | 17.3 | 363 | 23.2 | 19.6 | 374 |  | 2020-09-18 15:51 | 44092.6606 | 23.2 | 19.6 | 374 |  | low | 2020-09-14 | Pearso¦Courtroom f¦¦Sep-18-2020 15:51
2020-09-18 15:51 | 44092.6607 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 dependant |  | 1 | 25 | 14 | 356 | 21 | 23 | 365 |  | 2020-09-18 15:51 | 44092.6607 | 21 | 23 | 365 |  | low | 2020-09-14 | B20772¦H15 dependant¦¦Sep-18-2020 15:51
2020-09-18 15:52 | 44092.6613 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 rear right |  | 1 | 25 | 14 | 356 | 21 | 23 | 368 |  | 2020-09-18 15:52 | 44092.6613 | 21 | 23 | 368 |  | low | 2020-09-14 | B20772¦H15 rear right¦¦Sep-18-2020 15:52
2020-09-18 15:53 | 44092.6615 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Courtroom f back |  | 0 | 21.1 | 17.3 | 363 | 23.5 | 19.2 | 372 |  | 2020-09-18 15:53 | 44092.6615 | 23.5 | 19.2 | 372 |  | low | 2020-09-14 | Pearso¦Courtroom f back¦¦Sep-18-2020 15:52
2020-09-18 15:53 | 44092.6621 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 rear left |  | 1 | 25 | 14 | 356 | 21 | 23 | 370 |  | 2020-09-18 15:54 | 44092.6621 | 21 | 23 | 370 |  | low | 2020-09-14 | B20772¦H15 rear left ¦¦Sep-18-2020 15:53
2020-09-18 15:54 | 44092.6622 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Police room 1 |  | 0 | 21.1 | 17.3 | 363 | 23.3 | 19.4 | 372 |  | 2020-09-18 15:54 | 44092.6622 | 23.3 | 19.4 | 372 |  | low | 2020-09-14 | Pearso¦Police room 1¦¦Sep-18-2020 15:53
2020-09-18 15:56 | 44092.664 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 waiting area |  | 1 | 25 | 14 | 356 | 22 | 25 | 364 |  | 2020-09-18 15:56 | 44092.664 | 22 | 25 | 364 |  | low | 2020-09-14 | B20772¦H15 waiting area¦¦Sep-18-2020 15:56
2020-09-18 15:58 | 44092.6653 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | 201 |  | 1 | 11.1 | 31.7 | 400 | 21.5 | 24.2 | 460 | no | 2020-09-18 15:58 | 44092.6653 | 21.5 | 24.2 | 460 |  | low | 2020-09-14 | B70496¦201¦¦Sep-18-2020 15:58
2020-09-18 15:59 | 44092.6658 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | administration office |  | 4 | 11.1 | 31.7 | 400 | 21.5 | 26.3 | 602 | no | 2020-09-18 15:59 | 44092.6658 | 21.5 | 26.3 | 602 |  | low | 2020-09-14 | B70496¦administration office¦¦Sep-18-2020 15:58
2020-09-18 15:59 | 44092.666 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area north |  | 1 | 25 | 14 | 356 | 23 | 22 | 365 |  | 2020-09-18 15:59 | 44092.666 | 23 | 22 | 365 |  | low | 2020-09-14 | B20772¦Courtroom waiting area north¦¦Sep-18-2020 15:58
2020-09-18 16:00 | 44092.6664 | AINSWORTH | B70496 | B70496 - 10 Louisa St - Orangeville | outside customer service entrance |  | 1 | 11.1 | 31.7 | 400 | 12.1 | 28 | 399 | no | 2020-09-18 16:00 | 44092.6664 | 12.1 | 28 | 399 |  | low | 2020-09-14 | B70496¦outside customer service entrance¦¦Sep-18-2020 15:59
2020-09-18 16:00 | 44092.6665 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area south |  | 1 | 25 | 14 | 356 | 23 | 22 | 366 |  | 2020-09-18 16:00 | 44092.6665 | 23 | 22 | 366 |  | low | 2020-09-14 | B20772¦Courtroom waiting area south¦¦Sep-18-2020 15:59
2020-09-18 16:00 | 44092.6667 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE STAFF |  | 2 | 17 | 22 | 444 | 22 | 35.4 | 522 |  | 2020-09-18 16:00 | 44092.6667 | 22 | 35.4 | 522 |  | caution | 2020-09-14 | B20022¦JUDGE STAFF¦¦Sep-18-2020 15:59
2020-09-18 16:01 | 44092.6673 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE CORKERY |  | 1 | 17 | 22 | 444 | 21.9 | 37 | 450 |  | 2020-09-18 16:01 | 44092.6673 | 21.9 | 37 | 450 |  | caution | 2020-09-14 | B20022¦JUDGE CORKERY¦¦Sep-18-2020 16:00
2020-09-18 16:02 | 44092.6678 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 rear right |  | 1 | 25 | 14 | 356 | 22 | 22 | 360 |  | 2020-09-18 16:02 | 44092.6678 | 22 | 22 | 360 |  | low | 2020-09-14 | B20772¦H12 rear right¦¦Sep-18-2020 16:01
2020-09-18 16:02 | 44092.6678 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE INGRAM |  | 2 | 17 | 22 | 444 | 21.7 | 39 | 455 |  | 2020-09-18 16:02 | 44092.6678 | 21.7 | 39 | 455 |  | caution | 2020-09-14 | B20022¦JUDGE INGRAM¦¦Sep-18-2020 16:01
2020-09-18 16:02 | 44092.6682 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGE MCLEOD |  | 1 | 17 | 22 | 444 | 21.6 | 45 | 466 |  | 2020-09-18 16:02 | 44092.6682 | 21.6 | 45 | 466 |  |  | 2020-09-14 | B20022¦JUDGE MCLEOD¦¦Sep-18-2020 16:02
2020-09-18 16:02 | 44092.6684 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 rear left |  | 1 | 25 | 14 | 356 | 22 | 22 | 360 |  | 2020-09-18 16:02 | 44092.6684 | 22 | 22 | 360 |  | low | 2020-09-14 | B20772¦H12 rear left¦¦Sep-18-2020 16:02
2020-09-18 16:03 | 44092.6688 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 JUDGE |  | 2 | 17 | 22 | 444 | 21.5 | 39 | 452 |  | 2020-09-18 16:03 | 44092.6688 | 21.5 | 39 | 452 |  | caution | 2020-09-14 | B20022¦COURT 3 JUDGE¦¦Sep-18-2020 16:03
2020-09-18 16:03 | 44092.669 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 dependant |  | 1 | 25 | 14 | 356 | 22 | 22 | 360 |  | 2020-09-18 16:03 | 44092.669 | 22 | 22 | 360 |  | low | 2020-09-14 | B20772¦H12 dependant¦¦Sep-18-2020 16:03
2020-09-18 16:04 | 44092.6694 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 LAWYER |  | 2 | 17 | 22 | 444 | 21 | 33 | 428 |  | 2020-09-18 16:04 | 44092.6694 | 21 | 33 | 428 |  | low | 2020-09-14 | B20022¦COURT 3 LAWYER¦¦Sep-18-2020 16:03
2020-09-18 16:05 | 44092.6698 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | ADVICE COUNSEL |  | 2 | 17 | 22 | 444 | 20.9 | 32 | 414 |  | 2020-09-18 16:05 | 44092.6698 | 20.9 | 32 | 414 |  | low | 2020-09-14 | B20022¦ADVICE COUNSEL¦¦Sep-18-2020 16:04
2020-09-18 16:05 | 44092.6698 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 plaintiff’s |  | 1 | 25 | 14 | 356 | 22 | 22 | 361 |  | 2020-09-18 16:05 | 44092.6698 | 22 | 22 | 361 |  | low | 2020-09-14 | B20772¦H12 plaintiff’s ¦¦Sep-18-2020 16:04
2020-09-18 16:05 | 44092.6703 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 3 WAITING AREA |  | 2 | 17 | 22 | 444 | 21 | 30.9 | 413 |  | 2020-09-18 16:05 | 44092.6703 | 21 | 30.9 | 413 |  | low | 2020-09-14 | B20022¦COURT 3 WAITING AREA¦¦Sep-18-2020 16:05
2020-09-18 16:06 | 44092.6705 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 judge |  | 1 | 25 | 14 | 356 | 22 | 21 | 363 |  | 2020-09-18 16:06 | 44092.6705 | 22 | 21 | 363 |  | low | 2020-09-14 | B20772¦H12 judge¦¦Sep-18-2020 16:05
2020-09-18 16:06 | 44092.6711 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT OFFICE LOBBY |  | 4 | 17 | 22 | 444 | 22 | 39 | 740 |  | 2020-09-18 16:06 | 44092.6711 | 22 | 39 | 740 |  | caution | 2020-09-14 | B20022¦COURT OFFICE LOBBY¦¦Sep-18-2020 16:06
2020-09-18 16:07 | 44092.6712 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 retiring room |  | 1 | 25 | 14 | 356 | 22 | 24 | 366 |  | 2020-09-18 16:07 | 44092.6712 | 22 | 24 | 366 |  | low | 2020-09-14 | B20772¦H12 retiring room ¦¦Sep-18-2020 16:06
2020-09-18 16:07 | 44092.6718 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT OFFICE |  | 5 | 17 | 22 | 444 | 21.6 | 43 | 576 |  | 2020-09-18 16:07 | 44092.6718 | 21.6 | 43 | 576 |  |  | 2020-09-14 | B20022¦COURT OFFICE¦¦Sep-18-2020 16:07
2020-09-18 16:08 | 44092.672 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 retiring room |  | 1 | 25 | 14 | 356 | 22 | 25 | 364 |  | 2020-09-18 16:08 | 44092.672 | 22 | 25 | 364 |  | low | 2020-09-14 | B20772¦H11 retiring room ¦¦Sep-18-2020 16:07
2020-09-18 16:08 | 44092.6723 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | MEDIATION ROOM |  | 1 | 17 | 22 | 444 | 21 |  | 566 |  | 2020-09-18 16:08 | 44092.6723 | 21 |  | 566 |  |  | 2020-09-14 | B20022¦MEDIATION ROOM¦¦Sep-18-2020 16:08
2020-09-18 16:09 | 44092.6726 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 rear right |  | 1 | 25 | 14 | 356 | 22 | 22 | 363 |  | 2020-09-18 16:09 | 44092.6726 | 22 | 22 | 363 |  | low | 2020-09-14 | B20772¦H11 rear right ¦¦Sep-18-2020 16:08
2020-09-18 16:09 | 44092.673 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | OFFICER ROOM |  | 2 | 17 | 22 | 444 | 22.2 | 35.8 | 729 |  | 2020-09-18 16:09 | 44092.673 | 22.2 | 35.8 | 729 |  | caution | 2020-09-14 | B20022¦OFFICER ROOM¦¦Sep-18-2020 16:09
2020-09-18 16:10 | 44092.6735 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 1 FLOOR LOBBY |  | 5 | 17 | 22 | 444 | 22 | 37 | 566 |  | 2020-09-18 16:10 | 44092.6735 | 22 | 37 | 566 |  | caution | 2020-09-14 | B20022¦1 FLOOR LOBBY¦¦Sep-18-2020 16:09
2020-09-18 16:10 | 44092.6738 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | RM 14 JUDGE |  | 1 | 15.7 | 30 | 390 | 22.7 | 26 | 500 |  | 2020-09-18 16:10 | 44092.6738 | 22.7 | 26 | 500 |  | low | 2020-09-14 | B70740¦RM 14 JUDGE¦¦Sep-18-2020 16:10
2020-09-18 16:10 | 44092.6738 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 rear left |  | 1 | 25 | 14 | 356 | 22 | 22 | 368 |  | 2020-09-18 16:10 | 44092.6738 | 22 | 22 | 368 |  | low | 2020-09-14 | B20772¦H11 rear left¦¦Sep-18-2020 16:10
2020-09-18 16:10 | 44092.6739 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom #1 |  | 1 | 17.5 | 20.2 | 410 | 20.4 | 27 | 693 |  | 2020-09-18 16:10 | 44092.6739 | 20.4 | 27 | 693 |  | low | 2020-09-14 | B21554¦Courtroom #1¦¦Sep-18-2020 16:10
2020-09-18 16:10 | 44092.6739 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR LUNCH |  | 2 | 17 | 22 | 444 | 21.9 | 28.6 | 464 |  | 2020-09-18 16:10 | 44092.6739 | 21.9 | 28.6 | 464 |  | low | 2020-09-14 | B20022¦2 FLOOR LUNCH¦¦Sep-18-2020 16:10
2020-09-18 16:11 | 44092.6743 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 2 JUDGE |  | 2 | 17 | 22 | 444 | 21 | 29 | 434 |  | 2020-09-18 16:11 | 44092.6743 | 21 | 29 | 434 |  | low | 2020-09-14 | B20022¦COURT 2 JUDGE¦¦Sep-18-2020 16:10
2020-09-18 16:11 | 44092.6745 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 14 |  | 0 | 15.7 | 30 | 390 | 22.4 | 27 | 450 |  | 2020-09-18 16:11 | 44092.6745 | 22.4 | 27 | 450 |  | low | 2020-09-14 | B70740¦14¦¦Sep-18-2020 16:11
2020-09-18 16:12 | 44092.6747 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 2 LAWYER |  | 2 | 17 | 22 | 444 | 21.6 | 28 | 429 |  | 2020-09-18 16:12 | 44092.6747 | 21.6 | 28 | 429 |  | low | 2020-09-14 | B20022¦COURT 2 LAWYER¦¦Sep-18-2020 16:11
2020-09-18 16:12 | 44092.6751 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 14 SEATING AREA |  | 0 | 15.7 | 30 | 390 | 22.2 | 27 | 450 |  | 2020-09-18 16:12 | 44092.6751 | 22.2 | 27 | 450 |  | low | 2020-09-14 | B70740¦14 SEATING AREA¦¦Sep-18-2020 16:12
2020-09-18 16:12 | 44092.6751 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 defendant |  | 1 | 25 | 14 | 356 | 22 | 22 | 363 |  | 2020-09-18 16:12 | 44092.6751 | 22 | 22 | 363 |  | low | 2020-09-14 | B20772¦H12 defendant¦¦Sep-18-2020 16:12
2020-09-18 16:12 | 44092.6753 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 JUDGE |  | 3 | 17 | 22 | 444 | 21.9 | 33.6 | 437 |  | 2020-09-18 16:12 | 44092.6753 | 21.9 | 33.6 | 437 |  | low | 2020-09-14 | B20022¦COURT 1 JUDGE¦¦Sep-18-2020 16:12
2020-09-18 16:13 | 44092.6754 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom #2 |  | 1 | 17.5 | 20.2 | 410 | 20.6 | 21.3 | 453 |  | 2020-09-18 16:13 | 44092.6754 | 20.6 | 21.3 | 453 |  | low | 2020-09-14 | B21554¦Courtroom #2¦¦Sep-18-2020 16:12
2020-09-18 16:13 | 44092.6756 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | FRONT HRPS |  | 0 | 15.7 | 30 | 390 | 22.2 | 26 | 440 |  | 2020-09-18 16:13 | 44092.6756 | 22.2 | 26 | 440 |  | low | 2020-09-14 | B70740¦FRONT HRPS¦¦Sep-18-2020 16:12
2020-09-18 16:13 | 44092.6758 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 plaintiff |  | 1 | 25 | 14 | 356 | 22 | 22 | 363 |  | 2020-09-18 16:13 | 44092.6758 | 22 | 22 | 363 |  | low | 2020-09-14 | B20772¦H12 plaintiff ¦¦Sep-18-2020 16:13
2020-09-18 16:13 | 44092.6758 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 RIGHT SIDE |  | 3 | 17 | 22 | 444 | 21.8 | 35.6 | 569 |  | 2020-09-18 16:13 | 44092.6758 | 21.8 | 35.6 | 569 |  | caution | 2020-09-14 | B20022¦COURT 1 RIGHT SIDE¦¦Sep-18-2020 16:13
2020-09-18 16:14 | 44092.6763 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | COURT 1 LEFT SIDE |  | 3 | 17 | 22 | 444 | 22.1 | 33.3 | 500 |  | 2020-09-18 16:14 | 44092.6763 | 22.1 | 33.3 | 500 |  | low | 2020-09-14 | B20022¦COURT 1 LEFT SIDE¦¦Sep-18-2020 16:13
2020-09-18 16:14 | 44092.6764 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN WR CORR |  | 0 | 15.7 | 30 | 390 | 22.3 | 28 | 460 |  | 2020-09-18 16:14 | 44092.6764 | 22.3 | 28 | 460 |  | low | 2020-09-14 | B70740¦MAIN WR CORR¦¦Sep-18-2020 16:14
2020-09-18 16:14 | 44092.6766 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JURY ROOM |  | 2 | 17 | 22 | 444 | 22.3 | 31 | 458 |  | 2020-09-18 16:14 | 44092.6766 | 22.3 | 31 | 458 |  | low | 2020-09-14 | B20022¦JURY ROOM¦¦Sep-18-2020 16:14
2020-09-18 16:15 | 44092.6768 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 judge |  | 1 | 25 | 14 | 356 | 22 | 22 | 364 |  | 2020-09-18 16:15 | 44092.6768 | 22 | 22 | 364 |  | low | 2020-09-14 | B20772¦H11 judge¦¦Sep-18-2020 16:14
2020-09-18 16:15 | 44092.6771 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR LEFT MEETING |  | 1 | 17 | 22 | 444 | 21.5 | 37.6 | 582 |  | 2020-09-18 16:15 | 44092.6771 | 21.5 | 37.6 | 582 |  | caution | 2020-09-14 | B20022¦2 FLOOR LEFT MEETING¦¦Sep-18-2020 16:14
2020-09-18 16:15 | 44092.6771 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | SEATING 13 |  | 0 | 15.7 | 30 | 390 | 21.6 | 27 | 500 | 12 | 2020-09-18 16:15 | 44092.6771 | 21.6 | 27 | 500 |  | low | 2020-09-14 | B70740¦SEATING 13¦¦Sep-18-2020 16:14
2020-09-18 16:15 | 44092.6772 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Courtroom #3 |  | 3 | 17.5 | 20.2 | 410 | 21.5 | 30.1 | 702 |  | 2020-09-18 16:15 | 44092.6772 | 21.5 | 30.1 | 702 |  | low | 2020-09-14 | B21554¦Courtroom #3¦¦Sep-18-2020 16:15
2020-09-18 16:16 | 44092.6775 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 2 FLOOR RIGHT MEETING |  | 1 | 17 | 22 | 444 | 22 | 36 | 503 |  | 2020-09-18 16:16 | 44092.6775 | 22 | 36 | 503 |  | caution | 2020-09-14 | B20022¦2 FLOOR RIGHT MEETING¦¦Sep-18-2020 16:15
2020-09-18 16:16 | 44092.6776 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 13 |  | 0 | 15.7 | 30 | 390 | 22 | 31 | 480 |  | 2020-09-18 16:16 | 44092.6776 | 22 | 31 | 480 |  | low | 2020-09-14 | B70740¦13¦¦Sep-18-2020 16:15
2020-09-18 16:16 | 44092.6776 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H14 exit entrance |  | 1 | 25 | 14 | 356 | 22 | 23 | 363 |  | 2020-09-18 16:16 | 44092.6776 | 22 | 23 | 363 |  | low | 2020-09-14 | B20772¦H14 exit entrance¦¦Sep-18-2020 16:15
2020-09-18 16:16 | 44092.678 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | 1 FLOOR MAIN HALL |  | 1 | 17 | 22 | 444 | 21.8 | 30 | 550 |  | 2020-09-18 16:16 | 44092.678 | 21.8 | 30 | 550 |  | low | 2020-09-14 | B20022¦1 FLOOR MAIN HALL¦¦Sep-18-2020 16:16
2020-09-18 16:16 | 44092.6781 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H14 judge entrance |  | 1 | 25 | 14 | 356 | 22 | 23 | 364 |  | 2020-09-18 16:16 | 44092.6781 | 22 | 23 | 364 |  | low | 2020-09-14 | B20772¦H14 judge entrance¦¦Sep-18-2020 16:16
2020-09-18 16:17 | 44092.6782 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | SEATING 12 |  | 0 | 15.7 | 30 | 390 | 22 | 27 | 500 |  | 2020-09-18 16:17 | 44092.6782 | 22 | 27 | 500 |  | low | 2020-09-14 | B70740¦SEATING 12¦¦Sep-18-2020 16:16
2020-09-18 16:17 | 44092.6785 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | SOUTH WING ENTRANCE |  | 2 | 17 | 22 | 444 | 22.7 | 27 | 525 |  | 2020-09-18 16:17 | 44092.6785 | 22.7 | 27 | 525 |  | low | 2020-09-14 | B20022¦SOUTH WING ENTRANCE¦¦Sep-18-2020 16:17
2020-09-18 16:17 | 44092.6788 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | INERVIEW ROOM |  | 0 | 15.7 | 30 | 390 | 21.7 | 28 | 510 |  | 2020-09-18 16:17 | 44092.6788 | 21.7 | 28 | 510 |  | low | 2020-09-14 | B70740¦INERVIEW ROOM¦¦Sep-18-2020 16:17
2020-09-18 16:18 | 44092.6792 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | BOTTOM STAIRS CRT 2 |  | 2 | 17 | 22 | 444 | 21 | 32 | 414 | ADDITIONAL ADDED ROOM | 2020-09-18 16:18 | 44092.6792 | 21 | 32 | 414 |  | low | 2020-09-14 | B20022¦BOTTOM STAIRS CRT 2¦¦Sep-18-2020 16:18
2020-09-18 16:18 | 44092.6794 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 judge |  | 1 | 25 | 14 | 356 | 22 | 22 | 363 |  | 2020-09-18 16:18 | 44092.6794 | 22 | 22 | 363 |  | low | 2020-09-14 | B20772¦H13 judge¦¦Sep-18-2020 16:18
2020-09-18 16:18 | 44092.6795 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | POLICE WAITING RM |  | 0 | 15.7 | 30 | 390 | 21.6 | 26 | 510 |  | 2020-09-18 16:18 | 44092.6795 | 21.6 | 26 | 510 |  | low | 2020-09-14 | B70740¦POLICE WAITING RM¦¦Sep-18-2020 16:18
2020-09-18 16:19 | 44092.6797 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | TOP STAIRS SOUTH WING |  | 2 | 17 | 22 | 444 | 23 | 29 | 464 | ADDITIONAL READING | 2020-09-18 16:19 | 44092.6797 | 23 | 29 | 464 |  | low | 2020-09-14 | B20022¦TOP STAIRS SOUTH WING¦¦Sep-18-2020 16:18
2020-09-18 16:19 | 44092.6799 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Waiting area outside courtroom3 |  | 1 | 17.5 | 20.2 | 410 | 21.8 | 20.2 | 482 |  | 2020-09-18 16:19 | 44092.6799 | 21.8 | 20.2 | 482 |  | low | 2020-09-14 | B21554¦Waiting area outside courtroom3¦¦Sep-18-2020 16:19
2020-09-18 16:19 | 44092.68 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | 11 |  | 2 | 15.7 | 30 | 390 | 22 | 33 | 539 |  | 2020-09-18 16:19 | 44092.68 | 22 | 33 | 539 |  | low | 2020-09-14 | B70740¦11¦¦Sep-18-2020 16:19
2020-09-18 16:19 | 44092.68 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 plaintiff |  | 1 | 25 | 14 | 356 | 22 | 22 | 362 |  | 2020-09-18 16:19 | 44092.68 | 22 | 22 | 362 |  | low | 2020-09-14 | B20772¦H13 plaintiff¦¦Sep-18-2020 16:19
2020-09-18 16:20 | 44092.6807 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 defendant |  | 1 | 25 | 14 | 356 | 22 | 22 | 378 |  | 2020-09-18 16:20 | 44092.6807 | 22 | 22 | 378 |  | low | 2020-09-14 | B20772¦H13 defendant¦¦Sep-18-2020 16:20
2020-09-18 16:21 | 44092.681 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN AREA |  | 3 | 15.7 | 30 | 390 | 22.1 | 27 | 540 |  | 2020-09-18 16:21 | 44092.681 | 22.1 | 27 | 540 |  | low | 2020-09-14 | B70740¦MAIN AREA¦¦Sep-18-2020 16:20
2020-09-18 16:21 | 44092.6812 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 rear right |  | 1 | 25 | 14 | 356 | 22 | 22 | 372 |  | 2020-09-18 16:21 | 44092.6812 | 22 | 22 | 372 |  | low | 2020-09-14 | B20772¦H13 rear right¦¦Sep-18-2020 16:20
2020-09-18 16:21 | 44092.6812 | AINSWORTH | B20022 | B20022 - 470 Water St - Peterborough | JUDGES CHAMBERS |  | 1 | 17 | 22 | 444 | 23 | 28.9 | 433 | ADDITIONAL READING -- WAS NOT ABLE TO ACCESS "VISITING JUDGE ROOM" AS THE DOOR WAS LOCKED AND STAFF HAD ISSUES OPENING | 2020-09-18 16:21 | 44092.6812 | 23 | 28.9 | 433 |  | low | 2020-09-14 | B20022¦JUDGES CHAMBERS¦¦Sep-18-2020 16:20
2020-09-18 16:22 | 44092.6817 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | MAIN OFFICE |  | 4 | 15.7 | 30 | 390 | 22.5 | 30 | 540 |  | 2020-09-18 16:22 | 44092.6817 | 22.5 | 30 | 540 |  | low | 2020-09-14 | B70740¦MAIN OFFICE¦¦Sep-18-2020 16:21
2020-09-18 16:22 | 44092.6818 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H13 rear left |  | 1 | 25 | 14 | 356 | 22 | 23 | 371 |  | 2020-09-18 16:22 | 44092.6818 | 22 | 23 | 371 |  | low | 2020-09-14 | B20772¦H13 rear left¦¦Sep-18-2020 16:21
2020-09-18 16:23 | 44092.6824 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | JUSTICE BALDWIN |  | 1 | 15.7 | 30 | 390 | 23.6 | 30 | 550 |  | 2020-09-18 16:23 | 44092.6824 | 23.6 | 30 | 550 |  | low | 2020-09-14 | B70740¦JUSTICE BALDWIN¦¦Sep-18-2020 16:22
2020-09-18 16:24 | 44092.6832 | AINSWORTH | B70740 | B70740 - 2021 Plains Rd - Burlington | JUSTICE BROWN |  | 1 | 15.7 | 30 | 390 | 23 | 30 | 520 |  | 2020-09-18 16:24 | 44092.6832 | 23 | 30 | 520 |  | low | 2020-09-14 | B70740¦JUSTICE BROWN¦¦Sep-18-2020 16:23
2020-09-18 16:25 | 44092.684 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 printer |  | 1 | 25 | 14 | 356 | 22 | 24 | 371 |  | 2020-09-18 16:25 | 44092.684 | 22 | 24 | 371 |  | low | 2020-09-14 | B20772¦H16 printer¦¦Sep-18-2020 16:25
2020-09-18 16:26 | 44092.6847 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 judge |  | 1 | 25 | 14 | 356 | 22 | 24 | 371 |  | 2020-09-18 16:26 | 44092.6847 | 22 | 24 | 371 |  | low | 2020-09-14 | B20772¦H16 judge¦¦Sep-18-2020 16:26
2020-09-18 16:27 | 44092.6855 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 typer |  | 1 | 25 | 14 | 356 | 22 | 24 | 369 |  | 2020-09-18 16:27 | 44092.6855 | 22 | 24 | 369 |  | low | 2020-09-14 | B20772¦H16 typer ¦¦Sep-18-2020 16:27
2020-09-18 16:28 | 44092.6861 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 plaintiff |  | 1 | 25 | 14 | 356 | 22 | 24 | 367 |  | 2020-09-18 16:28 | 44092.6861 | 22 | 24 | 367 |  | low | 2020-09-14 | B20772¦H16 plaintiff ¦¦Sep-18-2020 16:28
2020-09-18 16:28 | 44092.6863 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Basement corridor at washrooms |  | 1 | 17.5 | 20.2 | 410 | 22 | 19.4 | 475 |  | 2020-09-18 16:28 | 44092.6863 | 22 | 19.4 | 475 |  | low | 2020-09-14 | B21554¦Basement corridor at washrooms¦¦Sep-18-2020 16:28
2020-09-18 16:29 | 44092.6866 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 defendant |  | 1 | 25 | 14 | 356 | 22 | 24 | 368 |  | 2020-09-18 16:29 | 44092.6866 | 22 | 24 | 368 |  | low | 2020-09-14 | B20772¦H16 defendant¦¦Sep-18-2020 16:28
2020-09-18 16:32 | 44092.6886 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Basement corridor at exit door |  | 1 | 17.5 | 20.2 | 410 | 22 | 18.9 | 473 |  | 2020-09-18 16:32 | 44092.6886 | 22 | 18.9 | 473 |  | low | 2020-09-14 | B21554¦Basement corridor at exit door¦¦Sep-18-2020 16:31
2020-09-18 16:33 | 44092.6899 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Stairway landing |  | 1 | 17.5 | 20.2 | 410 | 22.2 | 18.9 | 484 |  | 2020-09-18 16:33 | 44092.6899 | 22.2 | 18.9 | 484 |  | low | 2020-09-14 | B21554¦Stairway landing¦¦Sep-18-2020 16:33
2020-09-18 16:35 | 44092.6912 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Legal aid corridor |  | 1 | 17.5 | 20.2 | 410 | 22.1 | 18.4 | 471 |  | 2020-09-18 16:35 | 44092.6912 | 22.1 | 18.4 | 471 |  | low | 2020-09-14 | B21554¦Legal aid corridor¦¦Sep-18-2020 16:35
2020-09-18 16:37 | 44092.6924 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Main waiting area |  | 1 | 17.5 | 20.2 | 410 | 21.7 | 19.1 | 493 |  | 2020-09-18 16:37 | 44092.6924 | 21.7 | 19.1 | 493 |  | low | 2020-09-14 | B21554¦Main waiting area¦¦Sep-18-2020 16:37
2020-09-18 16:39 | 44092.6936 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Police room 1 |  | 0 | 21.1 | 17.3 | 363 | 23.3 | 19.4 | 372 |  | 2020-09-18 16:39 | 44092.6936 | 23.3 | 19.4 | 372 |  | low | 2020-09-14 | Pearso¦Police room 1¦¦Sep-18-2020 16:38
2020-09-18 16:41 | 44092.6949 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Police room 2 |  | 0 | 21.1 | 17.3 | 363 | 23.1 | 20 | 375 |  | 2020-09-18 16:41 | 44092.6949 | 23.1 | 20 | 375 |  | low | 2020-09-14 | Pearso¦Police room 2¦¦Sep-18-2020 16:40
2020-09-18 16:42 | 44092.6957 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Front desk |  | 3 | 17.5 | 20.2 | 410 | 21.4 | 18.6 | 463 |  | 2020-09-18 16:42 | 44092.6957 | 21.4 | 18.6 | 463 |  | low | 2020-09-14 | B21554¦Front desk¦¦Sep-18-2020 16:41
2020-09-18 16:42 | 44092.6961 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Police room 3 |  | 0 | 21.1 | 17.3 | 363 | 23.1 | 19.7 | 372 |  | 2020-09-18 16:42 | 44092.6961 | 23.1 | 19.7 | 372 |  | low | 2020-09-14 | Pearso¦Police room 3¦¦Sep-18-2020 16:42
2020-09-18 16:44 | 44092.697 | AINSWORTH | B21554 | B21554 - 36 Wyndham St S - Guelph | Main office |  | 3 | 17.5 | 20.2 | 410 | 21.1 | 18.9 | 438 |  | 2020-09-18 16:44 | 44092.697 | 21.1 | 18.9 | 438 |  | low | 2020-09-14 | B21554¦Main office¦¦Sep-18-2020 16:43
2020-09-18 16:44 | 44092.6975 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Police room 4 |  | 0 | 21.1 | 17.3 | 363 | 23 | 20.1 | 373 |  | 2020-09-18 16:44 | 44092.6975 | 23 | 20.1 | 373 |  | low | 2020-09-14 | Pearso¦Police room 4¦¦Sep-18-2020 16:44
2020-09-18 16:45 | 44092.6981 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 1 |  | 0 | 21.1 | 17.3 | 363 | 23.6 | 18.4 | 376 |  | 2020-09-18 16:45 | 44092.6981 | 23.6 | 18.4 | 376 |  | low | 2020-09-14 | Pearso¦Lobby 1¦¦Sep-18-2020 16:45
2020-09-18 16:46 | 44092.699 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 2 |  | 0 | 21.1 | 17.3 | 363 | 23.2 | 19.5 | 375 |  | 2020-09-18 16:46 | 44092.699 | 23.2 | 19.5 | 375 |  | low | 2020-09-14 | Pearso¦Lobby 2¦¦Sep-18-2020 16:46
2020-09-18 16:47 | 44092.6996 | AINSWORTH | Pearso | Pearson Centre - 2638 Steeles Ave E | Lobby 3 |  | 0 | 21.1 | 17.3 | 363 | 22.4 | 20.3 | 376 |  | 2020-09-18 16:48 | 44092.6996 | 22.4 | 20.3 | 376 |  | low | 2020-09-14 | Pearso¦Lobby 3¦¦Sep-18-2020 16:47
2020-09-18 16:53 | 44092.7037 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H16 defendant |  | 1 | 25 | 14 | 356 | 22 | 24 | 368 |  | 2020-09-18 16:53 | 44092.7037 | 22 | 24 | 368 |  | low | 2020-09-14 | B20772¦H16 defendant¦¦Sep-18-2020 16:53
2020-09-18 18:41 | 44092.7788 | AINSWORTH | B25479 | B25479 - 44 Queen St - Brantford | Courtroom 3 |  | 3 | 16 | 33 | 411 | 23 | 29 | 601 |  | 2020-09-18 18:41 | 44092.7788 | 23 | 29 | 601 |  | low | 2020-09-14 | B25479¦Courtroom 3¦¦Sep-18-2020 18:41
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 57 | 542 | public area | 2020-09-17 15:00 | 15:00 | 21 | 57 | 542 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 57 | 535 | judge area | 2020-09-17 15:00 | 15:00 | 21 | 57 | 535 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 59 | 551 | outside of 503 | 2020-09-17 15:00 | 15:00 | 21 | 59 | 551 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 59 | 552 | public area | 2020-09-17 15:00 | 15:00 | 21 | 59 | 552 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 59 | 543 | judge area | 2020-09-17 15:00 | 15:00 | 21 | 59 | 543 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 21 | 60 | 559 | outside of 506 | 2020-09-17 15:00 | 15:00 | 21 | 60 | 559 |  | caution | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 60 | 563 | public area | 2020-09-17 15:00 | 15:00 | 20 | 60 | 563 |  | caution | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 60 | 545 | judge area | 2020-09-17 15:00 | 15:00 | 20 | 60 | 545 |  | caution | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 61 | 548 | outside of 509 | 2020-09-17 15:00 | 15:00 | 20 | 61 | 548 |  | caution | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 61 | 550 | public area | 2020-09-17 15:00 | 15:00 | 20 | 61 | 550 |  | caution | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 61 | 549 | judge area | 2020-09-17 15:00 | 15:00 | 20 | 61 | 549 |  | caution | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 61 | 551 | outside of 510 | 2020-09-17 15:00 | 15:00 | 20 | 61 | 551 |  | caution | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 61 | 566 | public area | 2020-09-17 15:00 | 15:00 | 20 | 61 | 566 |  | caution | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 61 | 577 | judge area | 2020-09-17 15:00 | 15:00 | 20 | 61 | 577 |  | caution | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Back of main hallway | [5 empty] | 20 | 61 | 559 |  | 2020-09-17 15:00 | 15:00 | 20 | 61 | 559 |  | caution | 2020-09-14 | B70003¦Back of main hallway¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | elevator area | [5 empty] | 20 | 61 | 565 |  | 2020-09-17 15:00 | 15:00 | 20 | 61 | 565 |  | caution | 2020-09-14 | B70003¦elevator area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Outdoors |  |  | 22 | 66 | 394 |  |  |  | outside of 444 Yonge St. | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70003¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Outdoors |  |  | 16 | 74 | [5 empty] | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20619¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Courtroom 1-14 | [5 empty] | 22 | 48 | 454 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 454 |  |  | 2020-09-14 | B20619¦Courtroom 1-14¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 101 | [5 empty] | 19 | 59 | 567 |  | 2020-09-17 09:00 | 9:00 | 19 | 59 | 567 |  |  | 2020-09-14 | B25671¦Courtroom 101¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 201 | [5 empty] | 19 | 59 | 483 |  | 2020-09-17 09:00 | 9:00 | 19 | 59 | 483 |  |  | 2020-09-14 | B25671¦Courtroom 201¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 301 | [5 empty] | 20 | 59 | 421 |  | 2020-09-17 09:00 | 9:00 | 20 | 59 | 421 |  |  | 2020-09-14 | B25671¦Courtroom 301¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 | [5 empty] | 20 | 58 | 416 |  | 2020-09-17 09:00 | 9:00 | 20 | 58 | 416 |  |  | 2020-09-14 | B14209¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 8 | [5 empty] | 22 | 53 | 416 |  | 2020-09-17 09:00 | 9:00 | 22 | 53 | 416 |  |  | 2020-09-14 | B25683¦Courtroom 8¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 11 | [5 empty] | 22 | 53 | 416 |  | 2020-09-17 09:00 | 9:00 | 22 | 53 | 416 |  |  | 2020-09-14 | B25683¦Courtroom 11¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 - waiting area | [5 empty] | 22 | 48 | 407 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 407 |  |  | 2020-09-14 | B14209¦Courtroom 1 - waiting area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 9 | [5 empty] | 23 | 50 | 421 |  | 2020-09-17 09:00 | 9:00 | 23 | 50 | 421 |  |  | 2020-09-14 | B25683¦Courtroom 9¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 | [5 empty] | 20 | 50 | 435 |  | 2020-09-17 09:00 | 9:00 | 20 | 50 | 435 |  |  | 2020-09-14 | B14209¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Outdoors |  |  | 9 | 73 | 407 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B12948¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 1 | [5 empty] | 19 | 49 | 401 |  | 2020-09-17 09:00 | 9:00 | 19 | 49 | 401 |  |  | 2020-09-14 | B12948¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 | [5 empty] | 20 | 46 | 402 |  | 2020-09-17 09:00 | 9:00 | 20 | 46 | 402 |  |  | 2020-09-14 | B12948¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 | [5 empty] | 20 | 43 | 412 |  | 2020-09-17 09:00 | 9:00 | 20 | 43 | 412 |  |  | 2020-09-14 | B12948¦Courtroom 3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 101 | [5 empty] | 20 | 55 | 494 |  | 2020-09-17 09:00 | 9:00 | 20 | 55 | 494 |  |  | 2020-09-14 | B19512¦Courtroom 101¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 | [5 empty] | 21 | 43 | 418 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 418 |  |  | 2020-09-14 | B12948¦Courtroom 4¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 200 | [5 empty] | 21 | 52 | 520 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 520 |  |  | 2020-09-14 | B19512¦Courtroom 200¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 201 | [5 empty] | 22 | 52 | 520 |  | 2020-09-17 09:00 | 9:00 | 22 | 52 | 520 |  |  | 2020-09-14 | B19512¦Courtroom 201¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 101 | [5 empty] | 21 | 51 |  |  | 2020-09-17 09:00 | 9:00 | 21 | 51 |  |  |  | 2020-09-14 | B20080¦Courtroom 101¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 | [5 empty] | 21 | 42 | 429 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 429 |  |  | 2020-09-14 | B12948¦Courtroom 5¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Outdoors |  |  | 12 | 86 | [5 empty] | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B19512¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 201 | [5 empty] | 22 | 46 | 421 |  | 2020-09-17 09:00 | 9:00 | 22 | 46 | 421 |  |  | 2020-09-14 | B20080¦Courtroom 201¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 6 | [5 empty] | 21 | 41 | 428 |  | 2020-09-17 09:00 | 9:00 | 21 | 41 | 428 |  |  | 2020-09-14 | B12948¦Courtroom 6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 202 | [5 empty] | 23 | 46 | 419 |  | 2020-09-17 09:00 | 9:00 | 23 | 46 | 419 |  |  | 2020-09-14 | B20080¦Courtroom 202¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Admin Office Waiting Area | [5 empty] | 21 | 43 | 417 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 417 |  |  | 2020-09-14 | B12948¦Admin Office Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration office | [5 empty] | 21 | 44 | 419 |  | 2020-09-17 09:00 | 9:00 | 21 | 44 | 419 |  |  | 2020-09-14 | B12948¦Administration office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 301 | [5 empty] | 23 | 46 | 411 |  | 2020-09-17 09:00 | 9:00 | 23 | 46 | 411 |  |  | 2020-09-14 | B20080¦Courtroom 301¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Crown attorney admin area | [5 empty] | 22 | 46 | 430 |  | 2020-09-17 09:00 | 9:00 | 22 | 46 | 430 |  |  | 2020-09-14 | B12948¦Crown attorney admin area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 - waiting room | [5 empty] | 23 | 44 | 556 |  | 2020-09-17 09:00 | 9:00 | 23 | 44 | 556 |  |  | 2020-09-14 | B14209¦Courtroom 2 - waiting room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Cell Basement | [5 empty] | 21 | 42 | 430 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 430 |  |  | 2020-09-14 | B12948¦Cell Basement¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room | [5 empty] | 21 | 49 | 407 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 407 |  |  | 2020-09-14 | B14209¦Hearing Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main entrance | [5 empty] | 21 | 43 | 419 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 419 |  |  | 2020-09-14 | B12948¦Main entrance¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 302 | [5 empty] | 22 | 46 | 417 |  | 2020-09-17 09:00 | 9:00 | 22 | 46 | 417 |  |  | 2020-09-14 | B20080¦Courtroom 302¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room, Judge’s Chamber | [5 empty] | 21 | 50 | 412 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 412 |  |  | 2020-09-14 | B14209¦Hearing Room, Judge’s Chamber¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main Entrance Waiting Area | [5 empty] | 21 | 44 | 422 |  | 2020-09-17 12:00 | 12:00 | 21 | 44 | 422 |  |  | 2020-09-14 | B12948¦Main Entrance Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 303 | [5 empty] | 22 | 46 | 485 |  | 2020-09-17 09:00 | 9:00 | 22 | 46 | 485 |  |  | 2020-09-14 | B20080¦Courtroom 303¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room - Waiting area | [5 empty] | 23 | 46 | 413 |  | 2020-09-17 09:00 | 9:00 | 23 | 46 | 413 |  |  | 2020-09-14 | B14209¦Hearing Room - Waiting area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Outdoors |  |  | 14 | 75 | 422 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20080¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Front desk | [5 empty] | 21 | 53 | 432 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 432 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Front desk¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Court Room 1 Waiting Area | [5 empty] | 21 | 43 | 427 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 427 |  |  | 2020-09-14 | B12948¦Court Room 1 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown attorney admin area | [5 empty] | 21 | 51 | 421 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 421 |  |  | 2020-09-14 | B14209¦Crown attorney admin area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 Waiting Area | [5 empty] | 21 | 42 | 412 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 412 |  |  | 2020-09-14 | B12948¦Courtroom 2 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Print Room | [5 empty] | 21 | 53 | 405 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 405 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Print Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Assistant Crown Attorney Office (236) | [5 empty] | 21 | 55 | 403 |  | 2020-09-17 09:00 | 9:00 | 21 | 55 | 403 |  |  | 2020-09-14 | B14209¦Assistant Crown Attorney Office (236)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office | [5 empty] | 21 | 54 | 411 |  | 2020-09-17 09:00 | 9:00 | 21 | 54 | 411 |  |  | 2020-09-14 | B14209¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 Waiting Area | [5 empty] | 22 | 41 | 431 |  | 2020-09-17 09:00 | 9:00 | 22 | 41 | 431 |  |  | 2020-09-14 | B12948¦Courtroom 3 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Meeting Room (232) | [5 empty] | 21 | 55 | 403 |  | 2020-09-17 09:00 | 9:00 | 21 | 55 | 403 |  |  | 2020-09-14 | B14209¦Crown Attorney Meeting Room (232)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 Waiting Area | [5 empty] | 22 | 41 | 419 |  | 2020-09-17 09:00 | 9:00 | 22 | 41 | 419 |  |  | 2020-09-14 | B12948¦Courtroom 5 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 and 6 Waiting Area | [5 empty] | 22 | 41 | 421 |  | 2020-09-17 09:00 | 9:00 | 22 | 41 | 421 |  |  | 2020-09-14 | B12948¦Courtroom 4 and 6 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Lobby | [5 empty] | 23 | 51 | 426 |  | 2020-09-17 09:00 | 9:00 | 23 | 51 | 426 |  |  | 2020-09-14 | B14209¦Court Admin Office Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Cubicles | [5 empty] | 22 | 53 | 407 |  | 2020-09-17 09:00 | 9:00 | 22 | 53 | 407 |  |  | 2020-09-14 | B14209¦Court Admin Office Cubicles¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Holding Cell corridor | [5 empty] | 22 | 48 | 403 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 403 |  |  | 2020-09-14 | B14209¦Holding Cell corridor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Police Control Room | [5 empty] | 22 | 50 | 407 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 407 |  |  | 2020-09-14 | B14209¦Police Control Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Intake Court | [5 empty] | 23 | 53 | 418 |  | 2020-09-17 09:00 | 9:00 | 23 | 53 | 418 |  |  | 2020-09-14 | B14209¦Intake Court¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Law Library Meeting Room (028B) | [5 empty] | 22 | 51 | 498 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 498 |  |  | 2020-09-14 | B14209¦Law Library Meeting Room (028B)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Library | [5 empty] | 22 | 51 | 406 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 406 |  |  | 2020-09-14 | B14209¦Library¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Lunch Room | [5 empty] | 22 | 54 | 415 |  | 2020-09-17 09:00 | 9:00 | 22 | 54 | 415 |  |  | 2020-09-14 | B14209¦Lunch Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Entry/Waiting | [5 empty] | 22 | 51 | 464 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 464 |  |  | 2020-09-14 | B70510¦Entry/Waiting¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Entrance by Stair G | [5 empty] | 23 | 44 | 468 |  | 2020-09-17 09:00 | 9:00 | 23 | 44 | 468 |  |  | 2020-09-14 | B14209¦Entrance by Stair G¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room A | [5 empty] | 22 | 50 | 464 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 464 |  |  | 2020-09-14 | B70510¦Mediation Room A¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Main Floor Entrance Lobby | [5 empty] | 23 | 50 | 414 |  | 2020-09-17 09:00 | 9:00 | 23 | 50 | 414 |  |  | 2020-09-14 | B14209¦Main Floor Entrance Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Information Desk | [5 empty] | 22 | 50 | 454 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 454 |  |  | 2020-09-14 | B70510¦Information Desk¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd fl lobby | [5 empty] | 20 | 47 | 571 |  | 2020-09-17 09:00 | 9:00 | 20 | 47 | 571 |  |  | 2020-09-14 | B20226¦2nd fl lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Level 1 Corridor by room 103 | [5 empty] | 22 | 45 | 552 |  | 2020-09-17 09:00 | 9:00 | 22 | 45 | 552 |  |  | 2020-09-14 | B14209¦Level 1 Corridor by room 103¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Lunch Room 454 | [5 empty] | 22 | 50 | 448 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 448 |  |  | 2020-09-14 | B70510¦Lunch Room 454¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Outdoors |  |  | 18 | 62 | 341 |  |  |  | Base Readings | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B25165¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Outdoors |  |  | 10 | 60 | 400 |  |  |  | Morning dew and sunny, cold | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B14209¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Copy Room 455 | [5 empty] | 22 | 50 | 447 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 447 |  |  | 2020-09-14 | B70510¦Copy Room 455¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 2 | [5 empty] | 20 | 49 | 595 |  | 2020-09-17 09:00 | 9:00 | 20 | 49 | 595 |  |  | 2020-09-14 | B20226¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room B | [5 empty] | 22 | 50 | 447 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 447 |  |  | 2020-09-14 | B70510¦Mediation Room B¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | OTHER | [5 empty] | 21 | 51 | 503 | Courtroom 700, Please add to drop down box ,thank you | 2020-09-17 09:00 | 9:00 | 21 | 51 | 503 |  |  | 2020-09-14 | B25165¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 600 | [5 empty] | 22 | 51 | 436 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 436 |  |  | 2020-09-14 | B25165¦Courtroom 600¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Outdoors |  |  | 18 | 46 | 386 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B19652¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Center) | [5 empty] | 22 | 48 | 459 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 459 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Center)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 459 | [5 empty] | 22 | 50 | 454 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 454 |  |  | 2020-09-14 | B70510¦Office 459¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Judge Dias) | [5 empty] | 22 | 48 | 436 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 436 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Judge Dias)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 2 | [5 empty] | 21 | 51 | 647 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 647 |  |  | 2020-09-14 | B20226¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 308 | [5 empty] | 22 | 51 | 445 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 445 |  |  | 2020-09-14 | B25165¦Courtroom 308¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 48 | 435 | Superior judges chamber | 2020-09-17 09:00 | 9:00 | 21 | 48 | 435 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | office 467 | [5 empty] | 22 | 50 | 470 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 470 |  |  | 2020-09-14 | B70510¦office 467¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 306 | [5 empty] | 22 | 51 | 445 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 445 |  |  | 2020-09-14 | B25165¦Courtroom 306¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 49 | 452 | 3rd floor stair landing | 2020-09-17 09:00 | 9:00 | 21 | 49 | 452 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 469 | [5 empty] | 22 | 50 | 468 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 468 |  |  | 2020-09-14 | B70510¦Office 469¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 22 | 50 | 532 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 532 |  |  | 2020-09-14 | B20226¦2nd Floor Holding Cell¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 302 | [5 empty] | 21 | 51 | 443 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 443 |  |  | 2020-09-14 | B25165¦Courtroom 302¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 49 | 451 | 3rd floor Jury room | 2020-09-17 09:00 | 9:00 | 21 | 49 | 451 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 208 | [5 empty] | 21 | 51 | 439 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 439 |  |  | 2020-09-14 | B25165¦Courtroom 208¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Room 473 | [5 empty] | 22 | 50 | 458 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 458 |  |  | 2020-09-14 | B70510¦Room 473¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 49 | 449 | Justice McDonald chamber | 2020-09-17 09:00 | 9:00 | 21 | 49 | 449 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 3 | [5 empty] | 22 | 41 | 444 |  | 2020-09-17 09:00 | 9:00 | 22 | 41 | 444 |  |  | 2020-09-14 | B20226¦Courtroom 3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 206 | [5 empty] | 21 | 51 | 443 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 443 |  |  | 2020-09-14 | B25165¦Courtroom 206¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 49 | 439 | Justice McDonald secretary | 2020-09-17 09:00 | 9:00 | 21 | 49 | 439 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hall 475 or 466 | [5 empty] | 21 | 51 | 488 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 488 |  |  | 2020-09-14 | B70510¦Hall 475 or 466¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 204 | [5 empty] | 22 | 51 | 492 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 492 |  |  | 2020-09-14 | B25165¦Courtroom 204¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 49 | 427 | SCJTC office | 2020-09-17 09:00 | 9:00 | 21 | 49 | 427 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 1 | [5 empty] | 22 | 50 | 454 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 454 |  |  | 2020-09-14 | B70510¦Hearing Room 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 202 | [5 empty] | 21 | 51 | 443 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 443 |  |  | 2020-09-14 | B25165¦Courtroom 202¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 49 | 435 | Visiting justice chamber | 2020-09-17 09:00 | 9:00 | 21 | 49 | 435 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Meeting Rooms 1/2 | [5 empty] | 22 | 51 | 455 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 455 |  |  | 2020-09-14 | B70510¦Vestibule at Meeting Rooms 1/2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 200 | [5 empty] | 21 | 51 | 460 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 460 |  |  | 2020-09-14 | B25165¦Courtroom 200¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Center) | [5 empty] | 21 | 49 | 431 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 431 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Center)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Hearing Room 1 | [5 empty] | 22 | 51 | 462 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 462 |  |  | 2020-09-14 | B70510¦Vestibule at Hearing Room 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 100 | [5 empty] | 22 | 51 | 450 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 450 |  |  | 2020-09-14 | B25165¦Courtroom 100¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Judge Dias) | [5 empty] | 21 | 49 | 438 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 438 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Judge Dias)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Main Lobby | [5 empty] | 20 | 53 | 556 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 556 |  |  | 2020-09-14 | B70050¦Main Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 Waiting Area | [5 empty] | 21 | 50 | 440 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 440 |  |  | 2020-09-14 | B19652¦Courtroom 2 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 2 | [5 empty] | 22 | 51 | 505 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 505 |  |  | 2020-09-14 | B70510¦Hearing Room 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Center) | [5 empty] | 22 | 45 | 438 |  | 2020-09-17 09:00 | 9:00 | 22 | 45 | 438 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Center)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 439 | [5 empty] | 22 | 51 | 457 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 457 |  |  | 2020-09-14 | B70510¦Office 439¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Judge Dias) | [5 empty] | 22 | 44 | 456 |  | 2020-09-17 09:00 | 9:00 | 22 | 44 | 456 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Judge Dias)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 1 | [5 empty] | 20 | 54 | 428 |  | 2020-09-17 09:00 | 9:00 | 20 | 54 | 428 |  |  | 2020-09-14 | B70050¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 46 | 440 | Justice peace chamber | 2020-09-17 09:00 | 9:00 | 22 | 46 | 440 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | First Aid Desk | [5 empty] | 22 | 51 | 453 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 453 |  |  | 2020-09-14 | B70510¦First Aid Desk¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 45 | 435 | Council chamber dias | 2020-09-17 09:00 | 9:00 | 22 | 45 | 435 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 436 | [5 empty] | 22 | 51 | 454 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 454 |  |  | 2020-09-14 | B70510¦Office 436¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 20 | 55 | 428 |  | 2020-09-17 09:00 | 9:00 | 20 | 55 | 428 |  |  | 2020-09-14 | B70050¦2nd Floor Holding Cell¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 45 | 426 | Council chamber center | 2020-09-17 09:00 | 9:00 | 22 | 45 | 426 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 2nd Floor Lunchroom | [5 empty] | 22 | 48 | 477 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 477 |  |  | 2020-09-14 | B19652¦2nd Floor Lunchroom¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 432 | [5 empty] | 22 | 51 | 458 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 458 |  |  | 2020-09-14 | B70510¦Office 432¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 49 | 487 | 2nd floor stair landing | 2020-09-17 09:00 | 9:00 | 22 | 49 | 487 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 429 | [5 empty] | 22 | 51 | 456 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 456 |  |  | 2020-09-14 | B70510¦Office 429¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 49 | 478 | Court service kitchenette | 2020-09-17 09:00 | 9:00 | 22 | 49 | 478 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Yannick Bedard Office - 2nd Floor | [5 empty] | 22 | 55 | 472 |  | 2020-09-17 09:00 | 9:00 | 22 | 55 | 472 |  |  | 2020-09-14 | B70050¦Yannick Bedard Office - 2nd Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 427 | [5 empty] | 22 | 51 | 459 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 459 |  |  | 2020-09-14 | B70510¦Office 427¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 20 | 57 | 701 | Court service north | 2020-09-17 09:00 | 9:00 | 20 | 57 | 701 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mail Room | [5 empty] | 22 | 51 | 459 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 459 |  |  | 2020-09-14 | B70510¦Mail Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 2 | [5 empty] | 22 | 55 | 442 |  | 2020-09-17 09:00 | 9:00 | 22 | 55 | 442 |  |  | 2020-09-14 | B70050¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 420 | [5 empty] | 22 | 51 | 457 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 457 |  |  | 2020-09-14 | B70510¦Office 420¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 55 | 681 | Court service south | 2020-09-17 09:00 | 9:00 | 21 | 55 | 681 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-1 | [5 empty] | 20.9 | 53 | 710 |  | 2020-09-17 09:00 | 9:00 | 20.9 | 53 | 710 |  |  | 2020-09-14 | B10644¦Courtroom 2-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 54 | 671 | Court service entrance vestibule | 2020-09-17 09:00 | 9:00 | 21 | 54 | 671 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd fl lobby | [5 empty] | 20 | 55 | 423 |  | 2020-09-17 09:00 | 9:00 | 20 | 55 | 423 |  |  | 2020-09-14 | B70050¦2nd fl lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 418 | [5 empty] | 22 | 51 | 462 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 462 |  |  | 2020-09-14 | B70510¦Office 418¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 50 | 595 | 1st floor stair landing | 2020-09-17 09:00 | 9:00 | 22 | 50 | 595 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-2 | [5 empty] | 19.7 | 58.7 | 567 |  | 2020-09-17 09:00 | 9:00 | 19.7 | 58.7 | 567 |  |  | 2020-09-14 | B10644¦Courtroom 2-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Outdoors |  |  | 17 | 60 | 487 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20289¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | File Room | [5 empty] | 22 | 51 | 458 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 458 |  |  | 2020-09-14 | B70510¦File Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Outdoors |  |  | 12 | 72 | 429 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B90838¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 21 | 52 | 494 | judge | 2020-09-17 09:00 | 9:00 | 21 | 52 | 494 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Health Room | [5 empty] | 22 | 51 | 471 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 471 |  |  | 2020-09-14 | B70510¦Health Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Courtroom 101 Courtroom 102 | [5 empty] | 22 | 50 | 443 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 443 |  |  | 2020-09-14 | B90838¦Courtroom 101 Courtroom 102¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-3 | [5 empty] | 20.5 | 63 | 437 |  | 2020-09-17 09:00 | 9:00 | 20.5 | 63 | 437 |  | caution | 2020-09-14 | B10644¦Courtroom 2-3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 21 | 52 | 500 | public | 2020-09-17 09:00 | 9:00 | 21 | 52 | 500 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 | [5 empty] | 21 | 51 | 464 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 464 |  |  | 2020-09-14 | B70510¦Hearing Room 3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 22 | 51 | 502 | judge | 2020-09-17 09:00 | 9:00 | 22 | 51 | 502 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 22 | 51 | 501 | public | 2020-09-17 09:00 | 9:00 | 22 | 51 | 501 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 Waiting Area | [5 empty] | 22 | 52 | 452 |  | 2020-09-17 09:00 | 9:00 | 22 | 52 | 452 |  |  | 2020-09-14 | B70510¦Hearing Room 3 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-4 | [5 empty] | 23 | 46.9 | 545 |  | 2020-09-17 09:00 | 9:00 | 23 | 46.9 | 545 |  |  | 2020-09-14 | B10644¦Courtroom 2-4¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Outdoors |  |  | 6 | 57 | 402 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70050¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 300 | [5 empty] | 23 | 50 | 542 |  | 2020-09-17 09:00 | 9:00 | 23 | 50 | 542 |  |  | 2020-09-14 | B20289¦Courtroom 300¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 301 | [5 empty] | 23 | 49 | 548 |  | 2020-09-17 09:00 | 9:00 | 23 | 49 | 548 |  |  | 2020-09-14 | B20289¦Courtroom 301¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Elevator Lobby | [5 empty] | 22 | 53 | 452 |  | 2020-09-17 09:00 | 9:00 | 22 | 53 | 452 |  |  | 2020-09-14 | B70510¦Elevator Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 302 | [5 empty] | 23 | 50 | 539 |  | 2020-09-17 09:00 | 9:00 | 23 | 50 | 539 |  |  | 2020-09-14 | B20289¦Courtroom 302¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 303 | [5 empty] | 23 | 49 | 541 |  | 2020-09-17 09:00 | 9:00 | 23 | 49 | 541 |  |  | 2020-09-14 | B20289¦Courtroom 303¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Outdoors |  |  | 15 | 63 | 453 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70510¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom A | [5 empty] | 22 | 50 | 560 | in session; measurement taken outside courtroom | 2020-09-17 09:00 | 9:00 | 22 | 50 | 560 |  |  | 2020-09-14 | B20289¦Courtroom A¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-6 | [5 empty] | 23.2 | 56 | 431 |  | 2020-09-17 09:00 | 9:00 | 23.2 | 56 | 431 |  |  | 2020-09-14 | B10644¦Courtroom 2-6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom B | [5 empty] | 22 | 49 | 572 |  | 2020-09-17 09:00 | 9:00 | 22 | 49 | 572 |  |  | 2020-09-14 | B20289¦Courtroom B¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 100 Courtroom 102 Courtroom 104 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203 Courtroom 403 | [5 empty] | 21 | 49 | 460 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 460 |  |  | 2020-09-14 | B20616¦Courtroom 100 Courtroom 102 Courtroom 104 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203 Courtroom 403¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Outdoors |  |  | 5 | 51 | 388 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20226¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom C (North) | [5 empty] | 22 | 49 | 581 |  | 2020-09-17 09:00 | 9:00 | 22 | 49 | 581 |  |  | 2020-09-14 | B20289¦Courtroom C (North)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom D | [5 empty] | 23 | 51 | 570 | in session; measurement taken outside courtroom | 2020-09-17 09:00 | 9:00 | 23 | 51 | 570 |  |  | 2020-09-14 | B20289¦Courtroom D¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 1 | [5 empty] | 22 | 44 | 489 |  | 2020-09-17 09:00 | 9:00 | 22 | 44 | 489 |  |  | 2020-09-14 | B25602¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom E | [5 empty] | 23 | 53 | 591 | in session; measurement taken outside courtroom | 2020-09-17 09:00 | 9:00 | 23 | 53 | 591 |  |  | 2020-09-14 | B20289¦Courtroom E¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 101 Courtroom 103 Courtroom 105 Courtroom 401 Courtroom 402 | [5 empty] | 22 | 49 | 460 |  | 2020-09-17 09:00 | 9:00 | 22 | 49 | 460 |  |  | 2020-09-14 | B20616¦Courtroom 101 Courtroom 103 Courtroom 105 Courtroom 401 Courtroom 402¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom F | [5 empty] | 22 | 55 | 577 | in session; measurement taken outside courtroom | 2020-09-17 09:00 | 9:00 | 22 | 55 | 577 |  |  | 2020-09-14 | B20289¦Courtroom F¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 2 | [5 empty] | 22 | 45 | 481 |  | 2020-09-17 09:00 | 9:00 | 22 | 45 | 481 |  |  | 2020-09-14 | B25602¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 106 | [5 empty] | 20 | 52 | 459 |  | 2020-09-17 09:00 | 9:00 | 20 | 52 | 459 |  |  | 2020-09-14 | B20616¦Courtroom 106¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 3 | [5 empty] | 22 | 42 | 505 |  | 2020-09-17 09:00 | 9:00 | 22 | 42 | 505 |  |  | 2020-09-14 | B25602¦Courtroom 3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 4 | [5 empty] | 23 | 42 | 482 |  | 2020-09-17 09:00 | 9:00 | 23 | 42 | 482 |  |  | 2020-09-14 | B25602¦Courtroom 4¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 204 Courtroom 205 Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 405 | [5 empty] | 21 | 52 | 459 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 459 |  |  | 2020-09-14 | B20616¦Courtroom 204 Courtroom 205 Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 405¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-8 | [5 empty] | 21.5 | 53.1 | 661 |  | 2020-09-17 09:00 | 9:00 | 21.5 | 53.1 | 661 |  |  | 2020-09-14 | B10644¦Courtroom 2-8¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 5 | [5 empty] | 23 | 42 | 443 |  | 2020-09-17 09:00 | 9:00 | 23 | 42 | 443 |  |  | 2020-09-14 | B25602¦Courtroom 5¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 404 | [5 empty] | 22 | 52 | 459 |  | 2020-09-17 09:00 | 9:00 | 22 | 52 | 459 |  |  | 2020-09-14 | B20616¦Courtroom 404¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 6 | [5 empty] | 23 | 44 | 505 |  | 2020-09-17 09:00 | 9:00 | 23 | 44 | 505 |  |  | 2020-09-14 | B25602¦Courtroom 6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 3-2 | [5 empty] | 22.1 | 56.4 | 450 |  | 2020-09-17 09:00 | 9:00 | 22.1 | 56.4 | 450 |  |  | 2020-09-14 | B10644¦Courtroom 3-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 7 | [5 empty] | 23 | 42 | 496 |  | 2020-09-17 09:00 | 9:00 | 23 | 42 | 496 |  |  | 2020-09-14 | B25602¦Courtroom 7¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 107 Courtroom 108 | [5 empty] | 21 | 59 | 455 |  | 2020-09-17 09:00 | 9:00 | 21 | 59 | 455 |  |  | 2020-09-14 | B20616¦Courtroom 107 Courtroom 108¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 304 Courtroom 305 | [5 empty] | 22 | 52 | 567 |  | 2020-09-17 09:00 | 9:00 | 22 | 52 | 567 |  |  | 2020-09-14 | B20616¦Courtroom 304 Courtroom 305¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-1 | [5 empty] | 22.7 | 58.3 | 506 |  | 2020-09-17 09:00 | 9:00 | 22.7 | 58.3 | 506 |  |  | 2020-09-14 | B10644¦Courtroom 4-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-2 | [5 empty] | 20.9 | 56.5 | 433 |  | 2020-09-17 09:00 | 9:00 | 20.9 | 56.5 | 433 |  |  | 2020-09-14 | B10644¦Courtroom 4-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Outdoors |  |  | 14 | 63 | 687 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B25602¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-2 | [5 empty] | 20.9 | 56.5 | 433 |  | 2020-09-17 09:00 | 9:00 | 20.9 | 56.5 | 433 |  |  | 2020-09-14 | B10644¦Courtroom 4-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-3 | [5 empty] | 23.5 | 56.1 | 405 |  | 2020-09-17 09:00 | 9:00 | 23.5 | 56.1 | 405 |  |  | 2020-09-14 | B10644¦Courtroom 4-3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-4 | [5 empty] | 22.3 | 48.4 | 522 |  | 2020-09-17 09:00 | 9:00 | 22.3 | 48.4 | 522 |  |  | 2020-09-14 | B10644¦Courtroom 4-4¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | front seating area | [5 empty] | 21 | 57 | 411 |  | 2020-09-17 09:00 | 9:00 | 21 | 57 | 411 |  |  | 2020-09-14 | B18359¦front seating area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | northwest corridor | [5 empty] | 21 | 56 | 407 |  | 2020-09-17 09:00 | 9:00 | 21 | 56 | 407 |  |  | 2020-09-14 | B18359¦northwest corridor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-6 | [5 empty] | 22.6 | 49 | 433 |  | 2020-09-17 09:00 | 9:00 | 22.6 | 49 | 433 |  |  | 2020-09-14 | B10644¦Courtroom 4-6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 21 | 56 | 410 | north side | 2020-09-17 09:00 | 9:00 | 21 | 56 | 410 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 21 | 56 | 404 | south side | 2020-09-17 09:00 | 9:00 | 21 | 56 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-7 | [5 empty] | 22 | 43.5 | 404 |  | 2020-09-17 09:00 | 9:00 | 22 | 43.5 | 404 |  |  | 2020-09-14 | B10644¦Courtroom 4-7¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 21 | 55 | 409 | north side | 2020-09-17 09:00 | 9:00 | 21 | 55 | 409 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 21 | 55 | 405 | south side | 2020-09-17 09:00 | 9:00 | 21 | 55 | 405 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 21 | 55 | 404 | north side | 2020-09-17 09:00 | 9:00 | 21 | 55 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-8 | [5 empty] | 23.1 | 54.4 | 409 |  | 2020-09-17 09:00 | 9:00 | 23.1 | 54.4 | 409 |  |  | 2020-09-14 | B10644¦Courtroom 4-8¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 21 | 55 | 408 | south side | 2020-09-17 09:00 | 9:00 | 21 | 55 | 408 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 55 | 411 | north side | 2020-09-17 09:00 | 9:00 | 21 | 55 | 411 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22.6 | 54 | 516 |  | 2020-09-17 09:00 | 9:00 | 22.6 | 54 | 516 |  |  | 2020-09-14 | B10644¦Courtroom 5-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 55 | 405 | south side | 2020-09-17 09:00 | 9:00 | 21 | 55 | 405 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 54 | 404 | north side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-1 | [5 empty] | 17.5 | 55.1 | 407 |  | 2020-09-17 09:00 | 9:00 | 17.5 | 55.1 | 407 |  |  | 2020-09-14 | B10644¦Courtroom 6-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 54 | 397 | south side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 397 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 101 | [5 empty] | 21 | 53 | 506 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 506 |  |  | 2020-09-14 | B19512¦Courtroom 101¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 21 | 54 | 399 | north side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 399 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 200 | [5 empty] | 21 | 53 | 528 |  | 2020-09-17 12:00 | 12:00 | 21 | 53 | 528 |  |  | 2020-09-14 | B19512¦Courtroom 200¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 21 | 54 | 404 | south side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 21 | 54 | 404 | north side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 21 | 54 | 408 | south side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 408 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 21 | 55 | 415 | north side | 2020-09-17 09:00 | 9:00 | 21 | 55 | 415 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 201 | [5 empty] | 23 | 53 | 528 |  | 2020-09-17 12:00 | 12:00 | 23 | 53 | 528 |  |  | 2020-09-14 | B19512¦Courtroom 201¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 21 | 54 | 408 | south side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 408 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Outdoors |  |  | 15 | 75 | [5 empty] | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B19512¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 21 | 54 | 403 | north side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 403 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 22 | 54 | 407 | south side | 2020-09-17 09:00 | 9:00 | 22 | 54 | 407 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | northeast courtroom | [5 empty] | 22 | 54 | 411 |  | 2020-09-17 09:00 | 9:00 | 22 | 54 | 411 |  |  | 2020-09-14 | B18359¦northeast courtroom¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 22 | 53 | 398 | north side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 398 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 22 | 53 | 404 | south side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 22 | 53 | 402 | north side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 402 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Main entrance | [5 empty] | 21 | 58 | 472 |  | 2020-09-17 09:00 | 9:00 | 21 | 58 | 472 |  |  | 2020-09-14 | B90636¦Main entrance¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 22 | 53 | 400 | south side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 400 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 21 | 52 | 435 | north | 2020-09-17 09:00 | 9:00 | 21 | 52 | 435 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 22 | 53 | 399 | north side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 399 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 21 | 52 | 436 | south | 2020-09-17 09:00 | 9:00 | 21 | 52 | 436 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 22 | 53 | 405 | south side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 405 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 21 | 48 | 464 | vestibule | 2020-09-17 09:00 | 9:00 | 21 | 48 | 464 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtrooom 213 | [5 empty] | 22 | 53 | 402 | north side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 402 |  |  | 2020-09-14 | B18359¦courtrooom 213¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 21 | 47 | 462 | door entrance | 2020-09-17 09:00 | 9:00 | 21 | 47 | 462 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 22 | 53 | 402 | south side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 402 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | hallway by courtroom 203 | [5 empty] | 21 | 52 | 464 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 464 |  |  | 2020-09-14 | B90636¦hallway by courtroom 203¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 22 | 53 | 402 | north side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 402 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 2nd fl lobby | [5 empty] | 21 | 51 | 440 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 440 |  |  | 2020-09-14 | B90636¦2nd fl lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courrtoom 214 | [5 empty] | 22 | 53 | 401 | south side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 401 |  |  | 2020-09-14 | B18359¦courrtoom 214¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office North | [5 empty] | 23 | 34 | 556 |  | 2020-09-17 09:00 | 9:00 | 23 | 34 | 556 |  | low | 2020-09-14 | B14895¦Administration Office North¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | coutroom 215 | [5 empty] | 22 | 53 | 400 | north side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 400 |  |  | 2020-09-14 | B18359¦coutroom 215¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 3rd Floor Elevator Lobby | [5 empty] | 21 | 51 | 443 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 443 |  |  | 2020-09-14 | B90636¦3rd Floor Elevator Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office South | [5 empty] | 24 | 37 | 600 |  | 2020-09-17 09:00 | 9:00 | 24 | 37 | 600 |  | caution | 2020-09-14 | B14895¦Administration Office South¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 22 | 53 | 410 | south side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 410 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 21 | 51 | 432 | west | 2020-09-17 09:00 | 9:00 | 21 | 51 | 432 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main entrance | [5 empty] | 21 | 36 | 475 |  | 2020-09-17 09:00 | 9:00 | 21 | 36 | 475 |  | caution | 2020-09-14 | B14895¦Main entrance¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Outdoors |  |  | 16 | 67 | 394 |  |  |  | outside of 15 Grosvenor Ave. | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B18359¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 21 | 51 | 433 | east | 2020-09-17 09:00 | 9:00 | 21 | 51 | 433 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main Floor Waiting Area | [5 empty] | 22 | 34 | 451 |  | 2020-09-17 09:00 | 9:00 | 22 | 34 | 451 |  | low | 2020-09-14 | B14895¦Main Floor Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 4th floor waiting area | [5 empty] | 21 | 52 | 437 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 437 |  |  | 2020-09-14 | B90636¦4th floor waiting area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom A | [5 empty] | 22 | 36 | 427 |  | 2020-09-17 09:00 | 9:00 | 22 | 36 | 427 |  | caution | 2020-09-14 | B14895¦Courtroom A¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 210 | [5 empty] | 21 | 54 | 423 | west | 2020-09-17 09:00 | 9:00 | 21 | 54 | 423 |  |  | 2020-09-14 | B90636¦Courtroom 210¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 210 | [5 empty] | 20 | 55 | 421 | east | 2020-09-17 09:00 | 9:00 | 20 | 55 | 421 |  |  | 2020-09-14 | B90636¦Courtroom 210¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom B | [5 empty] | 21 | 38 | 430 |  | 2020-09-17 09:00 | 9:00 | 21 | 38 | 430 |  | caution | 2020-09-14 | B14895¦Courtroom B¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | courtroom 211 | [5 empty] | 20 | 54 | 422 | west | 2020-09-17 09:00 | 9:00 | 20 | 54 | 422 |  |  | 2020-09-14 | B90636¦courtroom 211¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | 2nd Floor Waiting Area | [5 empty] | 23 | 32 | 501 |  | 2020-09-17 09:00 | 9:00 | 23 | 32 | 501 |  | low | 2020-09-14 | B14895¦2nd Floor Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | courtroom 211 | [5 empty] | 21 | 54 | 417 | east | 2020-09-17 09:00 | 9:00 | 21 | 54 | 417 |  |  | 2020-09-14 | B90636¦courtroom 211¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Crown Attorney Office | [5 empty] | 23 | 34 | 423 |  | 2020-09-17 09:00 | 9:00 | 23 | 34 | 423 |  | low | 2020-09-14 | B14895¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | hallway by courtroom 210 | [5 empty] | 20 | 54 | 426 |  | 2020-09-17 09:00 | 9:00 | 20 | 54 | 426 |  |  | 2020-09-14 | B90636¦hallway by courtroom 210¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Waiting Area | [5 empty] | 23 | 34 | 521 |  | 2020-09-17 09:00 | 9:00 | 23 | 34 | 521 |  | low | 2020-09-14 | B14895¦Basement Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | outside | [5 empty] | 17 | 61 | 427 |  | 2020-09-17 09:00 | 9:00 | 17 | 61 | 427 |  | caution | 2020-09-14 | B90636¦outside¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | reception area | [5 empty] | 20 | 57 | 475 |  | 2020-09-17 09:00 | 9:00 | 20 | 57 | 475 |  |  | 2020-09-14 | B70003¦reception area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Boardroom | [5 empty] | 24 | 35 | 450 |  | 2020-09-17 09:00 | 9:00 | 24 | 35 | 450 |  | caution | 2020-09-14 | B14895¦Basement Boardroom¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Main entrance | [5 empty] | 20 | 51 | 450 |  | 2020-09-17 09:00 | 9:00 | 20 | 51 | 450 |  |  | 2020-09-14 | B20979¦Main entrance¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Male Holding Cell | [5 empty] | 24 | 31 | 419 |  | 2020-09-17 09:00 | 9:00 | 24 | 31 | 419 |  | low | 2020-09-14 | B14895¦Male Holding Cell¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 21 | 51 | 452 | north | 2020-09-17 09:00 | 9:00 | 21 | 51 | 452 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Female Holding Cell | [5 empty] | 24 | 32 | 491 |  | 2020-09-17 09:00 | 9:00 | 24 | 32 | 491 |  | low | 2020-09-14 | B14895¦Female Holding Cell¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Outdoors |  |  | 19 | 58 | 341 |  |  |  | Base Readings | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B25165¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 22 | 44 | 447 | south | 2020-09-17 09:00 | 9:00 | 22 | 44 | 447 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Outdoors |  |  | 14 | 19 | 393 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B14895¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | front of main hallway | [5 empty] | 20 | 57 | 460 |  | 2020-09-17 09:00 | 9:00 | 20 | 57 | 460 |  |  | 2020-09-14 | B70003¦front of main hallway¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 21 | 44 | 486 | south | 2020-09-17 09:00 | 9:00 | 21 | 44 | 486 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 20 | 57 | 461 | outside of 502 | 2020-09-17 09:00 | 9:00 | 20 | 57 | 461 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | OTHER | [5 empty] | 21 | 51 | 717 | Courtroom 700, Please add to drop down box thank you | 2020-09-17 12:00 | 12:00 | 21 | 51 | 717 |  |  | 2020-09-14 | B25165¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 22 | 45 | 454 | north | 2020-09-17 09:00 | 9:00 | 22 | 45 | 454 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 20 | 57 | 462 | public area | 2020-09-17 09:00 | 9:00 | 20 | 57 | 462 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 600 | [5 empty] | 22 | 51 | 436 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 436 |  |  | 2020-09-14 | B25165¦Courtroom 600¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 20 | 57 | 456 | judge area | 2020-09-17 09:00 | 9:00 | 20 | 57 | 456 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | courtroom 307 | [5 empty] | 21 | 46 | 444 | south | 2020-09-17 09:00 | 9:00 | 21 | 46 | 444 |  |  | 2020-09-14 | B20979¦courtroom 307¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 308 | [5 empty] | 22 | 51 | 524 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 524 |  |  | 2020-09-14 | B25165¦Courtroom 308¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 57 | 471 | outside of 503 | 2020-09-17 09:00 | 9:00 | 20 | 57 | 471 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | courtroom 307 | [5 empty] | 22 | 46 | 449 | north | 2020-09-17 09:00 | 9:00 | 22 | 46 | 449 |  |  | 2020-09-14 | B20979¦courtroom 307¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 57 | 459 | public area | 2020-09-17 09:00 | 9:00 | 20 | 57 | 459 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 56 | 460 | judge area | 2020-09-17 09:00 | 9:00 | 20 | 56 | 460 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | hallway by courtroom 307 | [5 empty] | 21 | 45 | 452 |  | 2020-09-17 09:00 | 9:00 | 21 | 45 | 452 |  |  | 2020-09-14 | B20979¦hallway by courtroom 307¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 56 | 468 | outside of 506 | 2020-09-17 09:00 | 9:00 | 20 | 56 | 468 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 306 | [5 empty] | 22 | 51 | 422 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 422 |  |  | 2020-09-14 | B25165¦Courtroom 306¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Outdoors |  |  | 17 | 72 | [5 empty] | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20619¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 21 | 46 | 450 | north | 2020-09-17 09:00 | 9:00 | 21 | 46 | 450 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 57 | 464 | public area | 2020-09-17 09:00 | 9:00 | 20 | 57 | 464 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 302 | [5 empty] | 21 | 51 | 522 |  | 2020-09-17 12:00 | 12:00 | 21 | 51 | 522 |  |  | 2020-09-14 | B25165¦Courtroom 302¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Courtroom 1-14 | [5 empty] | 22 | 49 | 469 |  | 2020-09-17 12:00 | 12:00 | 22 | 49 | 469 |  |  | 2020-09-14 | B20619¦Courtroom 1-14¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 56 | 481 | judge area | 2020-09-17 09:00 | 9:00 | 20 | 56 | 481 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 22 | 46 | 449 | south | 2020-09-17 09:00 | 9:00 | 22 | 46 | 449 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 208 | [5 empty] | 21 | 51 | 442 |  | 2020-09-17 12:00 | 12:00 | 21 | 51 | 442 |  |  | 2020-09-14 | B25165¦Courtroom 208¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 56 | 477 | outside of 509 | 2020-09-17 09:00 | 9:00 | 20 | 56 | 477 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | hallway by courtroom 302 | [5 empty] | 21 | 46 | 456 |  | 2020-09-17 09:00 | 9:00 | 21 | 46 | 456 |  |  | 2020-09-14 | B20979¦hallway by courtroom 302¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 56 | 451 | public area | 2020-09-17 09:00 | 9:00 | 20 | 56 | 451 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 206 | [5 empty] | 21 | 51 | 450 |  | 2020-09-17 12:00 | 12:00 | 21 | 51 | 450 |  |  | 2020-09-14 | B25165¦Courtroom 206¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 56 | 450 | judge area | 2020-09-17 09:00 | 9:00 | 20 | 56 | 450 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 50 | 440 | south | 2020-09-17 09:00 | 9:00 | 22 | 50 | 440 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 56 | 494 | outside of 510 | 2020-09-17 09:00 | 9:00 | 20 | 56 | 494 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 204 | [5 empty] | 21 | 51 | 477 |  | 2020-09-17 12:00 | 12:00 | 21 | 51 | 477 |  |  | 2020-09-14 | B25165¦Courtroom 204¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 56 | 466 | public area | 2020-09-17 09:00 | 9:00 | 20 | 56 | 466 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 49 | 436 | north | 2020-09-17 09:00 | 9:00 | 22 | 49 | 436 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 202 | [5 empty] | 21 | 51 | 452 |  | 2020-09-17 12:00 | 12:00 | 21 | 51 | 452 |  |  | 2020-09-14 | B25165¦Courtroom 202¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 56 | 457 | judge area | 2020-09-17 09:00 | 9:00 | 20 | 56 | 457 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 3 | [5 empty] | 23 | 48 | 340 |  | 2020-09-17 09:00 | 9:00 | 23 | 48 | 340 |  |  | 2020-09-14 | B24638¦Courtroom 3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Basement cells - hallway | [5 empty] | 23 | 50 | 443 |  | 2020-09-17 09:00 | 9:00 | 23 | 50 | 443 |  |  | 2020-09-14 | B20979¦Basement cells - hallway¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 200 | [5 empty] | 21 | 51 | 450 |  | 2020-09-17 12:00 | 12:00 | 21 | 51 | 450 |  |  | 2020-09-14 | B25165¦Courtroom 200¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | back of main hallway | [5 empty] | 20 | 56 | 521 |  | 2020-09-17 09:00 | 9:00 | 20 | 56 | 521 |  |  | 2020-09-14 | B70003¦back of main hallway¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 100 | [5 empty] | 22 | 51 | 450 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 450 |  |  | 2020-09-14 | B25165¦Courtroom 100¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | police office | [5 empty] | 23 | 45 | 522 |  | 2020-09-17 09:00 | 9:00 | 23 | 45 | 522 |  |  | 2020-09-14 | B20979¦police office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | elevator area | [5 empty] | 20 | 57 | 479 |  | 2020-09-17 09:00 | 9:00 | 20 | 57 | 479 |  |  | 2020-09-14 | B70003¦elevator area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Outdoors |  |  | 17 | 66 | 409 |  |  |  | outside of 444 Yonge St. | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70003¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | outside | [5 empty] | 17 | 61 | 427 |  | 2020-09-17 09:00 | 9:00 | 17 | 61 | 427 |  | caution | 2020-09-14 | B20979¦outside¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 3 | [5 empty] | 23 | 47 | 348 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 348 |  |  | 2020-09-14 | B24638¦Courtroom 3¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-1, 16th Floor OTHER | [5 empty] | 21 | 51 | 634 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 634 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-1, 16th Floor OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-3, 16th Floor OTHER | [5 empty] | 21 | 52 | 630 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 630 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-3, 16th Floor OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 16th Floor OTHER | [5 empty] | 21 | 52 | 625 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 625 |  |  | 2020-09-14 | B25398¦Elevator Lobby, 16th Floor OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 1 | [5 empty] | 23 | 48 | 313 |  | 2020-09-17 09:00 | 9:00 | 23 | 48 | 313 |  |  | 2020-09-14 | B24638¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Washrooms, 16th Floor OTHER | [5 empty] | 21 | 52 | 636 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 636 |  |  | 2020-09-14 | B25398¦Corridor adj. to Washrooms, 16th Floor OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 1 | [5 empty] | 23 | 48 | 348 |  | 2020-09-17 12:00 | 12:00 | 23 | 48 | 348 |  |  | 2020-09-14 | B24638¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Women's Washroom, 16th Floor | [5 empty] | 21 | 51 | 629 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 629 |  |  | 2020-09-14 | B25398¦OTHER Women's Washroom, 16th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Outdoors |  |  | 20 | 47 | 310 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B24638¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Outdoors |  |  | 23 | 47 | 322 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B24638¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 2 | [5 empty] | 21 | 61 | 562 |  | 2020-09-17 09:00 | 9:00 | 21 | 61 | 562 |  | caution | 2020-09-14 | B11586¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 20 | 63 | 501 | CROWN Attorney Beaton | 2020-09-17 09:00 | 9:00 | 20 | 63 | 501 |  | caution | 2020-09-14 | B11586¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 19 | 60 | 507 | Crown attorney heneault’s office | 2020-09-17 09:00 | 9:00 | 19 | 60 | 507 |  | caution | 2020-09-14 | B11586¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown attorney admin area | [5 empty] | 20 | 55 | 602 |  | 2020-09-17 09:00 | 9:00 | 20 | 55 | 602 |  |  | 2020-09-14 | B11586¦Crown attorney admin area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, West, 15th Floor | [5 empty] | 20 | 53 | 645 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 645 |  |  | 2020-09-14 | B25398¦OTHER Office Area, West, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 - waiting area | [5 empty] | 21 | 51 | 440 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 440 |  |  | 2020-09-14 | B11586¦Courtroom 1 - waiting area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 | [5 empty] | 21 | 44 | 427 |  | 2020-09-17 09:00 | 9:00 | 21 | 44 | 427 |  |  | 2020-09-14 | B11586¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North West, 15th Floor | [5 empty] | 20 | 53 | 645 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 645 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North West, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | 2nd Floor Holding Cell | [5 empty] | 21 | 48 | 446 |  | 2020-09-17 09:00 | 9:00 | 21 | 48 | 446 |  |  | 2020-09-14 | B11586¦2nd Floor Holding Cell¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North, 15th Floor | [5 empty] | 20 | 53 | 650 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 650 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Judge office | [5 empty] | 22 | 48 | 530 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 530 |  |  | 2020-09-14 | B11586¦Judge office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North East, 15th Floor | [5 empty] | 20 | 54 | 648 |  | 2020-09-17 09:00 | 9:00 | 20 | 54 | 648 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North East, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 21 | 52 | 482 | Courthouse administration office | 2020-09-17 09:00 | 9:00 | 21 | 52 | 482 |  |  | 2020-09-14 | B11586¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Main Lobby | [5 empty] | 22 | 52 | 472 |  | 2020-09-17 09:00 | 9:00 | 22 | 52 | 472 |  |  | 2020-09-14 | B11586¦Main Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, East, 15th Floor | [5 empty] | 20 | 54 | 657 |  | 2020-09-17 09:00 | 9:00 | 20 | 54 | 657 |  |  | 2020-09-14 | B25398¦OTHER Office Area, East, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Outdoors |  |  | 18 | 62 | 382 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B11586¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20893 | B20893 - 75 Mulcaster St. - Barrie | Courtroom 7,8,9 | [5 empty] | 21.4 | 45 | 442 |  | 2020-09-17 09:00 | 9:00 | 21.4 | 45 | 442 |  |  | 2020-09-14 | B20893¦Courtroom 7,8,9¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, Souoth East, 15th Floor | [5 empty] | 21 | 53 | 650 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 650 |  |  | 2020-09-14 | B25398¦OTHER Office Area, Souoth East, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92347 | B92347 - 75 Mulcaster Street - Barrie | Courtroom 15 | [5 empty] | 20.3 | 38 | 461 |  | 2020-09-17 09:00 | 9:00 | 20.3 | 38 | 461 |  | caution | 2020-09-14 | B92347¦Courtroom 15¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South, 15th Floor | [5 empty] | 20 | 53 | 641 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 641 |  |  | 2020-09-14 | B25398¦OTHER Office Area, South, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20893 | B20893 - 75 Mulcaster St. - Barrie | Courtroom 7,8,9 | [5 empty] | 22 | 42 | 522 |  | 2020-09-17 12:00 | 12:00 | 22 | 42 | 522 |  |  | 2020-09-14 | B20893¦Courtroom 7,8,9¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Reception, 15th Floor | [5 empty] | 20 | 53 | 644 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 644 |  |  | 2020-09-14 | B25398¦OTHER Reception, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Outdoors |  |  | 12 | 51 | 405 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B12948¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Mail Room, 15th Floor OTHER | [5 empty] | 21 | 53 | 655 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 655 |  |  | 2020-09-14 | B25398¦Mail Room, 15th Floor OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 1 | [5 empty] | 20 | 41 | 420 |  | 2020-09-17 12:00 | 12:00 | 20 | 41 | 420 |  |  | 2020-09-14 | B12948¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92347 | B92347 - 75 Mulcaster Street - Barrie | Courtroom 15 | [5 empty] | 21.3 | 47 | 481 |  | 2020-09-17 12:00 | 12:00 | 21.3 | 47 | 481 |  |  | 2020-09-14 | B92347¦Courtroom 15¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 15th Floor OTHER | [5 empty] | 21 | 53 | 640 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 640 |  |  | 2020-09-14 | B25398¦Elevator Lobby, 15th Floor OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 | [5 empty] | 21 | 39 | 434 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 434 |  | caution | 2020-09-14 | B12948¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Outdoors |  |  | 16 | 53 | 630 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B25398¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 | [5 empty] | 21 | 37 | 480 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 480 |  | caution | 2020-09-14 | B12948¦Courtroom 3¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 | [5 empty] | 21 | 36 | 408 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 408 |  | caution | 2020-09-14 | B12948¦Courtroom 4¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 101 | [5 empty] | 22 | 48 |  |  | 2020-09-17 12:00 | 12:00 | 22 | 48 |  |  |  | 2020-09-14 | B20080¦Courtroom 101¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 | [5 empty] | 21 | 36 | 410 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 410 |  | caution | 2020-09-14 | B12948¦Courtroom 5¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 6 | [5 empty] | 21 | 36 | 416 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 416 |  | caution | 2020-09-14 | B12948¦Courtroom 6¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration Office Waiting Area | [5 empty] | 22 | 37 | 427 |  | 2020-09-17 12:00 | 12:00 | 22 | 37 | 427 |  | caution | 2020-09-14 | B12948¦Administration Office Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 201 | [5 empty] | 22 | 45 | 456 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 456 |  |  | 2020-09-14 | B20080¦Courtroom 201¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration office | [5 empty] | 22 | 38 | 434 |  | 2020-09-17 12:00 | 12:00 | 22 | 38 | 434 |  | caution | 2020-09-14 | B12948¦Administration office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 202 | [5 empty] | 23 | 45 | 443 |  | 2020-09-17 12:00 | 12:00 | 23 | 45 | 443 |  |  | 2020-09-14 | B20080¦Courtroom 202¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Crown attorney admin area | [5 empty] | 22 | 40 | 579 |  | 2020-09-17 12:00 | 12:00 | 22 | 40 | 579 |  | caution | 2020-09-14 | B12948¦Crown attorney admin area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 301 | [5 empty] | 22 | 45 | 456 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 456 |  |  | 2020-09-14 | B20080¦Courtroom 301¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Cell Basement | [5 empty] | 22 | 38 | 497 |  | 2020-09-17 12:00 | 12:00 | 22 | 38 | 497 |  | caution | 2020-09-14 | B12948¦Cell Basement¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 302 | [5 empty] | 22 | 45 | 485 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 485 |  |  | 2020-09-14 | B20080¦Courtroom 302¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main entrance | [5 empty] | 22 | 37 | 483 |  | 2020-09-17 12:00 | 12:00 | 22 | 37 | 483 |  | caution | 2020-09-14 | B12948¦Main entrance¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 303 | [5 empty] | 22 | 45 | 546 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 546 |  |  | 2020-09-14 | B20080¦Courtroom 303¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main Entrance Waiting Area | [5 empty] | 22 | 37 | 445 |  | 2020-09-17 12:00 | 12:00 | 22 | 37 | 445 |  | caution | 2020-09-14 | B12948¦Main Entrance Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Outdoors |  |  | 17 | 63 | 416 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20080¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Court Room 1 Waiting Area | [5 empty] | 21 | 36 | 451 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 451 |  | caution | 2020-09-14 | B12948¦Court Room 1 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 Waiting Area | [5 empty] | 22 | 35 | 425 |  | 2020-09-17 12:00 | 12:00 | 22 | 35 | 425 |  | caution | 2020-09-14 | B12948¦Courtroom 2 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 Waiting Area | [5 empty] | 22 | 35 | 428 |  | 2020-09-17 12:00 | 12:00 | 22 | 35 | 428 |  | caution | 2020-09-14 | B12948¦Courtroom 3 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 Waiting Area | [5 empty] | 22 | 36 | 431 |  | 2020-09-17 12:00 | 12:00 | 22 | 36 | 431 |  | caution | 2020-09-14 | B12948¦Courtroom 5 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 and 6 Waiting Area | [5 empty] | 22 | 35 | 423 |  | 2020-09-17 12:00 | 12:00 | 22 | 35 | 423 |  | caution | 2020-09-14 | B12948¦Courtroom 4 and 6 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Outdoors |  |  | 18 | 47 | 478 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20289¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 21 | 50 | 506 | judge | 2020-09-17 12:00 | 12:00 | 21 | 50 | 506 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 21 | 49 | 503 | public | 2020-09-17 12:00 | 12:00 | 21 | 49 | 503 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 22 | 49 | 505 | judge | 2020-09-17 12:00 | 12:00 | 22 | 49 | 505 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 22 | 48 | 503 | public | 2020-09-17 12:00 | 12:00 | 22 | 48 | 503 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Entry/Waiting | [5 empty] | 23 | 47 | 625 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 625 |  |  | 2020-09-14 | B70510¦Entry/Waiting¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 300 | [5 empty] | 22 | 45 | 519 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 519 |  |  | 2020-09-14 | B20289¦Courtroom 300¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Crown Attorney Office | [5 empty] | 20 | 39 | 452 |  | 2020-09-17 09:00 | 9:00 | 20 | 39 | 452 |  | caution | 2020-09-14 | B20016¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room A | [5 empty] | 23 | 46 | 531 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 531 |  |  | 2020-09-14 | B70510¦Mediation Room A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 301 | [5 empty] | 22 | 45 | 510 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 510 |  |  | 2020-09-14 | B20289¦Courtroom 301¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Legal Aid Ontario | [5 empty] | 21 | 38 | 445 |  | 2020-09-17 09:00 | 9:00 | 21 | 38 | 445 |  | caution | 2020-09-14 | B20016¦Legal Aid Ontario¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 302 | [5 empty] | 23 | 46 | 509 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 509 |  |  | 2020-09-14 | B20289¦Courtroom 302¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Information Desk | [5 empty] | 23 | 47 | 462 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 462 |  |  | 2020-09-14 | B70510¦Information Desk¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel Waiting Area | [5 empty] | 21 | 37 | 448 |  | 2020-09-17 09:00 | 9:00 | 21 | 37 | 448 |  | caution | 2020-09-14 | B20016¦Duty Counsel Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 303 | [5 empty] | 23 | 46 | 501 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 501 |  |  | 2020-09-14 | B20289¦Courtroom 303¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Lunch Room 454 | [5 empty] | 23 | 47 | 455 |  | 2020-09-17 09:00 | 9:00 | 23 | 47 | 455 |  |  | 2020-09-14 | B70510¦Lunch Room 454¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel | [5 empty] | 21 | 40 | 444 |  | 2020-09-17 09:00 | 9:00 | 21 | 40 | 444 |  | caution | 2020-09-14 | B20016¦Duty Counsel¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom A | [5 empty] | 22 | 46 | 529 | in session; measurement taken outside courtroom | 2020-09-17 12:00 | 12:00 | 22 | 46 | 529 |  |  | 2020-09-14 | B20289¦Courtroom A¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lobby Courtroom 1 - 2 | [5 empty] | 22 | 36 | 447 |  | 2020-09-17 09:00 | 9:00 | 22 | 36 | 447 |  | caution | 2020-09-14 | B20016¦Lobby Courtroom 1 - 2¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Copy Room 455 | [5 empty] | 23 | 47 | 450 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 450 |  |  | 2020-09-14 | B70510¦Copy Room 455¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom B | [5 empty] | 22 | 47 | 553 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 553 |  |  | 2020-09-14 | B20289¦Courtroom B¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Main Lobby | [5 empty] | 22 | 37 | 484 |  | 2020-09-17 09:00 | 9:00 | 22 | 37 | 484 |  | caution | 2020-09-14 | B20016¦Main Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room B | [5 empty] | 23 | 48 | 515 |  | 2020-09-17 12:00 | 12:00 | 23 | 48 | 515 |  |  | 2020-09-14 | B70510¦Mediation Room B¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom C (North) | [5 empty] | 22 | 48 | 581 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 581 |  |  | 2020-09-14 | B20289¦Courtroom C (North)¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom D | [5 empty] | 22 | 48 | 565 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 565 |  |  | 2020-09-14 | B20289¦Courtroom D¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lower Hallway | [5 empty] | 22 | 36 | 456 |  | 2020-09-17 09:00 | 9:00 | 22 | 36 | 456 |  | caution | 2020-09-14 | B20016¦Lower Hallway¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 459 | [5 empty] | 23 | 47 | 699 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 699 |  |  | 2020-09-14 | B70510¦Office 459¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom E | [5 empty] | 22 | 47 | 580 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 580 |  |  | 2020-09-14 | B20289¦Courtroom E¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 467 | [5 empty] | 23 | 46 | 512 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 512 |  |  | 2020-09-14 | B70510¦Office 467¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom F | [5 empty] | 22 | 48 | 545 | in session; measurement taken outside courtroom | 2020-09-17 12:00 | 12:00 | 22 | 48 | 545 |  |  | 2020-09-14 | B20289¦Courtroom F¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Outdoors |  |  | 19 | 41 | 384 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B19652¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 469 | [5 empty] | 23 | 47 | 518 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 518 |  |  | 2020-09-14 | B70510¦Office 469¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | OTHER | [5 empty] | 21 | 37 | 444 | Courtroom 1-2-3 | 2020-09-17 09:00 | 9:00 | 21 | 37 | 444 |  | caution | 2020-09-14 | B20016¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Center) | [5 empty] | 22 | 44 | 454 |  | 2020-09-17 12:00 | 12:00 | 22 | 44 | 454 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Center)¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Room 473 (Printer) | [5 empty] | 23 | 47 | 515 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 515 |  |  | 2020-09-14 | B70510¦Room 473 (Printer)¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation | [5 empty] | 21 | 38 | 450 |  | 2020-09-17 09:00 | 9:00 | 21 | 38 | 450 |  | caution | 2020-09-14 | B20016¦Family Mediation¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Judge Dias) | [5 empty] | 22 | 45 | 420 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 420 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Judge Dias)¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hall 475 or 466 | [5 empty] | 23 | 47 | 487 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 487 |  |  | 2020-09-14 | B70510¦Hall 475 or 466¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation Across Stairs | [5 empty] | 19 | 38 | 457 |  | 2020-09-17 09:00 | 9:00 | 19 | 38 | 457 |  | caution | 2020-09-14 | B20016¦Family Mediation Across Stairs¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 1 | [5 empty] | 22 | 47 | 473 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 473 |  |  | 2020-09-14 | B70510¦Hearing Room 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 45 | 433 | Superior judges chamber | 2020-09-17 12:00 | 12:00 | 22 | 45 | 433 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Meeting Rooms 1/2 | [5 empty] | 22 | 48 | 570 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 570 |  |  | 2020-09-14 | B70510¦Vestibule at Meeting Rooms 1/2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 46 | 458 | 3rd floor stair landing | 2020-09-17 12:00 | 12:00 | 22 | 46 | 458 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Hearing Room 1 | [5 empty] | 22 | 48 | 504 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 504 |  |  | 2020-09-14 | B70510¦Vestibule at Hearing Room 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 47 | 438 | 3rd floor Jury room | 2020-09-17 12:00 | 12:00 | 22 | 47 | 438 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Security Check In | [5 empty] | 20 | 56 | 435 |  | 2020-09-17 09:00 | 9:00 | 20 | 56 | 435 |  |  | 2020-09-14 | B92624¦Security Check In¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 2 | [5 empty] | 22 | 48 | 520 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 520 |  |  | 2020-09-14 | B70510¦Hearing Room 2¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Main Lobby | [5 empty] | 19 | 59 | 476 |  | 2020-09-17 09:00 | 9:00 | 19 | 59 | 476 |  |  | 2020-09-14 | B19523¦Main Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 47 | 525 | Justice McDonald chamber | 2020-09-17 12:00 | 12:00 | 22 | 47 | 525 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701A | [5 empty] | 21 | 54 | 439 | West | 2020-09-17 09:00 | 9:00 | 21 | 54 | 439 |  |  | 2020-09-14 | B92624¦Room 701A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Outdoors |  |  | 13 | 63 | 429 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B90838¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 439 | [5 empty] | 23 | 48 | 545 |  | 2020-09-17 12:00 | 12:00 | 23 | 48 | 545 |  |  | 2020-09-14 | B70510¦Office 439¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Holding Cell | [5 empty] | 20 | 56 | 456 |  | 2020-09-17 09:00 | 9:00 | 20 | 56 | 456 |  |  | 2020-09-14 | B19523¦Holding Cell¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Courtroom 101 Courtroom 102 | [5 empty] | 21 | 43 | 437 |  | 2020-09-17 12:00 | 12:00 | 21 | 43 | 437 |  |  | 2020-09-14 | B90838¦Courtroom 101 Courtroom 102¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701A | [5 empty] | 21 | 54 | 432 | East | 2020-09-17 09:00 | 9:00 | 21 | 54 | 432 |  |  | 2020-09-14 | B92624¦Room 701A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 46 | 520 | Justice McDonald secretary | 2020-09-17 12:00 | 12:00 | 22 | 46 | 520 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | First Aid Desk | [5 empty] | 22 | 48 | 558 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 558 |  |  | 2020-09-14 | B70510¦First Aid Desk¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701A | [5 empty] | 21 | 54 | 436 | North | 2020-09-17 09:00 | 9:00 | 21 | 54 | 436 |  |  | 2020-09-14 | B92624¦Room 701A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 436 | [5 empty] | 23 | 47 | 581 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 581 |  |  | 2020-09-14 | B70510¦Office 436¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 46 | 521 | SCJTC office | 2020-09-17 12:00 | 12:00 | 21 | 46 | 521 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway | [5 empty] | 20 | 53 | 426 | by Room 701A | 2020-09-17 09:00 | 9:00 | 20 | 53 | 426 |  |  | 2020-09-14 | B92624¦Hallway¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 432 | [5 empty] | 23 | 47 | 575 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 575 |  |  | 2020-09-14 | B70510¦Office 432¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 46 | 517 | Visiting justice chamber | 2020-09-17 12:00 | 12:00 | 21 | 46 | 517 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 1 | [5 empty] | 21 | 52 | 454 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 454 |  |  | 2020-09-14 | B19523¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 20 | 55 | 442 | East | 2020-09-17 09:00 | 9:00 | 20 | 55 | 442 |  |  | 2020-09-14 | B92624¦Room 718A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 429 | [5 empty] | 23 | 46 | 780 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 780 |  |  | 2020-09-14 | B70510¦Office 429¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Court Services | [5 empty] | 21 | 51 | 458 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 458 |  |  | 2020-09-14 | B19523¦Court Services¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Center) | [5 empty] | 21 | 46 | 521 |  | 2020-09-17 12:00 | 12:00 | 21 | 46 | 521 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Center)¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 20 | 55 | 428 | West | 2020-09-17 09:00 | 9:00 | 20 | 55 | 428 |  |  | 2020-09-14 | B92624¦Room 718A¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | JP Office | [5 empty] | 21 | 51 | 454 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 454 |  |  | 2020-09-14 | B19523¦JP Office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Judge Dias) | [5 empty] | 21 | 46 | 508 |  | 2020-09-17 12:00 | 12:00 | 21 | 46 | 508 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Judge Dias)¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | OPP Office | [5 empty] | 21 | 52 | 458 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 458 |  |  | 2020-09-14 | B19523¦OPP Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718B | [5 empty] | 20 | 54 | 426 |  | 2020-09-17 09:00 | 9:00 | 20 | 54 | 426 |  |  | 2020-09-14 | B92624¦Room 718B¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Crown Attorney Office | [5 empty] | 21 | 50 | 462 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 462 |  |  | 2020-09-14 | B19523¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 Waiting Area | [5 empty] | 21 | 47 | 534 |  | 2020-09-17 12:00 | 12:00 | 21 | 47 | 534 |  |  | 2020-09-14 | B19652¦Courtroom 2 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 50 | 470 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 470 |  |  | 2020-09-14 | B19523¦VWAP Office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 427 | [5 empty] | 23 | 46 | 545 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 545 |  |  | 2020-09-14 | B70510¦Office 427¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716A | [5 empty] | 19 | 55 | 471 |  | 2020-09-17 09:00 | 9:00 | 19 | 55 | 471 |  |  | 2020-09-14 | B92624¦Room 716A¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 48 | 476 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 476 |  |  | 2020-09-14 | B19523¦VWAP Office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mail Room | [5 empty] | 23 | 46 | 490 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 490 |  |  | 2020-09-14 | B70510¦Mail Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Center) | [5 empty] | 22 | 46 | 484 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 484 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Center)¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717A | [5 empty] | 19 | 56 | 494 |  | 2020-09-17 09:00 | 9:00 | 19 | 56 | 494 |  |  | 2020-09-14 | B92624¦Room 717A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 420 | [5 empty] | 23 | 46 | 531 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 531 |  |  | 2020-09-14 | B70510¦Office 420¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Judge Dias) | [5 empty] | 22 | 44 | 478 |  | 2020-09-17 12:00 | 12:00 | 22 | 44 | 478 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Judge Dias)¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 5 | [5 empty] | 21 | 48 | 461 |  | 2020-09-17 09:00 | 9:00 | 21 | 48 | 461 |  |  | 2020-09-14 | B19523¦Courtroom 5¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716B | [5 empty] | 19 | 55 | 465 |  | 2020-09-17 09:00 | 9:00 | 19 | 55 | 465 |  |  | 2020-09-14 | B92624¦Room 716B¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 418 | [5 empty] | 23 | 46 | 620 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 620 |  |  | 2020-09-14 | B70510¦Office 418¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Remote Testimony Room | [5 empty] | 21 | 49 | 456 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 456 |  |  | 2020-09-14 | B19523¦Remote Testimony Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717B | [5 empty] | 19 | 55 | 491 |  | 2020-09-17 09:00 | 9:00 | 19 | 55 | 491 |  |  | 2020-09-14 | B92624¦Room 717B¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 47 | 566 | Justice peace chamber | 2020-09-17 12:00 | 12:00 | 23 | 47 | 566 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Conference Room 2 | [5 empty] | 21 | 49 | 466 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 466 |  |  | 2020-09-14 | B19523¦Conference Room 2¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | File Room | [5 empty] | 23 | 47 | 509 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 509 |  |  | 2020-09-14 | B70510¦File Room¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714A | [5 empty] | 19 | 55 | 475 |  | 2020-09-17 09:00 | 9:00 | 19 | 55 | 475 |  |  | 2020-09-14 | B92624¦Room 714A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 47 | 534 | Council chamber dias | 2020-09-17 12:00 | 12:00 | 22 | 47 | 534 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Health Room | [5 empty] | 22 | 47 | 494 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 494 |  |  | 2020-09-14 | B70510¦Health Room¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715A | [5 empty] | 19 | 55 | 459 |  | 2020-09-17 09:00 | 9:00 | 19 | 55 | 459 |  |  | 2020-09-14 | B92624¦Room 715A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 47 | 561 | Council chamber center | 2020-09-17 12:00 | 12:00 | 22 | 47 | 561 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715B | [5 empty] | 19 | 45 | 467 |  | 2020-09-17 09:00 | 9:00 | 19 | 45 | 467 |  |  | 2020-09-14 | B92624¦Room 715B¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 | [5 empty] | 22 | 47 | 504 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 504 |  |  | 2020-09-14 | B70510¦Hearing Room 3¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 | [5 empty] | 21 | 49 | 463 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 463 |  |  | 2020-09-14 | B19523¦Courtroom 3¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 2nd Floor Lunchroom | [5 empty] | 22 | 46 | 498 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 498 |  |  | 2020-09-14 | B19652¦2nd Floor Lunchroom¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 Waiting Area | [5 empty] | 21 | 49 | 466 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 466 |  |  | 2020-09-14 | B19523¦Courtroom 3 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714B | [5 empty] | 19 | 56 | 483 |  | 2020-09-17 09:00 | 9:00 | 19 | 56 | 483 |  |  | 2020-09-14 | B92624¦Room 714B¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 Waiting Area | [5 empty] | 22 | 48 | 555 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 555 |  |  | 2020-09-14 | B70510¦Hearing Room 3 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 45 | 489 | 2nd floor stair landing | 2020-09-17 12:00 | 12:00 | 22 | 45 | 489 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 21 | 50 | 472 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 472 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713A | [5 empty] | 19 | 56 | 473 |  | 2020-09-17 09:00 | 9:00 | 19 | 56 | 473 |  |  | 2020-09-14 | B92624¦Room 713A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Elevator Lobby | [5 empty] | 22 | 51 | 451 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 451 |  |  | 2020-09-14 | B70510¦Elevator Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Main entrance | [5 empty] | 20 | 54 | 541 |  | 2020-09-17 12:00 | 12:00 | 20 | 54 | 541 |  |  | 2020-09-14 | B20979¦Main entrance¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713B | [5 empty] | 19 | 55 | 481 |  | 2020-09-17 09:00 | 9:00 | 19 | 55 | 481 |  |  | 2020-09-14 | B92624¦Room 713B¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd fl lobby | [5 empty] | 21 | 35 | 648 |  | 2020-09-17 12:00 | 12:00 | 21 | 35 | 648 |  | caution | 2020-09-14 | B20226¦2nd fl lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 45 | 470 | Court service kitchenette | 2020-09-17 12:00 | 12:00 | 22 | 45 | 470 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801A | [5 empty] | 20 | 57 | 431 |  | 2020-09-17 09:00 | 9:00 | 20 | 57 | 431 |  |  | 2020-09-14 | B92624¦Room 801A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Outdoors |  |  | 18 | 56 | 462 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70510¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 46 | 695 | Court service north | 2020-09-17 12:00 | 12:00 | 23 | 46 | 695 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801B | [5 empty] | 20 | 57 | 422 |  | 2020-09-17 09:00 | 9:00 | 20 | 57 | 422 |  |  | 2020-09-14 | B92624¦Room 801B¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 21 | 52 | 578 | east | 2020-09-17 12:00 | 12:00 | 21 | 52 | 578 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 47 | 685 | Court service south | 2020-09-17 12:00 | 12:00 | 23 | 47 | 685 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 2 | [5 empty] | 20 | 35 | 646 |  | 2020-09-17 12:00 | 12:00 | 20 | 35 | 646 |  | caution | 2020-09-14 | B20226¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 21 | 50 | 477 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 477 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 22 | 50 | 534 | west | 2020-09-17 12:00 | 12:00 | 22 | 50 | 534 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway | [5 empty] | 20 | 55 | 423 | by Room 801A | 2020-09-17 09:00 | 9:00 | 20 | 55 | 423 |  |  | 2020-09-14 | B92624¦Hallway¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 48 | 710 | Court service entrance vestibule | 2020-09-17 12:00 | 12:00 | 23 | 48 | 710 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 21 | 49 | 578 | south | 2020-09-17 12:00 | 12:00 | 21 | 49 | 578 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 51 | 505 |  | 2020-09-17 09:00 | 9:00 | 20 | 51 | 505 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Outdoors |  |  | 19 | 56 | 413 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B92624¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 44 | 570 | 1st floor stair landing | 2020-09-17 12:00 | 12:00 | 23 | 44 | 570 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 2 | [5 empty] | 21 | 50 | 456 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 456 |  |  | 2020-09-14 | B19523¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 21 | 48 | 569 | north | 2020-09-17 12:00 | 12:00 | 21 | 48 | 569 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Escalator, 800 | [5 empty] | 20 | 53 | 436 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 436 |  |  | 2020-09-14 | B92624¦Hallway by Escalator, 800¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 1 | [5 empty] | 21 | 36 | 708 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 708 |  | caution | 2020-09-14 | B20226¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 21 | 52 | 783 | south | 2020-09-17 12:00 | 12:00 | 21 | 52 | 783 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Escalator, 700 | [5 empty] | 20 | 52 | 437 |  | 2020-09-17 09:00 | 9:00 | 20 | 52 | 437 |  |  | 2020-09-14 | B92624¦Hallway by Escalator, 700¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 100 Courtroom 102 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203 | [5 empty] | 21 | 46 | 466 |  | 2020-09-17 12:00 | 12:00 | 21 | 46 | 466 |  |  | 2020-09-14 | B20616¦Courtroom 100 Courtroom 102 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Lounge | [5 empty] | 20 | 54 | 417 |  | 2020-09-17 09:00 | 9:00 | 20 | 54 | 417 |  |  | 2020-09-14 | B92624¦Lounge¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 307 | [5 empty] | 21 | 52 | 783 | south | 2020-09-17 12:00 | 12:00 | 21 | 52 | 783 |  |  | 2020-09-14 | B20979¦Courtroom 307¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Halway by Room 718A | [5 empty] | 19 | 53 | 429 |  | 2020-09-17 09:00 | 9:00 | 19 | 53 | 429 |  |  | 2020-09-14 | B92624¦Halway by Room 718A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | courtroom 307 | [5 empty] | 22 | 51 | 813 | north | 2020-09-17 12:00 | 12:00 | 22 | 51 | 813 |  |  | 2020-09-14 | B20979¦courtroom 307¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 101 Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 401 Courtroom 402 Courtroom 403 | [5 empty] | 22 | 46 | 466 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 466 |  |  | 2020-09-14 | B20616¦Courtroom 101 Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 401 Courtroom 402 Courtroom 403¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Security Check In | [5 empty] | 21 | 49 | 464 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 464 |  |  | 2020-09-14 | B92624¦Security Check In¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 22 | 34 | 768 |  | 2020-09-17 12:00 | 12:00 | 22 | 34 | 768 |  | low | 2020-09-14 | B20226¦2nd Floor Holding Cell¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | hallway by courtroom 307 | [5 empty] | 22 | 46 | 560 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 560 |  |  | 2020-09-14 | B20979¦hallway by courtroom 307¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 20 | 52 | 428 | West | 2020-09-17 12:00 | 12:00 | 20 | 52 | 428 |  |  | 2020-09-14 | B92624¦Room 701¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 106 Courtroom 205 | [5 empty] | 20 | 50 | 465 |  | 2020-09-17 12:00 | 12:00 | 20 | 50 | 465 |  |  | 2020-09-14 | B20616¦Courtroom 106 Courtroom 205¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 22 | 49 | 762 | east | 2020-09-17 12:00 | 12:00 | 22 | 49 | 762 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 20 | 53 | 444 | East | 2020-09-17 12:00 | 12:00 | 20 | 53 | 444 |  |  | 2020-09-14 | B92624¦Room 701¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 22 | 50 | 789 | west | 2020-09-17 12:00 | 12:00 | 22 | 50 | 789 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 20 | 53 | 448 | North | 2020-09-17 12:00 | 12:00 | 20 | 53 | 448 |  |  | 2020-09-14 | B92624¦Room 701¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 47 | 428 | south | 2020-09-17 12:00 | 12:00 | 22 | 47 | 428 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 701 | [5 empty] | 19 | 52 | 436 |  | 2020-09-17 12:00 | 12:00 | 19 | 52 | 436 |  |  | 2020-09-14 | B92624¦Hallway by Room 701¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 204 Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 404 Courtroom 405 | [5 empty] | 21 | 50 | 465 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 465 |  |  | 2020-09-14 | B20616¦Courtroom 204 Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 404 Courtroom 405¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 46 | 428 | north | 2020-09-17 12:00 | 12:00 | 22 | 46 | 428 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Police Court Bureau | [5 empty] | 21 | 50 | 482 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 482 |  |  | 2020-09-14 | B19523¦Police Court Bureau¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 20 | 54 | 435 | East | 2020-09-17 12:00 | 12:00 | 20 | 54 | 435 |  |  | 2020-09-14 | B92624¦Room 718A¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 Waiting Area | [5 empty] | 21 | 50 | 507 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 507 |  |  | 2020-09-14 | B19523¦Courtroom 4 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | hallway by courtroom 302 | [5 empty] | 22 | 45 | 518 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 518 |  |  | 2020-09-14 | B20979¦hallway by courtroom 302¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 20 | 54 | 444 | West | 2020-09-17 12:00 | 12:00 | 20 | 54 | 444 |  |  | 2020-09-14 | B92624¦Room 718A¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 | [5 empty] | 21 | 49 | 460 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 460 |  |  | 2020-09-14 | B19523¦Courtroom 4¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 304 Courtroom 305 | [5 empty] | 21 | 46 | 569 |  | 2020-09-17 12:00 | 12:00 | 21 | 46 | 569 |  |  | 2020-09-14 | B20616¦Courtroom 304 Courtroom 305¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Basement cells - hallway | [5 empty] | 22 | 46 | 430 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 430 |  |  | 2020-09-14 | B20979¦Basement cells - hallway¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718B | [5 empty] | 20 | 54 | 439 |  | 2020-09-17 12:00 | 12:00 | 20 | 54 | 439 |  |  | 2020-09-14 | B92624¦Room 718B¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 3 | [5 empty] | 22 | 31 | 633 |  | 2020-09-17 12:00 | 12:00 | 22 | 31 | 633 |  | low | 2020-09-14 | B20226¦Courtroom 3¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 50 | 492 |  | 2020-09-17 09:00 | 9:00 | 20 | 50 | 492 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 718A | [5 empty] | 20 | 51 | 444 |  | 2020-09-17 12:00 | 12:00 | 20 | 51 | 444 |  |  | 2020-09-14 | B92624¦Hallway by Room 718A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | police office | [5 empty] | 23 | 47 | 582 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 582 |  |  | 2020-09-14 | B20979¦police office¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 52 | 477 |  | 2020-09-17 09:00 | 9:00 | 19 | 52 | 477 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717A | [5 empty] | 19 | 55 | 461 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 461 |  |  | 2020-09-14 | B92624¦Room 717A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | outside | [5 empty] | 19 | 53 | 403 |  | 2020-09-17 12:00 | 12:00 | 19 | 53 | 403 |  |  | 2020-09-14 | B20979¦outside¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716A | [5 empty] | 19 | 55 | 469 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 469 |  |  | 2020-09-14 | B92624¦Room 716A¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 53 | 485 |  | 2020-09-17 09:00 | 9:00 | 19 | 53 | 485 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Main entrance | [5 empty] | 20 | 55 | 482 |  | 2020-09-17 12:00 | 12:00 | 20 | 55 | 482 |  |  | 2020-09-14 | B90636¦Main entrance¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Jury Room | [5 empty] | 20 | 53 | 457 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 457 |  |  | 2020-09-14 | B19523¦Jury Room¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717B | [5 empty] | 19 | 55 | 494 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 494 |  |  | 2020-09-14 | B92624¦Room 717B¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 20 | 53 | 454 | north | 2020-09-17 12:00 | 12:00 | 20 | 53 | 454 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Ontario Court | [5 empty] | 20 | 51 | 454 |  | 2020-09-17 09:00 | 9:00 | 20 | 51 | 454 |  |  | 2020-09-14 | B19523¦Ontario Court¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 107 | [5 empty] | 21 | 49 | 435 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 435 |  |  | 2020-09-14 | B20616¦Courtroom 107¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 21 | 52 | 452 | south | 2020-09-17 12:00 | 12:00 | 21 | 52 | 452 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717B | [5 empty] | 19 | 55 | 475 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 475 |  |  | 2020-09-14 | B92624¦Room 717B¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Outdoors |  |  | 14 | 23 | 404 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20226¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Judicial Library | [5 empty] | 21 | 49 | 460 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 460 |  |  | 2020-09-14 | B19523¦Judicial Library¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 108 | [5 empty] | 20 | 49 | 435 |  | 2020-09-17 12:00 | 12:00 | 20 | 49 | 435 |  |  | 2020-09-14 | B20616¦Courtroom 108¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714A | [5 empty] | 20 | 56 | 578 |  | 2020-09-17 12:00 | 12:00 | 20 | 56 | 578 |  |  | 2020-09-14 | B92624¦Room 714A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 21 | 49 | 531 | vestibule, lobby | 2020-09-17 12:00 | 12:00 | 21 | 49 | 531 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 315 | [5 empty] | 21 | 49 | 452 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 452 |  |  | 2020-09-14 | B19523¦Office Room 315¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715A | [5 empty] | 19 | 55 | 451 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 451 |  |  | 2020-09-14 | B92624¦Room 715A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 2 | [5 empty] | 21 | 53 | 550 |  | 2020-09-17 12:00 | 12:00 | 21 | 53 | 550 |  |  | 2020-09-14 | B11586¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 316 | [5 empty] | 21 | 49 | 453 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 453 |  |  | 2020-09-14 | B19523¦Office Room 316¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 21 | 49 | 546 | main room entrance | 2020-09-17 12:00 | 12:00 | 21 | 49 | 546 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715B | [5 empty] | 19 | 55 | 485 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 485 |  |  | 2020-09-14 | B92624¦Room 715B¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 317 | [5 empty] | 21 | 48 | 451 |  | 2020-09-17 09:00 | 9:00 | 21 | 48 | 451 |  |  | 2020-09-14 | B19523¦Office Room 317¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 21 | 49 | 547 | Crown attorney beaton’s office | 2020-09-17 12:00 | 12:00 | 21 | 49 | 547 |  |  | 2020-09-14 | B11586¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | hallway by courtroom 203 | [5 empty] | 21 | 50 | 483 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 483 |  |  | 2020-09-14 | B90636¦hallway by courtroom 203¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Superior Court | [5 empty] | 22 | 46 | 512 |  | 2020-09-17 09:00 | 9:00 | 22 | 46 | 512 |  |  | 2020-09-14 | B19523¦Superior Court¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714B | [5 empty] | 20 | 56 | 585 |  | 2020-09-17 12:00 | 12:00 | 20 | 56 | 585 |  |  | 2020-09-14 | B92624¦Room 714B¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 313 | [5 empty] | 22 | 45 | 465 |  | 2020-09-17 09:00 | 9:00 | 22 | 45 | 465 |  |  | 2020-09-14 | B19523¦Office Room 313¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 2nd fl lobby | [5 empty] | 22 | 49 | 455 |  | 2020-09-17 12:00 | 12:00 | 22 | 49 | 455 |  |  | 2020-09-14 | B90636¦2nd fl lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713A | [5 empty] | 19 | 55 | 479 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 479 |  |  | 2020-09-14 | B92624¦Room 713A¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 312 | [5 empty] | 22 | 46 | 466 |  | 2020-09-17 09:00 | 9:00 | 22 | 46 | 466 |  |  | 2020-09-14 | B19523¦Office Room 312¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 3rd Floor Elevator Lobby | [5 empty] | 21 | 49 | 447 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 447 |  |  | 2020-09-14 | B90636¦3rd Floor Elevator Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 310 | [5 empty] | 22 | 46 | 518 |  | 2020-09-17 09:00 | 9:00 | 22 | 46 | 518 |  |  | 2020-09-14 | B19523¦Office Room 310¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713B | [5 empty] | 19 | 55 | 492 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 492 |  |  | 2020-09-14 | B92624¦Room 713B¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Law Association | [5 empty] | 21 | 46 | 454 |  | 2020-09-17 09:00 | 9:00 | 21 | 46 | 454 |  |  | 2020-09-14 | B19523¦Law Association¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 21 | 50 | 470 | west | 2020-09-17 12:00 | 12:00 | 21 | 50 | 470 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Escalator, 700 | [5 empty] | 19 | 54 | 444 |  | 2020-09-17 12:00 | 12:00 | 19 | 54 | 444 |  |  | 2020-09-14 | B92624¦Hallway by Escalator, 700¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 21 | 47 | 517 | Crown attorney henault’s office | 2020-09-17 12:00 | 12:00 | 21 | 47 | 517 |  |  | 2020-09-14 | B11586¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 22 | 50 | 476 | east | 2020-09-17 12:00 | 12:00 | 22 | 50 | 476 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801A | [5 empty] | 20 | 55 | 447 |  | 2020-09-17 12:00 | 12:00 | 20 | 55 | 447 |  |  | 2020-09-14 | B92624¦Room 801A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown attorney admin area | [5 empty] | 22 | 47 | 542 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 542 |  |  | 2020-09-14 | B11586¦Crown attorney admin area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801B | [5 empty] | 20 | 54 | 434 |  | 2020-09-17 12:00 | 12:00 | 20 | 54 | 434 |  |  | 2020-09-14 | B92624¦Room 801B¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 4th floor waiting area | [5 empty] | 21 | 50 | 446 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 446 |  |  | 2020-09-14 | B90636¦4th floor waiting area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-1 | [5 empty] | 20.4 | 52.8 | 718 |  | 2020-09-17 12:00 | 12:00 | 20.4 | 52.8 | 718 |  |  | 2020-09-14 | B10644¦Courtroom 2-1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Outdoors |  |  | 12 | 27 | 400 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70050¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 801 | [5 empty] | 20 | 53 | 427 |  | 2020-09-17 12:00 | 12:00 | 20 | 53 | 427 |  |  | 2020-09-14 | B92624¦Hallway by Room 801¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | courtroom 211 | [5 empty] | 21 | 50 | 421 | north | 2020-09-17 12:00 | 12:00 | 21 | 50 | 421 |  |  | 2020-09-14 | B90636¦courtroom 211¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Lounge | [5 empty] | 20 | 52 | 427 |  | 2020-09-17 12:00 | 12:00 | 20 | 52 | 427 |  |  | 2020-09-14 | B92624¦Lounge¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 - waiting area | [5 empty] | 21 | 38 | 527 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 527 |  | caution | 2020-09-14 | B11586¦Courtroom 1 - waiting area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 101 | [5 empty] | 20 | 54 | 474 |  | 2020-09-17 12:00 | 12:00 | 20 | 54 | 474 |  |  | 2020-09-14 | B25671¦Courtroom 101¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | courtroom 211 | [5 empty] | 21 | 50 | 420 | south | 2020-09-17 12:00 | 12:00 | 21 | 50 | 420 |  |  | 2020-09-14 | B90636¦courtroom 211¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 201 | [5 empty] | 20 | 55 | 768 |  | 2020-09-17 12:00 | 12:00 | 20 | 55 | 768 |  |  | 2020-09-14 | B25671¦Courtroom 201¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 | [5 empty] | 22 | 38 | 455 |  | 2020-09-17 12:00 | 12:00 | 22 | 38 | 455 |  | caution | 2020-09-14 | B11586¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 301 | [5 empty] | 20 | 53 | 552 |  | 2020-09-17 12:00 | 12:00 | 20 | 53 | 552 |  |  | 2020-09-14 | B25671¦Courtroom 301¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | hallway by courtroom 211 | [5 empty] | 21 | 48 | 430 |  | 2020-09-17 12:00 | 12:00 | 21 | 48 | 430 |  |  | 2020-09-14 | B90636¦hallway by courtroom 211¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | 2nd Floor Holding Cell | [5 empty] | 22 | 39 | 492 |  | 2020-09-17 12:00 | 12:00 | 22 | 39 | 492 |  | caution | 2020-09-14 | B11586¦2nd Floor Holding Cell¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-2 | [5 empty] | 19.8 | 58.5 | 567 |  | 2020-09-17 12:00 | 12:00 | 19.8 | 58.5 | 567 |  |  | 2020-09-14 | B10644¦Courtroom 2-2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Outdoors |  |  | 18 | 68 | 431 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B92624¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | outside | [5 empty] | 19 | 53 | 403 |  | 2020-09-17 12:00 | 12:00 | 19 | 53 | 403 |  |  | 2020-09-14 | B90636¦outside¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Judge office | [5 empty] | 22 | 39 | 530 |  | 2020-09-17 12:00 | 12:00 | 22 | 39 | 530 |  | caution | 2020-09-14 | B11586¦Judge office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-3 | [5 empty] | 20.5 | 62.1 | 516 |  | 2020-09-17 12:00 | 12:00 | 20.5 | 62.1 | 516 |  | caution | 2020-09-14 | B10644¦Courtroom 2-3¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Main Lobby | [5 empty] | 21 | 43 | 506 |  | 2020-09-17 12:00 | 12:00 | 21 | 43 | 506 |  |  | 2020-09-14 | B70050¦Main Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | court admin office | [5 empty] | 20 | 57 | 720 |  | 2020-09-17 12:00 | 12:00 | 20 | 57 | 720 |  |  | 2020-09-14 | B11586¦court admin office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-4 | [5 empty] | 22.4 | 45.9 | 551 |  | 2020-09-17 12:00 | 12:00 | 22.4 | 45.9 | 551 |  |  | 2020-09-14 | B10644¦Courtroom 2-4¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Main Lobby | [5 empty] | 20 | 42 | 523 |  | 2020-09-17 12:00 | 12:00 | 20 | 42 | 523 |  |  | 2020-09-14 | B11586¦Main Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 1 | [5 empty] | 21 | 43 | 503 |  | 2020-09-17 12:00 | 12:00 | 21 | 43 | 503 |  |  | 2020-09-14 | B70050¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-6 | [5 empty] | 23.4 | 54.1 | 455 |  | 2020-09-17 12:00 | 12:00 | 23.4 | 54.1 | 455 |  |  | 2020-09-14 | B10644¦Courtroom 2-6¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Outdoors |  |  | 19 | 64 | 368 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B11586¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-5 | [5 empty] | 20.8 | 55.6 | 421 |  | 2020-09-17 12:00 | 12:00 | 20.8 | 55.6 | 421 |  |  | 2020-09-14 | B10644¦Courtroom 2-5¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office North | [5 empty] | 25 | 29 | 585 |  | 2020-09-17 12:00 | 12:00 | 25 | 29 | 585 |  | low | 2020-09-14 | B14895¦Administration Office North¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 20 | 44 | 476 |  | 2020-09-17 12:00 | 12:00 | 20 | 44 | 476 |  |  | 2020-09-14 | B70050¦2nd Floor Holding Cell¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-8 | [5 empty] | 20.8 | 52.8 | 671 |  | 2020-09-17 12:00 | 12:00 | 20.8 | 52.8 | 671 |  |  | 2020-09-14 | B10644¦Courtroom 2-8¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office South | [5 empty] | 24 | 25 | 523 |  | 2020-09-17 12:00 | 12:00 | 24 | 25 | 523 |  | low | 2020-09-14 | B14895¦Administration Office South¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 3-2 | [5 empty] | 22.3 | 57.5 | 460 |  | 2020-09-17 12:00 | 12:00 | 22.3 | 57.5 | 460 |  |  | 2020-09-14 | B10644¦Courtroom 3-2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Yannick Bedard Office - 2nd Floor | [5 empty] | 21 | 45 | 601 |  | 2020-09-17 12:00 | 12:00 | 21 | 45 | 601 |  |  | 2020-09-14 | B70050¦Yannick Bedard Office - 2nd Floor¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-1 | [5 empty] | 22.7 | 58 | 505 |  | 2020-09-17 12:00 | 12:00 | 22.7 | 58 | 505 |  |  | 2020-09-14 | B10644¦Courtroom 4-1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 2 | [5 empty] | 21 | 45 | 570 |  | 2020-09-17 12:00 | 12:00 | 21 | 45 | 570 |  |  | 2020-09-14 | B70050¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main entrance | [5 empty] | 25 | 25 | 582 |  | 2020-09-17 12:00 | 12:00 | 25 | 25 | 582 |  | low | 2020-09-14 | B14895¦Main entrance¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-2 | [5 empty] | 21.3 | 56 | 443 |  | 2020-09-17 12:00 | 12:00 | 21.3 | 56 | 443 |  |  | 2020-09-14 | B10644¦Courtroom 4-2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main Floor Waiting Area | [5 empty] | 25 | 26 | 561 |  | 2020-09-17 12:00 | 12:00 | 25 | 26 | 561 |  | low | 2020-09-14 | B14895¦Main Floor Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd fl lobby | [5 empty] | 20 | 43 | 481 |  | 2020-09-17 12:00 | 12:00 | 20 | 43 | 481 |  |  | 2020-09-14 | B70050¦2nd fl lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom A | [5 empty] | 23 | 26 | 527 |  | 2020-09-17 12:00 | 12:00 | 23 | 26 | 527 |  | low | 2020-09-14 | B14895¦Courtroom A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom B | [5 empty] | 24 | 26 | 609 |  | 2020-09-17 12:00 | 12:00 | 24 | 26 | 609 |  | low | 2020-09-14 | B14895¦Courtroom B¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-3 | [5 empty] | 23.2 | 55.5 | 405 |  | 2020-09-17 12:00 | 12:00 | 23.2 | 55.5 | 405 |  |  | 2020-09-14 | B10644¦Courtroom 4-3¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-4 | [5 empty] | 22.3 | 57.8 | 542 |  | 2020-09-17 12:00 | 12:00 | 22.3 | 57.8 | 542 |  |  | 2020-09-14 | B10644¦Courtroom 4-4¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | 2nd Floor Waiting Area | [5 empty] | 24 | 27 | 553 |  | 2020-09-17 12:00 | 12:00 | 24 | 27 | 553 |  | low | 2020-09-14 | B14895¦2nd Floor Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-6 | [5 empty] | 22.7 | 57.9 | 436 |  | 2020-09-17 12:00 | 12:00 | 22.7 | 57.9 | 436 |  |  | 2020-09-14 | B10644¦Courtroom 4-6¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Crown Attorney Office | [5 empty] | 24 | 33 | 495 |  | 2020-09-17 12:00 | 12:00 | 24 | 33 | 495 |  | low | 2020-09-14 | B14895¦Crown Attorney Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Waiting Area | [5 empty] | 24 | 25 | 473 |  | 2020-09-17 12:00 | 12:00 | 24 | 25 | 473 |  | low | 2020-09-14 | B14895¦Basement Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-7 | [5 empty] | 22.8 | 60.4 | 446 |  | 2020-09-17 12:00 | 12:00 | 22.8 | 60.4 | 446 |  | caution | 2020-09-14 | B10644¦Courtroom 4-7¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Boardroom | [5 empty] | 25 | 32 | 442 |  | 2020-09-17 12:00 | 12:00 | 25 | 32 | 442 |  | low | 2020-09-14 | B14895¦Basement Boardroom¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-8 | [5 empty] | 23.2 | 54.1 | 416 |  | 2020-09-17 12:00 | 12:00 | 23.2 | 54.1 | 416 |  |  | 2020-09-14 | B10644¦Courtroom 4-8¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Male Holding Cell | [5 empty] | 24 | 29 | 503 |  | 2020-09-17 12:00 | 12:00 | 24 | 29 | 503 |  | low | 2020-09-14 | B14895¦Male Holding Cell¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Female Holding Cell | [5 empty] | 24 | 25 | 603 |  | 2020-09-17 12:00 | 12:00 | 24 | 25 | 603 |  | low | 2020-09-14 | B14895¦Female Holding Cell¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22.9 | 54.6 | 520 |  | 2020-09-17 12:00 | 12:00 | 22.9 | 54.6 | 520 |  |  | 2020-09-14 | B10644¦Courtroom 5-1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Outdoors |  |  | 16 | 18 | 395 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B14895¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-1 | [5 empty] | 19.9 | 52.6 | 448 |  | 2020-09-17 12:00 | 12:00 | 19.9 | 52.6 | 448 |  |  | 2020-09-14 | B10644¦Courtroom 6-1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 1 | [5 empty] | 22 | 40 | 461 |  | 2020-09-17 12:00 | 12:00 | 22 | 40 | 461 |  | caution | 2020-09-14 | B25602¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 2 | [5 empty] | 22 | 37 | 470 |  | 2020-09-17 12:00 | 12:00 | 22 | 37 | 470 |  | caution | 2020-09-14 | B25602¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 3 | [5 empty] | 22 | 35 | 496 |  | 2020-09-17 12:00 | 12:00 | 22 | 35 | 496 |  | caution | 2020-09-14 | B25602¦Courtroom 3¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 4 | [5 empty] | 23 | 37 | 453 |  | 2020-09-17 12:00 | 12:00 | 23 | 37 | 453 |  | caution | 2020-09-14 | B25602¦Courtroom 4¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 101 | [5 empty] | 21 | 52 | 529 |  | 2020-09-17 15:00 | 15:00 | 21 | 52 | 529 |  |  | 2020-09-14 | B19512¦Courtroom 101¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-1, 16th Floor OTHER | [5 empty] | 22 | 46 | 733 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 733 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-1, 16th Floor OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 200 | [5 empty] | 22.2 | 48 | 552 |  | 2020-09-17 15:00 | 15:00 | 22.2 | 48 | 552 |  |  | 2020-09-14 | B19512¦Courtroom 200¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 5 | [5 empty] | 35 | 35 | 417 |  | 2020-09-17 12:00 | 12:00 | 35 | 35 | 417 | high | caution | 2020-09-14 | B25602¦Courtroom 5¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 201 | [5 empty] | 23 | 48 | 552 |  | 2020-09-17 15:00 | 15:00 | 23 | 48 | 552 |  |  | 2020-09-14 | B19512¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 6 | [5 empty] | 23 | 38 | 490 |  | 2020-09-17 12:00 | 12:00 | 23 | 38 | 490 |  | caution | 2020-09-14 | B25602¦Courtroom 6¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 201 | [5 empty] | 23 | 48 | 552 |  | 2020-09-17 15:00 | 15:00 | 23 | 48 | 552 |  |  | 2020-09-14 | B19512¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Outdoors |  |  | 6 | 54 | 536 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10000¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Outdoors |  |  | 10 | 44 | 498 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10000¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Outdoors |  |  | 21 | 49 | [5 empty] | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B19512¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Outdoors |  |  | 13 | 43 | 506 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10000¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 7 | [5 empty] | 23 | 36 | 468 |  | 2020-09-17 12:00 | 12:00 | 23 | 36 | 468 |  | caution | 2020-09-14 | B25602¦Courtroom 7¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-3, 16th Floor OTHER | [5 empty] | 21 | 46 | 732 |  | 2020-09-17 12:00 | 12:00 | 21 | 46 | 732 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-3, 16th Floor OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 1 | [5 empty] | 20.5556 | 40 | 471 |  | 2020-09-17 09:00 | 9:00 | 20.5556 | 40 | 471 |  | caution | 2020-09-14 | B10000¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Outdoors |  |  | 14 | 53 | 678 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B25602¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 1 | [5 empty] | 21.1111 | 36 | 467 |  | 2020-09-17 12:00 | 12:00 | 21.1111 | 36 | 467 |  | caution | 2020-09-14 | B10000¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Washrooms, 16th Floor OTHER | [5 empty] | 21 | 47 | 709 |  | 2020-09-17 12:00 | 12:00 | 21 | 47 | 709 |  |  | 2020-09-14 | B25398¦Corridor adj. to Washrooms, 16th Floor OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 1 | [5 empty] | 21.1111 | 34 | 480 |  | 2020-09-17 15:00 | 15:00 | 21.1111 | 34 | 480 |  | low | 2020-09-14 | B10000¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 16th Floor OTHER | [5 empty] | 22 | 47 | 718 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 718 |  |  | 2020-09-14 | B25398¦Elevator Lobby, 16th Floor OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 2 | [5 empty] | 23.8889 | 32 | 439 |  | 2020-09-17 09:00 | 9:00 | 23.8889 | 32 | 439 |  | low | 2020-09-14 | B10000¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Women's Washroom, 16th Floor | [5 empty] | 21 | 47 | 705 |  | 2020-09-17 12:00 | 12:00 | 21 | 47 | 705 |  |  | 2020-09-14 | B25398¦OTHER Women's Washroom, 16th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 2 | [5 empty] | 23.8889 | 24 | 435 |  | 2020-09-17 12:00 | 12:00 | 23.8889 | 24 | 435 |  | low | 2020-09-14 | B10000¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Outdoors |  |  | 20 | 52 | 341 |  |  |  | Base Readings | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B25165¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, West, 15th Floor | [5 empty] | 21 | 50 | 725 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 725 |  |  | 2020-09-14 | B25398¦OTHER Office Area, West, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 2 | [5 empty] | 23.3333 | 23 | 435 |  | 2020-09-17 15:00 | 15:00 | 23.3333 | 23 | 435 |  | low | 2020-09-14 | B10000¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 101 | [5 empty] | 21 | 49 |  |  | 2020-09-17 15:00 | 15:00 | 21 | 49 |  |  |  | 2020-09-14 | B20080¦Courtroom 101¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | OTHER | [5 empty] | 21 | 48 | 440 | Courtroom 700, Please add to drop down box , thank you | 2020-09-17 15:00 | 15:00 | 21 | 48 | 440 |  |  | 2020-09-14 | B25165¦OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 3 | [5 empty] | 21.6667 | 39 | 439 |  | 2020-09-17 09:00 | 9:00 | 21.6667 | 39 | 439 |  | caution | 2020-09-14 | B10000¦Courtroom 3¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North West, 15th Floor | [5 empty] | 21 | 49 | 719 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 719 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North West, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 201 | [5 empty] | 22 | 47 | 448 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 448 |  |  | 2020-09-14 | B20080¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 3 | [5 empty] | 21.6667 | 34 | 456 |  | 2020-09-17 12:00 | 12:00 | 21.6667 | 34 | 456 |  | low | 2020-09-14 | B10000¦Courtroom 3¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 202 | [5 empty] | 23 | 47 | 438 |  | 2020-09-17 15:00 | 15:00 | 23 | 47 | 438 |  |  | 2020-09-14 | B20080¦Courtroom 202¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North, 15th Floor | [5 empty] | 21 | 49 | 722 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 722 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 3 | [5 empty] | 21.6667 | 32 | 434 |  | 2020-09-17 15:00 | 15:00 | 21.6667 | 32 | 434 |  | low | 2020-09-14 | B10000¦Courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North Easr, 15th Floor | [5 empty] | 21 | 49 | 725 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 725 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North Easr, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 4 | [5 empty] | 20.5556 | 28 | 458 |  | 2020-09-17 09:00 | 9:00 | 20.5556 | 28 | 458 |  | low | 2020-09-14 | B10000¦Courtroom 4¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 301 | [5 empty] | 22 | 47 | 446 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 446 |  |  | 2020-09-14 | B20080¦Courtroom 301¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 4 | [5 empty] | 22.2222 | 27 | 488 |  | 2020-09-17 12:00 | 12:00 | 22.2222 | 27 | 488 |  | low | 2020-09-14 | B10000¦Courtroom 4¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, East, 15th Floor | [5 empty] | 21 | 49 | 728 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 728 |  |  | 2020-09-14 | B25398¦OTHER Office Area, East, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 302 | [5 empty] | 22 | 47 | 441 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 441 |  |  | 2020-09-14 | B20080¦Courtroom 302¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 4 | [5 empty] | 22.2222 | 20 | 434 |  | 2020-09-17 15:00 | 15:00 | 22.2222 | 20 | 434 |  | low | 2020-09-14 | B10000¦Courtroom 4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 303 | [5 empty] | 22 | 47 | 465 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 465 |  |  | 2020-09-14 | B20080¦Courtroom 303¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South East, 15th Floor | [5 empty] | 21 | 48 | 717 |  | 2020-09-17 12:00 | 12:00 | 21 | 48 | 717 |  |  | 2020-09-14 | B25398¦OTHER Office Area, South East, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 600 | [5 empty] | 21 | 48 | 437 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 437 |  |  | 2020-09-14 | B25165¦Courtroom 600¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 5 | [5 empty] | 21.6667 | 38 | 450 |  | 2020-09-17 09:00 | 9:00 | 21.6667 | 38 | 450 |  | caution | 2020-09-14 | B10000¦Courtroom 5¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | front seating area | [5 empty] | 22 | 50 | 409 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 409 |  |  | 2020-09-14 | B18359¦front seating area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 308 | [5 empty] | 22 | 48 | 496 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 496 |  |  | 2020-09-14 | B25165¦Courtroom 308¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South, 15th Floor | [5 empty] | 21 | 48 | 722 |  | 2020-09-17 12:00 | 12:00 | 21 | 48 | 722 |  |  | 2020-09-14 | B25398¦OTHER Office Area, South, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 5 | [5 empty] | 21.1111 | 32 | 474 |  | 2020-09-17 12:00 | 12:00 | 21.1111 | 32 | 474 |  | low | 2020-09-14 | B10000¦Courtroom 5¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Northwest corridor | [5 empty] | 22 | 50 | 407 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 407 |  |  | 2020-09-14 | B18359¦Northwest corridor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 306 | [5 empty] | 21 | 48 | 441 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 441 |  |  | 2020-09-14 | B25165¦Courtroom 306¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Outdoors |  |  | 17 | 67 | 415 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20080¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 5 | [5 empty] | 21.6667 | 30 | 472 |  | 2020-09-17 15:00 | 15:00 | 21.6667 | 30 | 472 |  | low | 2020-09-14 | B10000¦Courtroom 5¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Reception, 15th Floor | [5 empty] | 22 | 47 | 720 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 720 |  |  | 2020-09-14 | B25398¦OTHER Reception, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 302 | [5 empty] | 21 | 48 | 483 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 483 |  |  | 2020-09-14 | B25165¦Courtroom 302¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 6 | [5 empty] | 21.1111 | 38 | 450 |  | 2020-09-17 09:00 | 9:00 | 21.1111 | 38 | 450 |  | caution | 2020-09-14 | B10000¦Courtroom 6¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 208 | [5 empty] | 21 | 48 | 441 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 441 |  |  | 2020-09-14 | B25165¦Courtroom 208¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 6 | [5 empty] | 21.6667 | 32 | 474 |  | 2020-09-17 12:00 | 12:00 | 21.6667 | 32 | 474 |  | low | 2020-09-14 | B10000¦Courtroom 6¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Mail Room, 15th Floor OTHER | [5 empty] | 22 | 48 | 727 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 727 |  |  | 2020-09-14 | B25398¦Corridor adj. to Mail Room, 15th Floor OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 206 | [5 empty] | 21 | 48 | 432 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 432 |  |  | 2020-09-14 | B25165¦Courtroom 206¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 6 | [5 empty] | 22.2222 | 30 | 472 |  | 2020-09-17 15:00 | 15:00 | 22.2222 | 30 | 472 |  | low | 2020-09-14 | B10000¦Courtroom 6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 204 | [5 empty] | 22 | 48 | 501 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 501 |  |  | 2020-09-14 | B25165¦Courtroom 204¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 15th Floor OTHER | [5 empty] | 22 | 47 | 721 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 721 |  |  | 2020-09-14 | B25398¦Elevator Lobby, 15th Floor OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 7 | [5 empty] | 21.6667 | 35 | 430 |  | 2020-09-17 09:00 | 9:00 | 21.6667 | 35 | 430 |  | caution | 2020-09-14 | B10000¦Courtroom 7¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 7 | [5 empty] | 21.6667 | 29 | 481 |  | 2020-09-17 12:00 | 12:00 | 21.6667 | 29 | 481 |  | low | 2020-09-14 | B10000¦Courtroom 7¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 202 | [5 empty] | 21 | 48 | 456 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 456 |  |  | 2020-09-14 | B25165¦Courtroom 202¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Outdoors |  |  | 18 | 54 | 668 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B25398¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 7 | [5 empty] | 22.2222 | 32 | 437 |  | 2020-09-17 15:00 | 15:00 | 22.2222 | 32 | 437 |  | low | 2020-09-14 | B10000¦Courtroom 7¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 200 | [5 empty] | 21 | 48 | 449 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 449 |  |  | 2020-09-14 | B25165¦Courtroom 200¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 22 | 50 | 403 | north side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 403 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 100 | [5 empty] | 22 | 48 | 454 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 454 |  |  | 2020-09-14 | B25165¦Courtroom 100¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 8 | [5 empty] | 21.1111 | 32 | 470 |  | 2020-09-17 09:00 | 9:00 | 21.1111 | 32 | 470 |  | low | 2020-09-14 | B10000¦Courtroom 8¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 201 | [5 empty] | 22 | 51 | 411 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 411 |  |  | 2020-09-14 | B70003¦Courtroom 201¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 8 | [5 empty] | 22.2222 | 24 | 434 |  | 2020-09-17 12:00 | 12:00 | 22.2222 | 24 | 434 |  | low | 2020-09-14 | B10000¦Courtroom 8¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 8 | [5 empty] | 21.1111 | 24 | 421 |  | 2020-09-17 15:00 | 15:00 | 21.1111 | 24 | 421 |  | low | 2020-09-14 | B10000¦Courtroom 8¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 9 | [5 empty] | 21.1111 | 38 | 450 |  | 2020-09-17 12:00 | 12:00 | 21.1111 | 38 | 450 |  | caution | 2020-09-14 | B10000¦Courtroom 9¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 22 | 51 | 405 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 405 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 9 | [5 empty] | 21.1111 | 32 | 474 |  | 2020-09-17 12:00 | 12:00 | 21.1111 | 32 | 474 |  | low | 2020-09-14 | B10000¦Courtroom 9¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 22 | 51 | 408 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 408 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 9 | [5 empty] | 22.2222 | 30 | 472 |  | 2020-09-17 15:00 | 15:00 | 22.2222 | 30 | 472 |  | low | 2020-09-14 | B10000¦Courtroom 9¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 22 | 51 | 409 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 409 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 22 | 51 | 412 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 412 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 22 | 51 | 410 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 410 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Entry/Waiting | [5 empty] | 23 | 45 | 486 |  | 2020-09-17 15:00 | 15:00 | 23 | 45 | 486 |  |  | 2020-09-14 | B70510¦Entry/Waiting¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 22 | 50 | 410 | south side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 410 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 22 | 50 | 408 | north side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 408 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 1 | [5 empty] | 24 | 48 | 398 |  | 2020-09-17 15:00 | 15:00 | 24 | 48 | 398 |  |  | 2020-09-14 | B24638¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 22 | 50 | 410 | south side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 410 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 3 | [5 empty] | 24 | 46 | 362 |  | 2020-09-17 15:00 | 15:00 | 24 | 46 | 362 |  |  | 2020-09-14 | B24638¦Courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 22 | 51 | 401 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 401 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Outdoors |  |  | 18 | 28 | 420 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B12948¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 22 | 51 | 405 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 405 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Outdoors |  |  | 23 | 47 | 351 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B24638¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 1 | [5 empty] | 21 | 29 | 424 |  | 2020-09-17 15:00 | 15:00 | 21 | 29 | 424 |  | low | 2020-09-14 | B12948¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 22 | 51 | 423 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 423 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 | [5 empty] | 21 | 29 | 430 |  | 2020-09-17 15:00 | 15:00 | 21 | 29 | 430 |  | low | 2020-09-14 | B12948¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room A | [5 empty] | 23 | 44 | 548 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 548 |  |  | 2020-09-14 | B70510¦Mediation Room A¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 22 | 51 | 422 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 422 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Information Desk | [5 empty] | 23 | 44 | 463 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 463 |  |  | 2020-09-14 | B70510¦Information Desk¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 | [5 empty] | 21 | 29 | 430 |  | 2020-09-17 15:00 | 15:00 | 21 | 29 | 430 |  | low | 2020-09-14 | B12948¦Courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 22 | 51 | 403 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 403 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Lunch Room 454 | [5 empty] | 23 | 44 | 450 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 450 |  |  | 2020-09-14 | B70510¦Lunch Room 454¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 | [5 empty] | 21 | 29 | 441 |  | 2020-09-17 15:00 | 15:00 | 21 | 29 | 441 |  | low | 2020-09-14 | B12948¦Courtroom 4¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 22 | 51 | 415 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 415 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Copy Room 455 | [5 empty] | 23 | 44 | 450 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 450 |  |  | 2020-09-14 | B70510¦Copy Room 455¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 22 | 51 | 409 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 409 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 | [5 empty] | 21 | 30 | 412 |  | 2020-09-17 15:00 | 15:00 | 21 | 30 | 412 |  | low | 2020-09-14 | B12948¦Courtroom 5¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 22 | 50 | 411 | south side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 411 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room B | [5 empty] | 23 | 46 | 470 |  | 2020-09-17 15:00 | 15:00 | 23 | 46 | 470 |  |  | 2020-09-14 | B70510¦Mediation Room B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 6 | [5 empty] | 21 | 30 | 410 |  | 2020-09-17 15:00 | 15:00 | 21 | 30 | 410 |  | low | 2020-09-14 | B12948¦Courtroom 6¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | northeast corridor | [5 empty] | 22 | 51 | 410 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 410 |  |  | 2020-09-14 | B18359¦northeast corridor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 459 | [5 empty] | 23 | 44 | 456 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 456 |  |  | 2020-09-14 | B70510¦Office 459¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Cell Basement | [5 empty] | 21 | 32 | 460 |  | 2020-09-17 15:00 | 15:00 | 21 | 32 | 460 |  | low | 2020-09-14 | B12948¦Cell Basement¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 22 | 50 | 405 | north side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 405 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | office 467 | [5 empty] | 23 | 44 | 457 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 457 |  |  | 2020-09-14 | B70510¦office 467¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 22 | 50 | 410 | south side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 410 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 469 | [5 empty] | 23 | 44 | 461 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 461 |  |  | 2020-09-14 | B70510¦Office 469¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 1 | [5 empty] | 22 | 37 | 448 |  | 2020-09-17 15:00 | 15:00 | 22 | 37 | 448 |  | caution | 2020-09-14 | B25602¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 22 | 50 | 400 | north side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 400 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Room 473 (Printer) | [5 empty] | 23 | 44 | 463 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 463 |  |  | 2020-09-14 | B70510¦Room 473 (Printer)¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 22 | 51 | 402 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 402 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hall 475 or 466 | [5 empty] | 23 | 44 | 463 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 463 |  |  | 2020-09-14 | B70510¦Hall 475 or 466¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 22 | 51 | 400 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 400 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 1 | [5 empty] | 22 | 44 | 467 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 467 |  |  | 2020-09-14 | B70510¦Hearing Room 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 22 | 51 | 407 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 407 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 2 | [5 empty] | 22 | 36 | 446 |  | 2020-09-17 15:00 | 15:00 | 22 | 36 | 446 |  | caution | 2020-09-14 | B25602¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Cell Basement | [5 empty] | 21 | 32 | 460 |  | 2020-09-17 15:00 | 15:00 | 21 | 32 | 460 |  | low | 2020-09-14 | B12948¦Cell Basement¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Meeting Rooms 1/2 | [5 empty] | 22 | 45 | 508 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 508 |  |  | 2020-09-14 | B70510¦Vestibule at Meeting Rooms 1/2¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 22 | 50 | 408 | north side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 408 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration Office Waiting Area | [5 empty] | 22 | 32 | 424 |  | 2020-09-17 15:00 | 15:00 | 22 | 32 | 424 |  | low | 2020-09-14 | B12948¦Administration Office Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Outdoors |  |  | 18 | 67 | [5 empty] | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20619¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtrooom 213 | [5 empty] | 22 | 50 | 411 | south side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 411 |  |  | 2020-09-14 | B18359¦courtrooom 213¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Hearing Room 1 | [5 empty] | 22 | 46 | 476 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 476 |  |  | 2020-09-14 | B70510¦Vestibule at Hearing Room 1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 8 | [5 empty] | 22 | 45 | 427 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 427 |  |  | 2020-09-14 | B25683¦Courtroom 8¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 22 | 50 | 408 | north side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 408 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration office | [5 empty] | 22 | 33 | 421 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 421 |  | low | 2020-09-14 | B12948¦Administration office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 11 | [5 empty] | 22 | 45 | 427 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 427 |  |  | 2020-09-14 | B25683¦Courtroom 11¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 2 | [5 empty] | 22 | 46 | 461 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 461 |  |  | 2020-09-14 | B70510¦Hearing Room 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Courtroom 1-14 | [5 empty] | 23 | 49 | 574 |  | 2020-09-17 15:00 | 15:00 | 23 | 49 | 574 |  |  | 2020-09-14 | B20619¦Courtroom 1-14¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 22 | 50 | 401 | south side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 401 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 9 | [5 empty] | 22 | 41 | 432 |  | 2020-09-17 15:00 | 15:00 | 22 | 41 | 432 |  |  | 2020-09-14 | B25683¦Courtroom 9¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 3 | [5 empty] | 22 | 34 | 426 |  | 2020-09-17 15:00 | 15:00 | 22 | 34 | 426 |  | low | 2020-09-14 | B25602¦Courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 22 | 50 | 404 | north side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 404 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 439 | [5 empty] | 23 | 45 | 452 |  | 2020-09-17 15:00 | 15:00 | 23 | 45 | 452 |  |  | 2020-09-14 | B70510¦Office 439¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Crown attorney admin area | [5 empty] | 22 | 33 | 534 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 534 |  | low | 2020-09-14 | B12948¦Crown attorney admin area¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 22 | 50 | 406 | south side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 406 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | First Aid Desk | [5 empty] | 22 | 46 | 453 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 453 |  |  | 2020-09-14 | B70510¦First Aid Desk¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main entrance | [5 empty] | 22 | 31 | 446 |  | 2020-09-17 15:00 | 15:00 | 22 | 31 | 446 |  | low | 2020-09-14 | B12948¦Main entrance¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Outdoors |  |  | 22 | 56 | 397 |  |  |  | outside of 15 Grosvenor Ave. | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B18359¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 436 | [5 empty] | 23 | 45 | 451 |  | 2020-09-17 15:00 | 15:00 | 23 | 45 | 451 |  |  | 2020-09-14 | B70510¦Office 436¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main Entrance Waiting Area | [5 empty] | 22 | 31 | 420 |  | 2020-09-17 15:00 | 15:00 | 22 | 31 | 420 |  | low | 2020-09-14 | B12948¦Main Entrance Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 432 | [5 empty] | 23 | 45 | 461 |  | 2020-09-17 15:00 | 15:00 | 23 | 45 | 461 |  |  | 2020-09-14 | B70510¦Office 432¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Court Room 1 Waiting Area | [5 empty] | 22 | 31 | 425 |  | 2020-09-17 15:00 | 15:00 | 22 | 31 | 425 |  | low | 2020-09-14 | B12948¦Court Room 1 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 4 | [5 empty] | 23 | 36 | 444 |  | 2020-09-17 15:00 | 15:00 | 23 | 36 | 444 |  | caution | 2020-09-14 | B25602¦Courtroom 4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 429 | [5 empty] | 23 | 45 | 468 |  | 2020-09-17 15:00 | 15:00 | 23 | 45 | 468 |  |  | 2020-09-14 | B70510¦Office 429¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 Waiting Area | [5 empty] | 22 | 31 | 435 |  | 2020-09-17 15:00 | 15:00 | 22 | 31 | 435 |  | low | 2020-09-14 | B12948¦Courtroom 2 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20893 | B20893 - 75 Mulcaster St. - Barrie | Courtroom 7,8,9 | [5 empty] | 23 | 38 | 527 |  | 2020-09-17 15:00 | 15:00 | 23 | 38 | 527 |  | caution | 2020-09-14 | B20893¦Courtroom 7,8,9¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 427 | [5 empty] | 23 | 44 | 458 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 458 |  |  | 2020-09-14 | B70510¦Office 427¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 Waiting Area | [5 empty] | 22 | 31 | 450 |  | 2020-09-17 15:00 | 15:00 | 22 | 31 | 450 |  | low | 2020-09-14 | B12948¦Courtroom 3 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 4 | [5 empty] | 23 | 35 | 420 |  | 2020-09-17 15:00 | 15:00 | 23 | 35 | 420 |  | caution | 2020-09-14 | B25602¦Courtroom 4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mail Room | [5 empty] | 23 | 44 | 460 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 460 |  |  | 2020-09-14 | B70510¦Mail Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92347 | B92347 - 75 Mulcaster Street - Barrie | Courtroom 15 | [5 empty] | 21 | 43 | 527 |  | 2020-09-17 15:00 | 15:00 | 21 | 43 | 527 |  |  | 2020-09-14 | B92347¦Courtroom 15¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 Waiting Area | [5 empty] | 22 | 31 | 447 |  | 2020-09-17 15:00 | 15:00 | 22 | 31 | 447 |  | low | 2020-09-14 | B12948¦Courtroom 5 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 6 | [5 empty] | 23 | 37 | 454 |  | 2020-09-17 15:00 | 15:00 | 23 | 37 | 454 |  | caution | 2020-09-14 | B25602¦Courtroom 6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 420 | [5 empty] | 23 | 44 | 460 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 460 |  |  | 2020-09-14 | B70510¦Office 420¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 and 6 Waiting Area | [5 empty] | 22 | 31 | 430 |  | 2020-09-17 15:00 | 15:00 | 22 | 31 | 430 |  | low | 2020-09-14 | B12948¦Courtroom 4 and 6 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 7 | [5 empty] | 23 | 35 | 450 |  | 2020-09-17 15:00 | 15:00 | 23 | 35 | 450 |  | caution | 2020-09-14 | B25602¦Courtroom 7¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 418 | [5 empty] | 23 | 44 | 465 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 465 |  |  | 2020-09-14 | B70510¦Office 418¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Crown Attorney Office | [5 empty] | 22 | 34 | 443 |  | 2020-09-17 12:00 | 12:00 | 22 | 34 | 443 |  | low | 2020-09-14 | B20016¦Crown Attorney Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | File Room | [5 empty] | 23 | 44 | 460 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 460 |  |  | 2020-09-14 | B70510¦File Room¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Legal Aid Ontario | [5 empty] | 22 | 33 | 442 |  | 2020-09-17 12:00 | 12:00 | 22 | 33 | 442 |  | low | 2020-09-14 | B20016¦Legal Aid Ontario¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Health Room | [5 empty] | 23 | 44 | 465 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 465 |  |  | 2020-09-14 | B70510¦Health Room¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel Waiting Area | [5 empty] | 23 | 32 | 441 |  | 2020-09-17 12:00 | 12:00 | 23 | 32 | 441 |  | low | 2020-09-14 | B20016¦Duty Counsel Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 | [5 empty] | 23 | 44 | 484 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 484 |  |  | 2020-09-14 | B70510¦Hearing Room 3¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Outdoors |  |  | 15 | 51 | 677 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B25602¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 Waiting Area | [5 empty] | 23 | 46 | 460 |  | 2020-09-17 15:00 | 15:00 | 23 | 46 | 460 |  |  | 2020-09-14 | B70510¦Hearing Room 3 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Elevator Lobby | [5 empty] | 22 | 45 | 456 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 456 |  |  | 2020-09-14 | B70510¦Elevator Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel | [5 empty] | 22 | 35 | 445 |  | 2020-09-17 12:00 | 12:00 | 22 | 35 | 445 |  | caution | 2020-09-14 | B20016¦Duty Counsel¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lobby Courtroom 1 - 2 | [5 empty] | 22 | 33 | 460 |  | 2020-09-17 12:00 | 12:00 | 22 | 33 | 460 |  | low | 2020-09-14 | B20016¦Lobby Courtroom 1 - 2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Main Lobby | [5 empty] | 22 | 34 | 498 |  | 2020-09-17 12:00 | 12:00 | 22 | 34 | 498 |  | low | 2020-09-14 | B20016¦Main Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lower Hallway | [5 empty] | 22 | 33 | 463 |  | 2020-09-17 12:00 | 12:00 | 22 | 33 | 463 |  | low | 2020-09-14 | B20016¦Lower Hallway¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | OTHER | [5 empty] | 21 | 33 | 472 | Courtroom 1-2-3 | 2020-09-17 12:00 | 12:00 | 21 | 33 | 472 |  | low | 2020-09-14 | B20016¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Outdoors |  |  | 23 | 35 | 448 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70510¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation | [5 empty] | 21 | 35 | 461 |  | 2020-09-17 12:00 | 12:00 | 21 | 35 | 461 |  | caution | 2020-09-14 | B20016¦Family Mediation¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation Across Stairs | [5 empty] | 20 | 34 | 491 |  | 2020-09-17 12:00 | 12:00 | 20 | 34 | 491 |  | low | 2020-09-14 | B20016¦Family Mediation Across Stairs¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Outdoors |  |  | 12 | 57 | 418 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B90838¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Main Lobby | [5 empty] | 19 | 45 | 458 |  | 2020-09-17 12:00 | 12:00 | 19 | 45 | 458 |  |  | 2020-09-14 | B19523¦Main Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Courtroom 101 Courtroom 102 | [5 empty] | 21 | 42 | 433 |  | 2020-09-17 15:00 | 15:00 | 21 | 42 | 433 |  |  | 2020-09-14 | B90838¦Courtroom 101 Courtroom 102¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Holding Cell | [5 empty] | 21 | 41 | 522 |  | 2020-09-17 12:00 | 12:00 | 21 | 41 | 522 |  |  | 2020-09-14 | B19523¦Holding Cell¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd fl lobby | [5 empty] | 21 | 33 | 718 |  | 2020-09-17 15:00 | 15:00 | 21 | 33 | 718 |  | low | 2020-09-14 | B20226¦2nd fl lobby¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 1 | [5 empty] | 21 | 41 | 440 |  | 2020-09-17 12:00 | 12:00 | 21 | 41 | 440 |  |  | 2020-09-14 | B19523¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Court Services | [5 empty] | 21 | 35 | 503 |  | 2020-09-17 12:00 | 12:00 | 21 | 35 | 503 |  | caution | 2020-09-14 | B19523¦Court Services¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | JP Office | [5 empty] | 21 | 39 | 455 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 455 |  | caution | 2020-09-14 | B19523¦JP Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 2 | [5 empty] | 21 | 32 | 660 |  | 2020-09-17 15:00 | 15:00 | 21 | 32 | 660 |  | low | 2020-09-14 | B20226¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | OPP Office | [5 empty] | 21 | 40 | 438 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 438 |  | caution | 2020-09-14 | B19523¦OPP Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Crown Attorney Office | [5 empty] | 21 | 42 | 447 |  | 2020-09-17 12:00 | 12:00 | 21 | 42 | 447 |  |  | 2020-09-14 | B19523¦Crown Attorney Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 42 | 468 |  | 2020-09-17 12:00 | 12:00 | 22 | 42 | 468 |  |  | 2020-09-14 | B19523¦VWAP Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 1 | [5 empty] | 21 | 34 | 814 |  | 2020-09-17 15:00 | 15:00 | 21 | 34 | 814 |  | low | 2020-09-14 | B20226¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 23 | 40 | 514 |  | 2020-09-17 12:00 | 12:00 | 23 | 40 | 514 |  | caution | 2020-09-14 | B19523¦VWAP Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 | [5 empty] | 23 | 48 | 481 |  | 2020-09-17 12:00 | 12:00 | 23 | 48 | 481 |  |  | 2020-09-14 | B14209¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 5 | [5 empty] | 21 | 38 | 429 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 429 |  | caution | 2020-09-14 | B19523¦Courtroom 5¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 - waiting area | [5 empty] | 22 | 48 | 490 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 490 |  |  | 2020-09-14 | B14209¦Courtroom 1 - waiting area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office North | [5 empty] | 24 | 31 | 755 |  | 2020-09-17 15:00 | 15:00 | 24 | 31 | 755 |  | low | 2020-09-14 | B14895¦Administration Office North¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 22 | 33 | 707 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 707 |  | low | 2020-09-14 | B20226¦2nd Floor Holding Cell¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 | [5 empty] | 22 | 46 | 471 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 471 |  |  | 2020-09-14 | B14209¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office South | [5 empty] | 23 | 26 | 570 |  | 2020-09-17 15:00 | 15:00 | 23 | 26 | 570 |  | low | 2020-09-14 | B14895¦Administration Office South¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 - waiting room | [5 empty] | 22 | 46 | 460 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 460 |  |  | 2020-09-14 | B14209¦Courtroom 2 - waiting room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Remote Testimony Room | [5 empty] | 21 | 39 | 435 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 435 |  | caution | 2020-09-14 | B19523¦Remote Testimony Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Conference Room 2 | [5 empty] | 21 | 41 | 434 |  | 2020-09-17 12:00 | 12:00 | 21 | 41 | 434 |  |  | 2020-09-14 | B19523¦Conference Room 2¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main entrance | [5 empty] | 22 | 37 | 587 |  | 2020-09-17 15:00 | 15:00 | 22 | 37 | 587 |  | caution | 2020-09-14 | B14895¦Main entrance¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 | [5 empty] | 21 | 40 | 429 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 429 |  | caution | 2020-09-14 | B19523¦Courtroom 3¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main Floor Waiting Area | [5 empty] | 24 | 27 | 588 |  | 2020-09-17 15:00 | 15:00 | 24 | 27 | 588 |  | low | 2020-09-14 | B14895¦Main Floor Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 Waiting Area | [5 empty] | 21 | 40 | 442 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 442 |  | caution | 2020-09-14 | B19523¦Courtroom 3 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom A | [5 empty] | 23 | 28 | 476 |  | 2020-09-17 15:00 | 15:00 | 23 | 28 | 476 |  | low | 2020-09-14 | B14895¦Courtroom A¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 40 | 464 |  | 2020-09-17 12:00 | 12:00 | 20 | 40 | 464 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom B | [5 empty] | 23 | 27 | 454 |  | 2020-09-17 15:00 | 15:00 | 23 | 27 | 454 |  | low | 2020-09-14 | B14895¦Courtroom B¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 21 | 40 | 476 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 476 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | 2nd Floor Waiting Area | [5 empty] | 24 | 28 | 605 |  | 2020-09-17 15:00 | 15:00 | 24 | 28 | 605 |  | low | 2020-09-14 | B14895¦2nd Floor Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 3 | [5 empty] | 22 | 28 | 547 |  | 2020-09-17 15:00 | 15:00 | 22 | 28 | 547 |  | low | 2020-09-14 | B20226¦Courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 40 | 492 |  | 2020-09-17 12:00 | 12:00 | 20 | 40 | 492 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Crown Attorney Office | [5 empty] | 24 | 34 | 695 |  | 2020-09-17 15:00 | 15:00 | 24 | 34 | 695 |  | low | 2020-09-14 | B14895¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 2 | [5 empty] | 21 | 41 | 468 |  | 2020-09-17 12:00 | 12:00 | 21 | 41 | 468 |  |  | 2020-09-14 | B19523¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Waiting Area | [5 empty] | 24 | 30 | 554 |  | 2020-09-17 15:00 | 15:00 | 24 | 30 | 554 |  | low | 2020-09-14 | B14895¦Basement Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Police Court Bureau | [5 empty] | 21 | 40 | 456 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 456 |  | caution | 2020-09-14 | B19523¦Police Court Bureau¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Boardroom | [5 empty] | 24 | 31 | 527 |  | 2020-09-17 15:00 | 15:00 | 24 | 31 | 527 |  | low | 2020-09-14 | B14895¦Basement Boardroom¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 Waiting Area | [5 empty] | 21 | 40 | 457 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 457 |  | caution | 2020-09-14 | B19523¦Courtroom 4 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Male Holding Cell | [5 empty] | 24 | 28 | 475 |  | 2020-09-17 15:00 | 15:00 | 24 | 28 | 475 |  | low | 2020-09-14 | B14895¦Male Holding Cell¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 | [5 empty] | 21 | 40 | 428 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 428 |  | caution | 2020-09-14 | B19523¦Courtroom 4¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Female Holding Cell | [5 empty] | 24 | 27 | 456 |  | 2020-09-17 15:00 | 15:00 | 24 | 27 | 456 |  | low | 2020-09-14 | B14895¦Female Holding Cell¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 40 | 478 |  | 2020-09-17 12:00 | 12:00 | 20 | 40 | 478 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Outdoors |  |  | 16 | 18 | 381 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B14895¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 41 | 462 |  | 2020-09-17 12:00 | 12:00 | 19 | 41 | 462 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 43 | 464 |  | 2020-09-17 12:00 | 12:00 | 19 | 43 | 464 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Jury Room | [5 empty] | 19 | 42 | 438 |  | 2020-09-17 12:00 | 12:00 | 19 | 42 | 438 |  |  | 2020-09-14 | B19523¦Jury Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Ontario Court | [5 empty] | 21 | 43 | 449 |  | 2020-09-17 12:00 | 12:00 | 21 | 43 | 449 |  |  | 2020-09-14 | B19523¦Ontario Court¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Judicial Library | [5 empty] | 21 | 40 | 435 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 435 |  | caution | 2020-09-14 | B19523¦Judicial Library¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 315 | [5 empty] | 21 | 39 | 430 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 430 |  | caution | 2020-09-14 | B19523¦Office Room 315¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Outdoors |  |  | 14 | 21 | 405 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20226¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 316 | [5 empty] | 21 | 39 | 427 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 427 |  | caution | 2020-09-14 | B19523¦Office Room 316¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 317 | [5 empty] | 21 | 39 | 429 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 429 |  | caution | 2020-09-14 | B19523¦Office Room 317¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Outdoors |  |  | 14 | 26 | 402 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70050¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Superior Court | [5 empty] | 21 | 39 | 439 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 439 |  | caution | 2020-09-14 | B19523¦Superior Court¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 313 | [5 empty] | 22 | 38 | 433 |  | 2020-09-17 12:00 | 12:00 | 22 | 38 | 433 |  | caution | 2020-09-14 | B19523¦Office Room 313¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 312 | [5 empty] | 22 | 39 | 441 |  | 2020-09-17 12:00 | 12:00 | 22 | 39 | 441 |  | caution | 2020-09-14 | B19523¦Office Room 312¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Main Lobby | [5 empty] | 20 | 45 | 556 |  | 2020-09-17 15:00 | 15:00 | 20 | 45 | 556 |  |  | 2020-09-14 | B70050¦Main Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 310 | [5 empty] | 22 | 39 | 479 |  | 2020-09-17 12:00 | 12:00 | 22 | 39 | 479 |  | caution | 2020-09-14 | B19523¦Office Room 310¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Law Association | [5 empty] | 21 | 38 | 448 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 448 |  | caution | 2020-09-14 | B19523¦Law Association¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room | [5 empty] | 22 | 47 | 428 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 428 |  |  | 2020-09-14 | B14209¦Hearing Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room, Judge’s Chamber | [5 empty] | 22 | 46 | 449 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 449 |  |  | 2020-09-14 | B14209¦Hearing Room, Judge’s Chamber¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room waiting Area | [5 empty] | 23 | 48 | 479 |  | 2020-09-17 12:00 | 12:00 | 23 | 48 | 479 |  |  | 2020-09-14 | B14209¦Hearing Room waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Front desk | [5 empty] | 22 | 49 | 475 |  | 2020-09-17 12:00 | 12:00 | 22 | 49 | 475 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Front desk¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 1 | [5 empty] | 20 | 42 | 517 |  | 2020-09-17 15:00 | 15:00 | 20 | 42 | 517 |  |  | 2020-09-14 | B70050¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown attorney admin area | [5 empty] | 23 | 49 | 484 |  | 2020-09-17 12:00 | 12:00 | 23 | 49 | 484 |  |  | 2020-09-14 | B14209¦Crown attorney admin area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 21 | 43 | 508 |  | 2020-09-17 15:00 | 15:00 | 21 | 43 | 508 |  |  | 2020-09-14 | B70050¦2nd Floor Holding Cell¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Meeting Room (232) | [5 empty] | 21 | 50 | 485 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 485 |  |  | 2020-09-14 | B14209¦Crown Attorney Meeting Room (232)¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Yannick Bedard Office - 2nd Floor | [5 empty] | 22 | 44 | 582 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 582 |  |  | 2020-09-14 | B70050¦Yannick Bedard Office - 2nd Floor¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office | [5 empty] | 22 | 50 | 440 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 440 |  |  | 2020-09-14 | B14209¦Crown Attorney Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 2 | [5 empty] | 21 | 44 | 537 |  | 2020-09-17 15:00 | 15:00 | 21 | 44 | 537 |  |  | 2020-09-14 | B70050¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd fl lobby | [5 empty] | 21 | 44 | 509 |  | 2020-09-17 15:00 | 15:00 | 21 | 44 | 509 |  |  | 2020-09-14 | B70050¦2nd fl lobby¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Assistant Crown Attorney Office (236) | [5 empty] | 22 | 50 | 452 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 452 |  |  | 2020-09-14 | B14209¦Assistant Crown Attorney Office (236)¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 101 | [5 empty] | 20 | 54 | 559 |  | 2020-09-17 15:00 | 15:00 | 20 | 54 | 559 |  |  | 2020-09-14 | B25671¦Courtroom 101¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 201 | [5 empty] | 21 | 54 | 601 |  | 2020-09-17 15:00 | 15:00 | 21 | 54 | 601 |  |  | 2020-09-14 | B25671¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 100 Courtroom 102 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203 | [5 empty] | 21 | 40 | 452 |  | 2020-09-17 15:00 | 15:00 | 21 | 40 | 452 |  | caution | 2020-09-14 | B20616¦Courtroom 100 Courtroom 102 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Lobby | [5 empty] | 23 | 50 | 491 |  | 2020-09-17 12:00 | 12:00 | 23 | 50 | 491 |  |  | 2020-09-14 | B14209¦Court Admin Office Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 301 | [5 empty] | 20 | 53 | 538 | FYI I am off tomorrow September 18th | 2020-09-17 15:00 | 15:00 | 20 | 53 | 538 |  |  | 2020-09-14 | B25671¦Courtroom 301¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Cubicles | [5 empty] | 22 | 46 | 491 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 491 |  |  | 2020-09-14 | B14209¦Court Admin Office Cubicles¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Holding Cell corridor | [5 empty] | 22 | 44 | 434 |  | 2020-09-17 12:00 | 12:00 | 22 | 44 | 434 |  |  | 2020-09-14 | B14209¦Holding Cell corridor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 101 Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 401 Courtroom 402 Courtroom 403 | [5 empty] | 22 | 40 | 452 |  | 2020-09-17 15:00 | 15:00 | 22 | 40 | 452 |  | caution | 2020-09-14 | B20616¦Courtroom 101 Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 401 Courtroom 402 Courtroom 403¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Police Control Room | [5 empty] | 22 | 45 | 457 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 457 |  |  | 2020-09-14 | B14209¦Police Control Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Intake Court | [5 empty] | 22 | 52 | 442 |  | 2020-09-17 12:00 | 12:00 | 22 | 52 | 442 |  |  | 2020-09-14 | B14209¦Intake Court¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 106 Courtroom 205 | [5 empty] | 20 | 45 | 451 |  | 2020-09-17 15:00 | 15:00 | 20 | 45 | 451 |  |  | 2020-09-14 | B20616¦Courtroom 106 Courtroom 205¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Level 1 Corridor by room 103 | [5 empty] | 23 | 49 | 465 |  | 2020-09-17 12:00 | 12:00 | 23 | 49 | 465 |  |  | 2020-09-14 | B14209¦Level 1 Corridor by room 103¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 204 Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 404 Courtroom 405 | [5 empty] | 21 | 45 | 451 |  | 2020-09-17 15:00 | 15:00 | 21 | 45 | 451 |  |  | 2020-09-14 | B20616¦Courtroom 204 Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 404 Courtroom 405¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Library | [5 empty] | 22 | 51 | 457 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 457 |  |  | 2020-09-14 | B14209¦Library¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Law Library Meeting Room (028B) | [5 empty] | 22 | 50 | 480 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 480 |  |  | 2020-09-14 | B14209¦Law Library Meeting Room (028B)¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Lunch Room | [5 empty] | 22 | 50 | 428 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 428 |  |  | 2020-09-14 | B14209¦Lunch Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Entrance by Stair G | [5 empty] | 22 | 44 | 445 |  | 2020-09-17 12:00 | 12:00 | 22 | 44 | 445 |  |  | 2020-09-14 | B14209¦Entrance by Stair G¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 304 Courtroom 305 | [5 empty] | 21 | 41 | 579 |  | 2020-09-17 15:00 | 15:00 | 21 | 41 | 579 |  |  | 2020-09-14 | B20616¦Courtroom 304 Courtroom 305¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 107 Courtroom 108 | [5 empty] | 21 | 40 | 417 |  | 2020-09-17 15:00 | 15:00 | 21 | 40 | 417 |  | caution | 2020-09-14 | B20616¦Courtroom 107 Courtroom 108¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Main Floor Entrance Lobby | [5 empty] | 23 | 43 | 639 |  | 2020-09-17 12:00 | 12:00 | 23 | 43 | 639 |  |  | 2020-09-14 | B14209¦Main Floor Entrance Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Outdoors |  |  | 19 | 35 | 391 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B14209¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Outdoors |  |  | 18 | 52 | 387 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B19652¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Social Benefits Tribunal Reception | [5 empty] | 21 | 43 | 463 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 463 |  |  | 2020-09-14 | B70485¦Social Benefits Tribunal Reception¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Outdoors |  |  | 18 | 46 | 479 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20289¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Print Room | [5 empty] | 22 | 41 | 468 |  | 2020-09-17 12:00 | 12:00 | 22 | 41 | 468 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Print Room¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | OTHER | [5 empty] | 21 | 43 | 448 | SBT Hearing Room #3 | 2020-09-17 09:00 | 9:00 | 21 | 43 | 448 |  |  | 2020-09-14 | B70485¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #4 | [5 empty] | 21 | 43 | 435 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 435 |  |  | 2020-09-14 | B70485¦SBT Hearing Room #4¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Center) | [5 empty] | 23 | 41 | 433 |  | 2020-09-17 15:00 | 15:00 | 23 | 41 | 433 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Center)¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | LTB Hearing Room #1 | [5 empty] | 21 | 43 | 418 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 418 |  |  | 2020-09-14 | B70485¦LTB Hearing Room #1¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 | [5 empty] | 23 | 42 | 453 |  | 2020-09-17 12:00 | 12:00 | 23 | 42 | 453 |  |  | 2020-09-14 | B14209¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Regional Managers Office | [5 empty] | 20 | 44 | 432 |  | 2020-09-17 09:00 | 9:00 | 20 | 44 | 432 |  |  | 2020-09-14 | B70485¦Regional Managers Office¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 - waiting area | [5 empty] | 23 | 48 | 457 |  | 2020-09-17 15:00 | 15:00 | 23 | 48 | 457 |  |  | 2020-09-14 | B14209¦Courtroom 1 - waiting area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 | [5 empty] | 23 | 42 | 453 |  | 2020-09-17 15:00 | 15:00 | 23 | 42 | 453 |  |  | 2020-09-14 | B14209¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Judge Dias) | [5 empty] | 22 | 42 | 422 |  | 2020-09-17 15:00 | 15:00 | 22 | 42 | 422 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Judge Dias)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 | [5 empty] | 23 | 46 | 462 |  | 2020-09-17 15:00 | 15:00 | 23 | 46 | 462 |  |  | 2020-09-14 | B14209¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 44 | 421 | superior judges chamber | 2020-09-17 15:00 | 15:00 | 22 | 44 | 421 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Cubes outside RM Office | [5 empty] | 20 | 43 | 416 |  | 2020-09-17 09:00 | 9:00 | 20 | 43 | 416 |  |  | 2020-09-14 | B70485¦Cubes outside RM Office¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 - waiting room | [5 empty] | 23 | 46 | 462 |  | 2020-09-17 15:00 | 15:00 | 23 | 46 | 462 |  |  | 2020-09-14 | B14209¦Courtroom 2 - waiting room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 45 | 452 | 3rd floor stair landing | 2020-09-17 15:00 | 15:00 | 22 | 45 | 452 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room | [5 empty] | 23 | 47 | 424 |  | 2020-09-17 15:00 | 15:00 | 23 | 47 | 424 |  |  | 2020-09-14 | B14209¦Hearing Room¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #1 | [5 empty] | 21 | 42 | 416 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 416 |  |  | 2020-09-14 | B70485¦Mediation Room #1¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room, Judge’s Chamber | [5 empty] | 23 | 46 | 423 |  | 2020-09-17 15:00 | 15:00 | 23 | 46 | 423 |  |  | 2020-09-14 | B14209¦Hearing Room, Judge’s Chamber¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room - Waiting area | [5 empty] | 23 | 47 | 448 |  | 2020-09-17 15:00 | 15:00 | 23 | 47 | 448 |  |  | 2020-09-14 | B14209¦Hearing Room - Waiting area¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #2 | [5 empty] | 21 | 42 | 417 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 417 |  |  | 2020-09-14 | B70485¦Mediation Room #2¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 3rd floor jury room | [5 empty] | 22 | 44 | 440 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 440 |  |  | 2020-09-14 | B19652¦3rd floor jury room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Outdoors |  |  | 21 | 50 | 508 |  |  |  | judge | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20289¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Front desk | [5 empty] | 23 | 42 | 479 |  | 2020-09-17 15:00 | 15:00 | 23 | 42 | 479 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Front desk¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Reception/ Administration LTB | [5 empty] | 21 | 42 | 425 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 425 |  |  | 2020-09-14 | B70485¦Reception/ Administration LTB¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | justice mcdonald chamber | [5 empty] | 22 | 46 | 564 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 564 |  |  | 2020-09-14 | B19652¦justice mcdonald chamber¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown attorney admin area | [5 empty] | 22 | 38 | 466 |  | 2020-09-17 15:00 | 15:00 | 22 | 38 | 466 |  | caution | 2020-09-14 | B14209¦Crown attorney admin area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 21 | 50 | 498 | public | 2020-09-17 15:00 | 15:00 | 21 | 50 | 498 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Print Room | [5 empty] | 22 | 45 | 481 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 481 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Print Room¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | OTHER | [5 empty] | 21 | 42 | 423 | Document Area | 2020-09-17 09:00 | 9:00 | 21 | 42 | 423 |  |  | 2020-09-14 | B70485¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | JUSTICE MCDONALD SECRETARY | [5 empty] | 22 | 47 | 570 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 570 |  |  | 2020-09-14 | B19652¦JUSTICE MCDONALD SECRETARY¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Assistant Crown Attorney Office (236) | [5 empty] | 22 | 47 | 452 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 452 |  |  | 2020-09-14 | B14209¦Assistant Crown Attorney Office (236)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 22 | 49 | 504 | judge | 2020-09-17 15:00 | 15:00 | 22 | 49 | 504 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 22 | 48 | 497 | public | 2020-09-17 15:00 | 15:00 | 22 | 48 | 497 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Meeting Room (232) | [5 empty] | 21 | 47 | 449 |  | 2020-09-17 15:00 | 15:00 | 21 | 47 | 449 |  |  | 2020-09-14 | B14209¦Crown Attorney Meeting Room (232)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | SCJTC Office | [5 empty] | 22 | 47 | 561 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 561 |  |  | 2020-09-14 | B19652¦SCJTC Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 300 | [5 empty] | 22 | 58 | 496 |  | 2020-09-17 15:00 | 15:00 | 22 | 58 | 496 |  |  | 2020-09-14 | B20289¦Courtroom 300¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office | [5 empty] | 21 | 48 | 446 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 446 |  |  | 2020-09-14 | B14209¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Copy Room | [5 empty] | 21 | 42 | 412 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 412 |  |  | 2020-09-14 | B70485¦Copy Room¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | visiting justice chamber | [5 empty] | 22 | 47 | 556 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 556 |  |  | 2020-09-14 | B19652¦visiting justice chamber¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 301 | [5 empty] | 21 | 58 | 498 |  | 2020-09-17 15:00 | 15:00 | 21 | 58 | 498 |  |  | 2020-09-14 | B20289¦Courtroom 301¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Lobby | [5 empty] | 23 | 43 | 477 |  | 2020-09-17 15:00 | 15:00 | 23 | 43 | 477 |  |  | 2020-09-14 | B14209¦Court Admin Office Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 302 | [5 empty] | 22 | 59 | 507 |  | 2020-09-17 15:00 | 15:00 | 22 | 59 | 507 |  |  | 2020-09-14 | B20289¦Courtroom 302¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 303 | [5 empty] | 21 | 46 | 498 |  | 2020-09-17 15:00 | 15:00 | 21 | 46 | 498 |  |  | 2020-09-14 | B20289¦Courtroom 303¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Cubicles | [5 empty] | 22 | 46 | 512 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 512 |  |  | 2020-09-14 | B14209¦Court Admin Office Cubicles¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Center) | [5 empty] | 22 | 47 | 552 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 552 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Center)¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #3 | [5 empty] | 21 | 41 | 413 |  | 2020-09-17 09:00 | 9:00 | 21 | 41 | 413 |  |  | 2020-09-14 | B70485¦Mediation Room #3¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Holding Cell corridor | [5 empty] | 22 | 42 | 430 |  | 2020-09-17 15:00 | 15:00 | 22 | 42 | 430 |  |  | 2020-09-14 | B14209¦Holding Cell corridor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom A | [5 empty] | 22 | 58 | 519 |  | 2020-09-17 15:00 | 15:00 | 22 | 58 | 519 |  |  | 2020-09-14 | B20289¦Courtroom A¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Corner Office | [5 empty] | 21 | 43 | 414 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 414 |  |  | 2020-09-14 | B70485¦Corner Office¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Police Control Room | [5 empty] | 22 | 43 | 449 |  | 2020-09-17 15:00 | 15:00 | 22 | 43 | 449 |  |  | 2020-09-14 | B14209¦Police Control Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom B | [5 empty] | 21 | 59 | 549 |  | 2020-09-17 15:00 | 15:00 | 21 | 59 | 549 |  |  | 2020-09-14 | B20289¦Courtroom B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Judge Dias) | [5 empty] | 22 | 47 | 570 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 570 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Judge Dias)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Intake Court | [5 empty] | 22 | 49 | 445 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 445 |  |  | 2020-09-14 | B14209¦Intake Court¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom C (North) | [5 empty] | 22 | 59 | 557 |  | 2020-09-17 15:00 | 15:00 | 22 | 59 | 557 |  |  | 2020-09-14 | B20289¦Courtroom C (North)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom D | [5 empty] | 22 | 59 | 569 |  | 2020-09-17 15:00 | 15:00 | 22 | 59 | 569 |  |  | 2020-09-14 | B20289¦Courtroom D¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Level 1 Corridor by room 103 | [5 empty] | 23 | 47 | 449 |  | 2020-09-17 15:00 | 15:00 | 23 | 47 | 449 |  |  | 2020-09-14 | B14209¦Level 1 Corridor by room 103¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 Waiting Area | [5 empty] | 22 | 47 | 586 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 586 |  |  | 2020-09-14 | B19652¦Courtroom 2 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom E | [5 empty] | 21 | 59 | 572 |  | 2020-09-17 15:00 | 15:00 | 21 | 59 | 572 |  |  | 2020-09-14 | B20289¦Courtroom E¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Center) | [5 empty] | 22 | 45 | 451 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 451 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Center)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom F | [5 empty] | 22 | 58 | 551 | in session; measurement taken outside courtroom | 2020-09-17 15:00 | 15:00 | 22 | 58 | 551 |  |  | 2020-09-14 | B20289¦Courtroom F¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Law Library Meeting Room (028B) | [5 empty] | 23 | 47 | 576 |  | 2020-09-17 15:00 | 15:00 | 23 | 47 | 576 |  |  | 2020-09-14 | B14209¦Law Library Meeting Room (028B)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Judge Dias) | [5 empty] | 22 | 44 | 461 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 461 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Judge Dias)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Library | [5 empty] | 22 | 49 | 441 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 441 |  |  | 2020-09-14 | B14209¦Library¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | justice peace chamber | [5 empty] | 23 | 45 | 501 |  | 2020-09-17 15:00 | 15:00 | 23 | 45 | 501 |  |  | 2020-09-14 | B19652¦justice peace chamber¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Crown Attorney Office | [5 empty] | 22 | 26 | 434 |  | 2020-09-17 15:00 | 15:00 | 22 | 26 | 434 |  | low | 2020-09-14 | B20016¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Entrance by Stair G | [5 empty] | 24 | 33 | 510 |  | 2020-09-17 15:00 | 15:00 | 24 | 33 | 510 |  | low | 2020-09-14 | B14209¦Entrance by Stair G¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Legal Aid Ontario | [5 empty] | 23 | 24 | 442 |  | 2020-09-17 15:00 | 15:00 | 23 | 24 | 442 |  | low | 2020-09-14 | B20016¦Legal Aid Ontario¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | council chamber dias | [5 empty] | 22 | 48 | 598 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 598 |  |  | 2020-09-14 | B19652¦council chamber dias¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Main Floor Entrance Lobby | [5 empty] | 22 | 42 | 671 |  | 2020-09-17 15:00 | 15:00 | 22 | 42 | 671 |  |  | 2020-09-14 | B14209¦Main Floor Entrance Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel Waiting Area | [5 empty] | 23 | 24 | 460 |  | 2020-09-17 15:00 | 15:00 | 23 | 24 | 460 |  | low | 2020-09-14 | B20016¦Duty Counsel Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel | [5 empty] | 23 | 30 | 459 |  | 2020-09-17 15:00 | 15:00 | 23 | 30 | 459 |  | low | 2020-09-14 | B20016¦Duty Counsel¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | council chamber center | [5 empty] | 22 | 47 | 585 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 585 |  |  | 2020-09-14 | B19523¦council chamber center¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Side Entry Door | [5 empty] | 21 | 43 | 427 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 427 |  |  | 2020-09-14 | B70485¦Side Entry Door¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Outdoors |  |  | 19 | 21 | 396 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B14209¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-1, 16th Floor OTHER | [5 empty] | 22 | 44 | 718 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 718 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-1, 16th Floor OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Filing Area | [5 empty] | 21 | 43 | 430 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 430 |  |  | 2020-09-14 | B70485¦Filing Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 2nd Floor Lunchroom | [5 empty] | 22 | 42 | 553 |  | 2020-09-17 15:00 | 15:00 | 22 | 42 | 553 |  |  | 2020-09-14 | B19652¦2nd Floor Lunchroom¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Entrance by Stair G | [5 empty] | 24 | 33 | 510 |  | 2020-09-17 15:00 | 15:00 | 24 | 33 | 510 |  | low | 2020-09-14 | B14209¦Entrance by Stair G¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lobby Courtroom 1 - 2 | [5 empty] | 23 | 25 | 464 |  | 2020-09-17 15:00 | 15:00 | 23 | 25 | 464 |  | low | 2020-09-14 | B20016¦Lobby Courtroom 1 - 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-3, 16th Floor OTHER | [5 empty] | 21 | 45 | 711 |  | 2020-09-17 15:00 | 15:00 | 21 | 45 | 711 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-3, 16th Floor OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 2nd floor stair landing | [5 empty] | 22 | 45 | 519 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 519 |  |  | 2020-09-14 | B19652¦2nd floor stair landing¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Staff Kitchen | [5 empty] | 21 | 43 | 434 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 434 |  |  | 2020-09-14 | B70485¦Staff Kitchen¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Main Lobby | [5 empty] | 23 | 27 | 514 |  | 2020-09-17 15:00 | 15:00 | 23 | 27 | 514 |  | low | 2020-09-14 | B20016¦Main Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | court services kitchenette | [5 empty] | 22 | 42 | 502 |  | 2020-09-17 15:00 | 15:00 | 22 | 42 | 502 |  |  | 2020-09-14 | B19652¦court services kitchenette¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Washrooms, 16th Floor OTHER | [5 empty] | 21 | 45 | 706 |  | 2020-09-17 15:00 | 15:00 | 21 | 45 | 706 |  |  | 2020-09-14 | B25398¦Corridor adj. to Washrooms, 16th Floor OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | court services north | [5 empty] | 23 | 41 | 634 |  | 2020-09-17 15:00 | 15:00 | 23 | 41 | 634 |  |  | 2020-09-14 | B19652¦court services north¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Hearing Room #2 | [5 empty] | 21 | 42 | 427 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 427 |  |  | 2020-09-14 | B70485¦Hearing Room #2¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lower Hallway | [5 empty] | 22 | 27 | 464 |  | 2020-09-17 15:00 | 15:00 | 22 | 27 | 464 |  | low | 2020-09-14 | B20016¦Lower Hallway¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Women's Washroom, 16th Floor | [5 empty] | 21 | 45 | 699 |  | 2020-09-17 15:00 | 15:00 | 21 | 45 | 699 |  |  | 2020-09-14 | B25398¦OTHER Women's Washroom, 16th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | OTHER | [5 empty] | 21 | 27 | 462 | Courtroom 1-2-3 | 2020-09-17 15:00 | 15:00 | 21 | 27 | 462 |  | low | 2020-09-14 | B20016¦OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | court service south | [5 empty] | 23 | 42 | 630 |  | 2020-09-17 15:00 | 15:00 | 23 | 42 | 630 |  |  | 2020-09-14 | B19652¦court service south¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER elevator Lobby, 16th Floor | [5 empty] | 22 | 45 | 703 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 703 |  |  | 2020-09-14 | B25398¦OTHER elevator Lobby, 16th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Elevators | [5 empty] | 22 | 41 | 412 |  | 2020-09-17 09:00 | 9:00 | 22 | 41 | 412 |  |  | 2020-09-14 | B70485¦Elevators¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation | [5 empty] | 21 | 28 | 472 |  | 2020-09-17 15:00 | 15:00 | 21 | 28 | 472 |  | low | 2020-09-14 | B20016¦Family Mediation¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | court service entrance vestibule | [5 empty] | 23 | 42 | 614 |  | 2020-09-17 15:00 | 15:00 | 23 | 42 | 614 |  |  | 2020-09-14 | B19652¦court service entrance vestibule¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation Across Stairs | [5 empty] | 20 | 27 | 484 |  | 2020-09-17 15:00 | 15:00 | 20 | 27 | 484 |  | low | 2020-09-14 | B20016¦Family Mediation Across Stairs¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, West, 15th Floor | [5 empty] | 21 | 49 | 720 |  | 2020-09-17 15:00 | 15:00 | 21 | 49 | 720 |  |  | 2020-09-14 | B25398¦OTHER Office Area, West, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 1st floor stair landing court service entrance vestibule | [5 empty] | 22 | 44 | 536 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 536 |  |  | 2020-09-14 | B19652¦1st floor stair landing court service entrance vestibule¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Justice of the Peace Office | [5 empty] | 22 | 30 | 632 |  | 2020-09-17 15:00 | 15:00 | 22 | 30 | 632 |  | low | 2020-09-14 | B20016¦Justice of the Peace Office¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Outdoors |  |  | 16 | 42 | 408 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70485¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North West, 15th Floor | [5 empty] | 21 | 48 | 723 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 723 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North West, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Holding Cell | [5 empty] | 21 | 28 | 463 |  | 2020-09-17 15:00 | 15:00 | 21 | 28 | 463 |  | low | 2020-09-14 | B20016¦Holding Cell¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North, 15th Floor | [5 empty] | 21 | 48 | 716 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 716 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Courtroom 1 | [5 empty] | 21 | 27 | 428 |  | 2020-09-17 15:00 | 15:00 | 21 | 27 | 428 |  | low | 2020-09-14 | B20016¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Main Lobby | [5 empty] | 20 | 40 | 453 |  | 2020-09-17 15:00 | 15:00 | 20 | 40 | 453 |  | caution | 2020-09-14 | B19523¦Main Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Front Security Desk | [5 empty] | 20 | 51 | 510 |  | 2020-09-17 09:00 | 9:00 | 20 | 51 | 510 |  |  | 2020-09-14 | B20705¦Front Security Desk¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North East, 15th Floor | [5 empty] | 21 | 47 | 715 |  | 2020-09-17 15:00 | 15:00 | 21 | 47 | 715 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North East, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Holding Cell | [5 empty] | 21 | 37 | 455 |  | 2020-09-17 15:00 | 15:00 | 21 | 37 | 455 |  | caution | 2020-09-14 | B19523¦Holding Cell¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family Law Reception | [5 empty] | 22 | 40 | 445 |  | 2020-09-17 09:00 | 9:00 | 22 | 40 | 445 |  | caution | 2020-09-14 | B20705¦Family Law Reception¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 1 | [5 empty] | 21 | 39 | 440 |  | 2020-09-17 15:00 | 15:00 | 21 | 39 | 440 |  | caution | 2020-09-14 | B19523¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Are, East, 15th Floor | [5 empty] | 21 | 47 | 713 |  | 2020-09-17 15:00 | 15:00 | 21 | 47 | 713 |  |  | 2020-09-14 | B25398¦OTHER Office Are, East, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Court Services | [5 empty] | 21 | 40 | 487 |  | 2020-09-17 15:00 | 15:00 | 21 | 40 | 487 |  | caution | 2020-09-14 | B19523¦Court Services¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Criminal Court Inquiry | [5 empty] | 22 | 41 | 475 |  | 2020-09-17 09:00 | 9:00 | 22 | 41 | 475 |  |  | 2020-09-14 | B20705¦Criminal Court Inquiry¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South East, 15th Floor | [5 empty] | 21 | 46 | 720 |  | 2020-09-17 15:00 | 15:00 | 21 | 46 | 720 |  |  | 2020-09-14 | B25398¦OTHER Office Area, South East, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | JP Office | [5 empty] | 21 | 38 | 477 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 477 |  | caution | 2020-09-14 | B19523¦JP Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | OPP Office | [5 empty] | 21 | 38 | 435 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 435 |  | caution | 2020-09-14 | B19523¦OPP Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South, 15th Floor | [5 empty] | 21 | 46 | 720 |  | 2020-09-17 15:00 | 15:00 | 21 | 46 | 720 |  |  | 2020-09-14 | B25398¦OTHER Office Area, South, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Crown Attorney Office | [5 empty] | 22 | 40 | 467 |  | 2020-09-17 15:00 | 15:00 | 22 | 40 | 467 |  | caution | 2020-09-14 | B19523¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family/Civil Waiting Area | [5 empty] | 22 | 44 | 446 |  | 2020-09-17 09:00 | 9:00 | 22 | 44 | 446 |  |  | 2020-09-14 | B20705¦Family/Civil Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 41 | 478 |  | 2020-09-17 15:00 | 15:00 | 22 | 41 | 478 |  |  | 2020-09-14 | B19523¦VWAP Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Reception, 15th Floor | [5 empty] | 22 | 46 | 712 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 712 |  |  | 2020-09-14 | B25398¦OTHER Reception, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 23 | 38 | 515 |  | 2020-09-17 15:00 | 15:00 | 23 | 38 | 515 |  | caution | 2020-09-14 | B19523¦VWAP Office¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Court Support Office | [5 empty] | 23 | 41 | 497 |  | 2020-09-17 09:00 | 9:00 | 23 | 41 | 497 |  |  | 2020-09-14 | B20705¦Court Support Office¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 5 | [5 empty] | 22 | 36 | 443 |  | 2020-09-17 15:00 | 15:00 | 22 | 36 | 443 |  | caution | 2020-09-14 | B19523¦Courtroom 5¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Mail Room, 15th Floor OTHER | [5 empty] | 21 | 48 | 720 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 720 |  |  | 2020-09-14 | B25398¦Corridor adj. to Mail Room, 15th Floor OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Remote Testimony Room | [5 empty] | 21 | 37 | 434 |  | 2020-09-17 15:00 | 15:00 | 21 | 37 | 434 |  | caution | 2020-09-14 | B19523¦Remote Testimony Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Conference Room 2 | [5 empty] | 21 | 39 | 429 |  | 2020-09-17 15:00 | 15:00 | 21 | 39 | 429 |  | caution | 2020-09-14 | B19523¦Conference Room 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 15th Floor OTHER | [5 empty] | 21 | 47 | 710 |  | 2020-09-17 15:00 | 15:00 | 21 | 47 | 710 |  |  | 2020-09-14 | B25398¦Elevator Lobby, 15th Floor OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 20-24 Waiting Area | [5 empty] | 23 | 40 | 453 |  | 2020-09-17 09:00 | 9:00 | 23 | 40 | 453 |  | caution | 2020-09-14 | B20705¦Courtroom 20-24 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 | [5 empty] | 21 | 39 | 433 |  | 2020-09-17 15:00 | 15:00 | 21 | 39 | 433 |  | caution | 2020-09-14 | B19523¦Courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | reception area | [5 empty] | 23 | 46 | 518 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 518 |  |  | 2020-09-14 | B70003¦reception area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 Waiting Area | [5 empty] | 21 | 38 | 442 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 442 |  | caution | 2020-09-14 | B19523¦Courtroom 3 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 2 | [5 empty] | 19 | 52 | 507 |  | 2020-09-17 15:00 | 15:00 | 19 | 52 | 507 |  |  | 2020-09-14 | B11586¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Outdoors |  |  | 19 | 42 | 685 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B25398¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Front of main hallway | [5 empty] | 22 | 47 | 512 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 512 |  |  | 2020-09-14 | B70003¦Front of main hallway¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 4-6 Waiting Area | [5 empty] | 23 | 39 | 450 |  | 2020-09-17 09:00 | 9:00 | 23 | 39 | 450 |  | caution | 2020-09-14 | B20705¦Courtroom 4-6 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 20 | 49 | 493 | Crown attorney beaton’s office | 2020-09-17 15:00 | 15:00 | 20 | 49 | 493 |  |  | 2020-09-14 | B11586¦OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 21 | 49 | 510 |  | 2020-09-17 15:00 | 15:00 | 21 | 49 | 510 |  |  | 2020-09-14 | B11586¦OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 1-3 Waiting Area | [5 empty] | 23 | 38 | 485 |  | 2020-09-17 09:00 | 9:00 | 23 | 38 | 485 |  | caution | 2020-09-14 | B20705¦Courtroom 1-3 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 22 | 49 | 491 | outside of 502 | 2020-09-17 12:00 | 12:00 | 22 | 49 | 491 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown attorney admin area | [5 empty] | 21 | 48 | 528 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 528 |  |  | 2020-09-14 | B11586¦Crown attorney admin area¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 50 | 469 | public area | 2020-09-17 12:00 | 12:00 | 21 | 50 | 469 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom waiting area | [5 empty] | 22 | 45 | 494 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 494 |  |  | 2020-09-14 | B11586¦Courtroom waiting area¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 51 | 472 | judge area | 2020-09-17 12:00 | 12:00 | 21 | 51 | 472 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 52 | 500 | outside of 503 | 2020-09-17 12:00 | 12:00 | 21 | 52 | 500 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 38 | 459 |  | 2020-09-17 15:00 | 15:00 | 20 | 38 | 459 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 | [5 empty] | 21 | 40 | 517 |  | 2020-09-17 15:00 | 15:00 | 21 | 40 | 517 |  | caution | 2020-09-14 | B11586¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 52 | 493 | public area | 2020-09-17 12:00 | 12:00 | 21 | 52 | 493 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 | [5 empty] | 21 | 40 | 517 |  | 2020-09-17 15:00 | 15:00 | 21 | 40 | 517 |  | caution | 2020-09-14 | B11586¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 39 | 479 |  | 2020-09-17 15:00 | 15:00 | 20 | 39 | 479 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 53 | 492 | judge area | 2020-09-17 12:00 | 12:00 | 20 | 53 | 492 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | 2nd Floor Holding Cell | [5 empty] | 21 | 41 | 478 |  | 2020-09-17 15:00 | 15:00 | 21 | 41 | 478 |  |  | 2020-09-14 | B11586¦2nd Floor Holding Cell¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 | [5 empty] | 20 | 39 | 462 |  | 2020-09-17 15:00 | 15:00 | 20 | 39 | 462 |  | caution | 2020-09-14 | B19523¦Courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 54 | 526 | outside of 506 | 2020-09-17 12:00 | 12:00 | 20 | 54 | 526 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Police Court Bureau | [5 empty] | 21 | 39 | 462 |  | 2020-09-17 15:00 | 15:00 | 21 | 39 | 462 |  | caution | 2020-09-14 | B19523¦Police Court Bureau¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 54 | 563 | public area | 2020-09-17 12:00 | 12:00 | 20 | 54 | 563 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 Waiting Area | [5 empty] | 21 | 39 | 465 |  | 2020-09-17 15:00 | 15:00 | 21 | 39 | 465 |  | caution | 2020-09-14 | B19523¦Courtroom 4 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 55 | 572 | judge area | 2020-09-17 12:00 | 12:00 | 20 | 55 | 572 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Judge office | [5 empty] | 21 | 39 | 462 |  | 2020-09-17 15:00 | 15:00 | 21 | 39 | 462 |  | caution | 2020-09-14 | B11586¦Judge office¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 56 | 551 | outside of 509 | 2020-09-17 12:00 | 12:00 | 20 | 56 | 551 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 54 | 500 | public area | 2020-09-17 12:00 | 12:00 | 20 | 54 | 500 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | court admin office | [5 empty] | 19 | 55 | 534 |  | 2020-09-17 15:00 | 15:00 | 19 | 55 | 534 |  |  | 2020-09-14 | B11586¦court admin office¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 7-9 Waiting Room | [5 empty] | 23 | 39 | 461 |  | 2020-09-17 09:00 | 9:00 | 23 | 39 | 461 |  | caution | 2020-09-14 | B20705¦Courtroom 7-9 Waiting Room¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 | [5 empty] | 21 | 39 | 430 |  | 2020-09-17 15:00 | 15:00 | 21 | 39 | 430 |  | caution | 2020-09-14 | B19523¦Courtroom 4¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 55 | 506 | judge area | 2020-09-17 12:00 | 12:00 | 20 | 55 | 506 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Main Lobby | [5 empty] | 18 | 54 | 511 |  | 2020-09-17 15:00 | 15:00 | 18 | 54 | 511 |  |  | 2020-09-14 | B11586¦Main Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 39 | 477 |  | 2020-09-17 15:00 | 15:00 | 20 | 39 | 477 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 55 | 538 | outside of 510 | 2020-09-17 12:00 | 12:00 | 20 | 55 | 538 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 40 | 463 |  | 2020-09-17 15:00 | 15:00 | 19 | 40 | 463 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Outdoors |  |  | 16 | 32 | 412 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B11586¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 54 | 638 | public area | 2020-09-17 12:00 | 12:00 | 20 | 54 | 638 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 42 | 465 |  | 2020-09-17 15:00 | 15:00 | 19 | 42 | 465 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 21 | 54 | 632 | judge area | 2020-09-17 12:00 | 12:00 | 21 | 54 | 632 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Jury Room | [5 empty] | 19 | 41 | 426 |  | 2020-09-17 15:00 | 15:00 | 19 | 41 | 426 |  |  | 2020-09-14 | B19523¦Jury Room¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 10-12 Waiting Area | [5 empty] | 23 | 39 | 472 |  | 2020-09-17 09:00 | 9:00 | 23 | 39 | 472 |  | caution | 2020-09-14 | B20705¦Courtroom 10-12 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Back of main hallway | [5 empty] | 20 | 54 | 558 |  | 2020-09-17 12:00 | 12:00 | 20 | 54 | 558 |  |  | 2020-09-14 | B70003¦Back of main hallway¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Ontario Court | [5 empty] | 21 | 42 | 449 |  | 2020-09-17 15:00 | 15:00 | 21 | 42 | 449 |  |  | 2020-09-14 | B19523¦Ontario Court¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Elevator area | [5 empty] | 20 | 54 | 523 |  | 2020-09-17 12:00 | 12:00 | 20 | 54 | 523 |  |  | 2020-09-14 | B70003¦Elevator area¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 13-14 Waiting Area | [5 empty] | 23 | 39 | 469 |  | 2020-09-17 09:00 | 9:00 | 23 | 39 | 469 |  | caution | 2020-09-14 | B20705¦Courtroom 13-14 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Main entrance | [5 empty] | 22 | 46 | 539 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 539 |  |  | 2020-09-14 | B20979¦Main entrance¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Outdoors |  |  | 19 | 52 | 419 |  |  |  | outside of 444 Yonge St. | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70003¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Judicial Library | [5 empty] | 21 | 40 | 449 |  | 2020-09-17 15:00 | 15:00 | 21 | 40 | 449 |  | caution | 2020-09-14 | B19523¦Judicial Library¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 34-36 Waiting Area | [5 empty] | 23 | 40 | 442 |  | 2020-09-17 09:00 | 9:00 | 23 | 40 | 442 |  | caution | 2020-09-14 | B20705¦Courtroom 34-36 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Front seating area | [5 empty] | 22 | 47 | 409 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 409 |  |  | 2020-09-14 | B18359¦Front seating area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 315 | [5 empty] | 21 | 38 | 440 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 440 |  | caution | 2020-09-14 | B19523¦Office Room 315¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Northwest corridor | [5 empty] | 22 | 47 | 413 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 413 |  |  | 2020-09-14 | B18359¦Northwest corridor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 316 | [5 empty] | 21 | 38 | 428 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 428 |  | caution | 2020-09-14 | B19523¦Office Room 316¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 30-33 Waiting Area | [5 empty] | 23 | 41 | 423 |  | 2020-09-17 09:00 | 9:00 | 23 | 41 | 423 |  |  | 2020-09-14 | B20705¦Courtroom 30-33 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 22 | 48 | 4033 | north side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 4033 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 317 | [5 empty] | 21 | 38 | 438 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 438 |  | caution | 2020-09-14 | B19523¦Office Room 317¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 22 | 48 | 404 | south side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Superior Court | [5 empty] | 21 | 38 | 428 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 428 |  | caution | 2020-09-14 | B19523¦Superior Court¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Crown Attorney Entrance | [5 empty] | 23 | 41 | 447 |  | 2020-09-17 09:00 | 9:00 | 23 | 41 | 447 |  |  | 2020-09-14 | B20705¦Crown Attorney Entrance¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 313 | [5 empty] | 22 | 38 | 429 |  | 2020-09-17 15:00 | 15:00 | 22 | 38 | 429 |  | caution | 2020-09-14 | B19523¦Office Room 313¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 23 | 47 | 407 | north side | 2020-09-17 15:00 | 15:00 | 23 | 47 | 407 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 312 | [5 empty] | 22 | 38 | 445 |  | 2020-09-17 15:00 | 15:00 | 22 | 38 | 445 |  | caution | 2020-09-14 | B19523¦Office Room 312¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 23 | 47 | 404 | south side | 2020-09-17 15:00 | 15:00 | 23 | 47 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Law Association | [5 empty] | 20 | 37 | 436 |  | 2020-09-17 15:00 | 15:00 | 20 | 37 | 436 |  | caution | 2020-09-14 | B19523¦Law Association¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 22 | 47 | 399 | north side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 399 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 22 | 46 | 616 | east | 2020-09-17 15:00 | 15:00 | 22 | 46 | 616 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 22 | 47 | 407 | south side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 407 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 22 | 47 | 406 | north side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 406 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 23 | 45 | 540 | west | 2020-09-17 15:00 | 15:00 | 23 | 45 | 540 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 22 | 47 | 407 | south side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 407 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Probation/Parole Waiting Area | [5 empty] | 23 | 38 | 491 |  | 2020-09-17 09:00 | 9:00 | 23 | 38 | 491 |  | caution | 2020-09-14 | B20705¦Probation/Parole Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 22 | 47 | 404 | north side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 22 | 45 | 658 | south | 2020-09-17 15:00 | 15:00 | 22 | 45 | 658 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 22 | 47 | 401 | south side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 401 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Land Registry Office | [5 empty] | 23 | 38 | 475 |  | 2020-09-17 09:00 | 9:00 | 23 | 38 | 475 |  | caution | 2020-09-14 | B20705¦Land Registry Office¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 22 | 46 | 611 | north | 2020-09-17 15:00 | 15:00 | 22 | 46 | 611 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 4th floor waiting area | [5 empty] | 23 | 38 | 445 |  | 2020-09-17 09:00 | 9:00 | 23 | 38 | 445 |  | caution | 2020-09-14 | B20705¦4th floor waiting area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 307 | [5 empty] | 22 | 48 | 731 | south | 2020-09-17 15:00 | 15:00 | 22 | 48 | 731 |  |  | 2020-09-14 | B20979¦Courtroom 307¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 53-55 Waiting Area | [5 empty] | 22 | 38 | 466 |  | 2020-09-17 09:00 | 9:00 | 22 | 38 | 466 |  | caution | 2020-09-14 | B20705¦Courtroom 53-55 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 51-52 Waiting Area | [5 empty] | 23 | 38 | 427 |  | 2020-09-17 09:00 | 9:00 | 23 | 38 | 427 |  | caution | 2020-09-14 | B20705¦Courtroom 51-52 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 307 | [5 empty] | 22 | 48 | 755 | north | 2020-09-17 15:00 | 15:00 | 22 | 48 | 755 |  |  | 2020-09-14 | B20979¦Courtroom 307¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 6th Floor Waiting Area | [5 empty] | 22 | 37 | 434 |  | 2020-09-17 09:00 | 9:00 | 22 | 37 | 434 |  | caution | 2020-09-14 | B20705¦6th Floor Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 22 | 47 | 760 | east | 2020-09-17 15:00 | 15:00 | 22 | 47 | 760 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Outdoors |  |  | 15 | 44 | 402 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20705¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 23 | 47 | 741 | west | 2020-09-17 15:00 | 15:00 | 23 | 47 | 741 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Hallway by courtroom 307 | [5 empty] | 22 | 43 | 556 |  | 2020-09-17 15:00 | 15:00 | 22 | 43 | 556 |  |  | 2020-09-14 | B20979¦Hallway by courtroom 307¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Hallway by courtroom 302 | [5 empty] | 22 | 44 | 525 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 525 |  |  | 2020-09-14 | B20979¦Hallway by courtroom 302¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Social Benefits Tribunal Reception | [5 empty] | 21 | 38 | 406 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 406 |  | caution | 2020-09-14 | B70485¦Social Benefits Tribunal Reception¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 43 | 459 | south | 2020-09-17 15:00 | 15:00 | 22 | 43 | 459 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #3 | [5 empty] | 21 | 38 | 401 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 401 |  | caution | 2020-09-14 | B70485¦SBT Hearing Room #3¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 23 | 43 | 492 | north | 2020-09-17 15:00 | 15:00 | 23 | 43 | 492 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #4 | [5 empty] | 21 | 36 | 404 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 404 |  | caution | 2020-09-14 | B70485¦SBT Hearing Room #4¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Basement cells - hallway | [5 empty] | 23 | 41 | 432 |  | 2020-09-17 15:00 | 15:00 | 23 | 41 | 432 |  |  | 2020-09-14 | B20979¦Basement cells - hallway¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | LTB Hearing Room #1 | [5 empty] | 21 | 37 | 407 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 407 |  | caution | 2020-09-14 | B70485¦LTB Hearing Room #1¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Police Office | [5 empty] | 23 | 44 | 557 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 557 |  |  | 2020-09-14 | B20979¦Police Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Outdoors |  |  | 20 | 40 | 411 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20979¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Regional Managers Office | [5 empty] | 21 | 37 | 396 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 396 |  | caution | 2020-09-14 | B70485¦Regional Managers Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Main entrance | [5 empty] | 22 | 43 | 458 |  | 2020-09-17 15:00 | 15:00 | 22 | 43 | 458 |  |  | 2020-09-14 | B90636¦Main entrance¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #1 | [5 empty] | 21 | 38 | 397 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 397 |  | caution | 2020-09-14 | B70485¦Mediation Room #1¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 22 | 43 | 428 | north | 2020-09-17 15:00 | 15:00 | 22 | 43 | 428 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Cubes outside RM Office | [5 empty] | 21 | 37 | 400 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 400 |  | caution | 2020-09-14 | B70485¦Cubes outside RM Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 22 | 43 | 433 | south | 2020-09-17 15:00 | 15:00 | 22 | 43 | 433 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 22 | 48 | 406 | north side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 406 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 22 | 48 | 403 | south side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 403 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 22 | 43 | 444 | courtroom lobby | 2020-09-17 15:00 | 15:00 | 22 | 43 | 444 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 22 | 48 | 407 | north side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 407 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #2 | [5 empty] | 21 | 37 | 422 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 422 |  | caution | 2020-09-14 | B70485¦Mediation Room #2¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 22 | 48 | 406 | south side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 406 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 22 | 44 | 442 | south | 2020-09-17 15:00 | 15:00 | 22 | 44 | 442 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 22 | 48 | 423 | north side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 423 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Reception/ Administration LTB | [5 empty] | 21 | 36 | 403 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 403 |  | caution | 2020-09-14 | B70485¦Reception/ Administration LTB¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 22 | 44 | 440 | north | 2020-09-17 15:00 | 15:00 | 22 | 44 | 440 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 22 | 48 | 412 | south side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 412 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 2nd fl lobby | [5 empty] | 22 | 44 | 441 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 441 |  |  | 2020-09-14 | B90636¦2nd fl lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 3rd Floor Elevator Lobby | [5 empty] | 22 | 43 | 436 |  | 2020-09-17 15:00 | 15:00 | 22 | 43 | 436 |  |  | 2020-09-14 | B90636¦3rd Floor Elevator Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Document Area | [5 empty] | 21 | 37 | 416 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 416 |  | caution | 2020-09-14 | B70485¦Document Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 23 | 43 | 447 | west | 2020-09-17 15:00 | 15:00 | 23 | 43 | 447 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 23 | 42 | 433 | east | 2020-09-17 15:00 | 15:00 | 23 | 42 | 433 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Copy Room | [5 empty] | 21 | 36 | 410 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 410 |  | caution | 2020-09-14 | B70485¦Copy Room¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 4th floor waiting area | [5 empty] | 23 | 39 | 427 |  | 2020-09-17 15:00 | 15:00 | 23 | 39 | 427 |  | caution | 2020-09-14 | B90636¦4th floor waiting area¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #3 | [5 empty] | 21 | 36 | 404 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 404 |  | caution | 2020-09-14 | B70485¦Mediation Room #3¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 211 | [5 empty] | 22 | 43 | 415 | north | 2020-09-17 15:00 | 15:00 | 22 | 43 | 415 |  |  | 2020-09-14 | B90636¦Courtroom 211¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Corner Office | [5 empty] | 21 | 37 | 413 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 413 |  | caution | 2020-09-14 | B70485¦Corner Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 211 | [5 empty] | 22 | 43 | 411 | south | 2020-09-17 15:00 | 15:00 | 22 | 43 | 411 |  |  | 2020-09-14 | B90636¦Courtroom 211¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Hallway by courtroom 211 | [5 empty] | 21 | 42 | 424 |  | 2020-09-17 15:00 | 15:00 | 21 | 42 | 424 |  |  | 2020-09-14 | B90636¦Hallway by courtroom 211¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Side Entry Door | [5 empty] | 21 | 38 | 460 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 460 |  | caution | 2020-09-14 | B70485¦Side Entry Door¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Outdoors |  |  | 20 | 40 | 411 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B90636¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Filing Area | [5 empty] | 21 | 38 | 418 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 418 |  | caution | 2020-09-14 | B70485¦Filing Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Staff Kitchen | [5 empty] | 21 | 37 | 420 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 420 |  | caution | 2020-09-14 | B70485¦Staff Kitchen¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Hearing Room #2 | [5 empty] | 20 | 41 | 412 |  | 2020-09-17 12:00 | 12:00 | 20 | 41 | 412 |  |  | 2020-09-14 | B70485¦Hearing Room #2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Elevators | [5 empty] | 20 | 44 | 413 |  | 2020-09-17 12:00 | 12:00 | 20 | 44 | 413 |  |  | 2020-09-14 | B70485¦Elevators¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Outdoors |  |  | 16 | 40 | 401 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70485¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Front Security Desk | [5 empty] | 21 | 43 | 478 |  | 2020-09-17 12:00 | 12:00 | 21 | 43 | 478 |  |  | 2020-09-14 | B20705¦Front Security Desk¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family Law Reception | [5 empty] | 21 | 40 | 485 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 485 |  | caution | 2020-09-14 | B20705¦Family Law Reception¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Criminal Court Inquiry | [5 empty] | 22 | 40 | 479 |  | 2020-09-17 12:00 | 12:00 | 22 | 40 | 479 |  | caution | 2020-09-14 | B20705¦Criminal Court Inquiry¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family/Civil Waiting Area | [5 empty] | 22 | 42 | 493 |  | 2020-09-17 12:00 | 12:00 | 22 | 42 | 493 |  |  | 2020-09-14 | B20705¦Family/Civil Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 20-24 Waiting Area | [5 empty] | 22 | 39 | 474 |  | 2020-09-17 12:00 | 12:00 | 22 | 39 | 474 |  | caution | 2020-09-14 | B20705¦Courtroom 20-24 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Security Check In | [5 empty] | 20 | 52 | 437 |  | 2020-09-17 15:00 | 15:00 | 20 | 52 | 437 |  |  | 2020-09-14 | B92624¦Security Check In¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 20 | 54 | 456 | West | 2020-09-17 15:00 | 15:00 | 20 | 54 | 456 |  |  | 2020-09-14 | B92624¦Room 701¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Court Support Office | [5 empty] | 22 | 38 | 437 |  | 2020-09-17 12:00 | 12:00 | 22 | 38 | 437 |  | caution | 2020-09-14 | B20705¦Court Support Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 20 | 53 | 458 | East | 2020-09-17 15:00 | 15:00 | 20 | 53 | 458 |  |  | 2020-09-14 | B92624¦Room 701¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 20 | 53 | 457 | North | 2020-09-17 15:00 | 15:00 | 20 | 53 | 457 |  |  | 2020-09-14 | B92624¦Room 701¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 701 | [5 empty] | 20 | 51 | 431 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 431 |  |  | 2020-09-14 | B92624¦Hallway by Room 701¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 20 | 53 | 442 | East | 2020-09-17 15:00 | 15:00 | 20 | 53 | 442 |  |  | 2020-09-14 | B92624¦Room 718A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 20 | 52 | 440 | West | 2020-09-17 15:00 | 15:00 | 20 | 52 | 440 |  |  | 2020-09-14 | B92624¦Room 718A¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 25-26 Waiting Area | [5 empty] | 22 | 38 | 436 |  | 2020-09-17 12:00 | 12:00 | 22 | 38 | 436 |  | caution | 2020-09-14 | B20705¦Courtroom 25-26 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718B | [5 empty] | 20 | 51 | 447 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 447 |  |  | 2020-09-14 | B92624¦Room 718B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 718A | [5 empty] | 20 | 49 | 451 |  | 2020-09-17 15:00 | 15:00 | 20 | 49 | 451 |  |  | 2020-09-14 | B92624¦Hallway by Room 718A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717A | [5 empty] | 20 | 52 | 493 |  | 2020-09-17 15:00 | 15:00 | 20 | 52 | 493 |  |  | 2020-09-14 | B92624¦Room 717A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717B | [5 empty] | 20 | 52 | 486 |  | 2020-09-17 15:00 | 15:00 | 20 | 52 | 486 |  |  | 2020-09-14 | B92624¦Room 717B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716A | [5 empty] | 19 | 53 | 482 |  | 2020-09-17 15:00 | 15:00 | 19 | 53 | 482 |  |  | 2020-09-14 | B92624¦Room 716A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716B | [5 empty] | 19 | 53 | 478 |  | 2020-09-17 15:00 | 15:00 | 19 | 53 | 478 |  |  | 2020-09-14 | B92624¦Room 716B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715A | [5 empty] | 20 | 51 | 561 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 561 |  |  | 2020-09-14 | B92624¦Room 715A¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 4-6 Waiting Area | [5 empty] | 22 | 37 | 467 |  | 2020-09-17 12:00 | 12:00 | 22 | 37 | 467 |  | caution | 2020-09-14 | B20705¦Courtroom 4-6 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715B | [5 empty] | 20 | 51 | 481 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 481 |  |  | 2020-09-14 | B92624¦Room 715B¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 1-3 Waiting Area | [5 empty] | 22 | 38 | 465 |  | 2020-09-17 12:00 | 12:00 | 22 | 38 | 465 |  | caution | 2020-09-14 | B20705¦Courtroom 1-3 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 7-9 Waiting Area | [5 empty] | 22 | 37 | 457 |  | 2020-09-17 12:00 | 12:00 | 22 | 37 | 457 |  | caution | 2020-09-14 | B20705¦Courtroom 7-9 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714A | [5 empty] | 19 | 53 | 485 |  | 2020-09-17 15:00 | 15:00 | 19 | 53 | 485 |  |  | 2020-09-14 | B92624¦Room 714A¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 10-12 Waiting Area | [5 empty] | 23 | 37 | 435 |  | 2020-09-17 12:00 | 12:00 | 23 | 37 | 435 |  | caution | 2020-09-14 | B20705¦Courtroom 10-12 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714B | [5 empty] | 19 | 53 | 452 |  | 2020-09-17 15:00 | 15:00 | 19 | 53 | 452 |  |  | 2020-09-14 | B92624¦Room 714B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713A | [5 empty] | 20 | 53 | 481 |  | 2020-09-17 15:00 | 15:00 | 20 | 53 | 481 |  |  | 2020-09-14 | B92624¦Room 713A¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 13-14 Waiting Area | [5 empty] | 23 | 23 | 460 |  | 2020-09-17 12:00 | 12:00 | 23 | 23 | 460 |  | low | 2020-09-14 | B20705¦Courtroom 13-14 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713B | [5 empty] | 20 | 52 | 520 |  | 2020-09-17 15:00 | 15:00 | 20 | 52 | 520 |  |  | 2020-09-14 | B92624¦Room 713B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Escalator, 700 | [5 empty] | 20 | 52 | 438 |  | 2020-09-17 15:00 | 15:00 | 20 | 52 | 438 |  |  | 2020-09-14 | B92624¦Hallway by Escalator, 700¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801A | [5 empty] | 20 | 51 | 417 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 417 |  |  | 2020-09-14 | B92624¦Room 801A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801B | [5 empty] | 20 | 51 | 427 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 427 |  |  | 2020-09-14 | B92624¦Room 801B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 801A | [5 empty] | 20 | 51 | 421 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 421 |  |  | 2020-09-14 | B92624¦Hallway by Room 801A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Lounge | [5 empty] | 21 | 48 | 439 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 439 |  |  | 2020-09-14 | B92624¦Lounge¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 34-36 Waiting Area | [5 empty] | 23 | 35 | 447 |  | 2020-09-17 12:00 | 12:00 | 23 | 35 | 447 |  | caution | 2020-09-14 | B20705¦Courtroom 34-36 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-1 | [5 empty] | 20.8 | 48.3 | 695 |  | 2020-09-17 15:00 | 15:00 | 20.8 | 48.3 | 695 |  |  | 2020-09-14 | B10644¦Courtroom 2-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Outdoors |  |  | 19 | 50 | 406 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B92624¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 30-33 Waiting Area | [5 empty] | 23 | 37 | 442 |  | 2020-09-17 12:00 | 12:00 | 23 | 37 | 442 |  | caution | 2020-09-14 | B20705¦Courtroom 30-33 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-2 | [5 empty] | 18.9 | 55.8 | 545 |  | 2020-09-17 15:00 | 15:00 | 18.9 | 55.8 | 545 |  |  | 2020-09-14 | B10644¦Courtroom 2-2¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 4th floor waiting area | [5 empty] | 23 | 36 | 454 |  | 2020-09-17 12:00 | 12:00 | 23 | 36 | 454 |  | caution | 2020-09-14 | B20705¦4th floor waiting area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-3 | [5 empty] | 20.5 | 73 | 419 |  | 2020-09-17 15:00 | 15:00 | 20.5 | 73 | 419 |  | high | 2020-09-14 | B10644¦Courtroom 2-3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Crown Attorney Admin Waiting Area | [5 empty] | 23 | 36 | 446 |  | 2020-09-17 12:00 | 12:00 | 23 | 36 | 446 |  | caution | 2020-09-14 | B20705¦Crown Attorney Admin Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Probation/Parole Waiting Area | [5 empty] | 23 | 37 | 442 |  | 2020-09-17 12:00 | 12:00 | 23 | 37 | 442 |  | caution | 2020-09-14 | B20705¦Probation/Parole Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-4 | [5 empty] | 21.9 | 38.6 | 531 |  | 2020-09-17 15:00 | 15:00 | 21.9 | 38.6 | 531 |  | caution | 2020-09-14 | B10644¦Courtroom 2-4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-5 | [5 empty] | 20.3 | 48 | 390 |  | 2020-09-17 15:00 | 15:00 | 20.3 | 48 | 390 |  |  | 2020-09-14 | B10644¦Courtroom 2-5¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 53-55 Waiting Area | [5 empty] | 22 | 36 | 445 |  | 2020-09-17 12:00 | 12:00 | 22 | 36 | 445 |  | caution | 2020-09-14 | B20705¦Courtroom 53-55 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-6 | [5 empty] | 23.2 | 46.7 | 413 |  | 2020-09-17 15:00 | 15:00 | 23.2 | 46.7 | 413 |  |  | 2020-09-14 | B10644¦Courtroom 2-6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-8 | [5 empty] | 21.1 | 49.1 | 643 |  | 2020-09-17 15:00 | 15:00 | 21.1 | 49.1 | 643 |  |  | 2020-09-14 | B10644¦Courtroom 2-8¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 51-52 Waiting Area | [5 empty] | 22 | 36 | 437 |  | 2020-09-17 12:00 | 12:00 | 22 | 36 | 437 |  | caution | 2020-09-14 | B20705¦Courtroom 51-52 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 6th Floor Waiting Area | [5 empty] | 22 | 35 | 433 |  | 2020-09-17 12:00 | 12:00 | 22 | 35 | 433 |  | caution | 2020-09-14 | B20705¦6th Floor Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Outdoors |  |  | 18 | 31 | 403 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20705¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 3-2 | [5 empty] | 22.2 | 34.5 | 576 |  | 2020-09-17 15:00 | 15:00 | 22.2 | 34.5 | 576 |  | low | 2020-09-14 | B10644¦Courtroom 3-2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Outdoors |  |  | 15 | 34 | 410 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70485¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-1 | [5 empty] | 22.7 | 53.3 | 483 |  | 2020-09-17 15:00 | 15:00 | 22.7 | 53.3 | 483 |  |  | 2020-09-14 | B10644¦Courtroom 4-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-2 | [5 empty] | 20.8 | 50 | 419 |  | 2020-09-17 15:00 | 15:00 | 20.8 | 50 | 419 |  |  | 2020-09-14 | B10644¦Courtroom 4-2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Social Benefits Tribunal Reception | [5 empty] | 22 | 29 | 412 |  | 2020-09-17 15:00 | 15:00 | 22 | 29 | 412 |  | low | 2020-09-14 | B70485¦Social Benefits Tribunal Reception¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-3 | [5 empty] | 25.4 | 50.8 | 405 |  | 2020-09-17 15:00 | 15:00 | 25.4 | 50.8 | 405 |  |  | 2020-09-14 | B10644¦Courtroom 4-3¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #3 | [5 empty] | 22 | 29 | 397 |  | 2020-09-17 15:00 | 15:00 | 22 | 29 | 397 |  | low | 2020-09-14 | B70485¦SBT Hearing Room #3¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #4 | [5 empty] | 22 | 28 | 402 |  | 2020-09-17 15:00 | 15:00 | 22 | 28 | 402 |  | low | 2020-09-14 | B70485¦SBT Hearing Room #4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | LTB Hearing Room #1 | [5 empty] | 22 | 30 | 402 |  | 2020-09-17 15:00 | 15:00 | 22 | 30 | 402 |  | low | 2020-09-14 | B70485¦LTB Hearing Room #1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Regional Managers Office | [5 empty] | 22 | 30 | 405 |  | 2020-09-17 15:00 | 15:00 | 22 | 30 | 405 |  | low | 2020-09-14 | B70485¦Regional Managers Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Cubes outside RM Office | [5 empty] | 21 | 31 | 399 |  | 2020-09-17 15:00 | 15:00 | 21 | 31 | 399 |  | low | 2020-09-14 | B70485¦Cubes outside RM Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #1 | [5 empty] | 21 | 30 | 407 |  | 2020-09-17 15:00 | 15:00 | 21 | 30 | 407 |  | low | 2020-09-14 | B70485¦Mediation Room #1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-4 | [5 empty] | 22.1 | 51.6 | 504 |  | 2020-09-17 15:00 | 15:00 | 22.1 | 51.6 | 504 |  |  | 2020-09-14 | B10644¦Courtroom 4-4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #2 | [5 empty] | 21 | 31 | 405 |  | 2020-09-17 15:00 | 15:00 | 21 | 31 | 405 |  | low | 2020-09-14 | B70485¦Mediation Room #2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-6 | [5 empty] | 22.6 | 51.6 | 380 |  | 2020-09-17 15:00 | 15:00 | 22.6 | 51.6 | 380 |  |  | 2020-09-14 | B10644¦Courtroom 4-6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Reception/ Administration LTB | [5 empty] | 21 | 31 | 414 |  | 2020-09-17 15:00 | 15:00 | 21 | 31 | 414 |  | low | 2020-09-14 | B70485¦Reception/ Administration LTB¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-7 | [5 empty] | 22.4 | 51.1 | 382 |  | 2020-09-17 15:00 | 15:00 | 22.4 | 51.1 | 382 |  |  | 2020-09-14 | B10644¦Courtroom 4-7¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Document Area | [5 empty] | 21 | 31 | 409 |  | 2020-09-17 15:00 | 15:00 | 21 | 31 | 409 |  | low | 2020-09-14 | B70485¦Document Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-8 | [5 empty] | 22.8 | 51.2 | 396 |  | 2020-09-17 15:00 | 15:00 | 22.8 | 51.2 | 396 |  |  | 2020-09-14 | B10644¦Courtroom 4-8¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Copy Room | [5 empty] | 21 | 30 | 404 |  | 2020-09-17 15:00 | 15:00 | 21 | 30 | 404 |  | low | 2020-09-14 | B70485¦Copy Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22.6 | 42.5 | 694 |  | 2020-09-17 15:00 | 15:00 | 22.6 | 42.5 | 694 |  |  | 2020-09-14 | B10644¦Courtroom 5-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-1 | [5 empty] | 21.3 | 54.8 | 395 |  | 2020-09-17 15:00 | 15:00 | 21.3 | 54.8 | 395 |  |  | 2020-09-14 | B10644¦Courtroom 6-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #3 | [5 empty] | 21 | 30 | 408 |  | 2020-09-17 15:00 | 15:00 | 21 | 30 | 408 |  | low | 2020-09-14 | B70485¦Mediation Room #3¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Corner Office | [5 empty] | 20 | 34 | 413 |  | 2020-09-17 15:00 | 15:00 | 20 | 34 | 413 |  | low | 2020-09-14 | B70485¦Corner Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Side Entry Door | [5 empty] | 20 | 35 | 427 |  | 2020-09-17 15:00 | 15:00 | 20 | 35 | 427 |  | caution | 2020-09-14 | B70485¦Side Entry Door¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Filing Area | [5 empty] | 21 | 33 | 414 |  | 2020-09-17 15:00 | 15:00 | 21 | 33 | 414 |  | low | 2020-09-14 | B70485¦Filing Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Staff Kitchen | [5 empty] | 21 | 32 | 418 |  | 2020-09-17 15:00 | 15:00 | 21 | 32 | 418 |  | low | 2020-09-14 | B70485¦Staff Kitchen¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Hearing Room #2 | [5 empty] | 21 | 33 | 412 |  | 2020-09-17 15:00 | 15:00 | 21 | 33 | 412 |  | low | 2020-09-14 | B70485¦Hearing Room #2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Elevators | [5 empty] | 19 | 39 | 420 |  | 2020-09-17 15:00 | 15:00 | 19 | 39 | 420 |  | caution | 2020-09-14 | B70485¦Elevators¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Front Security Desk | [5 empty] | 22 | 33 | 444 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 444 |  | low | 2020-09-14 | B20705¦Front Security Desk¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family Law Reception Area | [5 empty] | 22 | 33 | 459 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 459 |  | low | 2020-09-14 | B20705¦Family Law Reception Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Criminal Court Inquiry Area | [5 empty] | 22 | 33 | 473 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 473 |  | low | 2020-09-14 | B20705¦Criminal Court Inquiry Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family/Civil Division Waiting Area | [5 empty] | 22 | 34 | 505 |  | 2020-09-17 15:00 | 15:00 | 22 | 34 | 505 |  | low | 2020-09-14 | B20705¦Family/Civil Division Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Court Support Office | [5 empty] | 22 | 33 | 457 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 457 |  | low | 2020-09-14 | B20705¦Court Support Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 20-24 Waiting Area | [5 empty] | 20 | 42 | 459 |  | 2020-09-17 15:00 | 15:00 | 20 | 42 | 459 |  |  | 2020-09-14 | B20705¦Courtroom 20-24 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 25-26 Waiting Area | [5 empty] | 22 | 35 | 443 |  | 2020-09-17 15:00 | 15:00 | 22 | 35 | 443 |  | caution | 2020-09-14 | B20705¦Courtroom 25-26 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 4-6 Waiting Area | [5 empty] | 22 | 32 | 467 |  | 2020-09-17 15:00 | 15:00 | 22 | 32 | 467 |  | low | 2020-09-14 | B20705¦Courtroom 4-6 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 1-3 Waiting Area | [5 empty] | 22 | 33 | 484 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 484 |  | low | 2020-09-14 | B20705¦Courtroom 1-3 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 7-9 Waiting Area | [5 empty] | 22 | 32 | 447 |  | 2020-09-17 15:00 | 15:00 | 22 | 32 | 447 |  | low | 2020-09-14 | B20705¦Courtroom 7-9 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 10-12 Waiting Area | [5 empty] | 22 | 32 | 440 |  | 2020-09-17 15:00 | 15:00 | 22 | 32 | 440 |  | low | 2020-09-14 | B20705¦Courtroom 10-12 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 13-14 Waiting Area | [5 empty] | 22 | 32 | 423 |  | 2020-09-17 15:00 | 15:00 | 22 | 32 | 423 |  | low | 2020-09-14 | B20705¦Courtroom 13-14 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 34-36 Waiting Area | [5 empty] | 23 | 30 | 439 |  | 2020-09-17 15:00 | 15:00 | 23 | 30 | 439 |  | low | 2020-09-14 | B20705¦Courtroom 34-36 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 30-33 Waiting Area | [5 empty] | 23 | 32 | 432 |  | 2020-09-17 15:00 | 15:00 | 23 | 32 | 432 |  | low | 2020-09-14 | B20705¦Courtroom 30-33 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Crown Attorney Wing Entrance | [5 empty] | 23 | 33 | 444 |  | 2020-09-17 15:00 | 15:00 | 23 | 33 | 444 |  | low | 2020-09-14 | B20705¦Crown Attorney Wing Entrance¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Probation/Parole Waiting Area | [5 empty] | 23 | 31 | 572 |  | 2020-09-17 15:00 | 15:00 | 23 | 31 | 572 |  | low | 2020-09-14 | B20705¦Probation/Parole Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 4th floor waiting area | [5 empty] | 23 | 31 | 446 |  | 2020-09-17 15:00 | 15:00 | 23 | 31 | 446 |  | low | 2020-09-14 | B20705¦4th floor waiting area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 53-55 Waiting Area | [5 empty] | 23 | 30 | 441 |  | 2020-09-17 15:00 | 15:00 | 23 | 30 | 441 |  | low | 2020-09-14 | B20705¦Courtroom 53-55 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 51-52 Waiting Area | [5 empty] | 23 | 31 | 463 |  | 2020-09-17 15:00 | 15:00 | 23 | 31 | 463 |  | low | 2020-09-14 | B20705¦Courtroom 51-52 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 6th Floor Waiting Area | [5 empty] | 23 | 31 | 436 |  | 2020-09-17 15:00 | 15:00 | 23 | 31 | 436 |  | low | 2020-09-14 | B20705¦6th Floor Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Outdoors |  |  | 19 | 24 | 407 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20705¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Library | [5 empty] | 21.1111 | 42 | 482 |  | 2020-09-17 09:00 | 9:00 | 21.1111 | 42 | 482 |  |  | 2020-09-14 | B10246¦Library¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 20 | 38 | 455 | Justice Wilcox Chambers | 2020-09-17 09:00 | 9:00 | 20 | 38 | 455 |  | caution | 2020-09-14 | B10246¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | 2nd fl lobby | [5 empty] | 21.6667 | 36 | 453 | Middle of hallway | 2020-09-17 09:00 | 9:00 | 21.6667 | 36 | 453 |  | caution | 2020-09-14 | B10246¦2nd fl lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 2 | [5 empty] | 20.5556 | 38 | 458 |  | 2020-09-17 09:00 | 9:00 | 20.5556 | 38 | 458 |  | caution | 2020-09-14 | B10246¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Trial Co-ordinators Office | [5 empty] | 21.1111 | 35 | 507 |  | 2020-09-17 09:00 | 9:00 | 21.1111 | 35 | 507 |  | caution | 2020-09-14 | B10246¦Trial Co-ordinators Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Main Floor Entrance Lobby | [5 empty] | 20.5556 | 34 | 460 | Middle of hallway | 2020-09-17 09:00 | 9:00 | 20.5556 | 34 | 460 |  | low | 2020-09-14 | B10246¦Main Floor Entrance Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 20.5556 | 37 | 464 | Office to the left of office 10 | 2020-09-17 09:00 | 9:00 | 20.5556 | 37 | 464 |  | caution | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 20 | 38 | 456 | Office to the right of office 10 | 2020-09-17 09:00 | 9:00 | 20 | 38 | 456 |  | caution | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Lobby | [5 empty] | 20 | 45 | 559 |  | 2020-09-17 09:00 | 9:00 | 20 | 45 | 559 |  |  | 2020-09-14 | B10002¦Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Outdoors |  |  | 7 | 61 | 368 |  |  |  | North entrance - partly cloudy, light breeze | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B13049¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 2nd fl lobby | [5 empty] | 18 | 41 | 431 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 18 | 41 | 431 |  |  | 2020-09-14 | B13049¦2nd fl lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 250 | [5 empty] | 20 | 35 | 389 | No windows, no plants | 2020-09-17 09:00 | 9:00 | 20 | 35 | 389 |  | caution | 2020-09-14 | B13049¦Courtroom 250¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Skeggs | [5 empty] | 21 | 43 | 564 | Door Open | 2020-09-17 09:00 | 9:00 | 21 | 43 | 564 |  |  | 2020-09-14 | B10002¦Office Skeggs¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Administration office | [5 empty] | 21 | 33 | 423 | Windows closed, 4 plants total at various locations | 2020-09-17 09:00 | 9:00 | 21 | 33 | 423 |  | low | 2020-09-14 | B13049¦Administration office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Cubicle Office | [5 empty] | 22 | 42 | 602 | Door Open | 2020-09-17 09:00 | 9:00 | 22 | 42 | 602 |  |  | 2020-09-14 | B10002¦Cubicle Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 1 (Center) | [5 empty] | 20 | 33 | 439 |  | 2020-09-17 09:00 | 9:00 | 20 | 33 | 439 |  | low | 2020-09-14 | B10246¦Courtroom 1 (Center)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 1st Floor Lobby next to courtroom 122 | [5 empty] | 22 | 31 | 410 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 22 | 31 | 410 |  | low | 2020-09-14 | B13049¦1st Floor Lobby next to courtroom 122¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown attorney admin area | [5 empty] | 20.5556 | 38 | 540 |  | 2020-09-17 09:00 | 9:00 | 20.5556 | 38 | 540 |  | caution | 2020-09-14 | B10246¦Crown attorney admin area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | File Room | [5 empty] | 22 | 40 | 570 |  | 2020-09-17 09:00 | 9:00 | 22 | 40 | 570 |  | caution | 2020-09-14 | B10002¦File Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Administration office | [5 empty] | 20.5556 | 35 | 506 |  | 2020-09-17 09:00 | 9:00 | 20.5556 | 35 | 506 |  | caution | 2020-09-14 | B10246¦Administration office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 122 | [5 empty] | 21 | 31 | 426 | No windows, no plants | 2020-09-17 09:00 | 9:00 | 21 | 31 | 426 |  | low | 2020-09-14 | B13049¦Courtroom 122¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 21.1111 | 35 | 467 | Basement lobby - bottom of the stairs | 2020-09-17 09:00 | 9:00 | 21.1111 | 35 | 467 |  | caution | 2020-09-14 | B10246¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 20.5556 | 37 | 462 | Basement cells - hallway | 2020-09-17 09:00 | 9:00 | 20.5556 | 37 | 462 |  | caution | 2020-09-14 | B10246¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Didiodato | [5 empty] | 22 | 41 | 607 | Door Open | 2020-09-17 09:00 | 9:00 | 22 | 41 | 607 |  |  | 2020-09-14 | B10002¦Office Didiodato¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Outdoors |  |  | 11.1111 | 31 | 407 |  |  |  | Directly outside main entrance: clear and sunny | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10246¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Outdoors |  |  | 16 | 33 | 405 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10002¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Court Security office #142 | [5 empty] | 23 | 30 | 450 | No windows, no plants | 2020-09-17 09:00 | 9:00 | 23 | 30 | 450 |  | low | 2020-09-14 | B13049¦Court Security office #142¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Lobby Administration | [5 empty] | 16 | 56 | 446 |  | 2020-09-17 09:00 | 9:00 | 16 | 56 | 446 |  |  | 2020-09-14 | B10003¦Lobby Administration¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 140 | [5 empty] | 22 | 30 | 424 | No windows, no plants | 2020-09-17 09:00 | 9:00 | 22 | 30 | 424 |  | low | 2020-09-14 | B13049¦Courtroom 140¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Library | [5 empty] | 17 | 54 | 463 | Wall mount AC unit running | 2020-09-17 09:00 | 9:00 | 17 | 54 | 463 |  |  | 2020-09-14 | B10003¦Library¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 20 | 59 | 497 | north section | 2020-09-17 09:00 | 9:00 | 20 | 59 | 497 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 20 | 59 | 488 | south section | 2020-09-17 09:00 | 9:00 | 20 | 59 | 488 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 1st floor cell holding area Hallway | [5 empty] | 21 | 30 | 443 | Across from door #3 - no windows, no plants | 2020-09-17 09:00 | 9:00 | 21 | 30 | 443 |  | low | 2020-09-14 | B13049¦1st floor cell holding area Hallway¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 1E | [5 empty] | 20 | 58 | 486 | ground floor | 2020-09-17 09:00 | 9:00 | 20 | 58 | 486 |  |  | 2020-09-14 | B14164¦Hallway by courtroom 1E¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 20 | 60 | 479 | north section | 2020-09-17 09:00 | 9:00 | 20 | 60 | 479 |  | caution | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Basement Library | [5 empty] | 17 | 53 | 420 |  | 2020-09-17 09:00 | 9:00 | 17 | 53 | 420 |  |  | 2020-09-14 | B10003¦Basement Library¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 20 | 60 | 460 | south section | 2020-09-17 09:00 | 9:00 | 20 | 60 | 460 |  | caution | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by Courtoom 6 | [5 empty] | 20 | 60 | 473 | second floor | 2020-09-17 09:00 | 9:00 | 20 | 60 | 473 |  | caution | 2020-09-14 | B14164¦Hallway by Courtoom 6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtoom 10 | [5 empty] | 20 | 60 | 482 | North section | 2020-09-17 09:00 | 9:00 | 20 | 60 | 482 |  | caution | 2020-09-14 | B14164¦Courtoom 10¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 21 | 59 | 478 | south section | 2020-09-17 09:00 | 9:00 | 21 | 59 | 478 |  |  | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Outdoors |  |  | 15 | 70 | 451 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10639¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 10 | [5 empty] | 21 | 57 | 447 | basement | 2020-09-17 09:00 | 9:00 | 21 | 57 | 447 |  |  | 2020-09-14 | B14164¦Hallway by courtroom 10¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown Attorney Office | [5 empty] | 23 | 31 | 617 | Office #1 - east side - window closed, no plants | 2020-09-17 09:00 | 9:00 | 23 | 31 | 617 |  | low | 2020-09-14 | B13049¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Outdoors |  |  | 16 | 33 | 398 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10003¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, basement | [5 empty] | 21 | 59 | 520 |  | 2020-09-17 09:00 | 9:00 | 21 | 59 | 520 |  |  | 2020-09-14 | B14164¦Common area by elevator, basement¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, ground floor | [5 empty] | 21 | 56 | 493 |  | 2020-09-17 09:00 | 9:00 | 21 | 56 | 493 |  |  | 2020-09-14 | B14164¦Common area by elevator, ground floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Family office, Ground floor | [5 empty] | 21 | 57 | 563 |  | 2020-09-17 09:00 | 9:00 | 21 | 57 | 563 |  |  | 2020-09-14 | B14164¦Family office, Ground floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 6 North side | [5 empty] | 21 | 53 | 470 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 470 |  |  | 2020-09-14 | B10639¦courtroom 6 North side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Family office, ground floor | [5 empty] | 21 | 58 | 557 |  | 2020-09-17 09:00 | 9:00 | 21 | 58 | 557 |  |  | 2020-09-14 | B14164¦Family office, ground floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown Attorney Office | [5 empty] | 22 | 30 | 521 | Office #2 - north side - windows closed, no plants | 2020-09-17 09:00 | 9:00 | 22 | 30 | 521 |  | low | 2020-09-14 | B13049¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 60 | 483 | east | 2020-09-17 09:00 | 9:00 | 22 | 60 | 483 |  | caution | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 6 south | [5 empty] | 21 | 53 | 470 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 470 |  |  | 2020-09-14 | B10639¦courtroom 6 south¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 60 | 473 | west | 2020-09-17 09:00 | 9:00 | 22 | 60 | 473 |  | caution | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, second floor | [5 empty] | 21 | 56 | 511 |  | 2020-09-17 09:00 | 9:00 | 21 | 56 | 511 |  |  | 2020-09-14 | B14164¦Common area by elevator, second floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown attorney admin area | [5 empty] | 23 | 29 | 512 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 23 | 29 | 512 |  | low | 2020-09-14 | B13049¦Crown attorney admin area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 21 | 60 | 481 | east | 2020-09-17 09:00 | 9:00 | 21 | 60 | 481 |  | caution | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Outdoors |  |  | 19 | 57 | 423 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B14164¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 21 | 60 | 479 | west | 2020-09-17 09:00 | 9:00 | 21 | 60 | 479 |  | caution | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 21 | 60 | 496 | east | 2020-09-17 09:00 | 9:00 | 21 | 60 | 496 |  | caution | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 6 | [5 empty] | 21 | 53 | 468 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 468 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 21 | 60 | 485 | west | 2020-09-17 09:00 | 9:00 | 21 | 60 | 485 |  | caution | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 5 North side | [5 empty] | 21 | 56 | 506 |  | 2020-09-17 09:00 | 9:00 | 21 | 56 | 506 |  |  | 2020-09-14 | B10639¦courtroom 5 North side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 5 South side | [5 empty] | 21 | 55 | 490 |  | 2020-09-17 09:00 | 9:00 | 21 | 55 | 490 |  |  | 2020-09-14 | B10639¦courtroom 5 South side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 5 | [5 empty] | 21 | 54 | 515 |  | 2020-09-17 09:00 | 9:00 | 21 | 54 | 515 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 5¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 3 south east side | [5 empty] | 20 | 62 | 510 |  | 2020-09-17 09:00 | 9:00 | 20 | 62 | 510 |  | caution | 2020-09-14 | B10639¦courtroom 3 south east side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 3 northeast side | [5 empty] | 20 | 59 | 484 |  | 2020-09-17 09:00 | 9:00 | 20 | 59 | 484 |  |  | 2020-09-14 | B10639¦courtroom 3 northeast side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 21 | 60 | 511 | east | 2020-09-17 09:00 | 9:00 | 21 | 60 | 511 |  | caution | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | hallway by courtroom 3 | [5 empty] | 20 | 57 | 485 |  | 2020-09-17 09:00 | 9:00 | 20 | 57 | 485 |  |  | 2020-09-14 | B10639¦hallway by courtroom 3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 22 | 60 | 480 | west | 2020-09-17 09:00 | 9:00 | 22 | 60 | 480 |  | caution | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Outdoors |  |  | 12 | 37 | 411 |  |  |  | Window closed, no plants | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B13095¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 58 | 470 | east | 2020-09-17 09:00 | 9:00 | 22 | 58 | 470 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | lobby by statue | [5 empty] | 21 | 53 | 459 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 459 |  |  | 2020-09-14 | B10639¦lobby by statue¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Hallway | [5 empty] | 21 | 34 | 446 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 21 | 34 | 446 |  | low | 2020-09-14 | B13095¦Hallway¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby East Side | [5 empty] | 21 | 52 | 510 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 510 |  |  | 2020-09-14 | B10639¦Entrance Lobby East Side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 58 | 476 | west | 2020-09-17 09:00 | 9:00 | 22 | 58 | 476 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 58 | 480 | east | 2020-09-17 09:00 | 9:00 | 22 | 58 | 480 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby West Side | [5 empty] | 21 | 52 | 510 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 510 |  |  | 2020-09-14 | B10639¦Entrance Lobby West Side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 58 | 487 | west | 2020-09-17 09:00 | 9:00 | 22 | 58 | 487 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by COA intake office | [5 empty] | 21 | 52 | 548 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 548 |  |  | 2020-09-14 | B10639¦Hallway by COA intake office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by Law Society of Ontario | [5 empty] | 21 | 51 | 480 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 480 |  |  | 2020-09-14 | B10639¦Hallway by Law Society of Ontario¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Outdoors |  |  | 17 | 66 | 448 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20265¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 59 | 484 | east | 2020-09-17 09:00 | 9:00 | 21 | 59 | 484 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | office - B04A | [5 empty] | 21 |  | 34 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 21 |  | 34 |  |  | 2020-09-14 | B13095¦office - B04A¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 59 | 484 | west | 2020-09-17 09:00 | 9:00 | 21 | 59 | 484 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 north side | [5 empty] | 22 | 51 | 475 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 475 |  |  | 2020-09-14 | B20265¦courtroom M1 north side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 south side | [5 empty] | 22 | 51 | 465 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 465 |  |  | 2020-09-14 | B20265¦courtroom M1 south side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 21 | 59 | 482 | east | 2020-09-17 09:00 | 9:00 | 21 | 59 | 482 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by Courtroom M1 | [5 empty] | 22 | 53 | 482 |  | 2020-09-17 09:00 | 9:00 | 22 | 53 | 482 |  |  | 2020-09-14 | B20265¦hallway by Courtroom M1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 21 | 58 | 494 | east | 2020-09-17 09:00 | 9:00 | 21 | 58 | 494 |  |  | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 21 | 59 | 482 |  | 2020-09-17 09:00 | 9:00 | 21 | 59 | 482 |  |  | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom J south side | [5 empty] | 22 | 50 | 477 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 477 |  |  | 2020-09-14 | B20265¦courtroom J south side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Main Lobby | [5 empty] | 22 | 35 | 579 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 22 | 35 | 579 |  | caution | 2020-09-14 | B13095¦Main Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom J north side | [5 empty] | 22 | 50 | 473 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 473 |  |  | 2020-09-14 | B20265¦courtroom J north side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 21 | 59 | 501 | east | 2020-09-17 09:00 | 9:00 | 21 | 59 | 501 |  |  | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 21 | 60 | 512 | west | 2020-09-17 09:00 | 9:00 | 21 | 60 | 512 |  | caution | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom J | [5 empty] | 22 | 50 | 496 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 496 |  |  | 2020-09-14 | B20265¦hallway by courtroom J¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G south side | [5 empty] | 23 | 59 | 493 |  | 2020-09-17 09:00 | 9:00 | 23 | 59 | 493 |  |  | 2020-09-14 | B20265¦courtroom G south side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 21 | 54 | 500 | east | 2020-09-17 09:00 | 9:00 | 21 | 54 | 500 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 21 | 54 | 505 | west | 2020-09-17 09:00 | 9:00 | 21 | 54 | 505 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G north side | [5 empty] | 22 | 50 | 499 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 499 |  |  | 2020-09-14 | B20265¦courtroom G north side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 59 | 495 | east | 2020-09-17 09:00 | 9:00 | 21 | 59 | 495 |  |  | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 121 west side | [5 empty] | 22 | 47 | 460 |  | 2020-09-17 09:00 | 9:00 | 22 | 47 | 460 |  |  | 2020-09-14 | B20265¦courtroom 121 west side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 59 | 480 | west | 2020-09-17 09:00 | 9:00 | 21 | 59 | 480 |  |  | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 121 East side | [5 empty] | 22 | 47 | 463 |  | 2020-09-17 09:00 | 9:00 | 22 | 47 | 463 |  |  | 2020-09-14 | B20265¦courtroom 121 East side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Outdoors |  |  | 19 | 61 | 489 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B91122¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 123 east side | [5 empty] | 22 | 50 | 470 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 470 |  |  | 2020-09-14 | B20265¦courtroom 123 east side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 123 west side | [5 empty] | 22 | 49 | 461 |  | 2020-09-17 09:00 | 9:00 | 22 | 49 | 461 |  |  | 2020-09-14 | B20265¦courtroom 123 west side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 east side | [5 empty] | 22 | 51 | 485 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 485 |  |  | 2020-09-14 | B20265¦courtroom 124 east side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 west side | [5 empty] | 22 | 50 | 485 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 485 |  |  | 2020-09-14 | B20265¦courtroom 124 west side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Outdoors |  |  | 7 | 55 | 417 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B12955¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 125 south side | [5 empty] | 22 | 47 | 465 |  | 2020-09-17 09:00 | 9:00 | 22 | 47 | 465 |  |  | 2020-09-14 | B20265¦courtroom 125 south side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Main Floor Entrance Lobby | [5 empty] | 9 | 60 | 456 | front lobby | 2020-09-17 09:00 | 9:00 | 9 | 60 | 456 |  | caution | 2020-09-14 | B12955¦Main Floor Entrance Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 125 north side | [5 empty] | 21 | 49 | 457 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 457 |  |  | 2020-09-14 | B20265¦courtroom 125 north side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | OTHER | [5 empty] | 11 | 69 | 494 | waiting room | 2020-09-17 09:00 | 9:00 | 11 | 69 | 494 |  | high | 2020-09-14 | B12955¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 126 south side | [5 empty] | 22 | 47 | 473 |  | 2020-09-17 09:00 | 9:00 | 22 | 47 | 473 |  |  | 2020-09-14 | B20265¦courtroom 126 south side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Administration office | [5 empty] | 15 | 64 | 505 |  | 2020-09-17 09:00 | 9:00 | 15 | 64 | 505 |  | caution | 2020-09-14 | B12955¦Administration office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 203 | [5 empty] | 18 | 53 | 452 |  | 2020-09-17 09:00 | 9:00 | 18 | 53 | 452 |  |  | 2020-09-14 | B12955¦Courtroom 203¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom 126 | [5 empty] | 23 | 49 | 483 |  | 2020-09-17 09:00 | 9:00 | 23 | 49 | 483 |  |  | 2020-09-14 | B20265¦hallway by courtroom 126¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 103 | [5 empty] | 17 | 56 | 418 |  | 2020-09-17 09:00 | 9:00 | 17 | 56 | 418 |  |  | 2020-09-14 | B12955¦Courtroom 103¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by receiving | [5 empty] | 20 | 61 | 555 |  | 2020-09-17 09:00 | 9:00 | 20 | 61 | 555 |  | caution | 2020-09-14 | B20265¦hallway by receiving¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Outdoors |  |  | 20 | 50 | 440 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10639¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 6 north side | [5 empty] | 21 | 50 | 443 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 443 |  |  | 2020-09-14 | B10639¦courtroom 6 north side¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Lunch Room | [5 empty] | 23 | 54 | 489 |  | 2020-09-17 09:00 | 9:00 | 23 | 54 | 489 |  |  | 2020-09-14 | B70451¦Lunch Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 23 | 54 | 504 | east | 2020-09-17 09:00 | 9:00 | 23 | 54 | 504 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 6 south side | [5 empty] | 21 | 48 | 443 |  | 2020-09-17 12:00 | 12:00 | 21 | 48 | 443 |  |  | 2020-09-14 | B10639¦courtroom 6 south side¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 23 | 54 | 497 | west | 2020-09-17 09:00 | 9:00 | 23 | 54 | 497 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 6 | [5 empty] | 21 | 49 | 458 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 458 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 6¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 602 | [5 empty] | 23 | 55 | 511 |  | 2020-09-17 09:00 | 9:00 | 23 | 55 | 511 |  |  | 2020-09-14 | B70451¦hallway by courtroom 602¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 5 North side | [5 empty] | 21 | 49 | 445 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 445 |  |  | 2020-09-14 | B10639¦courtroom 5 North side¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 603 | [5 empty] | 23 | 55 | 509 |  | 2020-09-17 09:00 | 9:00 | 23 | 55 | 509 |  |  | 2020-09-14 | B70451¦hallway by courtroom 603¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | conference room 4 | [5 empty] | 23 | 54 | 488 |  | 2020-09-17 09:00 | 9:00 | 23 | 54 | 488 |  |  | 2020-09-14 | B70451¦conference room 4¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Lobby | [5 empty] | 23 | 32 | 583 |  | 2020-09-17 12:00 | 12:00 | 23 | 32 | 583 |  | low | 2020-09-14 | B10002¦Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 5 south side | [5 empty] | 21 | 48 | 440 |  | 2020-09-17 12:00 | 12:00 | 21 | 48 | 440 |  |  | 2020-09-14 | B10639¦courtroom 5 south side¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 56 | 496 | east | 2020-09-17 09:00 | 9:00 | 23 | 56 | 496 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 56 | 475 | west | 2020-09-17 09:00 | 9:00 | 23 | 56 | 475 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 5 | [5 empty] | 21 | 48 | 443 |  | 2020-09-17 12:00 | 12:00 | 21 | 48 | 443 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 5¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 607 | [5 empty] | 23 | 56 | 484 |  | 2020-09-17 09:00 | 9:00 | 23 | 56 | 484 |  |  | 2020-09-14 | B70451¦hallway by courtroom 607¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 3 southeast side | [5 empty] | 22 | 49 | 457 |  | 2020-09-17 12:00 | 12:00 | 22 | 49 | 457 |  |  | 2020-09-14 | B10639¦courtroom 3 southeast side¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | enforcement/finance office | [5 empty] | 23 | 55 | 509 |  | 2020-09-17 09:00 | 9:00 | 23 | 55 | 509 |  |  | 2020-09-14 | B70451¦enforcement/finance office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Skeggs | [5 empty] | 22 | 34 | 615 | Door Open | 2020-09-17 12:00 | 12:00 | 22 | 34 | 615 |  | low | 2020-09-14 | B10002¦Office Skeggs¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 22 | 57 | 487 | east | 2020-09-17 09:00 | 9:00 | 22 | 57 | 487 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 3 northeast side | [5 empty] | 22 | 49 | 453 |  | 2020-09-17 12:00 | 12:00 | 22 | 49 | 453 |  |  | 2020-09-14 | B10639¦courtroom 3 northeast side¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 22 | 57 | 475 | west | 2020-09-17 09:00 | 9:00 | 22 | 57 | 475 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 605 | [5 empty] | 22 | 57 | 485 |  | 2020-09-17 09:00 | 9:00 | 22 | 57 | 485 |  |  | 2020-09-14 | B70451¦hallway by courtroom 605¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | hallway by courtroom 3 | [5 empty] | 22 | 49 | 478 |  | 2020-09-17 12:00 | 12:00 | 22 | 49 | 478 |  |  | 2020-09-14 | B10639¦hallway by courtroom 3¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters administration office | [5 empty] | 23 | 54 | 492 |  | 2020-09-17 09:00 | 9:00 | 23 | 54 | 492 |  |  | 2020-09-14 | B70451¦masters administration office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | lobby by statue | [5 empty] | 21 | 53 | 463 |  | 2020-09-17 12:00 | 12:00 | 21 | 53 | 463 |  |  | 2020-09-14 | B10639¦lobby by statue¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-10 | [5 empty] | 23 | 54 | 483 |  | 2020-09-17 09:00 | 9:00 | 23 | 54 | 483 |  |  | 2020-09-14 | B70451¦room 6-10¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-9 | [5 empty] | 22 | 55 | 495 |  | 2020-09-17 09:00 | 9:00 | 22 | 55 | 495 |  |  | 2020-09-14 | B70451¦room 6-9¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby East Side | [5 empty] | 21 | 52 | 473 |  | 2020-09-17 12:00 | 12:00 | 21 | 52 | 473 |  |  | 2020-09-14 | B10639¦Entrance Lobby East Side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Cubicle Office | [5 empty] | 23 | 31 | 599 | Door Open | 2020-09-17 12:00 | 12:00 | 23 | 31 | 599 |  | low | 2020-09-14 | B10002¦Cubicle Office¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters library | [5 empty] | 22 | 55 | 485 |  | 2020-09-17 09:00 | 9:00 | 22 | 55 | 485 |  |  | 2020-09-14 | B70451¦masters library¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby West Side | [5 empty] | 21 | 52 | 510 |  | 2020-09-17 12:00 | 12:00 | 21 | 52 | 510 |  |  | 2020-09-14 | B10639¦Entrance Lobby West Side¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-4 | [5 empty] | 23 | 52 | 490 |  | 2020-09-17 09:00 | 9:00 | 23 | 52 | 490 |  |  | 2020-09-14 | B70451¦room 6-4¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | reception area-masters | [5 empty] | 23 | 55 | 493 |  | 2020-09-17 09:00 | 9:00 | 23 | 55 | 493 |  |  | 2020-09-14 | B70451¦reception area-masters¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by COA intake office | [5 empty] | 21 | 51 | 480 |  | 2020-09-17 12:00 | 12:00 | 21 | 51 | 480 |  |  | 2020-09-14 | B10639¦Hallway by COA intake office¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Outdoors |  |  | 19 | 61 | 489 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70451¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by Law Society of Ontario | [5 empty] | 21 | 50 | 470 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 470 |  |  | 2020-09-14 | B10639¦Hallway by Law Society of Ontario¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Library | [5 empty] | 21.1111 | 37 | 507 |  | 2020-09-17 12:00 | 12:00 | 21.1111 | 37 | 507 |  | caution | 2020-09-14 | B10246¦Library¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Outdoors |  |  | 18 | 60 | 438 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20265¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | File Room | [5 empty] | 23 | 34 | 605 |  | 2020-09-17 12:00 | 12:00 | 23 | 34 | 605 |  | low | 2020-09-14 | B10002¦File Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Lunch Room | [5 empty] | 23 | 53 | 528 |  | 2020-09-17 12:00 | 12:00 | 23 | 53 | 528 |  |  | 2020-09-14 | B70451¦Lunch Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 north side | [5 empty] | 22 | 51 | 526 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 526 |  |  | 2020-09-14 | B20265¦courtroom M1 north side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 23 | 53 | 507 | east | 2020-09-17 12:00 | 12:00 | 23 | 53 | 507 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 21.1111 | 33 | 480 | Justice Wilcox Chambers | 2020-09-17 12:00 | 12:00 | 21.1111 | 33 | 480 |  | low | 2020-09-14 | B10246¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 22 | 53 | 500 | west | 2020-09-17 12:00 | 12:00 | 22 | 53 | 500 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 602 | [5 empty] | 23 | 53 | 513 |  | 2020-09-17 12:00 | 12:00 | 23 | 53 | 513 |  |  | 2020-09-14 | B70451¦hallway by courtroom 602¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 south side | [5 empty] | 22 | 50 | 533 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 533 |  |  | 2020-09-14 | B20265¦courtroom M1 south side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 603 | [5 empty] | 23 | 52 | 514 |  | 2020-09-17 12:00 | 12:00 | 23 | 52 | 514 |  |  | 2020-09-14 | B70451¦hallway by courtroom 603¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by Courtroom M1 | [5 empty] | 22 | 52 | 520 |  | 2020-09-17 12:00 | 12:00 | 22 | 52 | 520 |  |  | 2020-09-14 | B20265¦hallway by Courtroom M1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Didiodato | [5 empty] | 22 | 36 | 651 | Door Open | 2020-09-17 12:00 | 12:00 | 22 | 36 | 651 |  | caution | 2020-09-14 | B10002¦Office Didiodato¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | 2nd fl lobby | [5 empty] | 21.1111 | 32 | 474 | Middle of hallway | 2020-09-17 12:00 | 12:00 | 21.1111 | 32 | 474 |  | low | 2020-09-14 | B10246¦2nd fl lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom J south side | [5 empty] | 22 | 50 | 520 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 520 |  |  | 2020-09-14 | B20265¦courtroom J south side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | conference room 4 | [5 empty] | 23 | 51 | 482 |  | 2020-09-17 12:00 | 12:00 | 23 | 51 | 482 |  |  | 2020-09-14 | B70451¦conference room 4¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Outdoors |  |  | 11 | 28 | 377 |  |  |  | North entrance - partly cloudy, light breeze | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B21030¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 52 | 501 | east | 2020-09-17 12:00 | 12:00 | 23 | 52 | 501 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom J north side | [5 empty] | 22 | 50 | 522 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 522 |  |  | 2020-09-14 | B20265¦courtroom J north side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 52 | 484 | west | 2020-09-17 12:00 | 12:00 | 23 | 52 | 484 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 2 | [5 empty] | 21.6111 | 34 | 557 |  | 2020-09-17 12:00 | 12:00 | 21.6111 | 34 | 557 |  | low | 2020-09-14 | B10246¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom J | [5 empty] | 22 | 50 | 526 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 526 |  |  | 2020-09-14 | B20265¦hallway by courtroom J¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 607 | [5 empty] | 24 | 51 | 519 |  | 2020-09-17 12:00 | 12:00 | 24 | 51 | 519 |  |  | 2020-09-14 | B70451¦hallway by courtroom 607¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Trial Co-ordinators Office | [5 empty] | 21.6667 | 30 | 555 |  | 2020-09-17 12:00 | 12:00 | 21.6667 | 30 | 555 |  | low | 2020-09-14 | B10246¦Trial Co-ordinators Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G south side | [5 empty] | 22 | 50 | 564 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 564 |  |  | 2020-09-14 | B20265¦courtroom G south side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | enforcement/finance office | [5 empty] | 23 | 50 | 506 |  | 2020-09-17 12:00 | 12:00 | 23 | 50 | 506 |  |  | 2020-09-14 | B70451¦enforcement/finance office¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Boardroom used as a courtroom | [5 empty] | 22 | 30 | 487 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 22 | 30 | 487 |  | low | 2020-09-14 | B21030¦Boardroom used as a courtroom¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Main Floor Entrance Lobby | [5 empty] | 21.1111 | 31 | 484 | Middle of hallway | 2020-09-17 12:00 | 12:00 | 21.1111 | 31 | 484 |  | low | 2020-09-14 | B10246¦Main Floor Entrance Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 23 | 51 | 504 | east | 2020-09-17 12:00 | 12:00 | 23 | 51 | 504 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G north side | [5 empty] | 22 | 50 | 590 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 590 |  |  | 2020-09-14 | B20265¦courtroom G north side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Outdoors |  |  | 15 | 31 | 402 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10002¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 21.1111 | 33 | 490 | Office to the left of office 10 | 2020-09-17 12:00 | 12:00 | 21.1111 | 33 | 490 |  | low | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 23 | 51 | 501 | west | 2020-09-17 12:00 | 12:00 | 23 | 51 | 501 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 605 | [5 empty] | 23 | 52 | 549 |  | 2020-09-17 12:00 | 12:00 | 23 | 52 | 549 |  |  | 2020-09-14 | B70451¦hallway by courtroom 605¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 121 west side | [5 empty] | 22 | 48 | 544 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 544 |  |  | 2020-09-14 | B20265¦courtroom 121 west side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters administration office | [5 empty] | 23 | 52 | 494 |  | 2020-09-17 12:00 | 12:00 | 23 | 52 | 494 |  |  | 2020-09-14 | B70451¦masters administration office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 121 east side | [5 empty] | 21 | 49 | 533 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 533 |  |  | 2020-09-14 | B20265¦courtroom 121 east side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-10 | [5 empty] | 23 | 51 | 480 |  | 2020-09-17 12:00 | 12:00 | 23 | 51 | 480 |  |  | 2020-09-14 | B70451¦room 6-10¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | 2nd Floor Holding Cell (hallway) | [5 empty] | 23 | 28 | 462 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 23 | 28 | 462 |  | low | 2020-09-14 | B21030¦2nd Floor Holding Cell (hallway)¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-9 | [5 empty] | 22 | 53 | 484 |  | 2020-09-17 12:00 | 12:00 | 22 | 53 | 484 |  |  | 2020-09-14 | B70451¦room 6-9¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 123 east side | [5 empty] | 22 | 52 | 558 |  | 2020-09-17 12:00 | 12:00 | 22 | 52 | 558 |  |  | 2020-09-14 | B20265¦courtroom 123 east side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters library | [5 empty] | 22 | 53 | 485 |  | 2020-09-17 12:00 | 12:00 | 22 | 53 | 485 |  |  | 2020-09-14 | B70451¦masters library¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-4 | [5 empty] | 22 | 53 | 486 |  | 2020-09-17 12:00 | 12:00 | 22 | 53 | 486 |  |  | 2020-09-14 | B70451¦room 6-4¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Lobby Administration | [5 empty] | 18 | 53 | 543 |  | 2020-09-17 12:00 | 12:00 | 18 | 53 | 543 |  |  | 2020-09-14 | B10003¦Lobby Administration¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 123 west side | [5 empty] | 22 | 51 | 548 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 548 |  |  | 2020-09-14 | B20265¦courtroom 123 west side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 21.1111 | 33 | 487 | Office to the right of office 10 | 2020-09-17 12:00 | 12:00 | 21.1111 | 33 | 487 |  | low | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | reception area-masters | [5 empty] | 22 | 53 | 484 |  | 2020-09-17 12:00 | 12:00 | 22 | 53 | 484 |  |  | 2020-09-14 | B70451¦reception area-masters¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 1 (Center) | [5 empty] | 20.5556 | 28 | 443 |  | 2020-09-17 12:00 | 12:00 | 20.5556 | 28 | 443 |  | low | 2020-09-14 | B10246¦Courtroom 1 (Center)¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Outdoors |  |  | 19 | 55 | 500 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70451¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Courtroom 113 | [5 empty] | 24 | 28 | 621 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 24 | 28 | 621 |  | low | 2020-09-14 | B21030¦Courtroom 113¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 east side | [5 empty] | 22 | 50 | 605 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 605 |  |  | 2020-09-14 | B20265¦courtroom 124 east side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 west side | [5 empty] | 22 | 50 | 607 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 607 |  |  | 2020-09-14 | B20265¦courtroom 124 west side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 125 south side | [5 empty] | 21 | 48 | 542 |  | 2020-09-17 12:00 | 12:00 | 21 | 48 | 542 |  |  | 2020-09-14 | B20265¦courtroom 125 south side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown attorney admin area | [5 empty] | 21.6667 | 33 | 489 |  | 2020-09-17 12:00 | 12:00 | 21.6667 | 33 | 489 |  | low | 2020-09-14 | B10246¦Crown attorney admin area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 125 north side | [5 empty] | 21 | 50 | 549 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 549 |  |  | 2020-09-14 | B20265¦courtroom 125 north side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Library | [5 empty] | 18 | 52 | 553 | Wall mount AC unit running | 2020-09-17 12:00 | 12:00 | 18 | 52 | 553 |  |  | 2020-09-14 | B10003¦Library¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 126 south side | [5 empty] | 22 | 48 | 508 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 508 |  |  | 2020-09-14 | B20265¦courtroom 126 south side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom 126 | [5 empty] | 22 | 50 | 538 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 538 |  |  | 2020-09-14 | B20265¦hallway by courtroom 126¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Administration office | [5 empty] | 22.2222 | 29 | 498 |  | 2020-09-17 12:00 | 12:00 | 22.2222 | 29 | 498 |  | low | 2020-09-14 | B10246¦Administration office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by recieving | [5 empty] | 20 | 55 | 525 |  | 2020-09-17 12:00 | 12:00 | 20 | 55 | 525 |  |  | 2020-09-14 | B20265¦hallway by recieving¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Basement cells - hallway | [5 empty] | 21.6667 | 31 | 478 |  | 2020-09-17 12:00 | 12:00 | 21.6667 | 31 | 478 |  | low | 2020-09-14 | B10246¦Basement cells - hallway¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Administration office | [5 empty] | 24 | 28 | 596 | Windows closed - 4 plants total along south window | 2020-09-17 09:00 | 9:00 | 24 | 28 | 596 |  | low | 2020-09-14 | B21030¦Administration office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Basement lobby - bottom of stairs | [5 empty] | 20.5556 | 33 | 471 |  | 2020-09-17 12:00 | 12:00 | 20.5556 | 33 | 471 |  | low | 2020-09-14 | B10246¦Basement lobby - bottom of stairs¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 21 | 59 | 727 | north section | 2020-09-17 12:00 | 12:00 | 21 | 59 | 727 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Basement Library | [5 empty] | 17 | 52 | 437 |  | 2020-09-17 12:00 | 12:00 | 17 | 52 | 437 |  |  | 2020-09-14 | B10003¦Basement Library¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 21 | 59 | 758 | south section | 2020-09-17 12:00 | 12:00 | 21 | 59 | 758 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by Courtrooom 1E | [5 empty] | 21 | 57 | 514 | ground floor | 2020-09-17 12:00 | 12:00 | 21 | 57 | 514 |  |  | 2020-09-14 | B14164¦Hallway by Courtrooom 1E¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Outdoors |  |  | 15 | 33 | 410 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10003¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 20 | 60 | 624 | north section | 2020-09-17 12:00 | 12:00 | 20 | 60 | 624 |  | caution | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown attorney lobby | [5 empty] | 24 | 29 | 674 | No windows, no plants | 2020-09-17 09:00 | 9:00 | 24 | 29 | 674 |  | low | 2020-09-14 | B21030¦Crown attorney lobby¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 20 | 60 | 563 | south section | 2020-09-17 12:00 | 12:00 | 20 | 60 | 563 |  | caution | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Outdoors |  |  | 12.6111 | 24 | 429 |  |  |  | Directly outside main entrance: clear/sunny | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10246¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown attorney admin area | [5 empty] | 24 | 28 | 524 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 24 | 28 | 524 |  | low | 2020-09-14 | B21030¦Crown attorney admin area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 24 | 27 | 476 | Office #1 - SW corner - windows closed, no plants | 2020-09-17 09:00 | 9:00 | 24 | 27 | 476 |  | low | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 24 | 29 | 574 | Office #2 - NE corner - no windows, no plants | 2020-09-17 09:00 | 9:00 | 24 | 29 | 574 |  | low | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 6 | [5 empty] | 20 | 60 | 552 | second floor | 2020-09-17 12:00 | 12:00 | 20 | 60 | 552 |  | caution | 2020-09-14 | B14164¦Hallway by courtroom 6¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 21 | 64 | 860 | north section | 2020-09-17 12:00 | 12:00 | 21 | 64 | 860 |  | caution | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 22 | 62 | 841 | south section | 2020-09-17 12:00 | 12:00 | 22 | 62 | 841 |  | caution | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by Courtroom 10 | [5 empty] | 22 | 56 | 567 | basement | 2020-09-17 12:00 | 12:00 | 22 | 56 | 567 |  |  | 2020-09-14 | B14164¦Hallway by Courtroom 10¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, basement | [5 empty] | 21 | 57 | 598 |  | 2020-09-17 12:00 | 12:00 | 21 | 57 | 598 |  |  | 2020-09-14 | B14164¦Common area by elevator, basement¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, ground floor | [5 empty] | 21 | 57 | 523 |  | 2020-09-17 12:00 | 12:00 | 21 | 57 | 523 |  |  | 2020-09-14 | B14164¦Common area by elevator, ground floor¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Youth office, ground floor | [5 empty] | 21 | 58 | 627 |  | 2020-09-17 12:00 | 12:00 | 21 | 58 | 627 |  |  | 2020-09-14 | B14164¦Youth office, ground floor¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Family office, ground floor | [5 empty] | 21 | 58 | 578 |  | 2020-09-17 12:00 | 12:00 | 21 | 58 | 578 |  |  | 2020-09-14 | B14164¦Family office, ground floor¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | common area by elevator, second floor | [5 empty] | 21 | 57 | 534 |  | 2020-09-17 12:00 | 12:00 | 21 | 57 | 534 |  |  | 2020-09-14 | B14164¦common area by elevator, second floor¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Outdoors |  |  | 20 | 55 | 431 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B14164¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Outdoors |  |  | 11 | 32 | 415 |  |  |  | North entrance - partly cloudy, light breeze | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B21030¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Boardroom used as a courtroom | [5 empty] | 23 | 28 | 497 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 23 | 28 | 497 |  | low | 2020-09-14 | B21030¦Boardroom used as a courtroom¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | 2nd Floor Holding Cell (hallway) | [5 empty] | 23 | 27 | 474 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 23 | 27 | 474 |  | low | 2020-09-14 | B21030¦2nd Floor Holding Cell (hallway)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Courtroom 113 | [5 empty] | 24 | 26 | 500 | Windows closed, no windows | 2020-09-17 15:00 | 15:00 | 24 | 26 | 500 |  | low | 2020-09-14 | B21030¦Courtroom 113¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Administration office | [5 empty] | 25 | 26 | 474 | Windows closed, 4 plants total along south window | 2020-09-17 15:00 | 15:00 | 25 | 26 | 474 |  | low | 2020-09-14 | B21030¦Administration office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown attorney lobby | [5 empty] | 24 | 29 | 566 | No windows, no plants | 2020-09-17 15:00 | 15:00 | 24 | 29 | 566 |  | low | 2020-09-14 | B21030¦Crown attorney lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown attorney admin area | [5 empty] | 24 | 27 | 521 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 24 | 27 | 521 |  | low | 2020-09-14 | B21030¦Crown attorney admin area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Coourtroom 1E | [5 empty] | 22 | 51 | 595 | north section | 2020-09-17 15:00 | 15:00 | 22 | 51 | 595 |  |  | 2020-09-14 | B14164¦Coourtroom 1E¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 22 | 51 | 586 | south section | 2020-09-17 15:00 | 15:00 | 22 | 51 | 586 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by Courtroom 1E | [5 empty] | 23 | 49 | 525 | ground floor | 2020-09-17 15:00 | 15:00 | 23 | 49 | 525 |  |  | 2020-09-14 | B14164¦Hallway by Courtroom 1E¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 21 | 57 | 579 | north section | 2020-09-17 15:00 | 15:00 | 21 | 57 | 579 |  |  | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 21 | 57 | 596 | south section | 2020-09-17 15:00 | 15:00 | 21 | 57 | 596 |  |  | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 24 | 26 | 477 | Office #1 - SW corner - windows closed, no plants | 2020-09-17 15:00 | 15:00 | 24 | 26 | 477 |  | low | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 6 | [5 empty] | 20 | 56 | 537 | second floor | 2020-09-17 15:00 | 15:00 | 20 | 56 | 537 |  |  | 2020-09-14 | B14164¦Hallway by courtroom 6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 21 | 58 | 701 | north section | 2020-09-17 15:00 | 15:00 | 21 | 58 | 701 |  |  | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 22 | 57 | 721 | south section | 2020-09-17 15:00 | 15:00 | 22 | 57 | 721 |  |  | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 10 | [5 empty] | 22 | 54 | 563 | basement | 2020-09-17 15:00 | 15:00 | 22 | 54 | 563 |  |  | 2020-09-14 | B14164¦Hallway by courtroom 10¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, basement | [5 empty] | 21 | 54 | 583 |  | 2020-09-17 15:00 | 15:00 | 21 | 54 | 583 |  |  | 2020-09-14 | B14164¦Common area by elevator, basement¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, ground floor | [5 empty] | 22 | 52 | 532 |  | 2020-09-17 15:00 | 15:00 | 22 | 52 | 532 |  |  | 2020-09-14 | B14164¦Common area by elevator, ground floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 24 | 29 | 687 | Office #2 - NE corner - no windows, no plants | 2020-09-17 15:00 | 15:00 | 24 | 29 | 687 |  | low | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Youth office, ground floor | [5 empty] | 21 | 57 | 677 |  | 2020-09-17 15:00 | 15:00 | 21 | 57 | 677 |  |  | 2020-09-14 | B14164¦Youth office, ground floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Family office, ground floor | [5 empty] | 21 | 55 | 569 |  | 2020-09-17 15:00 | 15:00 | 21 | 55 | 569 |  |  | 2020-09-14 | B14164¦Family office, ground floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Commmon area by elevator, second floor | [5 empty] | 21 | 55 | 533 |  | 2020-09-17 15:00 | 15:00 | 21 | 55 | 533 |  |  | 2020-09-14 | B14164¦Commmon area by elevator, second floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Outdoors |  |  | 20 | 50 | 426 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B14164¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Outdoors |  |  | 12 | 29 | 391 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B11589¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Security Desk | [5 empty] | 18 | 47 | 659 |  | 2020-09-17 12:00 | 12:00 | 18 | 47 | 659 |  |  | 2020-09-14 | B11589¦Security Desk¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom A | [5 empty] | 20 | 44 | 470 |  | 2020-09-17 12:00 | 12:00 | 20 | 44 | 470 |  |  | 2020-09-14 | B11589¦Courtroom A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom B | [5 empty] | 21 | 26 | 422 |  | 2020-09-17 12:00 | 12:00 | 21 | 26 | 422 |  | low | 2020-09-14 | B11589¦Courtroom B¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom D | [5 empty] | 20 | 32 | 562 |  | 2020-09-17 12:00 | 12:00 | 20 | 32 | 562 |  | low | 2020-09-14 | B11589¦Courtroom D¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom E | [5 empty] | 21 | 26 | 444 |  | 2020-09-17 12:00 | 12:00 | 21 | 26 | 444 |  | low | 2020-09-14 | B11589¦Courtroom E¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Walker | [5 empty] | 21 | 37 | 502 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 502 |  | caution | 2020-09-14 | B11589¦Office Walker¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Martin | [5 empty] | 21 | 39 | 509 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 509 |  | caution | 2020-09-14 | B11589¦Office Martin¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Baker | [5 empty] | 21 | 30 | 455 |  | 2020-09-17 12:00 | 12:00 | 21 | 30 | 455 |  | low | 2020-09-14 | B11589¦Office Baker¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Attorney General Administration Office | [5 empty] | 22 | 28 | 544 |  | 2020-09-17 12:00 | 12:00 | 22 | 28 | 544 |  | low | 2020-09-14 | B11589¦Attorney General Administration Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Hallway | [5 empty] | 22 | 29 | 508 |  | 2020-09-17 12:00 | 12:00 | 22 | 29 | 508 |  | low | 2020-09-14 | B11589¦Hallway¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom H | [5 empty] | 22 | 29 | 432 |  | 2020-09-17 12:00 | 12:00 | 22 | 29 | 432 |  | low | 2020-09-14 | B11589¦Courtroom H¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Outdoors |  |  | 13 | 27 | 405 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B12955¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom J | [5 empty] | 21 | 20 | 400 | Window Open | 2020-09-17 12:00 | 12:00 | 21 | 20 | 400 |  | low | 2020-09-14 | B11589¦Courtroom J¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Main Floor Entrance Lobby | [5 empty] | 14 | 35 | 417 | Front lobby | 2020-09-17 12:00 | 12:00 | 14 | 35 | 417 |  | caution | 2020-09-14 | B12955¦Main Floor Entrance Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | OTHER | [6 empty] | 43 | 15 | waiting area | 2020-09-17 12:00 | 12:00 |  | 43 | 15 |  |  | 2020-09-14 | B12955¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Administration office | [5 empty] | 18 | 48 | 477 |  | 2020-09-17 12:00 | 12:00 | 18 | 48 | 477 |  |  | 2020-09-14 | B12955¦Administration office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 103 | [5 empty] | 20 | 34 | 442 |  | 2020-09-17 12:00 | 12:00 | 20 | 34 | 442 |  | low | 2020-09-14 | B12955¦Courtroom 103¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 203 | [5 empty] | 20 | 28 | 436 |  | 2020-09-17 12:00 | 12:00 | 20 | 28 | 436 |  | low | 2020-09-14 | B12955¦Courtroom 203¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Lobby | [5 empty] | 25 | 26 | 591 |  | 2020-09-17 15:00 | 15:00 | 25 | 26 | 591 |  | low | 2020-09-14 | B10002¦Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Skeggs | [5 empty] | 24 | 28 | 545 | Door Open | 2020-09-17 15:00 | 15:00 | 24 | 28 | 545 |  | low | 2020-09-14 | B10002¦Office Skeggs¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Cubicle Office | [5 empty] | 24 | 29 | 548 | Door Open | 2020-09-17 15:00 | 15:00 | 24 | 29 | 548 |  | low | 2020-09-14 | B10002¦Cubicle Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | File Room | [5 empty] | 23 | 31 | 551 |  | 2020-09-17 15:00 | 15:00 | 23 | 31 | 551 |  | low | 2020-09-14 | B10002¦File Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Didiodato | [5 empty] | 22 | 32 | 554 | Door Open | 2020-09-17 15:00 | 15:00 | 22 | 32 | 554 |  | low | 2020-09-14 | B10002¦Office Didiodato¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Outdoors |  |  | 14 | 27 | 397 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10002¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Library | [5 empty] | 21.1111 | 32 | 462 |  | 2020-09-17 15:00 | 15:00 | 21.1111 | 32 | 462 |  | low | 2020-09-14 | B10246¦Library¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Justice Wilcox Chambers | [5 empty] | 20.5556 | 25 | 428 |  | 2020-09-17 15:00 | 15:00 | 20.5556 | 25 | 428 |  | low | 2020-09-14 | B10246¦Justice Wilcox Chambers¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Lobby Administration | [5 empty] | 18 | 53 | 556 |  | 2020-09-17 15:00 | 15:00 | 18 | 53 | 556 |  |  | 2020-09-14 | B10003¦Lobby Administration¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Library | [5 empty] | 19 | 51 | 576 | Wall mount AC unit running | 2020-09-17 15:00 | 15:00 | 19 | 51 | 576 |  |  | 2020-09-14 | B10003¦Library¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | 2nd fl lobby | [5 empty] | 21.1111 | 30 | 456 | Middle of hallway | 2020-09-17 15:00 | 15:00 | 21.1111 | 30 | 456 |  | low | 2020-09-14 | B10246¦2nd fl lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 2 | [5 empty] | 21.6667 | 29 | 556 |  | 2020-09-17 15:00 | 15:00 | 21.6667 | 29 | 556 |  | low | 2020-09-14 | B10246¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Basement Library | [5 empty] | 18 | 52 | 441 |  | 2020-09-17 15:00 | 15:00 | 18 | 52 | 441 |  |  | 2020-09-14 | B10003¦Basement Library¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Trial Co-ordinators Office | [5 empty] | 21.6667 | 29 | 532 |  | 2020-09-17 15:00 | 15:00 | 21.6667 | 29 | 532 |  | low | 2020-09-14 | B10246¦Trial Co-ordinators Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Main Floor Entrance Lobby | [5 empty] | 21.6667 | 28 | 459 | Middle of hallway | 2020-09-17 15:00 | 15:00 | 21.6667 | 28 | 459 |  | low | 2020-09-14 | B10246¦Main Floor Entrance Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 21.1111 | 27 | 455 | Office to the left of office 10 | 2020-09-17 15:00 | 15:00 | 21.1111 | 27 | 455 |  | low | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Outdoors |  |  | 14 | 28 | 409 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10003¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Outdoors |  |  | 20 | 50 | 431 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10639¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 21.1111 | 29 | 452 | Office to the right of office 10 | 2020-09-17 15:00 | 15:00 | 21.1111 | 29 | 452 |  | low | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 6 north side | [5 empty] | 21 | 47 | 440 |  | 2020-09-17 15:00 | 15:00 | 21 | 47 | 440 |  |  | 2020-09-14 | B10639¦courtroom 6 north side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown attorney admin area | [5 empty] | 21.6667 | 33 | 521 |  | 2020-09-17 15:00 | 15:00 | 21.6667 | 33 | 521 |  | low | 2020-09-14 | B10246¦Crown attorney admin area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Administration office | [5 empty] | 21.6667 | 27 | 509 |  | 2020-09-17 15:00 | 15:00 | 21.6667 | 27 | 509 |  | low | 2020-09-14 | B10246¦Administration office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 6 south side | [5 empty] | 21 | 47 | 441 |  | 2020-09-17 15:00 | 15:00 | 21 | 47 | 441 |  |  | 2020-09-14 | B10639¦courtroom 6 south side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 1 (Center) | [5 empty] | 21.1111 | 24 | 420 |  | 2020-09-17 15:00 | 15:00 | 21.1111 | 24 | 420 |  | low | 2020-09-14 | B10246¦Courtroom 1 (Center)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 6 | [5 empty] | 21 | 48 | 452 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 452 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Outdoors |  |  | 16 | 28 | 420 |  |  |  | East entrance - partly cloudy, light Breeze | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B13095¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 5 north side | [5 empty] | 21 | 49 | 452 |  | 2020-09-17 15:00 | 15:00 | 21 | 49 | 452 |  |  | 2020-09-14 | B10639¦courtroom 5 north side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 5 south side | [5 empty] | 21 | 49 | 460 |  | 2020-09-17 15:00 | 15:00 | 21 | 49 | 460 |  |  | 2020-09-14 | B10639¦courtroom 5 south side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 5 | [5 empty] | 21 | 48 | 467 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 467 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 5¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Basement cells - hallway | [5 empty] | 20.5556 | 33 | 460 |  | 2020-09-17 15:00 | 15:00 | 20.5556 | 33 | 460 |  | low | 2020-09-14 | B10246¦Basement cells - hallway¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 3 southeast side | [5 empty] | 21 | 48 | 459 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 459 |  |  | 2020-09-14 | B10639¦courtroom 3 southeast side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 3 northeast side | [5 empty] | 21 | 49 | 485 |  | 2020-09-17 15:00 | 15:00 | 21 | 49 | 485 |  |  | 2020-09-14 | B10639¦courtroom 3 northeast side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Basement lobby - bottom of stairs | [5 empty] | 20.5556 | 31 | 452 |  | 2020-09-17 15:00 | 15:00 | 20.5556 | 31 | 452 |  | low | 2020-09-14 | B10246¦Basement lobby - bottom of stairs¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | hallway by courtroom 3 | [5 empty] | 22 | 48 | 487 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 487 |  |  | 2020-09-14 | B10639¦hallway by courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Outdoors |  |  | 13 | 27 | 13405 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B12955¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | lobby by statue | [5 empty] | 21 | 51 | 468 |  | 2020-09-17 15:00 | 15:00 | 21 | 51 | 468 |  |  | 2020-09-14 | B10639¦lobby by statue¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Outdoors |  |  | 16.1111 | 22 | 407 |  |  |  | Directly outside main entrance: clear/sunny | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10246¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby East Side | [5 empty] | 21 | 48 | 467 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 467 |  |  | 2020-09-14 | B10639¦Entrance Lobby East Side¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Outdoors |  |  | 12 | 44 | 436 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B11589¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Security Desk | [5 empty] | 19 | 52 | 520 |  | 2020-09-17 09:00 | 9:00 | 19 | 52 | 520 |  |  | 2020-09-14 | B11589¦Security Desk¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby West Side | [5 empty] | 21 | 48 | 470 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 470 |  |  | 2020-09-14 | B10639¦Entrance Lobby West Side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Hallway | [5 empty] | 21 | 32 | 518 | Window closed, no plants | 2020-09-17 15:00 | 15:00 | 21 | 32 | 518 |  | low | 2020-09-14 | B13095¦Hallway¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom A | [5 empty] | 21 | 45 | 430 |  | 2020-09-17 09:00 | 9:00 | 21 | 45 | 430 |  |  | 2020-09-14 | B11589¦Courtroom A¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by COA intake office | [5 empty] | 21 | 48 | 468 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 468 |  |  | 2020-09-14 | B10639¦Hallway by COA intake office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Main Floor Entrance Lobby | [5 empty] | 14 | 35 | 417 | front lobby | 2020-09-17 15:00 | 15:00 | 14 | 35 | 417 |  | caution | 2020-09-14 | B12955¦Main Floor Entrance Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom B | [5 empty] | 21 | 35 | 420 |  | 2020-09-17 09:00 | 9:00 | 21 | 35 | 420 |  | caution | 2020-09-14 | B11589¦Courtroom B¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | office - B04A | [5 empty] | 21 | 30 | 476 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 21 | 30 | 476 |  | low | 2020-09-14 | B13095¦office - B04A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | OTHER | [5 empty] | 15 | 43 | 441 | Waiting area | 2020-09-17 15:00 | 15:00 | 15 | 43 | 441 |  |  | 2020-09-14 | B12955¦OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom C | [5 empty] | 21 | 35 | 435 |  | 2020-09-17 09:00 | 9:00 | 21 | 35 | 435 |  | caution | 2020-09-14 | B11589¦Courtroom C¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by Law Society of Ontario | [5 empty] | 21 | 48 | 467 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 467 |  |  | 2020-09-14 | B10639¦Hallway by Law Society of Ontario¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Administration office | [5 empty] | 18 | 48 | 477 |  | 2020-09-17 15:00 | 15:00 | 18 | 48 | 477 |  |  | 2020-09-14 | B12955¦Administration office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Main Lobby | [5 empty] | 21 | 29 | 491 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 21 | 29 | 491 |  | low | 2020-09-14 | B13095¦Main Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom D | [5 empty] | 21 | 37 | 520 |  | 2020-09-17 09:00 | 9:00 | 21 | 37 | 520 |  | caution | 2020-09-14 | B11589¦Courtroom D¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 203 | [5 empty] | 20 | 34 | 484 |  | 2020-09-17 15:00 | 15:00 | 20 | 34 | 484 |  | low | 2020-09-14 | B12955¦Courtroom 203¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom E | [5 empty] | 21 | 33 | 477 |  | 2020-09-17 09:00 | 9:00 | 21 | 33 | 477 |  | low | 2020-09-14 | B11589¦Courtroom E¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Outdoors |  |  | 19 | 54 | 439 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20265¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 103 | [5 empty] | 19 | 31 | 445 |  | 2020-09-17 15:00 | 15:00 | 19 | 31 | 445 |  | low | 2020-09-14 | B12955¦Courtroom 103¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Walker | [5 empty] | 21 | 39 | 431 | Door Open | 2020-09-17 09:00 | 9:00 | 21 | 39 | 431 |  | caution | 2020-09-14 | B11589¦Office Walker¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Martin | [5 empty] | 21 | 40 | 438 |  | 2020-09-17 09:00 | 9:00 | 21 | 40 | 438 |  | caution | 2020-09-14 | B11589¦Office Martin¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 north side | [5 empty] | 22 | 49 | 556 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 556 |  |  | 2020-09-14 | B20265¦courtroom M1 north side¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Baker | [5 empty] | 21 | 38 | 420 |  | 2020-09-17 09:00 | 9:00 | 21 | 38 | 420 |  | caution | 2020-09-14 | B11589¦Office Baker¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Outdoors |  |  | 12 | 35 | 412 |  |  |  | North entrance - partly cloudy, light breeze | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B13049¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom M1 south side | [5 empty] | 22 | 49 | 556 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 556 |  |  | 2020-09-14 | B10639¦courtroom M1 south side¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Attorney General Administration Office | [5 empty] | 22 | 38 | 506 |  | 2020-09-17 09:00 | 9:00 | 22 | 38 | 506 |  | caution | 2020-09-14 | B11589¦Attorney General Administration Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Hallway | [5 empty] | 22 | 37 | 497 |  | 2020-09-17 09:00 | 9:00 | 22 | 37 | 497 |  | caution | 2020-09-14 | B11589¦Hallway¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by Courtroom M1 | [5 empty] | 22 | 50 | 565 |  | 2020-09-17 15:00 | 15:00 | 22 | 50 | 565 |  |  | 2020-09-14 | B20265¦hallway by Courtroom M1¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom H | [5 empty] | 22 | 36 | 430 |  | 2020-09-17 09:00 | 9:00 | 22 | 36 | 430 |  | caution | 2020-09-14 | B11589¦Courtroom H¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom J | [5 empty] | 22 | 41 | 418 |  | 2020-09-17 09:00 | 9:00 | 22 | 41 | 418 |  |  | 2020-09-14 | B11589¦Courtroom J¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom J south side | [5 empty] | 22 | 47 | 506 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 506 |  |  | 2020-09-14 | B20265¦courtroom J south side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Outdoors |  |  | 14 | 28 | 373 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B11589¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Security Desk | [5 empty] | 17 | 47 | 569 |  | 2020-09-17 15:00 | 15:00 | 17 | 47 | 569 |  |  | 2020-09-14 | B11589¦Security Desk¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom J north side | [5 empty] | 22 | 48 | 532 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 532 |  |  | 2020-09-14 | B20265¦courtroom J north side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom A | [5 empty] | 20 | 44 | 473 |  | 2020-09-17 15:00 | 15:00 | 20 | 44 | 473 |  |  | 2020-09-14 | B11589¦Courtroom A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom B | [5 empty] | 21 | 27 | 425 |  | 2020-09-17 15:00 | 15:00 | 21 | 27 | 425 |  | low | 2020-09-14 | B11589¦Courtroom B¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 57 | 692 | east | 2020-09-17 12:00 | 12:00 | 22 | 57 | 692 |  |  | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 2nd fl lobby | [5 empty] | 19 | 32 | 477 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 19 | 32 | 477 |  | low | 2020-09-14 | B13049¦2nd fl lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom J | [5 empty] | 22 | 48 | 532 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 532 |  |  | 2020-09-14 | B20265¦hallway by courtroom J¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom C | [5 empty] | 21 | 26 | 473 |  | 2020-09-17 15:00 | 15:00 | 21 | 26 | 473 |  | low | 2020-09-14 | B11589¦Courtroom C¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 23 | 56 | 695 | west | 2020-09-17 12:00 | 12:00 | 23 | 56 | 695 |  |  | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom D | [5 empty] | 21 | 30 | 444 |  | 2020-09-17 15:00 | 15:00 | 21 | 30 | 444 |  | low | 2020-09-14 | B11589¦Courtroom D¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G south side | [5 empty] | 22 | 49 | 615 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 615 |  |  | 2020-09-14 | B20265¦courtroom G south side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom E | [5 empty] | 21 | 25 | 453 |  | 2020-09-17 15:00 | 15:00 | 21 | 25 | 453 |  | low | 2020-09-14 | B11589¦Courtroom E¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 22 | 56 | 493 | east | 2020-09-17 12:00 | 12:00 | 22 | 56 | 493 |  |  | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Walker | [5 empty] | 22 | 36 | 503 |  | 2020-09-17 15:00 | 15:00 | 22 | 36 | 503 |  | caution | 2020-09-14 | B11589¦Office Walker¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 22 | 56 | 501 | west | 2020-09-17 12:00 | 12:00 | 22 | 56 | 501 |  |  | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G north side | [5 empty] | 22 | 49 | 598 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 598 |  |  | 2020-09-14 | B20265¦courtroom G north side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Martin | [5 empty] | 21 | 38 | 503 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 503 |  | caution | 2020-09-14 | B11589¦Office Martin¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Baker | [5 empty] | 21 | 31 | 460 |  | 2020-09-17 15:00 | 15:00 | 21 | 31 | 460 |  | low | 2020-09-14 | B11589¦Office Baker¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 21 | 58 | 491 | east | 2020-09-17 12:00 | 12:00 | 21 | 58 | 491 |  |  | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 121 west side | [5 empty] | 22 | 47 | 545 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 545 |  |  | 2020-09-14 | B20265¦courtroom 121 west side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 250 | [5 empty] | 20 | 26 | 400 | No windows, no plants | 2020-09-17 15:00 | 15:00 | 20 | 26 | 400 |  | low | 2020-09-14 | B13049¦Courtroom 250¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 22 | 57 | 490 | west | 2020-09-17 12:00 | 12:00 | 22 | 57 | 490 |  |  | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Attorney General Administration Office | [5 empty] | 22 | 30 | 490 |  | 2020-09-17 15:00 | 15:00 | 22 | 30 | 490 |  | low | 2020-09-14 | B11589¦Attorney General Administration Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Hallway | [5 empty] | 22 | 30 | 498 |  | 2020-09-17 15:00 | 15:00 | 22 | 30 | 498 |  | low | 2020-09-14 | B11589¦Hallway¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 22 | 57 | 485 | east | 2020-09-17 12:00 | 12:00 | 22 | 57 | 485 |  |  | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 121 east side | [5 empty] | 22 | 47 | 548 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 548 |  |  | 2020-09-14 | B20265¦courtroom 121 east side¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 22 | 57 | 485 | west | 2020-09-17 12:00 | 12:00 | 22 | 57 | 485 |  |  | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom H | [5 empty] | 22 | 28 | 425 |  | 2020-09-17 15:00 | 15:00 | 22 | 28 | 425 |  | low | 2020-09-14 | B11589¦Courtroom H¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 123 east side | [5 empty] | 22 | 48 | 580 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 580 |  |  | 2020-09-14 | B20265¦courtroom 123 east side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom J | [5 empty] | 22 | 21 | 388 | Open Window | 2020-09-17 15:00 | 15:00 | 22 | 21 | 388 |  | low | 2020-09-14 | B11589¦Courtroom J¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 57 | 521 | east | 2020-09-17 12:00 | 12:00 | 22 | 57 | 521 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 57 | 521 | west | 2020-09-17 12:00 | 12:00 | 22 | 57 | 521 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 123 west side | [5 empty] | 22 | 47 | 593 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 593 |  |  | 2020-09-14 | B20265¦courtroom 123 west side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Administration office | [5 empty] | 22 | 26 | 532 | Windows closed, 4 plants total at various locations | 2020-09-17 15:00 | 15:00 | 22 | 26 | 532 |  | low | 2020-09-14 | B13049¦Administration office¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 57 | 532 | east | 2020-09-17 12:00 | 12:00 | 22 | 57 | 532 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 east side | [5 empty] | 22 | 49 | 550 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 550 |  |  | 2020-09-14 | B20265¦courtroom 124 east side¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 57 | 522 | west | 2020-09-17 12:00 | 12:00 | 22 | 57 | 522 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 58 | 531 | east | 2020-09-17 12:00 | 12:00 | 21 | 58 | 531 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 west side | [5 empty] | 22 | 49 | 545 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 545 |  |  | 2020-09-14 | B20265¦courtroom 124 west side¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 58 | 534 | west | 2020-09-17 12:00 | 12:00 | 21 | 58 | 534 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 57 | 543 | east | 2020-09-17 12:00 | 12:00 | 22 | 57 | 543 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courroom 125 south side | [5 empty] | 21 | 46 | 522 |  | 2020-09-17 15:00 | 15:00 | 21 | 46 | 522 |  |  | 2020-09-14 | B20265¦courroom 125 south side¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 57 | 546 | west | 2020-09-17 12:00 | 12:00 | 22 | 57 | 546 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 21 | 54 | 488 | east | 2020-09-17 12:00 | 12:00 | 21 | 54 | 488 |  |  | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 125 north side | [5 empty] | 21 | 47 | 533 |  | 2020-09-17 15:00 | 15:00 | 21 | 47 | 533 |  |  | 2020-09-14 | B20265¦courtroom 125 north side¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 21 | 55 | 476 | west | 2020-09-17 12:00 | 12:00 | 21 | 55 | 476 |  |  | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown Attorney Office | [5 empty] | 22 | 25 | 446 | Office #2 - north side - windows closed, no plants | 2020-09-17 15:00 | 15:00 | 22 | 25 | 446 |  | low | 2020-09-14 | B13049¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 21 | 55 | 537 | east | 2020-09-17 12:00 | 12:00 | 21 | 55 | 537 |  |  | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 126 south side | [5 empty] | 22 | 46 | 506 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 506 |  |  | 2020-09-14 | B20265¦courtroom 126 south side¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 21 | 55 | 503 | west | 2020-09-17 12:00 | 12:00 | 21 | 55 | 503 |  |  | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 22 | 53 | 572 | east | 2020-09-17 12:00 | 12:00 | 22 | 53 | 572 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom 126 | [5 empty] | 22 | 48 | 586 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 586 |  |  | 2020-09-14 | B20265¦hallway by courtroom 126¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 22 | 51 | 544 | west | 2020-09-17 12:00 | 12:00 | 22 | 51 | 544 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 54 | 532 | east | 2020-09-17 12:00 | 12:00 | 21 | 54 | 532 |  |  | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by receiving | [5 empty] | 20 | 55 | 586 |  | 2020-09-17 15:00 | 15:00 | 20 | 55 | 586 |  |  | 2020-09-14 | B20265¦hallway by receiving¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 54 | 526 | west | 2020-09-17 12:00 | 12:00 | 21 | 54 | 526 |  |  | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Outdoors |  |  | 19 | 55 | 500 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B91122¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown attorney admin area | [5 empty] | 22 | 25 | 522 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 22 | 25 | 522 |  | low | 2020-09-14 | B13049¦Crown attorney admin area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 56 | 614 | east | 2020-09-17 15:00 | 15:00 | 22 | 56 | 614 |  |  | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 56 | 615 | west | 2020-09-17 15:00 | 15:00 | 22 | 56 | 615 |  |  | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 22 | 57 | 561 | east | 2020-09-17 15:00 | 15:00 | 22 | 57 | 561 |  |  | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 22 | 57 | 554 | west | 2020-09-17 15:00 | 15:00 | 22 | 57 | 554 |  |  | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 22 | 57 | 499 | east | 2020-09-17 15:00 | 15:00 | 22 | 57 | 499 |  |  | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown Attorney Office | [5 empty] | 22 | 24 | 491 | Office #1 - east side - windows closed, no plants | 2020-09-17 15:00 | 15:00 | 22 | 24 | 491 |  | low | 2020-09-14 | B13049¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 22 | 57 | 502 | west | 2020-09-17 15:00 | 15:00 | 22 | 57 | 502 |  |  | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 22 | 57 | 489 | east | 2020-09-17 15:00 | 15:00 | 22 | 57 | 489 |  |  | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 22 | 57 | 486 | west | 2020-09-17 15:00 | 15:00 | 22 | 57 | 486 |  |  | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 57 | 530 | est | 2020-09-17 15:00 | 15:00 | 22 | 57 | 530 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 57 | 529 | west | 2020-09-17 15:00 | 15:00 | 22 | 57 | 529 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 58 | 526 | east | 2020-09-17 15:00 | 15:00 | 22 | 58 | 526 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 57 | 530 | west | 2020-09-17 15:00 | 15:00 | 22 | 57 | 530 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 58 | 539 | east | 2020-09-17 15:00 | 15:00 | 21 | 58 | 539 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 58 | 533 | west | 2020-09-17 15:00 | 15:00 | 21 | 58 | 533 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 57 | 530 | east | 2020-09-17 15:00 | 15:00 | 22 | 57 | 530 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 58 | 534 | west | 2020-09-17 15:00 | 15:00 | 22 | 58 | 534 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 21 | 53 | 491 | east | 2020-09-17 15:00 | 15:00 | 21 | 53 | 491 |  |  | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 1st Floor Lobby next to courtroom 122 | [5 empty] | 22 | 24 | 420 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 22 | 24 | 420 |  | low | 2020-09-14 | B13049¦1st Floor Lobby next to courtroom 122¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 21 | 53 | 477 | west | 2020-09-17 15:00 | 15:00 | 21 | 53 | 477 |  |  | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 21 | 55 | 509 | east | 2020-09-17 15:00 | 15:00 | 21 | 55 | 509 |  |  | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 21 | 54 | 511 | west | 2020-09-17 15:00 | 15:00 | 21 | 54 | 511 |  |  | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 22 | 52 | 588 | east | 2020-09-17 15:00 | 15:00 | 22 | 52 | 588 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 22 | 51 | 558 | west | 2020-09-17 15:00 | 15:00 | 22 | 51 | 558 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 55 | 533 | east | 2020-09-17 15:00 | 15:00 | 21 | 55 | 533 |  |  | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 55 | 481 | west | 2020-09-17 15:00 | 15:00 | 21 | 55 | 481 |  |  | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 122 | [5 empty] | 20 | 24 | 456 | No windows, no plants | 2020-09-17 15:00 | 15:00 | 20 | 24 | 456 |  | low | 2020-09-14 | B13049¦Courtroom 122¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Outdoors |  |  | 21 | 50 | 481 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B91122¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Lunch Room | [5 empty] | 23 | 52 | 531 |  | 2020-09-17 15:00 | 15:00 | 23 | 52 | 531 |  |  | 2020-09-14 | B70451¦Lunch Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Court Security office #142 | [5 empty] | 22 | 26 | 420 | No windows, no plants | 2020-09-17 15:00 | 15:00 | 22 | 26 | 420 |  | low | 2020-09-14 | B13049¦Court Security office #142¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 23 | 51 | 527 | east | 2020-09-17 15:00 | 15:00 | 23 | 51 | 527 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 22 | 52 | 522 | west | 2020-09-17 15:00 | 15:00 | 22 | 52 | 522 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 602 | [5 empty] | 23 | 53 | 560 |  | 2020-09-17 15:00 | 15:00 | 23 | 53 | 560 |  |  | 2020-09-14 | B70451¦hallway by courtroom 602¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 603 | [5 empty] | 22 | 53 | 537 |  | 2020-09-17 15:00 | 15:00 | 22 | 53 | 537 |  |  | 2020-09-14 | B70451¦hallway by courtroom 603¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | conference room 4 | [5 empty] | 23 | 52 | 512 |  | 2020-09-17 15:00 | 15:00 | 23 | 52 | 512 |  |  | 2020-09-14 | B70451¦conference room 4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 22 | 54 | 509 | east | 2020-09-17 15:00 | 15:00 | 22 | 54 | 509 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 22 | 54 | 501 | west | 2020-09-17 15:00 | 15:00 | 22 | 54 | 501 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 607 | [5 empty] | 23 | 52 | 511 |  | 2020-09-17 15:00 | 15:00 | 23 | 52 | 511 |  |  | 2020-09-14 | B70451¦hallway by courtroom 607¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | enforcementoffice | [5 empty] | 23 | 51 | 523 |  | 2020-09-17 15:00 | 15:00 | 23 | 51 | 523 |  |  | 2020-09-14 | B70451¦enforcementoffice¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 23 | 52 | 517 | east | 2020-09-17 15:00 | 15:00 | 23 | 52 | 517 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 140 | [5 empty] | 22 | 24 | 421 | No windows, no plants | 2020-09-17 15:00 | 15:00 | 22 | 24 | 421 |  | low | 2020-09-14 | B13049¦Courtroom 140¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 22 | 52 | 505 | west | 2020-09-17 15:00 | 15:00 | 22 | 52 | 505 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 605 | [5 empty] | 22 | 53 | 514 |  | 2020-09-17 15:00 | 15:00 | 22 | 53 | 514 |  |  | 2020-09-14 | B70451¦hallway by courtroom 605¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters administration office | [5 empty] | 23 | 52 | 540 |  | 2020-09-17 15:00 | 15:00 | 23 | 52 | 540 |  |  | 2020-09-14 | B70451¦masters administration office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-10 | [5 empty] | 22 | 52 | 505 |  | 2020-09-17 15:00 | 15:00 | 22 | 52 | 505 |  |  | 2020-09-14 | B70451¦room 6-10¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-9 | [5 empty] | 21 | 53 | 507 |  | 2020-09-17 15:00 | 15:00 | 21 | 53 | 507 |  |  | 2020-09-14 | B70451¦room 6-9¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters library | [5 empty] | 22 | 54 | 507 |  | 2020-09-17 15:00 | 15:00 | 22 | 54 | 507 |  |  | 2020-09-14 | B70451¦masters library¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-4 | [5 empty] | 22 | 53 | 504 |  | 2020-09-17 15:00 | 15:00 | 22 | 53 | 504 |  |  | 2020-09-14 | B70451¦room 6-4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | reception area-masters | [5 empty] | 22 | 54 | 505 |  | 2020-09-17 15:00 | 15:00 | 22 | 54 | 505 |  |  | 2020-09-14 | B70451¦reception area-masters¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 1st floor cell holding area Hallway | [5 empty] | 22 | 24 | 440 | Across from door #3 - no windows, no plants | 2020-09-17 15:00 | 15:00 | 22 | 24 | 440 |  | low | 2020-09-14 | B13049¦1st floor cell holding area Hallway¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Outdoors |  |  | 21 | 50 | 481 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70451¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 57 | 542 | public area | 2020-09-17 15:00 | 15:00 | 21 | 57 | 542 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 57 | 535 | judge area | 2020-09-17 15:00 | 15:00 | 21 | 57 | 535 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 59 | 551 | outside of 503 | 2020-09-17 15:00 | 15:00 | 21 | 59 | 551 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 59 | 552 | public area | 2020-09-17 15:00 | 15:00 | 21 | 59 | 552 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 59 | 543 | judge area | 2020-09-17 15:00 | 15:00 | 21 | 59 | 543 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 21 | 60 | 559 | outside of 506 | 2020-09-17 15:00 | 15:00 | 21 | 60 | 559 |  | caution | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 60 | 563 | public area | 2020-09-17 15:00 | 15:00 | 20 | 60 | 563 |  | caution | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 60 | 545 | judge area | 2020-09-17 15:00 | 15:00 | 20 | 60 | 545 |  | caution | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 61 | 548 | outside of 509 | 2020-09-17 15:00 | 15:00 | 20 | 61 | 548 |  | caution | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 61 | 550 | public area | 2020-09-17 15:00 | 15:00 | 20 | 61 | 550 |  | caution | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 61 | 549 | judge area | 2020-09-17 15:00 | 15:00 | 20 | 61 | 549 |  | caution | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 61 | 551 | outside of 510 | 2020-09-17 15:00 | 15:00 | 20 | 61 | 551 |  | caution | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 61 | 566 | public area | 2020-09-17 15:00 | 15:00 | 20 | 61 | 566 |  | caution | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 61 | 577 | judge area | 2020-09-17 15:00 | 15:00 | 20 | 61 | 577 |  | caution | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Back of main hallway | [5 empty] | 20 | 61 | 559 |  | 2020-09-17 15:00 | 15:00 | 20 | 61 | 559 |  | caution | 2020-09-14 | B70003¦Back of main hallway¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | elevator area | [5 empty] | 20 | 61 | 565 |  | 2020-09-17 15:00 | 15:00 | 20 | 61 | 565 |  | caution | 2020-09-14 | B70003¦elevator area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Outdoors |  |  | 22 | 66 | 394 |  |  |  | outside of 444 Yonge St. | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70003¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Outdoors |  |  | 16 | 74 | [5 empty] | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20619¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Courtroom 1-14 | [5 empty] | 22 | 48 | 454 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 454 |  |  | 2020-09-14 | B20619¦Courtroom 1-14¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 101 | [5 empty] | 19 | 59 | 567 |  | 2020-09-17 09:00 | 9:00 | 19 | 59 | 567 |  |  | 2020-09-14 | B25671¦Courtroom 101¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 201 | [5 empty] | 19 | 59 | 483 |  | 2020-09-17 09:00 | 9:00 | 19 | 59 | 483 |  |  | 2020-09-14 | B25671¦Courtroom 201¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 301 | [5 empty] | 20 | 59 | 421 |  | 2020-09-17 09:00 | 9:00 | 20 | 59 | 421 |  |  | 2020-09-14 | B25671¦Courtroom 301¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 | [5 empty] | 20 | 58 | 416 |  | 2020-09-17 09:00 | 9:00 | 20 | 58 | 416 |  |  | 2020-09-14 | B14209¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 8 | [5 empty] | 22 | 53 | 416 |  | 2020-09-17 09:00 | 9:00 | 22 | 53 | 416 |  |  | 2020-09-14 | B25683¦Courtroom 8¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 11 | [5 empty] | 22 | 53 | 416 |  | 2020-09-17 09:00 | 9:00 | 22 | 53 | 416 |  |  | 2020-09-14 | B25683¦Courtroom 11¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 - waiting area | [5 empty] | 22 | 48 | 407 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 407 |  |  | 2020-09-14 | B14209¦Courtroom 1 - waiting area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 9 | [5 empty] | 23 | 50 | 421 |  | 2020-09-17 09:00 | 9:00 | 23 | 50 | 421 |  |  | 2020-09-14 | B25683¦Courtroom 9¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 | [5 empty] | 20 | 50 | 435 |  | 2020-09-17 09:00 | 9:00 | 20 | 50 | 435 |  |  | 2020-09-14 | B14209¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Outdoors |  |  | 9 | 73 | 407 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B12948¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 1 | [5 empty] | 19 | 49 | 401 |  | 2020-09-17 09:00 | 9:00 | 19 | 49 | 401 |  |  | 2020-09-14 | B12948¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 | [5 empty] | 20 | 46 | 402 |  | 2020-09-17 09:00 | 9:00 | 20 | 46 | 402 |  |  | 2020-09-14 | B12948¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 | [5 empty] | 20 | 43 | 412 |  | 2020-09-17 09:00 | 9:00 | 20 | 43 | 412 |  |  | 2020-09-14 | B12948¦Courtroom 3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 101 | [5 empty] | 20 | 55 | 494 |  | 2020-09-17 09:00 | 9:00 | 20 | 55 | 494 |  |  | 2020-09-14 | B19512¦Courtroom 101¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 | [5 empty] | 21 | 43 | 418 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 418 |  |  | 2020-09-14 | B12948¦Courtroom 4¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 200 | [5 empty] | 21 | 52 | 520 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 520 |  |  | 2020-09-14 | B19512¦Courtroom 200¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 201 | [5 empty] | 22 | 52 | 520 |  | 2020-09-17 09:00 | 9:00 | 22 | 52 | 520 |  |  | 2020-09-14 | B19512¦Courtroom 201¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 101 | [5 empty] | 21 | 51 |  |  | 2020-09-17 09:00 | 9:00 | 21 | 51 |  |  |  | 2020-09-14 | B20080¦Courtroom 101¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 | [5 empty] | 21 | 42 | 429 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 429 |  |  | 2020-09-14 | B12948¦Courtroom 5¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Outdoors |  |  | 12 | 86 | [5 empty] | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B19512¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 201 | [5 empty] | 22 | 46 | 421 |  | 2020-09-17 09:00 | 9:00 | 22 | 46 | 421 |  |  | 2020-09-14 | B20080¦Courtroom 201¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 6 | [5 empty] | 21 | 41 | 428 |  | 2020-09-17 09:00 | 9:00 | 21 | 41 | 428 |  |  | 2020-09-14 | B12948¦Courtroom 6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 202 | [5 empty] | 23 | 46 | 419 |  | 2020-09-17 09:00 | 9:00 | 23 | 46 | 419 |  |  | 2020-09-14 | B20080¦Courtroom 202¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Admin Office Waiting Area | [5 empty] | 21 | 43 | 417 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 417 |  |  | 2020-09-14 | B12948¦Admin Office Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration office | [5 empty] | 21 | 44 | 419 |  | 2020-09-17 09:00 | 9:00 | 21 | 44 | 419 |  |  | 2020-09-14 | B12948¦Administration office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 301 | [5 empty] | 23 | 46 | 411 |  | 2020-09-17 09:00 | 9:00 | 23 | 46 | 411 |  |  | 2020-09-14 | B20080¦Courtroom 301¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Crown attorney admin area | [5 empty] | 22 | 46 | 430 |  | 2020-09-17 09:00 | 9:00 | 22 | 46 | 430 |  |  | 2020-09-14 | B12948¦Crown attorney admin area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 - waiting room | [5 empty] | 23 | 44 | 556 |  | 2020-09-17 09:00 | 9:00 | 23 | 44 | 556 |  |  | 2020-09-14 | B14209¦Courtroom 2 - waiting room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Cell Basement | [5 empty] | 21 | 42 | 430 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 430 |  |  | 2020-09-14 | B12948¦Cell Basement¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room | [5 empty] | 21 | 49 | 407 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 407 |  |  | 2020-09-14 | B14209¦Hearing Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main entrance | [5 empty] | 21 | 43 | 419 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 419 |  |  | 2020-09-14 | B12948¦Main entrance¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 302 | [5 empty] | 22 | 46 | 417 |  | 2020-09-17 09:00 | 9:00 | 22 | 46 | 417 |  |  | 2020-09-14 | B20080¦Courtroom 302¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room, Judge’s Chamber | [5 empty] | 21 | 50 | 412 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 412 |  |  | 2020-09-14 | B14209¦Hearing Room, Judge’s Chamber¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main Entrance Waiting Area | [5 empty] | 21 | 44 | 422 |  | 2020-09-17 12:00 | 12:00 | 21 | 44 | 422 |  |  | 2020-09-14 | B12948¦Main Entrance Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 303 | [5 empty] | 22 | 46 | 485 |  | 2020-09-17 09:00 | 9:00 | 22 | 46 | 485 |  |  | 2020-09-14 | B20080¦Courtroom 303¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room - Waiting area | [5 empty] | 23 | 46 | 413 |  | 2020-09-17 09:00 | 9:00 | 23 | 46 | 413 |  |  | 2020-09-14 | B14209¦Hearing Room - Waiting area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Outdoors |  |  | 14 | 75 | 422 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20080¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Front desk | [5 empty] | 21 | 53 | 432 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 432 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Front desk¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Court Room 1 Waiting Area | [5 empty] | 21 | 43 | 427 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 427 |  |  | 2020-09-14 | B12948¦Court Room 1 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown attorney admin area | [5 empty] | 21 | 51 | 421 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 421 |  |  | 2020-09-14 | B14209¦Crown attorney admin area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 Waiting Area | [5 empty] | 21 | 42 | 412 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 412 |  |  | 2020-09-14 | B12948¦Courtroom 2 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Print Room | [5 empty] | 21 | 53 | 405 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 405 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Print Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Assistant Crown Attorney Office (236) | [5 empty] | 21 | 55 | 403 |  | 2020-09-17 09:00 | 9:00 | 21 | 55 | 403 |  |  | 2020-09-14 | B14209¦Assistant Crown Attorney Office (236)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office | [5 empty] | 21 | 54 | 411 |  | 2020-09-17 09:00 | 9:00 | 21 | 54 | 411 |  |  | 2020-09-14 | B14209¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 Waiting Area | [5 empty] | 22 | 41 | 431 |  | 2020-09-17 09:00 | 9:00 | 22 | 41 | 431 |  |  | 2020-09-14 | B12948¦Courtroom 3 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Meeting Room (232) | [5 empty] | 21 | 55 | 403 |  | 2020-09-17 09:00 | 9:00 | 21 | 55 | 403 |  |  | 2020-09-14 | B14209¦Crown Attorney Meeting Room (232)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 Waiting Area | [5 empty] | 22 | 41 | 419 |  | 2020-09-17 09:00 | 9:00 | 22 | 41 | 419 |  |  | 2020-09-14 | B12948¦Courtroom 5 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 and 6 Waiting Area | [5 empty] | 22 | 41 | 421 |  | 2020-09-17 09:00 | 9:00 | 22 | 41 | 421 |  |  | 2020-09-14 | B12948¦Courtroom 4 and 6 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Lobby | [5 empty] | 23 | 51 | 426 |  | 2020-09-17 09:00 | 9:00 | 23 | 51 | 426 |  |  | 2020-09-14 | B14209¦Court Admin Office Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Cubicles | [5 empty] | 22 | 53 | 407 |  | 2020-09-17 09:00 | 9:00 | 22 | 53 | 407 |  |  | 2020-09-14 | B14209¦Court Admin Office Cubicles¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Holding Cell corridor | [5 empty] | 22 | 48 | 403 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 403 |  |  | 2020-09-14 | B14209¦Holding Cell corridor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Police Control Room | [5 empty] | 22 | 50 | 407 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 407 |  |  | 2020-09-14 | B14209¦Police Control Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Intake Court | [5 empty] | 23 | 53 | 418 |  | 2020-09-17 09:00 | 9:00 | 23 | 53 | 418 |  |  | 2020-09-14 | B14209¦Intake Court¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Law Library Meeting Room (028B) | [5 empty] | 22 | 51 | 498 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 498 |  |  | 2020-09-14 | B14209¦Law Library Meeting Room (028B)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Library | [5 empty] | 22 | 51 | 406 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 406 |  |  | 2020-09-14 | B14209¦Library¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Lunch Room | [5 empty] | 22 | 54 | 415 |  | 2020-09-17 09:00 | 9:00 | 22 | 54 | 415 |  |  | 2020-09-14 | B14209¦Lunch Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Entry/Waiting | [5 empty] | 22 | 51 | 464 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 464 |  |  | 2020-09-14 | B70510¦Entry/Waiting¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Entrance by Stair G | [5 empty] | 23 | 44 | 468 |  | 2020-09-17 09:00 | 9:00 | 23 | 44 | 468 |  |  | 2020-09-14 | B14209¦Entrance by Stair G¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room A | [5 empty] | 22 | 50 | 464 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 464 |  |  | 2020-09-14 | B70510¦Mediation Room A¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Main Floor Entrance Lobby | [5 empty] | 23 | 50 | 414 |  | 2020-09-17 09:00 | 9:00 | 23 | 50 | 414 |  |  | 2020-09-14 | B14209¦Main Floor Entrance Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Information Desk | [5 empty] | 22 | 50 | 454 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 454 |  |  | 2020-09-14 | B70510¦Information Desk¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd fl lobby | [5 empty] | 20 | 47 | 571 |  | 2020-09-17 09:00 | 9:00 | 20 | 47 | 571 |  |  | 2020-09-14 | B20226¦2nd fl lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Level 1 Corridor by room 103 | [5 empty] | 22 | 45 | 552 |  | 2020-09-17 09:00 | 9:00 | 22 | 45 | 552 |  |  | 2020-09-14 | B14209¦Level 1 Corridor by room 103¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Lunch Room 454 | [5 empty] | 22 | 50 | 448 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 448 |  |  | 2020-09-14 | B70510¦Lunch Room 454¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Outdoors |  |  | 18 | 62 | 341 |  |  |  | Base Readings | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B25165¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Outdoors |  |  | 10 | 60 | 400 |  |  |  | Morning dew and sunny, cold | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B14209¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Copy Room 455 | [5 empty] | 22 | 50 | 447 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 447 |  |  | 2020-09-14 | B70510¦Copy Room 455¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 2 | [5 empty] | 20 | 49 | 595 |  | 2020-09-17 09:00 | 9:00 | 20 | 49 | 595 |  |  | 2020-09-14 | B20226¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room B | [5 empty] | 22 | 50 | 447 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 447 |  |  | 2020-09-14 | B70510¦Mediation Room B¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | OTHER | [5 empty] | 21 | 51 | 503 | Courtroom 700, Please add to drop down box ,thank you | 2020-09-17 09:00 | 9:00 | 21 | 51 | 503 |  |  | 2020-09-14 | B25165¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 600 | [5 empty] | 22 | 51 | 436 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 436 |  |  | 2020-09-14 | B25165¦Courtroom 600¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Outdoors |  |  | 18 | 46 | 386 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B19652¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Center) | [5 empty] | 22 | 48 | 459 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 459 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Center)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 459 | [5 empty] | 22 | 50 | 454 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 454 |  |  | 2020-09-14 | B70510¦Office 459¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Judge Dias) | [5 empty] | 22 | 48 | 436 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 436 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Judge Dias)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 2 | [5 empty] | 21 | 51 | 647 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 647 |  |  | 2020-09-14 | B20226¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 308 | [5 empty] | 22 | 51 | 445 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 445 |  |  | 2020-09-14 | B25165¦Courtroom 308¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 48 | 435 | Superior judges chamber | 2020-09-17 09:00 | 9:00 | 21 | 48 | 435 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | office 467 | [5 empty] | 22 | 50 | 470 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 470 |  |  | 2020-09-14 | B70510¦office 467¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 306 | [5 empty] | 22 | 51 | 445 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 445 |  |  | 2020-09-14 | B25165¦Courtroom 306¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 49 | 452 | 3rd floor stair landing | 2020-09-17 09:00 | 9:00 | 21 | 49 | 452 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 469 | [5 empty] | 22 | 50 | 468 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 468 |  |  | 2020-09-14 | B70510¦Office 469¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 22 | 50 | 532 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 532 |  |  | 2020-09-14 | B20226¦2nd Floor Holding Cell¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 302 | [5 empty] | 21 | 51 | 443 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 443 |  |  | 2020-09-14 | B25165¦Courtroom 302¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 49 | 451 | 3rd floor Jury room | 2020-09-17 09:00 | 9:00 | 21 | 49 | 451 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 208 | [5 empty] | 21 | 51 | 439 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 439 |  |  | 2020-09-14 | B25165¦Courtroom 208¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Room 473 | [5 empty] | 22 | 50 | 458 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 458 |  |  | 2020-09-14 | B70510¦Room 473¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 49 | 449 | Justice McDonald chamber | 2020-09-17 09:00 | 9:00 | 21 | 49 | 449 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 3 | [5 empty] | 22 | 41 | 444 |  | 2020-09-17 09:00 | 9:00 | 22 | 41 | 444 |  |  | 2020-09-14 | B20226¦Courtroom 3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 206 | [5 empty] | 21 | 51 | 443 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 443 |  |  | 2020-09-14 | B25165¦Courtroom 206¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 49 | 439 | Justice McDonald secretary | 2020-09-17 09:00 | 9:00 | 21 | 49 | 439 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hall 475 or 466 | [5 empty] | 21 | 51 | 488 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 488 |  |  | 2020-09-14 | B70510¦Hall 475 or 466¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 204 | [5 empty] | 22 | 51 | 492 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 492 |  |  | 2020-09-14 | B25165¦Courtroom 204¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 49 | 427 | SCJTC office | 2020-09-17 09:00 | 9:00 | 21 | 49 | 427 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 1 | [5 empty] | 22 | 50 | 454 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 454 |  |  | 2020-09-14 | B70510¦Hearing Room 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 202 | [5 empty] | 21 | 51 | 443 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 443 |  |  | 2020-09-14 | B25165¦Courtroom 202¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 49 | 435 | Visiting justice chamber | 2020-09-17 09:00 | 9:00 | 21 | 49 | 435 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Meeting Rooms 1/2 | [5 empty] | 22 | 51 | 455 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 455 |  |  | 2020-09-14 | B70510¦Vestibule at Meeting Rooms 1/2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 200 | [5 empty] | 21 | 51 | 460 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 460 |  |  | 2020-09-14 | B25165¦Courtroom 200¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Center) | [5 empty] | 21 | 49 | 431 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 431 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Center)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Hearing Room 1 | [5 empty] | 22 | 51 | 462 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 462 |  |  | 2020-09-14 | B70510¦Vestibule at Hearing Room 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 100 | [5 empty] | 22 | 51 | 450 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 450 |  |  | 2020-09-14 | B25165¦Courtroom 100¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Judge Dias) | [5 empty] | 21 | 49 | 438 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 438 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Judge Dias)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Main Lobby | [5 empty] | 20 | 53 | 556 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 556 |  |  | 2020-09-14 | B70050¦Main Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 Waiting Area | [5 empty] | 21 | 50 | 440 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 440 |  |  | 2020-09-14 | B19652¦Courtroom 2 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 2 | [5 empty] | 22 | 51 | 505 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 505 |  |  | 2020-09-14 | B70510¦Hearing Room 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Center) | [5 empty] | 22 | 45 | 438 |  | 2020-09-17 09:00 | 9:00 | 22 | 45 | 438 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Center)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 439 | [5 empty] | 22 | 51 | 457 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 457 |  |  | 2020-09-14 | B70510¦Office 439¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Judge Dias) | [5 empty] | 22 | 44 | 456 |  | 2020-09-17 09:00 | 9:00 | 22 | 44 | 456 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Judge Dias)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 1 | [5 empty] | 20 | 54 | 428 |  | 2020-09-17 09:00 | 9:00 | 20 | 54 | 428 |  |  | 2020-09-14 | B70050¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 46 | 440 | Justice peace chamber | 2020-09-17 09:00 | 9:00 | 22 | 46 | 440 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | First Aid Desk | [5 empty] | 22 | 51 | 453 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 453 |  |  | 2020-09-14 | B70510¦First Aid Desk¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 45 | 435 | Council chamber dias | 2020-09-17 09:00 | 9:00 | 22 | 45 | 435 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 436 | [5 empty] | 22 | 51 | 454 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 454 |  |  | 2020-09-14 | B70510¦Office 436¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 20 | 55 | 428 |  | 2020-09-17 09:00 | 9:00 | 20 | 55 | 428 |  |  | 2020-09-14 | B70050¦2nd Floor Holding Cell¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 45 | 426 | Council chamber center | 2020-09-17 09:00 | 9:00 | 22 | 45 | 426 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 2nd Floor Lunchroom | [5 empty] | 22 | 48 | 477 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 477 |  |  | 2020-09-14 | B19652¦2nd Floor Lunchroom¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 432 | [5 empty] | 22 | 51 | 458 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 458 |  |  | 2020-09-14 | B70510¦Office 432¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 49 | 487 | 2nd floor stair landing | 2020-09-17 09:00 | 9:00 | 22 | 49 | 487 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 429 | [5 empty] | 22 | 51 | 456 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 456 |  |  | 2020-09-14 | B70510¦Office 429¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 49 | 478 | Court service kitchenette | 2020-09-17 09:00 | 9:00 | 22 | 49 | 478 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Yannick Bedard Office - 2nd Floor | [5 empty] | 22 | 55 | 472 |  | 2020-09-17 09:00 | 9:00 | 22 | 55 | 472 |  |  | 2020-09-14 | B70050¦Yannick Bedard Office - 2nd Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 427 | [5 empty] | 22 | 51 | 459 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 459 |  |  | 2020-09-14 | B70510¦Office 427¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 20 | 57 | 701 | Court service north | 2020-09-17 09:00 | 9:00 | 20 | 57 | 701 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mail Room | [5 empty] | 22 | 51 | 459 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 459 |  |  | 2020-09-14 | B70510¦Mail Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 2 | [5 empty] | 22 | 55 | 442 |  | 2020-09-17 09:00 | 9:00 | 22 | 55 | 442 |  |  | 2020-09-14 | B70050¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 420 | [5 empty] | 22 | 51 | 457 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 457 |  |  | 2020-09-14 | B70510¦Office 420¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 55 | 681 | Court service south | 2020-09-17 09:00 | 9:00 | 21 | 55 | 681 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-1 | [5 empty] | 20.9 | 53 | 710 |  | 2020-09-17 09:00 | 9:00 | 20.9 | 53 | 710 |  |  | 2020-09-14 | B10644¦Courtroom 2-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 54 | 671 | Court service entrance vestibule | 2020-09-17 09:00 | 9:00 | 21 | 54 | 671 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd fl lobby | [5 empty] | 20 | 55 | 423 |  | 2020-09-17 09:00 | 9:00 | 20 | 55 | 423 |  |  | 2020-09-14 | B70050¦2nd fl lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 418 | [5 empty] | 22 | 51 | 462 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 462 |  |  | 2020-09-14 | B70510¦Office 418¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 50 | 595 | 1st floor stair landing | 2020-09-17 09:00 | 9:00 | 22 | 50 | 595 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-2 | [5 empty] | 19.7 | 58.7 | 567 |  | 2020-09-17 09:00 | 9:00 | 19.7 | 58.7 | 567 |  |  | 2020-09-14 | B10644¦Courtroom 2-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Outdoors |  |  | 17 | 60 | 487 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20289¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | File Room | [5 empty] | 22 | 51 | 458 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 458 |  |  | 2020-09-14 | B70510¦File Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Outdoors |  |  | 12 | 72 | 429 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B90838¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 21 | 52 | 494 | judge | 2020-09-17 09:00 | 9:00 | 21 | 52 | 494 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Health Room | [5 empty] | 22 | 51 | 471 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 471 |  |  | 2020-09-14 | B70510¦Health Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Courtroom 101 Courtroom 102 | [5 empty] | 22 | 50 | 443 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 443 |  |  | 2020-09-14 | B90838¦Courtroom 101 Courtroom 102¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-3 | [5 empty] | 20.5 | 63 | 437 |  | 2020-09-17 09:00 | 9:00 | 20.5 | 63 | 437 |  | caution | 2020-09-14 | B10644¦Courtroom 2-3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 21 | 52 | 500 | public | 2020-09-17 09:00 | 9:00 | 21 | 52 | 500 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 | [5 empty] | 21 | 51 | 464 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 464 |  |  | 2020-09-14 | B70510¦Hearing Room 3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 22 | 51 | 502 | judge | 2020-09-17 09:00 | 9:00 | 22 | 51 | 502 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 22 | 51 | 501 | public | 2020-09-17 09:00 | 9:00 | 22 | 51 | 501 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 Waiting Area | [5 empty] | 22 | 52 | 452 |  | 2020-09-17 09:00 | 9:00 | 22 | 52 | 452 |  |  | 2020-09-14 | B70510¦Hearing Room 3 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-4 | [5 empty] | 23 | 46.9 | 545 |  | 2020-09-17 09:00 | 9:00 | 23 | 46.9 | 545 |  |  | 2020-09-14 | B10644¦Courtroom 2-4¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Outdoors |  |  | 6 | 57 | 402 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70050¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 300 | [5 empty] | 23 | 50 | 542 |  | 2020-09-17 09:00 | 9:00 | 23 | 50 | 542 |  |  | 2020-09-14 | B20289¦Courtroom 300¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 301 | [5 empty] | 23 | 49 | 548 |  | 2020-09-17 09:00 | 9:00 | 23 | 49 | 548 |  |  | 2020-09-14 | B20289¦Courtroom 301¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Elevator Lobby | [5 empty] | 22 | 53 | 452 |  | 2020-09-17 09:00 | 9:00 | 22 | 53 | 452 |  |  | 2020-09-14 | B70510¦Elevator Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 302 | [5 empty] | 23 | 50 | 539 |  | 2020-09-17 09:00 | 9:00 | 23 | 50 | 539 |  |  | 2020-09-14 | B20289¦Courtroom 302¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 303 | [5 empty] | 23 | 49 | 541 |  | 2020-09-17 09:00 | 9:00 | 23 | 49 | 541 |  |  | 2020-09-14 | B20289¦Courtroom 303¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Outdoors |  |  | 15 | 63 | 453 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70510¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom A | [5 empty] | 22 | 50 | 560 | in session; measurement taken outside courtroom | 2020-09-17 09:00 | 9:00 | 22 | 50 | 560 |  |  | 2020-09-14 | B20289¦Courtroom A¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-6 | [5 empty] | 23.2 | 56 | 431 |  | 2020-09-17 09:00 | 9:00 | 23.2 | 56 | 431 |  |  | 2020-09-14 | B10644¦Courtroom 2-6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom B | [5 empty] | 22 | 49 | 572 |  | 2020-09-17 09:00 | 9:00 | 22 | 49 | 572 |  |  | 2020-09-14 | B20289¦Courtroom B¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 100 Courtroom 102 Courtroom 104 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203 Courtroom 403 | [5 empty] | 21 | 49 | 460 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 460 |  |  | 2020-09-14 | B20616¦Courtroom 100 Courtroom 102 Courtroom 104 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203 Courtroom 403¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Outdoors |  |  | 5 | 51 | 388 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20226¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom C (North) | [5 empty] | 22 | 49 | 581 |  | 2020-09-17 09:00 | 9:00 | 22 | 49 | 581 |  |  | 2020-09-14 | B20289¦Courtroom C (North)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom D | [5 empty] | 23 | 51 | 570 | in session; measurement taken outside courtroom | 2020-09-17 09:00 | 9:00 | 23 | 51 | 570 |  |  | 2020-09-14 | B20289¦Courtroom D¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 1 | [5 empty] | 22 | 44 | 489 |  | 2020-09-17 09:00 | 9:00 | 22 | 44 | 489 |  |  | 2020-09-14 | B25602¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom E | [5 empty] | 23 | 53 | 591 | in session; measurement taken outside courtroom | 2020-09-17 09:00 | 9:00 | 23 | 53 | 591 |  |  | 2020-09-14 | B20289¦Courtroom E¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 101 Courtroom 103 Courtroom 105 Courtroom 401 Courtroom 402 | [5 empty] | 22 | 49 | 460 |  | 2020-09-17 09:00 | 9:00 | 22 | 49 | 460 |  |  | 2020-09-14 | B20616¦Courtroom 101 Courtroom 103 Courtroom 105 Courtroom 401 Courtroom 402¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom F | [5 empty] | 22 | 55 | 577 | in session; measurement taken outside courtroom | 2020-09-17 09:00 | 9:00 | 22 | 55 | 577 |  |  | 2020-09-14 | B20289¦Courtroom F¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 2 | [5 empty] | 22 | 45 | 481 |  | 2020-09-17 09:00 | 9:00 | 22 | 45 | 481 |  |  | 2020-09-14 | B25602¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 106 | [5 empty] | 20 | 52 | 459 |  | 2020-09-17 09:00 | 9:00 | 20 | 52 | 459 |  |  | 2020-09-14 | B20616¦Courtroom 106¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 3 | [5 empty] | 22 | 42 | 505 |  | 2020-09-17 09:00 | 9:00 | 22 | 42 | 505 |  |  | 2020-09-14 | B25602¦Courtroom 3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 4 | [5 empty] | 23 | 42 | 482 |  | 2020-09-17 09:00 | 9:00 | 23 | 42 | 482 |  |  | 2020-09-14 | B25602¦Courtroom 4¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 204 Courtroom 205 Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 405 | [5 empty] | 21 | 52 | 459 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 459 |  |  | 2020-09-14 | B20616¦Courtroom 204 Courtroom 205 Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 405¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-8 | [5 empty] | 21.5 | 53.1 | 661 |  | 2020-09-17 09:00 | 9:00 | 21.5 | 53.1 | 661 |  |  | 2020-09-14 | B10644¦Courtroom 2-8¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 5 | [5 empty] | 23 | 42 | 443 |  | 2020-09-17 09:00 | 9:00 | 23 | 42 | 443 |  |  | 2020-09-14 | B25602¦Courtroom 5¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 404 | [5 empty] | 22 | 52 | 459 |  | 2020-09-17 09:00 | 9:00 | 22 | 52 | 459 |  |  | 2020-09-14 | B20616¦Courtroom 404¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 6 | [5 empty] | 23 | 44 | 505 |  | 2020-09-17 09:00 | 9:00 | 23 | 44 | 505 |  |  | 2020-09-14 | B25602¦Courtroom 6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 3-2 | [5 empty] | 22.1 | 56.4 | 450 |  | 2020-09-17 09:00 | 9:00 | 22.1 | 56.4 | 450 |  |  | 2020-09-14 | B10644¦Courtroom 3-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 7 | [5 empty] | 23 | 42 | 496 |  | 2020-09-17 09:00 | 9:00 | 23 | 42 | 496 |  |  | 2020-09-14 | B25602¦Courtroom 7¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 107 Courtroom 108 | [5 empty] | 21 | 59 | 455 |  | 2020-09-17 09:00 | 9:00 | 21 | 59 | 455 |  |  | 2020-09-14 | B20616¦Courtroom 107 Courtroom 108¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 304 Courtroom 305 | [5 empty] | 22 | 52 | 567 |  | 2020-09-17 09:00 | 9:00 | 22 | 52 | 567 |  |  | 2020-09-14 | B20616¦Courtroom 304 Courtroom 305¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-1 | [5 empty] | 22.7 | 58.3 | 506 |  | 2020-09-17 09:00 | 9:00 | 22.7 | 58.3 | 506 |  |  | 2020-09-14 | B10644¦Courtroom 4-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-2 | [5 empty] | 20.9 | 56.5 | 433 |  | 2020-09-17 09:00 | 9:00 | 20.9 | 56.5 | 433 |  |  | 2020-09-14 | B10644¦Courtroom 4-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Outdoors |  |  | 14 | 63 | 687 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B25602¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-2 | [5 empty] | 20.9 | 56.5 | 433 |  | 2020-09-17 09:00 | 9:00 | 20.9 | 56.5 | 433 |  |  | 2020-09-14 | B10644¦Courtroom 4-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-3 | [5 empty] | 23.5 | 56.1 | 405 |  | 2020-09-17 09:00 | 9:00 | 23.5 | 56.1 | 405 |  |  | 2020-09-14 | B10644¦Courtroom 4-3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-4 | [5 empty] | 22.3 | 48.4 | 522 |  | 2020-09-17 09:00 | 9:00 | 22.3 | 48.4 | 522 |  |  | 2020-09-14 | B10644¦Courtroom 4-4¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | front seating area | [5 empty] | 21 | 57 | 411 |  | 2020-09-17 09:00 | 9:00 | 21 | 57 | 411 |  |  | 2020-09-14 | B18359¦front seating area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | northwest corridor | [5 empty] | 21 | 56 | 407 |  | 2020-09-17 09:00 | 9:00 | 21 | 56 | 407 |  |  | 2020-09-14 | B18359¦northwest corridor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-6 | [5 empty] | 22.6 | 49 | 433 |  | 2020-09-17 09:00 | 9:00 | 22.6 | 49 | 433 |  |  | 2020-09-14 | B10644¦Courtroom 4-6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 21 | 56 | 410 | north side | 2020-09-17 09:00 | 9:00 | 21 | 56 | 410 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 21 | 56 | 404 | south side | 2020-09-17 09:00 | 9:00 | 21 | 56 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-7 | [5 empty] | 22 | 43.5 | 404 |  | 2020-09-17 09:00 | 9:00 | 22 | 43.5 | 404 |  |  | 2020-09-14 | B10644¦Courtroom 4-7¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 21 | 55 | 409 | north side | 2020-09-17 09:00 | 9:00 | 21 | 55 | 409 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 21 | 55 | 405 | south side | 2020-09-17 09:00 | 9:00 | 21 | 55 | 405 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 21 | 55 | 404 | north side | 2020-09-17 09:00 | 9:00 | 21 | 55 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-8 | [5 empty] | 23.1 | 54.4 | 409 |  | 2020-09-17 09:00 | 9:00 | 23.1 | 54.4 | 409 |  |  | 2020-09-14 | B10644¦Courtroom 4-8¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 21 | 55 | 408 | south side | 2020-09-17 09:00 | 9:00 | 21 | 55 | 408 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 55 | 411 | north side | 2020-09-17 09:00 | 9:00 | 21 | 55 | 411 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22.6 | 54 | 516 |  | 2020-09-17 09:00 | 9:00 | 22.6 | 54 | 516 |  |  | 2020-09-14 | B10644¦Courtroom 5-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 55 | 405 | south side | 2020-09-17 09:00 | 9:00 | 21 | 55 | 405 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 54 | 404 | north side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-1 | [5 empty] | 17.5 | 55.1 | 407 |  | 2020-09-17 09:00 | 9:00 | 17.5 | 55.1 | 407 |  |  | 2020-09-14 | B10644¦Courtroom 6-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 54 | 397 | south side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 397 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 101 | [5 empty] | 21 | 53 | 506 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 506 |  |  | 2020-09-14 | B19512¦Courtroom 101¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 21 | 54 | 399 | north side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 399 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 200 | [5 empty] | 21 | 53 | 528 |  | 2020-09-17 12:00 | 12:00 | 21 | 53 | 528 |  |  | 2020-09-14 | B19512¦Courtroom 200¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 21 | 54 | 404 | south side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 21 | 54 | 404 | north side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 21 | 54 | 408 | south side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 408 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 21 | 55 | 415 | north side | 2020-09-17 09:00 | 9:00 | 21 | 55 | 415 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 201 | [5 empty] | 23 | 53 | 528 |  | 2020-09-17 12:00 | 12:00 | 23 | 53 | 528 |  |  | 2020-09-14 | B19512¦Courtroom 201¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 21 | 54 | 408 | south side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 408 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Outdoors |  |  | 15 | 75 | [5 empty] | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B19512¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 21 | 54 | 403 | north side | 2020-09-17 09:00 | 9:00 | 21 | 54 | 403 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 22 | 54 | 407 | south side | 2020-09-17 09:00 | 9:00 | 22 | 54 | 407 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | northeast courtroom | [5 empty] | 22 | 54 | 411 |  | 2020-09-17 09:00 | 9:00 | 22 | 54 | 411 |  |  | 2020-09-14 | B18359¦northeast courtroom¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 22 | 53 | 398 | north side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 398 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 22 | 53 | 404 | south side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 22 | 53 | 402 | north side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 402 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Main entrance | [5 empty] | 21 | 58 | 472 |  | 2020-09-17 09:00 | 9:00 | 21 | 58 | 472 |  |  | 2020-09-14 | B90636¦Main entrance¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 22 | 53 | 400 | south side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 400 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 21 | 52 | 435 | north | 2020-09-17 09:00 | 9:00 | 21 | 52 | 435 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 22 | 53 | 399 | north side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 399 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 21 | 52 | 436 | south | 2020-09-17 09:00 | 9:00 | 21 | 52 | 436 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 22 | 53 | 405 | south side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 405 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 21 | 48 | 464 | vestibule | 2020-09-17 09:00 | 9:00 | 21 | 48 | 464 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtrooom 213 | [5 empty] | 22 | 53 | 402 | north side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 402 |  |  | 2020-09-14 | B18359¦courtrooom 213¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 21 | 47 | 462 | door entrance | 2020-09-17 09:00 | 9:00 | 21 | 47 | 462 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 22 | 53 | 402 | south side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 402 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | hallway by courtroom 203 | [5 empty] | 21 | 52 | 464 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 464 |  |  | 2020-09-14 | B90636¦hallway by courtroom 203¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 22 | 53 | 402 | north side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 402 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 2nd fl lobby | [5 empty] | 21 | 51 | 440 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 440 |  |  | 2020-09-14 | B90636¦2nd fl lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courrtoom 214 | [5 empty] | 22 | 53 | 401 | south side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 401 |  |  | 2020-09-14 | B18359¦courrtoom 214¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office North | [5 empty] | 23 | 34 | 556 |  | 2020-09-17 09:00 | 9:00 | 23 | 34 | 556 |  | low | 2020-09-14 | B14895¦Administration Office North¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | coutroom 215 | [5 empty] | 22 | 53 | 400 | north side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 400 |  |  | 2020-09-14 | B18359¦coutroom 215¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 3rd Floor Elevator Lobby | [5 empty] | 21 | 51 | 443 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 443 |  |  | 2020-09-14 | B90636¦3rd Floor Elevator Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office South | [5 empty] | 24 | 37 | 600 |  | 2020-09-17 09:00 | 9:00 | 24 | 37 | 600 |  | caution | 2020-09-14 | B14895¦Administration Office South¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 22 | 53 | 410 | south side | 2020-09-17 09:00 | 9:00 | 22 | 53 | 410 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 21 | 51 | 432 | west | 2020-09-17 09:00 | 9:00 | 21 | 51 | 432 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main entrance | [5 empty] | 21 | 36 | 475 |  | 2020-09-17 09:00 | 9:00 | 21 | 36 | 475 |  | caution | 2020-09-14 | B14895¦Main entrance¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Outdoors |  |  | 16 | 67 | 394 |  |  |  | outside of 15 Grosvenor Ave. | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B18359¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 21 | 51 | 433 | east | 2020-09-17 09:00 | 9:00 | 21 | 51 | 433 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main Floor Waiting Area | [5 empty] | 22 | 34 | 451 |  | 2020-09-17 09:00 | 9:00 | 22 | 34 | 451 |  | low | 2020-09-14 | B14895¦Main Floor Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 4th floor waiting area | [5 empty] | 21 | 52 | 437 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 437 |  |  | 2020-09-14 | B90636¦4th floor waiting area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom A | [5 empty] | 22 | 36 | 427 |  | 2020-09-17 09:00 | 9:00 | 22 | 36 | 427 |  | caution | 2020-09-14 | B14895¦Courtroom A¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 210 | [5 empty] | 21 | 54 | 423 | west | 2020-09-17 09:00 | 9:00 | 21 | 54 | 423 |  |  | 2020-09-14 | B90636¦Courtroom 210¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 210 | [5 empty] | 20 | 55 | 421 | east | 2020-09-17 09:00 | 9:00 | 20 | 55 | 421 |  |  | 2020-09-14 | B90636¦Courtroom 210¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom B | [5 empty] | 21 | 38 | 430 |  | 2020-09-17 09:00 | 9:00 | 21 | 38 | 430 |  | caution | 2020-09-14 | B14895¦Courtroom B¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | courtroom 211 | [5 empty] | 20 | 54 | 422 | west | 2020-09-17 09:00 | 9:00 | 20 | 54 | 422 |  |  | 2020-09-14 | B90636¦courtroom 211¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | 2nd Floor Waiting Area | [5 empty] | 23 | 32 | 501 |  | 2020-09-17 09:00 | 9:00 | 23 | 32 | 501 |  | low | 2020-09-14 | B14895¦2nd Floor Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | courtroom 211 | [5 empty] | 21 | 54 | 417 | east | 2020-09-17 09:00 | 9:00 | 21 | 54 | 417 |  |  | 2020-09-14 | B90636¦courtroom 211¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Crown Attorney Office | [5 empty] | 23 | 34 | 423 |  | 2020-09-17 09:00 | 9:00 | 23 | 34 | 423 |  | low | 2020-09-14 | B14895¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | hallway by courtroom 210 | [5 empty] | 20 | 54 | 426 |  | 2020-09-17 09:00 | 9:00 | 20 | 54 | 426 |  |  | 2020-09-14 | B90636¦hallway by courtroom 210¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Waiting Area | [5 empty] | 23 | 34 | 521 |  | 2020-09-17 09:00 | 9:00 | 23 | 34 | 521 |  | low | 2020-09-14 | B14895¦Basement Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | outside | [5 empty] | 17 | 61 | 427 |  | 2020-09-17 09:00 | 9:00 | 17 | 61 | 427 |  | caution | 2020-09-14 | B90636¦outside¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | reception area | [5 empty] | 20 | 57 | 475 |  | 2020-09-17 09:00 | 9:00 | 20 | 57 | 475 |  |  | 2020-09-14 | B70003¦reception area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Boardroom | [5 empty] | 24 | 35 | 450 |  | 2020-09-17 09:00 | 9:00 | 24 | 35 | 450 |  | caution | 2020-09-14 | B14895¦Basement Boardroom¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Main entrance | [5 empty] | 20 | 51 | 450 |  | 2020-09-17 09:00 | 9:00 | 20 | 51 | 450 |  |  | 2020-09-14 | B20979¦Main entrance¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Male Holding Cell | [5 empty] | 24 | 31 | 419 |  | 2020-09-17 09:00 | 9:00 | 24 | 31 | 419 |  | low | 2020-09-14 | B14895¦Male Holding Cell¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 21 | 51 | 452 | north | 2020-09-17 09:00 | 9:00 | 21 | 51 | 452 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Female Holding Cell | [5 empty] | 24 | 32 | 491 |  | 2020-09-17 09:00 | 9:00 | 24 | 32 | 491 |  | low | 2020-09-14 | B14895¦Female Holding Cell¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Outdoors |  |  | 19 | 58 | 341 |  |  |  | Base Readings | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B25165¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 22 | 44 | 447 | south | 2020-09-17 09:00 | 9:00 | 22 | 44 | 447 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Outdoors |  |  | 14 | 19 | 393 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B14895¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | front of main hallway | [5 empty] | 20 | 57 | 460 |  | 2020-09-17 09:00 | 9:00 | 20 | 57 | 460 |  |  | 2020-09-14 | B70003¦front of main hallway¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 21 | 44 | 486 | south | 2020-09-17 09:00 | 9:00 | 21 | 44 | 486 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 20 | 57 | 461 | outside of 502 | 2020-09-17 09:00 | 9:00 | 20 | 57 | 461 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | OTHER | [5 empty] | 21 | 51 | 717 | Courtroom 700, Please add to drop down box thank you | 2020-09-17 12:00 | 12:00 | 21 | 51 | 717 |  |  | 2020-09-14 | B25165¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 22 | 45 | 454 | north | 2020-09-17 09:00 | 9:00 | 22 | 45 | 454 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 20 | 57 | 462 | public area | 2020-09-17 09:00 | 9:00 | 20 | 57 | 462 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 600 | [5 empty] | 22 | 51 | 436 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 436 |  |  | 2020-09-14 | B25165¦Courtroom 600¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 20 | 57 | 456 | judge area | 2020-09-17 09:00 | 9:00 | 20 | 57 | 456 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | courtroom 307 | [5 empty] | 21 | 46 | 444 | south | 2020-09-17 09:00 | 9:00 | 21 | 46 | 444 |  |  | 2020-09-14 | B20979¦courtroom 307¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 308 | [5 empty] | 22 | 51 | 524 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 524 |  |  | 2020-09-14 | B25165¦Courtroom 308¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 57 | 471 | outside of 503 | 2020-09-17 09:00 | 9:00 | 20 | 57 | 471 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | courtroom 307 | [5 empty] | 22 | 46 | 449 | north | 2020-09-17 09:00 | 9:00 | 22 | 46 | 449 |  |  | 2020-09-14 | B20979¦courtroom 307¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 57 | 459 | public area | 2020-09-17 09:00 | 9:00 | 20 | 57 | 459 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 56 | 460 | judge area | 2020-09-17 09:00 | 9:00 | 20 | 56 | 460 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | hallway by courtroom 307 | [5 empty] | 21 | 45 | 452 |  | 2020-09-17 09:00 | 9:00 | 21 | 45 | 452 |  |  | 2020-09-14 | B20979¦hallway by courtroom 307¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 56 | 468 | outside of 506 | 2020-09-17 09:00 | 9:00 | 20 | 56 | 468 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 306 | [5 empty] | 22 | 51 | 422 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 422 |  |  | 2020-09-14 | B25165¦Courtroom 306¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Outdoors |  |  | 17 | 72 | [5 empty] | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20619¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 21 | 46 | 450 | north | 2020-09-17 09:00 | 9:00 | 21 | 46 | 450 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 57 | 464 | public area | 2020-09-17 09:00 | 9:00 | 20 | 57 | 464 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 302 | [5 empty] | 21 | 51 | 522 |  | 2020-09-17 12:00 | 12:00 | 21 | 51 | 522 |  |  | 2020-09-14 | B25165¦Courtroom 302¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Courtroom 1-14 | [5 empty] | 22 | 49 | 469 |  | 2020-09-17 12:00 | 12:00 | 22 | 49 | 469 |  |  | 2020-09-14 | B20619¦Courtroom 1-14¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 56 | 481 | judge area | 2020-09-17 09:00 | 9:00 | 20 | 56 | 481 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 22 | 46 | 449 | south | 2020-09-17 09:00 | 9:00 | 22 | 46 | 449 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 208 | [5 empty] | 21 | 51 | 442 |  | 2020-09-17 12:00 | 12:00 | 21 | 51 | 442 |  |  | 2020-09-14 | B25165¦Courtroom 208¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 56 | 477 | outside of 509 | 2020-09-17 09:00 | 9:00 | 20 | 56 | 477 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | hallway by courtroom 302 | [5 empty] | 21 | 46 | 456 |  | 2020-09-17 09:00 | 9:00 | 21 | 46 | 456 |  |  | 2020-09-14 | B20979¦hallway by courtroom 302¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 56 | 451 | public area | 2020-09-17 09:00 | 9:00 | 20 | 56 | 451 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 206 | [5 empty] | 21 | 51 | 450 |  | 2020-09-17 12:00 | 12:00 | 21 | 51 | 450 |  |  | 2020-09-14 | B25165¦Courtroom 206¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 56 | 450 | judge area | 2020-09-17 09:00 | 9:00 | 20 | 56 | 450 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 50 | 440 | south | 2020-09-17 09:00 | 9:00 | 22 | 50 | 440 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 56 | 494 | outside of 510 | 2020-09-17 09:00 | 9:00 | 20 | 56 | 494 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 204 | [5 empty] | 21 | 51 | 477 |  | 2020-09-17 12:00 | 12:00 | 21 | 51 | 477 |  |  | 2020-09-14 | B25165¦Courtroom 204¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 56 | 466 | public area | 2020-09-17 09:00 | 9:00 | 20 | 56 | 466 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 49 | 436 | north | 2020-09-17 09:00 | 9:00 | 22 | 49 | 436 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 202 | [5 empty] | 21 | 51 | 452 |  | 2020-09-17 12:00 | 12:00 | 21 | 51 | 452 |  |  | 2020-09-14 | B25165¦Courtroom 202¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 56 | 457 | judge area | 2020-09-17 09:00 | 9:00 | 20 | 56 | 457 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 3 | [5 empty] | 23 | 48 | 340 |  | 2020-09-17 09:00 | 9:00 | 23 | 48 | 340 |  |  | 2020-09-14 | B24638¦Courtroom 3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Basement cells - hallway | [5 empty] | 23 | 50 | 443 |  | 2020-09-17 09:00 | 9:00 | 23 | 50 | 443 |  |  | 2020-09-14 | B20979¦Basement cells - hallway¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 200 | [5 empty] | 21 | 51 | 450 |  | 2020-09-17 12:00 | 12:00 | 21 | 51 | 450 |  |  | 2020-09-14 | B25165¦Courtroom 200¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | back of main hallway | [5 empty] | 20 | 56 | 521 |  | 2020-09-17 09:00 | 9:00 | 20 | 56 | 521 |  |  | 2020-09-14 | B70003¦back of main hallway¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 100 | [5 empty] | 22 | 51 | 450 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 450 |  |  | 2020-09-14 | B25165¦Courtroom 100¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | police office | [5 empty] | 23 | 45 | 522 |  | 2020-09-17 09:00 | 9:00 | 23 | 45 | 522 |  |  | 2020-09-14 | B20979¦police office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | elevator area | [5 empty] | 20 | 57 | 479 |  | 2020-09-17 09:00 | 9:00 | 20 | 57 | 479 |  |  | 2020-09-14 | B70003¦elevator area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Outdoors |  |  | 17 | 66 | 409 |  |  |  | outside of 444 Yonge St. | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70003¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | outside | [5 empty] | 17 | 61 | 427 |  | 2020-09-17 09:00 | 9:00 | 17 | 61 | 427 |  | caution | 2020-09-14 | B20979¦outside¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 3 | [5 empty] | 23 | 47 | 348 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 348 |  |  | 2020-09-14 | B24638¦Courtroom 3¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-1, 16th Floor OTHER | [5 empty] | 21 | 51 | 634 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 634 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-1, 16th Floor OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-3, 16th Floor OTHER | [5 empty] | 21 | 52 | 630 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 630 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-3, 16th Floor OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 16th Floor OTHER | [5 empty] | 21 | 52 | 625 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 625 |  |  | 2020-09-14 | B25398¦Elevator Lobby, 16th Floor OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 1 | [5 empty] | 23 | 48 | 313 |  | 2020-09-17 09:00 | 9:00 | 23 | 48 | 313 |  |  | 2020-09-14 | B24638¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Washrooms, 16th Floor OTHER | [5 empty] | 21 | 52 | 636 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 636 |  |  | 2020-09-14 | B25398¦Corridor adj. to Washrooms, 16th Floor OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 1 | [5 empty] | 23 | 48 | 348 |  | 2020-09-17 12:00 | 12:00 | 23 | 48 | 348 |  |  | 2020-09-14 | B24638¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Women's Washroom, 16th Floor | [5 empty] | 21 | 51 | 629 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 629 |  |  | 2020-09-14 | B25398¦OTHER Women's Washroom, 16th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Outdoors |  |  | 20 | 47 | 310 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B24638¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Outdoors |  |  | 23 | 47 | 322 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B24638¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 2 | [5 empty] | 21 | 61 | 562 |  | 2020-09-17 09:00 | 9:00 | 21 | 61 | 562 |  | caution | 2020-09-14 | B11586¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 20 | 63 | 501 | CROWN Attorney Beaton | 2020-09-17 09:00 | 9:00 | 20 | 63 | 501 |  | caution | 2020-09-14 | B11586¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 19 | 60 | 507 | Crown attorney heneault’s office | 2020-09-17 09:00 | 9:00 | 19 | 60 | 507 |  | caution | 2020-09-14 | B11586¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown attorney admin area | [5 empty] | 20 | 55 | 602 |  | 2020-09-17 09:00 | 9:00 | 20 | 55 | 602 |  |  | 2020-09-14 | B11586¦Crown attorney admin area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, West, 15th Floor | [5 empty] | 20 | 53 | 645 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 645 |  |  | 2020-09-14 | B25398¦OTHER Office Area, West, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 - waiting area | [5 empty] | 21 | 51 | 440 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 440 |  |  | 2020-09-14 | B11586¦Courtroom 1 - waiting area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 | [5 empty] | 21 | 44 | 427 |  | 2020-09-17 09:00 | 9:00 | 21 | 44 | 427 |  |  | 2020-09-14 | B11586¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North West, 15th Floor | [5 empty] | 20 | 53 | 645 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 645 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North West, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | 2nd Floor Holding Cell | [5 empty] | 21 | 48 | 446 |  | 2020-09-17 09:00 | 9:00 | 21 | 48 | 446 |  |  | 2020-09-14 | B11586¦2nd Floor Holding Cell¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North, 15th Floor | [5 empty] | 20 | 53 | 650 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 650 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Judge office | [5 empty] | 22 | 48 | 530 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 530 |  |  | 2020-09-14 | B11586¦Judge office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North East, 15th Floor | [5 empty] | 20 | 54 | 648 |  | 2020-09-17 09:00 | 9:00 | 20 | 54 | 648 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North East, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 21 | 52 | 482 | Courthouse administration office | 2020-09-17 09:00 | 9:00 | 21 | 52 | 482 |  |  | 2020-09-14 | B11586¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Main Lobby | [5 empty] | 22 | 52 | 472 |  | 2020-09-17 09:00 | 9:00 | 22 | 52 | 472 |  |  | 2020-09-14 | B11586¦Main Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, East, 15th Floor | [5 empty] | 20 | 54 | 657 |  | 2020-09-17 09:00 | 9:00 | 20 | 54 | 657 |  |  | 2020-09-14 | B25398¦OTHER Office Area, East, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Outdoors |  |  | 18 | 62 | 382 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B11586¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20893 | B20893 - 75 Mulcaster St. - Barrie | Courtroom 7,8,9 | [5 empty] | 21.4 | 45 | 442 |  | 2020-09-17 09:00 | 9:00 | 21.4 | 45 | 442 |  |  | 2020-09-14 | B20893¦Courtroom 7,8,9¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, Souoth East, 15th Floor | [5 empty] | 21 | 53 | 650 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 650 |  |  | 2020-09-14 | B25398¦OTHER Office Area, Souoth East, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92347 | B92347 - 75 Mulcaster Street - Barrie | Courtroom 15 | [5 empty] | 20.3 | 38 | 461 |  | 2020-09-17 09:00 | 9:00 | 20.3 | 38 | 461 |  | caution | 2020-09-14 | B92347¦Courtroom 15¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South, 15th Floor | [5 empty] | 20 | 53 | 641 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 641 |  |  | 2020-09-14 | B25398¦OTHER Office Area, South, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20893 | B20893 - 75 Mulcaster St. - Barrie | Courtroom 7,8,9 | [5 empty] | 22 | 42 | 522 |  | 2020-09-17 12:00 | 12:00 | 22 | 42 | 522 |  |  | 2020-09-14 | B20893¦Courtroom 7,8,9¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Reception, 15th Floor | [5 empty] | 20 | 53 | 644 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 644 |  |  | 2020-09-14 | B25398¦OTHER Reception, 15th Floor¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Outdoors |  |  | 12 | 51 | 405 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B12948¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Mail Room, 15th Floor OTHER | [5 empty] | 21 | 53 | 655 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 655 |  |  | 2020-09-14 | B25398¦Mail Room, 15th Floor OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 1 | [5 empty] | 20 | 41 | 420 |  | 2020-09-17 12:00 | 12:00 | 20 | 41 | 420 |  |  | 2020-09-14 | B12948¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92347 | B92347 - 75 Mulcaster Street - Barrie | Courtroom 15 | [5 empty] | 21.3 | 47 | 481 |  | 2020-09-17 12:00 | 12:00 | 21.3 | 47 | 481 |  |  | 2020-09-14 | B92347¦Courtroom 15¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 15th Floor OTHER | [5 empty] | 21 | 53 | 640 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 640 |  |  | 2020-09-14 | B25398¦Elevator Lobby, 15th Floor OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 | [5 empty] | 21 | 39 | 434 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 434 |  | caution | 2020-09-14 | B12948¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Outdoors |  |  | 16 | 53 | 630 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B25398¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 | [5 empty] | 21 | 37 | 480 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 480 |  | caution | 2020-09-14 | B12948¦Courtroom 3¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 | [5 empty] | 21 | 36 | 408 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 408 |  | caution | 2020-09-14 | B12948¦Courtroom 4¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 101 | [5 empty] | 22 | 48 |  |  | 2020-09-17 12:00 | 12:00 | 22 | 48 |  |  |  | 2020-09-14 | B20080¦Courtroom 101¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 | [5 empty] | 21 | 36 | 410 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 410 |  | caution | 2020-09-14 | B12948¦Courtroom 5¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 6 | [5 empty] | 21 | 36 | 416 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 416 |  | caution | 2020-09-14 | B12948¦Courtroom 6¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration Office Waiting Area | [5 empty] | 22 | 37 | 427 |  | 2020-09-17 12:00 | 12:00 | 22 | 37 | 427 |  | caution | 2020-09-14 | B12948¦Administration Office Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 201 | [5 empty] | 22 | 45 | 456 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 456 |  |  | 2020-09-14 | B20080¦Courtroom 201¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration office | [5 empty] | 22 | 38 | 434 |  | 2020-09-17 12:00 | 12:00 | 22 | 38 | 434 |  | caution | 2020-09-14 | B12948¦Administration office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 202 | [5 empty] | 23 | 45 | 443 |  | 2020-09-17 12:00 | 12:00 | 23 | 45 | 443 |  |  | 2020-09-14 | B20080¦Courtroom 202¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Crown attorney admin area | [5 empty] | 22 | 40 | 579 |  | 2020-09-17 12:00 | 12:00 | 22 | 40 | 579 |  | caution | 2020-09-14 | B12948¦Crown attorney admin area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 301 | [5 empty] | 22 | 45 | 456 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 456 |  |  | 2020-09-14 | B20080¦Courtroom 301¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Cell Basement | [5 empty] | 22 | 38 | 497 |  | 2020-09-17 12:00 | 12:00 | 22 | 38 | 497 |  | caution | 2020-09-14 | B12948¦Cell Basement¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 302 | [5 empty] | 22 | 45 | 485 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 485 |  |  | 2020-09-14 | B20080¦Courtroom 302¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main entrance | [5 empty] | 22 | 37 | 483 |  | 2020-09-17 12:00 | 12:00 | 22 | 37 | 483 |  | caution | 2020-09-14 | B12948¦Main entrance¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 303 | [5 empty] | 22 | 45 | 546 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 546 |  |  | 2020-09-14 | B20080¦Courtroom 303¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main Entrance Waiting Area | [5 empty] | 22 | 37 | 445 |  | 2020-09-17 12:00 | 12:00 | 22 | 37 | 445 |  | caution | 2020-09-14 | B12948¦Main Entrance Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Outdoors |  |  | 17 | 63 | 416 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20080¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Court Room 1 Waiting Area | [5 empty] | 21 | 36 | 451 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 451 |  | caution | 2020-09-14 | B12948¦Court Room 1 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 Waiting Area | [5 empty] | 22 | 35 | 425 |  | 2020-09-17 12:00 | 12:00 | 22 | 35 | 425 |  | caution | 2020-09-14 | B12948¦Courtroom 2 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 Waiting Area | [5 empty] | 22 | 35 | 428 |  | 2020-09-17 12:00 | 12:00 | 22 | 35 | 428 |  | caution | 2020-09-14 | B12948¦Courtroom 3 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 Waiting Area | [5 empty] | 22 | 36 | 431 |  | 2020-09-17 12:00 | 12:00 | 22 | 36 | 431 |  | caution | 2020-09-14 | B12948¦Courtroom 5 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 and 6 Waiting Area | [5 empty] | 22 | 35 | 423 |  | 2020-09-17 12:00 | 12:00 | 22 | 35 | 423 |  | caution | 2020-09-14 | B12948¦Courtroom 4 and 6 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Outdoors |  |  | 18 | 47 | 478 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20289¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 21 | 50 | 506 | judge | 2020-09-17 12:00 | 12:00 | 21 | 50 | 506 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 21 | 49 | 503 | public | 2020-09-17 12:00 | 12:00 | 21 | 49 | 503 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 22 | 49 | 505 | judge | 2020-09-17 12:00 | 12:00 | 22 | 49 | 505 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 22 | 48 | 503 | public | 2020-09-17 12:00 | 12:00 | 22 | 48 | 503 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Entry/Waiting | [5 empty] | 23 | 47 | 625 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 625 |  |  | 2020-09-14 | B70510¦Entry/Waiting¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 300 | [5 empty] | 22 | 45 | 519 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 519 |  |  | 2020-09-14 | B20289¦Courtroom 300¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Crown Attorney Office | [5 empty] | 20 | 39 | 452 |  | 2020-09-17 09:00 | 9:00 | 20 | 39 | 452 |  | caution | 2020-09-14 | B20016¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room A | [5 empty] | 23 | 46 | 531 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 531 |  |  | 2020-09-14 | B70510¦Mediation Room A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 301 | [5 empty] | 22 | 45 | 510 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 510 |  |  | 2020-09-14 | B20289¦Courtroom 301¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Legal Aid Ontario | [5 empty] | 21 | 38 | 445 |  | 2020-09-17 09:00 | 9:00 | 21 | 38 | 445 |  | caution | 2020-09-14 | B20016¦Legal Aid Ontario¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 302 | [5 empty] | 23 | 46 | 509 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 509 |  |  | 2020-09-14 | B20289¦Courtroom 302¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Information Desk | [5 empty] | 23 | 47 | 462 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 462 |  |  | 2020-09-14 | B70510¦Information Desk¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel Waiting Area | [5 empty] | 21 | 37 | 448 |  | 2020-09-17 09:00 | 9:00 | 21 | 37 | 448 |  | caution | 2020-09-14 | B20016¦Duty Counsel Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 303 | [5 empty] | 23 | 46 | 501 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 501 |  |  | 2020-09-14 | B20289¦Courtroom 303¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Lunch Room 454 | [5 empty] | 23 | 47 | 455 |  | 2020-09-17 09:00 | 9:00 | 23 | 47 | 455 |  |  | 2020-09-14 | B70510¦Lunch Room 454¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel | [5 empty] | 21 | 40 | 444 |  | 2020-09-17 09:00 | 9:00 | 21 | 40 | 444 |  | caution | 2020-09-14 | B20016¦Duty Counsel¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom A | [5 empty] | 22 | 46 | 529 | in session; measurement taken outside courtroom | 2020-09-17 12:00 | 12:00 | 22 | 46 | 529 |  |  | 2020-09-14 | B20289¦Courtroom A¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lobby Courtroom 1 - 2 | [5 empty] | 22 | 36 | 447 |  | 2020-09-17 09:00 | 9:00 | 22 | 36 | 447 |  | caution | 2020-09-14 | B20016¦Lobby Courtroom 1 - 2¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Copy Room 455 | [5 empty] | 23 | 47 | 450 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 450 |  |  | 2020-09-14 | B70510¦Copy Room 455¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom B | [5 empty] | 22 | 47 | 553 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 553 |  |  | 2020-09-14 | B20289¦Courtroom B¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Main Lobby | [5 empty] | 22 | 37 | 484 |  | 2020-09-17 09:00 | 9:00 | 22 | 37 | 484 |  | caution | 2020-09-14 | B20016¦Main Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room B | [5 empty] | 23 | 48 | 515 |  | 2020-09-17 12:00 | 12:00 | 23 | 48 | 515 |  |  | 2020-09-14 | B70510¦Mediation Room B¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom C (North) | [5 empty] | 22 | 48 | 581 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 581 |  |  | 2020-09-14 | B20289¦Courtroom C (North)¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom D | [5 empty] | 22 | 48 | 565 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 565 |  |  | 2020-09-14 | B20289¦Courtroom D¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lower Hallway | [5 empty] | 22 | 36 | 456 |  | 2020-09-17 09:00 | 9:00 | 22 | 36 | 456 |  | caution | 2020-09-14 | B20016¦Lower Hallway¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 459 | [5 empty] | 23 | 47 | 699 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 699 |  |  | 2020-09-14 | B70510¦Office 459¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom E | [5 empty] | 22 | 47 | 580 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 580 |  |  | 2020-09-14 | B20289¦Courtroom E¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 467 | [5 empty] | 23 | 46 | 512 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 512 |  |  | 2020-09-14 | B70510¦Office 467¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom F | [5 empty] | 22 | 48 | 545 | in session; measurement taken outside courtroom | 2020-09-17 12:00 | 12:00 | 22 | 48 | 545 |  |  | 2020-09-14 | B20289¦Courtroom F¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Outdoors |  |  | 19 | 41 | 384 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B19652¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 469 | [5 empty] | 23 | 47 | 518 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 518 |  |  | 2020-09-14 | B70510¦Office 469¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | OTHER | [5 empty] | 21 | 37 | 444 | Courtroom 1-2-3 | 2020-09-17 09:00 | 9:00 | 21 | 37 | 444 |  | caution | 2020-09-14 | B20016¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Center) | [5 empty] | 22 | 44 | 454 |  | 2020-09-17 12:00 | 12:00 | 22 | 44 | 454 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Center)¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Room 473 (Printer) | [5 empty] | 23 | 47 | 515 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 515 |  |  | 2020-09-14 | B70510¦Room 473 (Printer)¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation | [5 empty] | 21 | 38 | 450 |  | 2020-09-17 09:00 | 9:00 | 21 | 38 | 450 |  | caution | 2020-09-14 | B20016¦Family Mediation¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Judge Dias) | [5 empty] | 22 | 45 | 420 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 420 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Judge Dias)¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hall 475 or 466 | [5 empty] | 23 | 47 | 487 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 487 |  |  | 2020-09-14 | B70510¦Hall 475 or 466¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation Across Stairs | [5 empty] | 19 | 38 | 457 |  | 2020-09-17 09:00 | 9:00 | 19 | 38 | 457 |  | caution | 2020-09-14 | B20016¦Family Mediation Across Stairs¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 1 | [5 empty] | 22 | 47 | 473 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 473 |  |  | 2020-09-14 | B70510¦Hearing Room 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 45 | 433 | Superior judges chamber | 2020-09-17 12:00 | 12:00 | 22 | 45 | 433 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Meeting Rooms 1/2 | [5 empty] | 22 | 48 | 570 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 570 |  |  | 2020-09-14 | B70510¦Vestibule at Meeting Rooms 1/2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 46 | 458 | 3rd floor stair landing | 2020-09-17 12:00 | 12:00 | 22 | 46 | 458 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Hearing Room 1 | [5 empty] | 22 | 48 | 504 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 504 |  |  | 2020-09-14 | B70510¦Vestibule at Hearing Room 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 47 | 438 | 3rd floor Jury room | 2020-09-17 12:00 | 12:00 | 22 | 47 | 438 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Security Check In | [5 empty] | 20 | 56 | 435 |  | 2020-09-17 09:00 | 9:00 | 20 | 56 | 435 |  |  | 2020-09-14 | B92624¦Security Check In¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 2 | [5 empty] | 22 | 48 | 520 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 520 |  |  | 2020-09-14 | B70510¦Hearing Room 2¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Main Lobby | [5 empty] | 19 | 59 | 476 |  | 2020-09-17 09:00 | 9:00 | 19 | 59 | 476 |  |  | 2020-09-14 | B19523¦Main Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 47 | 525 | Justice McDonald chamber | 2020-09-17 12:00 | 12:00 | 22 | 47 | 525 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701A | [5 empty] | 21 | 54 | 439 | West | 2020-09-17 09:00 | 9:00 | 21 | 54 | 439 |  |  | 2020-09-14 | B92624¦Room 701A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Outdoors |  |  | 13 | 63 | 429 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B90838¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 439 | [5 empty] | 23 | 48 | 545 |  | 2020-09-17 12:00 | 12:00 | 23 | 48 | 545 |  |  | 2020-09-14 | B70510¦Office 439¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Holding Cell | [5 empty] | 20 | 56 | 456 |  | 2020-09-17 09:00 | 9:00 | 20 | 56 | 456 |  |  | 2020-09-14 | B19523¦Holding Cell¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Courtroom 101 Courtroom 102 | [5 empty] | 21 | 43 | 437 |  | 2020-09-17 12:00 | 12:00 | 21 | 43 | 437 |  |  | 2020-09-14 | B90838¦Courtroom 101 Courtroom 102¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701A | [5 empty] | 21 | 54 | 432 | East | 2020-09-17 09:00 | 9:00 | 21 | 54 | 432 |  |  | 2020-09-14 | B92624¦Room 701A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 46 | 520 | Justice McDonald secretary | 2020-09-17 12:00 | 12:00 | 22 | 46 | 520 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | First Aid Desk | [5 empty] | 22 | 48 | 558 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 558 |  |  | 2020-09-14 | B70510¦First Aid Desk¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701A | [5 empty] | 21 | 54 | 436 | North | 2020-09-17 09:00 | 9:00 | 21 | 54 | 436 |  |  | 2020-09-14 | B92624¦Room 701A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 436 | [5 empty] | 23 | 47 | 581 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 581 |  |  | 2020-09-14 | B70510¦Office 436¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 46 | 521 | SCJTC office | 2020-09-17 12:00 | 12:00 | 21 | 46 | 521 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway | [5 empty] | 20 | 53 | 426 | by Room 701A | 2020-09-17 09:00 | 9:00 | 20 | 53 | 426 |  |  | 2020-09-14 | B92624¦Hallway¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 432 | [5 empty] | 23 | 47 | 575 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 575 |  |  | 2020-09-14 | B70510¦Office 432¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 46 | 517 | Visiting justice chamber | 2020-09-17 12:00 | 12:00 | 21 | 46 | 517 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 1 | [5 empty] | 21 | 52 | 454 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 454 |  |  | 2020-09-14 | B19523¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 20 | 55 | 442 | East | 2020-09-17 09:00 | 9:00 | 20 | 55 | 442 |  |  | 2020-09-14 | B92624¦Room 718A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 429 | [5 empty] | 23 | 46 | 780 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 780 |  |  | 2020-09-14 | B70510¦Office 429¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Court Services | [5 empty] | 21 | 51 | 458 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 458 |  |  | 2020-09-14 | B19523¦Court Services¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Center) | [5 empty] | 21 | 46 | 521 |  | 2020-09-17 12:00 | 12:00 | 21 | 46 | 521 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Center)¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 20 | 55 | 428 | West | 2020-09-17 09:00 | 9:00 | 20 | 55 | 428 |  |  | 2020-09-14 | B92624¦Room 718A¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | JP Office | [5 empty] | 21 | 51 | 454 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 454 |  |  | 2020-09-14 | B19523¦JP Office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Judge Dias) | [5 empty] | 21 | 46 | 508 |  | 2020-09-17 12:00 | 12:00 | 21 | 46 | 508 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Judge Dias)¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | OPP Office | [5 empty] | 21 | 52 | 458 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 458 |  |  | 2020-09-14 | B19523¦OPP Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718B | [5 empty] | 20 | 54 | 426 |  | 2020-09-17 09:00 | 9:00 | 20 | 54 | 426 |  |  | 2020-09-14 | B92624¦Room 718B¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Crown Attorney Office | [5 empty] | 21 | 50 | 462 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 462 |  |  | 2020-09-14 | B19523¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 Waiting Area | [5 empty] | 21 | 47 | 534 |  | 2020-09-17 12:00 | 12:00 | 21 | 47 | 534 |  |  | 2020-09-14 | B19652¦Courtroom 2 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 50 | 470 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 470 |  |  | 2020-09-14 | B19523¦VWAP Office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 427 | [5 empty] | 23 | 46 | 545 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 545 |  |  | 2020-09-14 | B70510¦Office 427¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716A | [5 empty] | 19 | 55 | 471 |  | 2020-09-17 09:00 | 9:00 | 19 | 55 | 471 |  |  | 2020-09-14 | B92624¦Room 716A¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 48 | 476 |  | 2020-09-17 09:00 | 9:00 | 22 | 48 | 476 |  |  | 2020-09-14 | B19523¦VWAP Office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mail Room | [5 empty] | 23 | 46 | 490 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 490 |  |  | 2020-09-14 | B70510¦Mail Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Center) | [5 empty] | 22 | 46 | 484 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 484 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Center)¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717A | [5 empty] | 19 | 56 | 494 |  | 2020-09-17 09:00 | 9:00 | 19 | 56 | 494 |  |  | 2020-09-14 | B92624¦Room 717A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 420 | [5 empty] | 23 | 46 | 531 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 531 |  |  | 2020-09-14 | B70510¦Office 420¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Judge Dias) | [5 empty] | 22 | 44 | 478 |  | 2020-09-17 12:00 | 12:00 | 22 | 44 | 478 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Judge Dias)¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 5 | [5 empty] | 21 | 48 | 461 |  | 2020-09-17 09:00 | 9:00 | 21 | 48 | 461 |  |  | 2020-09-14 | B19523¦Courtroom 5¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716B | [5 empty] | 19 | 55 | 465 |  | 2020-09-17 09:00 | 9:00 | 19 | 55 | 465 |  |  | 2020-09-14 | B92624¦Room 716B¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 418 | [5 empty] | 23 | 46 | 620 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 620 |  |  | 2020-09-14 | B70510¦Office 418¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Remote Testimony Room | [5 empty] | 21 | 49 | 456 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 456 |  |  | 2020-09-14 | B19523¦Remote Testimony Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717B | [5 empty] | 19 | 55 | 491 |  | 2020-09-17 09:00 | 9:00 | 19 | 55 | 491 |  |  | 2020-09-14 | B92624¦Room 717B¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 47 | 566 | Justice peace chamber | 2020-09-17 12:00 | 12:00 | 23 | 47 | 566 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Conference Room 2 | [5 empty] | 21 | 49 | 466 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 466 |  |  | 2020-09-14 | B19523¦Conference Room 2¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | File Room | [5 empty] | 23 | 47 | 509 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 509 |  |  | 2020-09-14 | B70510¦File Room¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714A | [5 empty] | 19 | 55 | 475 |  | 2020-09-17 09:00 | 9:00 | 19 | 55 | 475 |  |  | 2020-09-14 | B92624¦Room 714A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 47 | 534 | Council chamber dias | 2020-09-17 12:00 | 12:00 | 22 | 47 | 534 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Health Room | [5 empty] | 22 | 47 | 494 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 494 |  |  | 2020-09-14 | B70510¦Health Room¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715A | [5 empty] | 19 | 55 | 459 |  | 2020-09-17 09:00 | 9:00 | 19 | 55 | 459 |  |  | 2020-09-14 | B92624¦Room 715A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 47 | 561 | Council chamber center | 2020-09-17 12:00 | 12:00 | 22 | 47 | 561 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715B | [5 empty] | 19 | 45 | 467 |  | 2020-09-17 09:00 | 9:00 | 19 | 45 | 467 |  |  | 2020-09-14 | B92624¦Room 715B¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 | [5 empty] | 22 | 47 | 504 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 504 |  |  | 2020-09-14 | B70510¦Hearing Room 3¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 | [5 empty] | 21 | 49 | 463 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 463 |  |  | 2020-09-14 | B19523¦Courtroom 3¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 2nd Floor Lunchroom | [5 empty] | 22 | 46 | 498 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 498 |  |  | 2020-09-14 | B19652¦2nd Floor Lunchroom¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 Waiting Area | [5 empty] | 21 | 49 | 466 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 466 |  |  | 2020-09-14 | B19523¦Courtroom 3 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714B | [5 empty] | 19 | 56 | 483 |  | 2020-09-17 09:00 | 9:00 | 19 | 56 | 483 |  |  | 2020-09-14 | B92624¦Room 714B¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 Waiting Area | [5 empty] | 22 | 48 | 555 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 555 |  |  | 2020-09-14 | B70510¦Hearing Room 3 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 45 | 489 | 2nd floor stair landing | 2020-09-17 12:00 | 12:00 | 22 | 45 | 489 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 21 | 50 | 472 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 472 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713A | [5 empty] | 19 | 56 | 473 |  | 2020-09-17 09:00 | 9:00 | 19 | 56 | 473 |  |  | 2020-09-14 | B92624¦Room 713A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Elevator Lobby | [5 empty] | 22 | 51 | 451 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 451 |  |  | 2020-09-14 | B70510¦Elevator Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Main entrance | [5 empty] | 20 | 54 | 541 |  | 2020-09-17 12:00 | 12:00 | 20 | 54 | 541 |  |  | 2020-09-14 | B20979¦Main entrance¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713B | [5 empty] | 19 | 55 | 481 |  | 2020-09-17 09:00 | 9:00 | 19 | 55 | 481 |  |  | 2020-09-14 | B92624¦Room 713B¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd fl lobby | [5 empty] | 21 | 35 | 648 |  | 2020-09-17 12:00 | 12:00 | 21 | 35 | 648 |  | caution | 2020-09-14 | B20226¦2nd fl lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 45 | 470 | Court service kitchenette | 2020-09-17 12:00 | 12:00 | 22 | 45 | 470 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801A | [5 empty] | 20 | 57 | 431 |  | 2020-09-17 09:00 | 9:00 | 20 | 57 | 431 |  |  | 2020-09-14 | B92624¦Room 801A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Outdoors |  |  | 18 | 56 | 462 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70510¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 46 | 695 | Court service north | 2020-09-17 12:00 | 12:00 | 23 | 46 | 695 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801B | [5 empty] | 20 | 57 | 422 |  | 2020-09-17 09:00 | 9:00 | 20 | 57 | 422 |  |  | 2020-09-14 | B92624¦Room 801B¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 21 | 52 | 578 | east | 2020-09-17 12:00 | 12:00 | 21 | 52 | 578 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 47 | 685 | Court service south | 2020-09-17 12:00 | 12:00 | 23 | 47 | 685 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 2 | [5 empty] | 20 | 35 | 646 |  | 2020-09-17 12:00 | 12:00 | 20 | 35 | 646 |  | caution | 2020-09-14 | B20226¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 21 | 50 | 477 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 477 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 22 | 50 | 534 | west | 2020-09-17 12:00 | 12:00 | 22 | 50 | 534 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway | [5 empty] | 20 | 55 | 423 | by Room 801A | 2020-09-17 09:00 | 9:00 | 20 | 55 | 423 |  |  | 2020-09-14 | B92624¦Hallway¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 48 | 710 | Court service entrance vestibule | 2020-09-17 12:00 | 12:00 | 23 | 48 | 710 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 21 | 49 | 578 | south | 2020-09-17 12:00 | 12:00 | 21 | 49 | 578 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 51 | 505 |  | 2020-09-17 09:00 | 9:00 | 20 | 51 | 505 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Outdoors |  |  | 19 | 56 | 413 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B92624¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 44 | 570 | 1st floor stair landing | 2020-09-17 12:00 | 12:00 | 23 | 44 | 570 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 2 | [5 empty] | 21 | 50 | 456 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 456 |  |  | 2020-09-14 | B19523¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 21 | 48 | 569 | north | 2020-09-17 12:00 | 12:00 | 21 | 48 | 569 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Escalator, 800 | [5 empty] | 20 | 53 | 436 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 436 |  |  | 2020-09-14 | B92624¦Hallway by Escalator, 800¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 1 | [5 empty] | 21 | 36 | 708 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 708 |  | caution | 2020-09-14 | B20226¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 21 | 52 | 783 | south | 2020-09-17 12:00 | 12:00 | 21 | 52 | 783 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Escalator, 700 | [5 empty] | 20 | 52 | 437 |  | 2020-09-17 09:00 | 9:00 | 20 | 52 | 437 |  |  | 2020-09-14 | B92624¦Hallway by Escalator, 700¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 100 Courtroom 102 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203 | [5 empty] | 21 | 46 | 466 |  | 2020-09-17 12:00 | 12:00 | 21 | 46 | 466 |  |  | 2020-09-14 | B20616¦Courtroom 100 Courtroom 102 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Lounge | [5 empty] | 20 | 54 | 417 |  | 2020-09-17 09:00 | 9:00 | 20 | 54 | 417 |  |  | 2020-09-14 | B92624¦Lounge¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 307 | [5 empty] | 21 | 52 | 783 | south | 2020-09-17 12:00 | 12:00 | 21 | 52 | 783 |  |  | 2020-09-14 | B20979¦Courtroom 307¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Halway by Room 718A | [5 empty] | 19 | 53 | 429 |  | 2020-09-17 09:00 | 9:00 | 19 | 53 | 429 |  |  | 2020-09-14 | B92624¦Halway by Room 718A¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | courtroom 307 | [5 empty] | 22 | 51 | 813 | north | 2020-09-17 12:00 | 12:00 | 22 | 51 | 813 |  |  | 2020-09-14 | B20979¦courtroom 307¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 101 Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 401 Courtroom 402 Courtroom 403 | [5 empty] | 22 | 46 | 466 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 466 |  |  | 2020-09-14 | B20616¦Courtroom 101 Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 401 Courtroom 402 Courtroom 403¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Security Check In | [5 empty] | 21 | 49 | 464 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 464 |  |  | 2020-09-14 | B92624¦Security Check In¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 22 | 34 | 768 |  | 2020-09-17 12:00 | 12:00 | 22 | 34 | 768 |  | low | 2020-09-14 | B20226¦2nd Floor Holding Cell¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | hallway by courtroom 307 | [5 empty] | 22 | 46 | 560 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 560 |  |  | 2020-09-14 | B20979¦hallway by courtroom 307¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 20 | 52 | 428 | West | 2020-09-17 12:00 | 12:00 | 20 | 52 | 428 |  |  | 2020-09-14 | B92624¦Room 701¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 106 Courtroom 205 | [5 empty] | 20 | 50 | 465 |  | 2020-09-17 12:00 | 12:00 | 20 | 50 | 465 |  |  | 2020-09-14 | B20616¦Courtroom 106 Courtroom 205¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 22 | 49 | 762 | east | 2020-09-17 12:00 | 12:00 | 22 | 49 | 762 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 20 | 53 | 444 | East | 2020-09-17 12:00 | 12:00 | 20 | 53 | 444 |  |  | 2020-09-14 | B92624¦Room 701¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 22 | 50 | 789 | west | 2020-09-17 12:00 | 12:00 | 22 | 50 | 789 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 20 | 53 | 448 | North | 2020-09-17 12:00 | 12:00 | 20 | 53 | 448 |  |  | 2020-09-14 | B92624¦Room 701¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 47 | 428 | south | 2020-09-17 12:00 | 12:00 | 22 | 47 | 428 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 701 | [5 empty] | 19 | 52 | 436 |  | 2020-09-17 12:00 | 12:00 | 19 | 52 | 436 |  |  | 2020-09-14 | B92624¦Hallway by Room 701¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 204 Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 404 Courtroom 405 | [5 empty] | 21 | 50 | 465 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 465 |  |  | 2020-09-14 | B20616¦Courtroom 204 Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 404 Courtroom 405¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 46 | 428 | north | 2020-09-17 12:00 | 12:00 | 22 | 46 | 428 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Police Court Bureau | [5 empty] | 21 | 50 | 482 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 482 |  |  | 2020-09-14 | B19523¦Police Court Bureau¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 20 | 54 | 435 | East | 2020-09-17 12:00 | 12:00 | 20 | 54 | 435 |  |  | 2020-09-14 | B92624¦Room 718A¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 Waiting Area | [5 empty] | 21 | 50 | 507 |  | 2020-09-17 09:00 | 9:00 | 21 | 50 | 507 |  |  | 2020-09-14 | B19523¦Courtroom 4 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | hallway by courtroom 302 | [5 empty] | 22 | 45 | 518 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 518 |  |  | 2020-09-14 | B20979¦hallway by courtroom 302¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 20 | 54 | 444 | West | 2020-09-17 12:00 | 12:00 | 20 | 54 | 444 |  |  | 2020-09-14 | B92624¦Room 718A¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 | [5 empty] | 21 | 49 | 460 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 460 |  |  | 2020-09-14 | B19523¦Courtroom 4¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 304 Courtroom 305 | [5 empty] | 21 | 46 | 569 |  | 2020-09-17 12:00 | 12:00 | 21 | 46 | 569 |  |  | 2020-09-14 | B20616¦Courtroom 304 Courtroom 305¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Basement cells - hallway | [5 empty] | 22 | 46 | 430 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 430 |  |  | 2020-09-14 | B20979¦Basement cells - hallway¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718B | [5 empty] | 20 | 54 | 439 |  | 2020-09-17 12:00 | 12:00 | 20 | 54 | 439 |  |  | 2020-09-14 | B92624¦Room 718B¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 3 | [5 empty] | 22 | 31 | 633 |  | 2020-09-17 12:00 | 12:00 | 22 | 31 | 633 |  | low | 2020-09-14 | B20226¦Courtroom 3¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 50 | 492 |  | 2020-09-17 09:00 | 9:00 | 20 | 50 | 492 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 718A | [5 empty] | 20 | 51 | 444 |  | 2020-09-17 12:00 | 12:00 | 20 | 51 | 444 |  |  | 2020-09-14 | B92624¦Hallway by Room 718A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | police office | [5 empty] | 23 | 47 | 582 |  | 2020-09-17 12:00 | 12:00 | 23 | 47 | 582 |  |  | 2020-09-14 | B20979¦police office¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 52 | 477 |  | 2020-09-17 09:00 | 9:00 | 19 | 52 | 477 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717A | [5 empty] | 19 | 55 | 461 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 461 |  |  | 2020-09-14 | B92624¦Room 717A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | outside | [5 empty] | 19 | 53 | 403 |  | 2020-09-17 12:00 | 12:00 | 19 | 53 | 403 |  |  | 2020-09-14 | B20979¦outside¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716A | [5 empty] | 19 | 55 | 469 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 469 |  |  | 2020-09-14 | B92624¦Room 716A¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 53 | 485 |  | 2020-09-17 09:00 | 9:00 | 19 | 53 | 485 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Main entrance | [5 empty] | 20 | 55 | 482 |  | 2020-09-17 12:00 | 12:00 | 20 | 55 | 482 |  |  | 2020-09-14 | B90636¦Main entrance¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Jury Room | [5 empty] | 20 | 53 | 457 |  | 2020-09-17 09:00 | 9:00 | 20 | 53 | 457 |  |  | 2020-09-14 | B19523¦Jury Room¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717B | [5 empty] | 19 | 55 | 494 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 494 |  |  | 2020-09-14 | B92624¦Room 717B¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 20 | 53 | 454 | north | 2020-09-17 12:00 | 12:00 | 20 | 53 | 454 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Ontario Court | [5 empty] | 20 | 51 | 454 |  | 2020-09-17 09:00 | 9:00 | 20 | 51 | 454 |  |  | 2020-09-14 | B19523¦Ontario Court¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 107 | [5 empty] | 21 | 49 | 435 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 435 |  |  | 2020-09-14 | B20616¦Courtroom 107¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 21 | 52 | 452 | south | 2020-09-17 12:00 | 12:00 | 21 | 52 | 452 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717B | [5 empty] | 19 | 55 | 475 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 475 |  |  | 2020-09-14 | B92624¦Room 717B¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Outdoors |  |  | 14 | 23 | 404 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20226¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Judicial Library | [5 empty] | 21 | 49 | 460 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 460 |  |  | 2020-09-14 | B19523¦Judicial Library¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 108 | [5 empty] | 20 | 49 | 435 |  | 2020-09-17 12:00 | 12:00 | 20 | 49 | 435 |  |  | 2020-09-14 | B20616¦Courtroom 108¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714A | [5 empty] | 20 | 56 | 578 |  | 2020-09-17 12:00 | 12:00 | 20 | 56 | 578 |  |  | 2020-09-14 | B92624¦Room 714A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 21 | 49 | 531 | vestibule, lobby | 2020-09-17 12:00 | 12:00 | 21 | 49 | 531 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 315 | [5 empty] | 21 | 49 | 452 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 452 |  |  | 2020-09-14 | B19523¦Office Room 315¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715A | [5 empty] | 19 | 55 | 451 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 451 |  |  | 2020-09-14 | B92624¦Room 715A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 2 | [5 empty] | 21 | 53 | 550 |  | 2020-09-17 12:00 | 12:00 | 21 | 53 | 550 |  |  | 2020-09-14 | B11586¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 316 | [5 empty] | 21 | 49 | 453 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 453 |  |  | 2020-09-14 | B19523¦Office Room 316¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 21 | 49 | 546 | main room entrance | 2020-09-17 12:00 | 12:00 | 21 | 49 | 546 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715B | [5 empty] | 19 | 55 | 485 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 485 |  |  | 2020-09-14 | B92624¦Room 715B¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 317 | [5 empty] | 21 | 48 | 451 |  | 2020-09-17 09:00 | 9:00 | 21 | 48 | 451 |  |  | 2020-09-14 | B19523¦Office Room 317¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 21 | 49 | 547 | Crown attorney beaton’s office | 2020-09-17 12:00 | 12:00 | 21 | 49 | 547 |  |  | 2020-09-14 | B11586¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | hallway by courtroom 203 | [5 empty] | 21 | 50 | 483 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 483 |  |  | 2020-09-14 | B90636¦hallway by courtroom 203¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Superior Court | [5 empty] | 22 | 46 | 512 |  | 2020-09-17 09:00 | 9:00 | 22 | 46 | 512 |  |  | 2020-09-14 | B19523¦Superior Court¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714B | [5 empty] | 20 | 56 | 585 |  | 2020-09-17 12:00 | 12:00 | 20 | 56 | 585 |  |  | 2020-09-14 | B92624¦Room 714B¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 313 | [5 empty] | 22 | 45 | 465 |  | 2020-09-17 09:00 | 9:00 | 22 | 45 | 465 |  |  | 2020-09-14 | B19523¦Office Room 313¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 2nd fl lobby | [5 empty] | 22 | 49 | 455 |  | 2020-09-17 12:00 | 12:00 | 22 | 49 | 455 |  |  | 2020-09-14 | B90636¦2nd fl lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713A | [5 empty] | 19 | 55 | 479 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 479 |  |  | 2020-09-14 | B92624¦Room 713A¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 312 | [5 empty] | 22 | 46 | 466 |  | 2020-09-17 09:00 | 9:00 | 22 | 46 | 466 |  |  | 2020-09-14 | B19523¦Office Room 312¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 3rd Floor Elevator Lobby | [5 empty] | 21 | 49 | 447 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 447 |  |  | 2020-09-14 | B90636¦3rd Floor Elevator Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 310 | [5 empty] | 22 | 46 | 518 |  | 2020-09-17 09:00 | 9:00 | 22 | 46 | 518 |  |  | 2020-09-14 | B19523¦Office Room 310¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713B | [5 empty] | 19 | 55 | 492 |  | 2020-09-17 12:00 | 12:00 | 19 | 55 | 492 |  |  | 2020-09-14 | B92624¦Room 713B¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Law Association | [5 empty] | 21 | 46 | 454 |  | 2020-09-17 09:00 | 9:00 | 21 | 46 | 454 |  |  | 2020-09-14 | B19523¦Law Association¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 21 | 50 | 470 | west | 2020-09-17 12:00 | 12:00 | 21 | 50 | 470 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Escalator, 700 | [5 empty] | 19 | 54 | 444 |  | 2020-09-17 12:00 | 12:00 | 19 | 54 | 444 |  |  | 2020-09-14 | B92624¦Hallway by Escalator, 700¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 21 | 47 | 517 | Crown attorney henault’s office | 2020-09-17 12:00 | 12:00 | 21 | 47 | 517 |  |  | 2020-09-14 | B11586¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 22 | 50 | 476 | east | 2020-09-17 12:00 | 12:00 | 22 | 50 | 476 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801A | [5 empty] | 20 | 55 | 447 |  | 2020-09-17 12:00 | 12:00 | 20 | 55 | 447 |  |  | 2020-09-14 | B92624¦Room 801A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown attorney admin area | [5 empty] | 22 | 47 | 542 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 542 |  |  | 2020-09-14 | B11586¦Crown attorney admin area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801B | [5 empty] | 20 | 54 | 434 |  | 2020-09-17 12:00 | 12:00 | 20 | 54 | 434 |  |  | 2020-09-14 | B92624¦Room 801B¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 4th floor waiting area | [5 empty] | 21 | 50 | 446 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 446 |  |  | 2020-09-14 | B90636¦4th floor waiting area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-1 | [5 empty] | 20.4 | 52.8 | 718 |  | 2020-09-17 12:00 | 12:00 | 20.4 | 52.8 | 718 |  |  | 2020-09-14 | B10644¦Courtroom 2-1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Outdoors |  |  | 12 | 27 | 400 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70050¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 801 | [5 empty] | 20 | 53 | 427 |  | 2020-09-17 12:00 | 12:00 | 20 | 53 | 427 |  |  | 2020-09-14 | B92624¦Hallway by Room 801¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | courtroom 211 | [5 empty] | 21 | 50 | 421 | north | 2020-09-17 12:00 | 12:00 | 21 | 50 | 421 |  |  | 2020-09-14 | B90636¦courtroom 211¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Lounge | [5 empty] | 20 | 52 | 427 |  | 2020-09-17 12:00 | 12:00 | 20 | 52 | 427 |  |  | 2020-09-14 | B92624¦Lounge¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 - waiting area | [5 empty] | 21 | 38 | 527 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 527 |  | caution | 2020-09-14 | B11586¦Courtroom 1 - waiting area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 101 | [5 empty] | 20 | 54 | 474 |  | 2020-09-17 12:00 | 12:00 | 20 | 54 | 474 |  |  | 2020-09-14 | B25671¦Courtroom 101¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | courtroom 211 | [5 empty] | 21 | 50 | 420 | south | 2020-09-17 12:00 | 12:00 | 21 | 50 | 420 |  |  | 2020-09-14 | B90636¦courtroom 211¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 201 | [5 empty] | 20 | 55 | 768 |  | 2020-09-17 12:00 | 12:00 | 20 | 55 | 768 |  |  | 2020-09-14 | B25671¦Courtroom 201¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 | [5 empty] | 22 | 38 | 455 |  | 2020-09-17 12:00 | 12:00 | 22 | 38 | 455 |  | caution | 2020-09-14 | B11586¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 301 | [5 empty] | 20 | 53 | 552 |  | 2020-09-17 12:00 | 12:00 | 20 | 53 | 552 |  |  | 2020-09-14 | B25671¦Courtroom 301¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | hallway by courtroom 211 | [5 empty] | 21 | 48 | 430 |  | 2020-09-17 12:00 | 12:00 | 21 | 48 | 430 |  |  | 2020-09-14 | B90636¦hallway by courtroom 211¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | 2nd Floor Holding Cell | [5 empty] | 22 | 39 | 492 |  | 2020-09-17 12:00 | 12:00 | 22 | 39 | 492 |  | caution | 2020-09-14 | B11586¦2nd Floor Holding Cell¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-2 | [5 empty] | 19.8 | 58.5 | 567 |  | 2020-09-17 12:00 | 12:00 | 19.8 | 58.5 | 567 |  |  | 2020-09-14 | B10644¦Courtroom 2-2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Outdoors |  |  | 18 | 68 | 431 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B92624¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | outside | [5 empty] | 19 | 53 | 403 |  | 2020-09-17 12:00 | 12:00 | 19 | 53 | 403 |  |  | 2020-09-14 | B90636¦outside¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Judge office | [5 empty] | 22 | 39 | 530 |  | 2020-09-17 12:00 | 12:00 | 22 | 39 | 530 |  | caution | 2020-09-14 | B11586¦Judge office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-3 | [5 empty] | 20.5 | 62.1 | 516 |  | 2020-09-17 12:00 | 12:00 | 20.5 | 62.1 | 516 |  | caution | 2020-09-14 | B10644¦Courtroom 2-3¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Main Lobby | [5 empty] | 21 | 43 | 506 |  | 2020-09-17 12:00 | 12:00 | 21 | 43 | 506 |  |  | 2020-09-14 | B70050¦Main Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | court admin office | [5 empty] | 20 | 57 | 720 |  | 2020-09-17 12:00 | 12:00 | 20 | 57 | 720 |  |  | 2020-09-14 | B11586¦court admin office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-4 | [5 empty] | 22.4 | 45.9 | 551 |  | 2020-09-17 12:00 | 12:00 | 22.4 | 45.9 | 551 |  |  | 2020-09-14 | B10644¦Courtroom 2-4¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Main Lobby | [5 empty] | 20 | 42 | 523 |  | 2020-09-17 12:00 | 12:00 | 20 | 42 | 523 |  |  | 2020-09-14 | B11586¦Main Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 1 | [5 empty] | 21 | 43 | 503 |  | 2020-09-17 12:00 | 12:00 | 21 | 43 | 503 |  |  | 2020-09-14 | B70050¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-6 | [5 empty] | 23.4 | 54.1 | 455 |  | 2020-09-17 12:00 | 12:00 | 23.4 | 54.1 | 455 |  |  | 2020-09-14 | B10644¦Courtroom 2-6¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Outdoors |  |  | 19 | 64 | 368 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B11586¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-5 | [5 empty] | 20.8 | 55.6 | 421 |  | 2020-09-17 12:00 | 12:00 | 20.8 | 55.6 | 421 |  |  | 2020-09-14 | B10644¦Courtroom 2-5¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office North | [5 empty] | 25 | 29 | 585 |  | 2020-09-17 12:00 | 12:00 | 25 | 29 | 585 |  | low | 2020-09-14 | B14895¦Administration Office North¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 20 | 44 | 476 |  | 2020-09-17 12:00 | 12:00 | 20 | 44 | 476 |  |  | 2020-09-14 | B70050¦2nd Floor Holding Cell¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-8 | [5 empty] | 20.8 | 52.8 | 671 |  | 2020-09-17 12:00 | 12:00 | 20.8 | 52.8 | 671 |  |  | 2020-09-14 | B10644¦Courtroom 2-8¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office South | [5 empty] | 24 | 25 | 523 |  | 2020-09-17 12:00 | 12:00 | 24 | 25 | 523 |  | low | 2020-09-14 | B14895¦Administration Office South¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 3-2 | [5 empty] | 22.3 | 57.5 | 460 |  | 2020-09-17 12:00 | 12:00 | 22.3 | 57.5 | 460 |  |  | 2020-09-14 | B10644¦Courtroom 3-2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Yannick Bedard Office - 2nd Floor | [5 empty] | 21 | 45 | 601 |  | 2020-09-17 12:00 | 12:00 | 21 | 45 | 601 |  |  | 2020-09-14 | B70050¦Yannick Bedard Office - 2nd Floor¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-1 | [5 empty] | 22.7 | 58 | 505 |  | 2020-09-17 12:00 | 12:00 | 22.7 | 58 | 505 |  |  | 2020-09-14 | B10644¦Courtroom 4-1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 2 | [5 empty] | 21 | 45 | 570 |  | 2020-09-17 12:00 | 12:00 | 21 | 45 | 570 |  |  | 2020-09-14 | B70050¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main entrance | [5 empty] | 25 | 25 | 582 |  | 2020-09-17 12:00 | 12:00 | 25 | 25 | 582 |  | low | 2020-09-14 | B14895¦Main entrance¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-2 | [5 empty] | 21.3 | 56 | 443 |  | 2020-09-17 12:00 | 12:00 | 21.3 | 56 | 443 |  |  | 2020-09-14 | B10644¦Courtroom 4-2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main Floor Waiting Area | [5 empty] | 25 | 26 | 561 |  | 2020-09-17 12:00 | 12:00 | 25 | 26 | 561 |  | low | 2020-09-14 | B14895¦Main Floor Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd fl lobby | [5 empty] | 20 | 43 | 481 |  | 2020-09-17 12:00 | 12:00 | 20 | 43 | 481 |  |  | 2020-09-14 | B70050¦2nd fl lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom A | [5 empty] | 23 | 26 | 527 |  | 2020-09-17 12:00 | 12:00 | 23 | 26 | 527 |  | low | 2020-09-14 | B14895¦Courtroom A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom B | [5 empty] | 24 | 26 | 609 |  | 2020-09-17 12:00 | 12:00 | 24 | 26 | 609 |  | low | 2020-09-14 | B14895¦Courtroom B¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-3 | [5 empty] | 23.2 | 55.5 | 405 |  | 2020-09-17 12:00 | 12:00 | 23.2 | 55.5 | 405 |  |  | 2020-09-14 | B10644¦Courtroom 4-3¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-4 | [5 empty] | 22.3 | 57.8 | 542 |  | 2020-09-17 12:00 | 12:00 | 22.3 | 57.8 | 542 |  |  | 2020-09-14 | B10644¦Courtroom 4-4¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | 2nd Floor Waiting Area | [5 empty] | 24 | 27 | 553 |  | 2020-09-17 12:00 | 12:00 | 24 | 27 | 553 |  | low | 2020-09-14 | B14895¦2nd Floor Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-6 | [5 empty] | 22.7 | 57.9 | 436 |  | 2020-09-17 12:00 | 12:00 | 22.7 | 57.9 | 436 |  |  | 2020-09-14 | B10644¦Courtroom 4-6¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Crown Attorney Office | [5 empty] | 24 | 33 | 495 |  | 2020-09-17 12:00 | 12:00 | 24 | 33 | 495 |  | low | 2020-09-14 | B14895¦Crown Attorney Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Waiting Area | [5 empty] | 24 | 25 | 473 |  | 2020-09-17 12:00 | 12:00 | 24 | 25 | 473 |  | low | 2020-09-14 | B14895¦Basement Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-7 | [5 empty] | 22.8 | 60.4 | 446 |  | 2020-09-17 12:00 | 12:00 | 22.8 | 60.4 | 446 |  | caution | 2020-09-14 | B10644¦Courtroom 4-7¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Boardroom | [5 empty] | 25 | 32 | 442 |  | 2020-09-17 12:00 | 12:00 | 25 | 32 | 442 |  | low | 2020-09-14 | B14895¦Basement Boardroom¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-8 | [5 empty] | 23.2 | 54.1 | 416 |  | 2020-09-17 12:00 | 12:00 | 23.2 | 54.1 | 416 |  |  | 2020-09-14 | B10644¦Courtroom 4-8¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Male Holding Cell | [5 empty] | 24 | 29 | 503 |  | 2020-09-17 12:00 | 12:00 | 24 | 29 | 503 |  | low | 2020-09-14 | B14895¦Male Holding Cell¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Female Holding Cell | [5 empty] | 24 | 25 | 603 |  | 2020-09-17 12:00 | 12:00 | 24 | 25 | 603 |  | low | 2020-09-14 | B14895¦Female Holding Cell¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22.9 | 54.6 | 520 |  | 2020-09-17 12:00 | 12:00 | 22.9 | 54.6 | 520 |  |  | 2020-09-14 | B10644¦Courtroom 5-1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Outdoors |  |  | 16 | 18 | 395 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B14895¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-1 | [5 empty] | 19.9 | 52.6 | 448 |  | 2020-09-17 12:00 | 12:00 | 19.9 | 52.6 | 448 |  |  | 2020-09-14 | B10644¦Courtroom 6-1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 1 | [5 empty] | 22 | 40 | 461 |  | 2020-09-17 12:00 | 12:00 | 22 | 40 | 461 |  | caution | 2020-09-14 | B25602¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 2 | [5 empty] | 22 | 37 | 470 |  | 2020-09-17 12:00 | 12:00 | 22 | 37 | 470 |  | caution | 2020-09-14 | B25602¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 3 | [5 empty] | 22 | 35 | 496 |  | 2020-09-17 12:00 | 12:00 | 22 | 35 | 496 |  | caution | 2020-09-14 | B25602¦Courtroom 3¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 4 | [5 empty] | 23 | 37 | 453 |  | 2020-09-17 12:00 | 12:00 | 23 | 37 | 453 |  | caution | 2020-09-14 | B25602¦Courtroom 4¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 101 | [5 empty] | 21 | 52 | 529 |  | 2020-09-17 15:00 | 15:00 | 21 | 52 | 529 |  |  | 2020-09-14 | B19512¦Courtroom 101¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-1, 16th Floor OTHER | [5 empty] | 22 | 46 | 733 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 733 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-1, 16th Floor OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 200 | [5 empty] | 22.2 | 48 | 552 |  | 2020-09-17 15:00 | 15:00 | 22.2 | 48 | 552 |  |  | 2020-09-14 | B19512¦Courtroom 200¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 5 | [5 empty] | 35 | 35 | 417 |  | 2020-09-17 12:00 | 12:00 | 35 | 35 | 417 | high | caution | 2020-09-14 | B25602¦Courtroom 5¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 201 | [5 empty] | 23 | 48 | 552 |  | 2020-09-17 15:00 | 15:00 | 23 | 48 | 552 |  |  | 2020-09-14 | B19512¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 6 | [5 empty] | 23 | 38 | 490 |  | 2020-09-17 12:00 | 12:00 | 23 | 38 | 490 |  | caution | 2020-09-14 | B25602¦Courtroom 6¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 201 | [5 empty] | 23 | 48 | 552 |  | 2020-09-17 15:00 | 15:00 | 23 | 48 | 552 |  |  | 2020-09-14 | B19512¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Outdoors |  |  | 6 | 54 | 536 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10000¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Outdoors |  |  | 10 | 44 | 498 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10000¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Outdoors |  |  | 21 | 49 | [5 empty] | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B19512¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Outdoors |  |  | 13 | 43 | 506 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10000¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 7 | [5 empty] | 23 | 36 | 468 |  | 2020-09-17 12:00 | 12:00 | 23 | 36 | 468 |  | caution | 2020-09-14 | B25602¦Courtroom 7¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-3, 16th Floor OTHER | [5 empty] | 21 | 46 | 732 |  | 2020-09-17 12:00 | 12:00 | 21 | 46 | 732 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-3, 16th Floor OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 1 | [5 empty] | 20.5556 | 40 | 471 |  | 2020-09-17 09:00 | 9:00 | 20.5556 | 40 | 471 |  | caution | 2020-09-14 | B10000¦Courtroom 1¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Outdoors |  |  | 14 | 53 | 678 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B25602¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 1 | [5 empty] | 21.1111 | 36 | 467 |  | 2020-09-17 12:00 | 12:00 | 21.1111 | 36 | 467 |  | caution | 2020-09-14 | B10000¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Washrooms, 16th Floor OTHER | [5 empty] | 21 | 47 | 709 |  | 2020-09-17 12:00 | 12:00 | 21 | 47 | 709 |  |  | 2020-09-14 | B25398¦Corridor adj. to Washrooms, 16th Floor OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 1 | [5 empty] | 21.1111 | 34 | 480 |  | 2020-09-17 15:00 | 15:00 | 21.1111 | 34 | 480 |  | low | 2020-09-14 | B10000¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 16th Floor OTHER | [5 empty] | 22 | 47 | 718 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 718 |  |  | 2020-09-14 | B25398¦Elevator Lobby, 16th Floor OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 2 | [5 empty] | 23.8889 | 32 | 439 |  | 2020-09-17 09:00 | 9:00 | 23.8889 | 32 | 439 |  | low | 2020-09-14 | B10000¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Women's Washroom, 16th Floor | [5 empty] | 21 | 47 | 705 |  | 2020-09-17 12:00 | 12:00 | 21 | 47 | 705 |  |  | 2020-09-14 | B25398¦OTHER Women's Washroom, 16th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 2 | [5 empty] | 23.8889 | 24 | 435 |  | 2020-09-17 12:00 | 12:00 | 23.8889 | 24 | 435 |  | low | 2020-09-14 | B10000¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Outdoors |  |  | 20 | 52 | 341 |  |  |  | Base Readings | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B25165¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, West, 15th Floor | [5 empty] | 21 | 50 | 725 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 725 |  |  | 2020-09-14 | B25398¦OTHER Office Area, West, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 2 | [5 empty] | 23.3333 | 23 | 435 |  | 2020-09-17 15:00 | 15:00 | 23.3333 | 23 | 435 |  | low | 2020-09-14 | B10000¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 101 | [5 empty] | 21 | 49 |  |  | 2020-09-17 15:00 | 15:00 | 21 | 49 |  |  |  | 2020-09-14 | B20080¦Courtroom 101¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | OTHER | [5 empty] | 21 | 48 | 440 | Courtroom 700, Please add to drop down box , thank you | 2020-09-17 15:00 | 15:00 | 21 | 48 | 440 |  |  | 2020-09-14 | B25165¦OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 3 | [5 empty] | 21.6667 | 39 | 439 |  | 2020-09-17 09:00 | 9:00 | 21.6667 | 39 | 439 |  | caution | 2020-09-14 | B10000¦Courtroom 3¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North West, 15th Floor | [5 empty] | 21 | 49 | 719 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 719 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North West, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 201 | [5 empty] | 22 | 47 | 448 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 448 |  |  | 2020-09-14 | B20080¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 3 | [5 empty] | 21.6667 | 34 | 456 |  | 2020-09-17 12:00 | 12:00 | 21.6667 | 34 | 456 |  | low | 2020-09-14 | B10000¦Courtroom 3¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 202 | [5 empty] | 23 | 47 | 438 |  | 2020-09-17 15:00 | 15:00 | 23 | 47 | 438 |  |  | 2020-09-14 | B20080¦Courtroom 202¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North, 15th Floor | [5 empty] | 21 | 49 | 722 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 722 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 3 | [5 empty] | 21.6667 | 32 | 434 |  | 2020-09-17 15:00 | 15:00 | 21.6667 | 32 | 434 |  | low | 2020-09-14 | B10000¦Courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North Easr, 15th Floor | [5 empty] | 21 | 49 | 725 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 725 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North Easr, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 4 | [5 empty] | 20.5556 | 28 | 458 |  | 2020-09-17 09:00 | 9:00 | 20.5556 | 28 | 458 |  | low | 2020-09-14 | B10000¦Courtroom 4¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 301 | [5 empty] | 22 | 47 | 446 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 446 |  |  | 2020-09-14 | B20080¦Courtroom 301¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 4 | [5 empty] | 22.2222 | 27 | 488 |  | 2020-09-17 12:00 | 12:00 | 22.2222 | 27 | 488 |  | low | 2020-09-14 | B10000¦Courtroom 4¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, East, 15th Floor | [5 empty] | 21 | 49 | 728 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 728 |  |  | 2020-09-14 | B25398¦OTHER Office Area, East, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 302 | [5 empty] | 22 | 47 | 441 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 441 |  |  | 2020-09-14 | B20080¦Courtroom 302¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 4 | [5 empty] | 22.2222 | 20 | 434 |  | 2020-09-17 15:00 | 15:00 | 22.2222 | 20 | 434 |  | low | 2020-09-14 | B10000¦Courtroom 4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 303 | [5 empty] | 22 | 47 | 465 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 465 |  |  | 2020-09-14 | B20080¦Courtroom 303¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South East, 15th Floor | [5 empty] | 21 | 48 | 717 |  | 2020-09-17 12:00 | 12:00 | 21 | 48 | 717 |  |  | 2020-09-14 | B25398¦OTHER Office Area, South East, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 600 | [5 empty] | 21 | 48 | 437 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 437 |  |  | 2020-09-14 | B25165¦Courtroom 600¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 5 | [5 empty] | 21.6667 | 38 | 450 |  | 2020-09-17 09:00 | 9:00 | 21.6667 | 38 | 450 |  | caution | 2020-09-14 | B10000¦Courtroom 5¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | front seating area | [5 empty] | 22 | 50 | 409 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 409 |  |  | 2020-09-14 | B18359¦front seating area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 308 | [5 empty] | 22 | 48 | 496 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 496 |  |  | 2020-09-14 | B25165¦Courtroom 308¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South, 15th Floor | [5 empty] | 21 | 48 | 722 |  | 2020-09-17 12:00 | 12:00 | 21 | 48 | 722 |  |  | 2020-09-14 | B25398¦OTHER Office Area, South, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 5 | [5 empty] | 21.1111 | 32 | 474 |  | 2020-09-17 12:00 | 12:00 | 21.1111 | 32 | 474 |  | low | 2020-09-14 | B10000¦Courtroom 5¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Northwest corridor | [5 empty] | 22 | 50 | 407 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 407 |  |  | 2020-09-14 | B18359¦Northwest corridor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 306 | [5 empty] | 21 | 48 | 441 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 441 |  |  | 2020-09-14 | B25165¦Courtroom 306¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Outdoors |  |  | 17 | 67 | 415 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20080¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 5 | [5 empty] | 21.6667 | 30 | 472 |  | 2020-09-17 15:00 | 15:00 | 21.6667 | 30 | 472 |  | low | 2020-09-14 | B10000¦Courtroom 5¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Reception, 15th Floor | [5 empty] | 22 | 47 | 720 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 720 |  |  | 2020-09-14 | B25398¦OTHER Reception, 15th Floor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 302 | [5 empty] | 21 | 48 | 483 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 483 |  |  | 2020-09-14 | B25165¦Courtroom 302¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 6 | [5 empty] | 21.1111 | 38 | 450 |  | 2020-09-17 09:00 | 9:00 | 21.1111 | 38 | 450 |  | caution | 2020-09-14 | B10000¦Courtroom 6¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 208 | [5 empty] | 21 | 48 | 441 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 441 |  |  | 2020-09-14 | B25165¦Courtroom 208¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 6 | [5 empty] | 21.6667 | 32 | 474 |  | 2020-09-17 12:00 | 12:00 | 21.6667 | 32 | 474 |  | low | 2020-09-14 | B10000¦Courtroom 6¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Mail Room, 15th Floor OTHER | [5 empty] | 22 | 48 | 727 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 727 |  |  | 2020-09-14 | B25398¦Corridor adj. to Mail Room, 15th Floor OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 206 | [5 empty] | 21 | 48 | 432 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 432 |  |  | 2020-09-14 | B25165¦Courtroom 206¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 6 | [5 empty] | 22.2222 | 30 | 472 |  | 2020-09-17 15:00 | 15:00 | 22.2222 | 30 | 472 |  | low | 2020-09-14 | B10000¦Courtroom 6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 204 | [5 empty] | 22 | 48 | 501 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 501 |  |  | 2020-09-14 | B25165¦Courtroom 204¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 15th Floor OTHER | [5 empty] | 22 | 47 | 721 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 721 |  |  | 2020-09-14 | B25398¦Elevator Lobby, 15th Floor OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 7 | [5 empty] | 21.6667 | 35 | 430 |  | 2020-09-17 09:00 | 9:00 | 21.6667 | 35 | 430 |  | caution | 2020-09-14 | B10000¦Courtroom 7¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 7 | [5 empty] | 21.6667 | 29 | 481 |  | 2020-09-17 12:00 | 12:00 | 21.6667 | 29 | 481 |  | low | 2020-09-14 | B10000¦Courtroom 7¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 202 | [5 empty] | 21 | 48 | 456 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 456 |  |  | 2020-09-14 | B25165¦Courtroom 202¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Outdoors |  |  | 18 | 54 | 668 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B25398¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 7 | [5 empty] | 22.2222 | 32 | 437 |  | 2020-09-17 15:00 | 15:00 | 22.2222 | 32 | 437 |  | low | 2020-09-14 | B10000¦Courtroom 7¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 200 | [5 empty] | 21 | 48 | 449 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 449 |  |  | 2020-09-14 | B25165¦Courtroom 200¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 22 | 50 | 403 | north side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 403 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 100 | [5 empty] | 22 | 48 | 454 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 454 |  |  | 2020-09-14 | B25165¦Courtroom 100¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 8 | [5 empty] | 21.1111 | 32 | 470 |  | 2020-09-17 09:00 | 9:00 | 21.1111 | 32 | 470 |  | low | 2020-09-14 | B10000¦Courtroom 8¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 201 | [5 empty] | 22 | 51 | 411 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 411 |  |  | 2020-09-14 | B70003¦Courtroom 201¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 8 | [5 empty] | 22.2222 | 24 | 434 |  | 2020-09-17 12:00 | 12:00 | 22.2222 | 24 | 434 |  | low | 2020-09-14 | B10000¦Courtroom 8¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 8 | [5 empty] | 21.1111 | 24 | 421 |  | 2020-09-17 15:00 | 15:00 | 21.1111 | 24 | 421 |  | low | 2020-09-14 | B10000¦Courtroom 8¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 9 | [5 empty] | 21.1111 | 38 | 450 |  | 2020-09-17 12:00 | 12:00 | 21.1111 | 38 | 450 |  | caution | 2020-09-14 | B10000¦Courtroom 9¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 22 | 51 | 405 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 405 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 9 | [5 empty] | 21.1111 | 32 | 474 |  | 2020-09-17 12:00 | 12:00 | 21.1111 | 32 | 474 |  | low | 2020-09-14 | B10000¦Courtroom 9¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 22 | 51 | 408 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 408 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 9 | [5 empty] | 22.2222 | 30 | 472 |  | 2020-09-17 15:00 | 15:00 | 22.2222 | 30 | 472 |  | low | 2020-09-14 | B10000¦Courtroom 9¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 22 | 51 | 409 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 409 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 22 | 51 | 412 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 412 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 22 | 51 | 410 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 410 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Entry/Waiting | [5 empty] | 23 | 45 | 486 |  | 2020-09-17 15:00 | 15:00 | 23 | 45 | 486 |  |  | 2020-09-14 | B70510¦Entry/Waiting¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 22 | 50 | 410 | south side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 410 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 22 | 50 | 408 | north side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 408 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 1 | [5 empty] | 24 | 48 | 398 |  | 2020-09-17 15:00 | 15:00 | 24 | 48 | 398 |  |  | 2020-09-14 | B24638¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 22 | 50 | 410 | south side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 410 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 3 | [5 empty] | 24 | 46 | 362 |  | 2020-09-17 15:00 | 15:00 | 24 | 46 | 362 |  |  | 2020-09-14 | B24638¦Courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 22 | 51 | 401 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 401 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Outdoors |  |  | 18 | 28 | 420 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B12948¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 22 | 51 | 405 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 405 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Outdoors |  |  | 23 | 47 | 351 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B24638¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 1 | [5 empty] | 21 | 29 | 424 |  | 2020-09-17 15:00 | 15:00 | 21 | 29 | 424 |  | low | 2020-09-14 | B12948¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 22 | 51 | 423 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 423 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 | [5 empty] | 21 | 29 | 430 |  | 2020-09-17 15:00 | 15:00 | 21 | 29 | 430 |  | low | 2020-09-14 | B12948¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room A | [5 empty] | 23 | 44 | 548 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 548 |  |  | 2020-09-14 | B70510¦Mediation Room A¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 22 | 51 | 422 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 422 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Information Desk | [5 empty] | 23 | 44 | 463 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 463 |  |  | 2020-09-14 | B70510¦Information Desk¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 | [5 empty] | 21 | 29 | 430 |  | 2020-09-17 15:00 | 15:00 | 21 | 29 | 430 |  | low | 2020-09-14 | B12948¦Courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 22 | 51 | 403 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 403 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Lunch Room 454 | [5 empty] | 23 | 44 | 450 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 450 |  |  | 2020-09-14 | B70510¦Lunch Room 454¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 | [5 empty] | 21 | 29 | 441 |  | 2020-09-17 15:00 | 15:00 | 21 | 29 | 441 |  | low | 2020-09-14 | B12948¦Courtroom 4¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 22 | 51 | 415 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 415 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Copy Room 455 | [5 empty] | 23 | 44 | 450 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 450 |  |  | 2020-09-14 | B70510¦Copy Room 455¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 22 | 51 | 409 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 409 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 | [5 empty] | 21 | 30 | 412 |  | 2020-09-17 15:00 | 15:00 | 21 | 30 | 412 |  | low | 2020-09-14 | B12948¦Courtroom 5¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 22 | 50 | 411 | south side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 411 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room B | [5 empty] | 23 | 46 | 470 |  | 2020-09-17 15:00 | 15:00 | 23 | 46 | 470 |  |  | 2020-09-14 | B70510¦Mediation Room B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 6 | [5 empty] | 21 | 30 | 410 |  | 2020-09-17 15:00 | 15:00 | 21 | 30 | 410 |  | low | 2020-09-14 | B12948¦Courtroom 6¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | northeast corridor | [5 empty] | 22 | 51 | 410 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 410 |  |  | 2020-09-14 | B18359¦northeast corridor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 459 | [5 empty] | 23 | 44 | 456 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 456 |  |  | 2020-09-14 | B70510¦Office 459¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Cell Basement | [5 empty] | 21 | 32 | 460 |  | 2020-09-17 15:00 | 15:00 | 21 | 32 | 460 |  | low | 2020-09-14 | B12948¦Cell Basement¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 22 | 50 | 405 | north side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 405 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | office 467 | [5 empty] | 23 | 44 | 457 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 457 |  |  | 2020-09-14 | B70510¦office 467¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 22 | 50 | 410 | south side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 410 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 469 | [5 empty] | 23 | 44 | 461 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 461 |  |  | 2020-09-14 | B70510¦Office 469¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 1 | [5 empty] | 22 | 37 | 448 |  | 2020-09-17 15:00 | 15:00 | 22 | 37 | 448 |  | caution | 2020-09-14 | B25602¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 22 | 50 | 400 | north side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 400 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Room 473 (Printer) | [5 empty] | 23 | 44 | 463 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 463 |  |  | 2020-09-14 | B70510¦Room 473 (Printer)¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 22 | 51 | 402 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 402 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hall 475 or 466 | [5 empty] | 23 | 44 | 463 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 463 |  |  | 2020-09-14 | B70510¦Hall 475 or 466¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 22 | 51 | 400 | north side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 400 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 1 | [5 empty] | 22 | 44 | 467 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 467 |  |  | 2020-09-14 | B70510¦Hearing Room 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 22 | 51 | 407 | south side | 2020-09-17 12:00 | 12:00 | 22 | 51 | 407 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 2 | [5 empty] | 22 | 36 | 446 |  | 2020-09-17 15:00 | 15:00 | 22 | 36 | 446 |  | caution | 2020-09-14 | B25602¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Cell Basement | [5 empty] | 21 | 32 | 460 |  | 2020-09-17 15:00 | 15:00 | 21 | 32 | 460 |  | low | 2020-09-14 | B12948¦Cell Basement¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Meeting Rooms 1/2 | [5 empty] | 22 | 45 | 508 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 508 |  |  | 2020-09-14 | B70510¦Vestibule at Meeting Rooms 1/2¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 22 | 50 | 408 | north side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 408 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration Office Waiting Area | [5 empty] | 22 | 32 | 424 |  | 2020-09-17 15:00 | 15:00 | 22 | 32 | 424 |  | low | 2020-09-14 | B12948¦Administration Office Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Outdoors |  |  | 18 | 67 | [5 empty] | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20619¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtrooom 213 | [5 empty] | 22 | 50 | 411 | south side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 411 |  |  | 2020-09-14 | B18359¦courtrooom 213¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Hearing Room 1 | [5 empty] | 22 | 46 | 476 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 476 |  |  | 2020-09-14 | B70510¦Vestibule at Hearing Room 1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 8 | [5 empty] | 22 | 45 | 427 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 427 |  |  | 2020-09-14 | B25683¦Courtroom 8¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 22 | 50 | 408 | north side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 408 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration office | [5 empty] | 22 | 33 | 421 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 421 |  | low | 2020-09-14 | B12948¦Administration office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 11 | [5 empty] | 22 | 45 | 427 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 427 |  |  | 2020-09-14 | B25683¦Courtroom 11¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 2 | [5 empty] | 22 | 46 | 461 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 461 |  |  | 2020-09-14 | B70510¦Hearing Room 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Courtroom 1-14 | [5 empty] | 23 | 49 | 574 |  | 2020-09-17 15:00 | 15:00 | 23 | 49 | 574 |  |  | 2020-09-14 | B20619¦Courtroom 1-14¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 22 | 50 | 401 | south side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 401 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 9 | [5 empty] | 22 | 41 | 432 |  | 2020-09-17 15:00 | 15:00 | 22 | 41 | 432 |  |  | 2020-09-14 | B25683¦Courtroom 9¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 3 | [5 empty] | 22 | 34 | 426 |  | 2020-09-17 15:00 | 15:00 | 22 | 34 | 426 |  | low | 2020-09-14 | B25602¦Courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 22 | 50 | 404 | north side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 404 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 439 | [5 empty] | 23 | 45 | 452 |  | 2020-09-17 15:00 | 15:00 | 23 | 45 | 452 |  |  | 2020-09-14 | B70510¦Office 439¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Crown attorney admin area | [5 empty] | 22 | 33 | 534 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 534 |  | low | 2020-09-14 | B12948¦Crown attorney admin area¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 22 | 50 | 406 | south side | 2020-09-17 12:00 | 12:00 | 22 | 50 | 406 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | First Aid Desk | [5 empty] | 22 | 46 | 453 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 453 |  |  | 2020-09-14 | B70510¦First Aid Desk¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main entrance | [5 empty] | 22 | 31 | 446 |  | 2020-09-17 15:00 | 15:00 | 22 | 31 | 446 |  | low | 2020-09-14 | B12948¦Main entrance¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Outdoors |  |  | 22 | 56 | 397 |  |  |  | outside of 15 Grosvenor Ave. | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B18359¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 436 | [5 empty] | 23 | 45 | 451 |  | 2020-09-17 15:00 | 15:00 | 23 | 45 | 451 |  |  | 2020-09-14 | B70510¦Office 436¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main Entrance Waiting Area | [5 empty] | 22 | 31 | 420 |  | 2020-09-17 15:00 | 15:00 | 22 | 31 | 420 |  | low | 2020-09-14 | B12948¦Main Entrance Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 432 | [5 empty] | 23 | 45 | 461 |  | 2020-09-17 15:00 | 15:00 | 23 | 45 | 461 |  |  | 2020-09-14 | B70510¦Office 432¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Court Room 1 Waiting Area | [5 empty] | 22 | 31 | 425 |  | 2020-09-17 15:00 | 15:00 | 22 | 31 | 425 |  | low | 2020-09-14 | B12948¦Court Room 1 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 4 | [5 empty] | 23 | 36 | 444 |  | 2020-09-17 15:00 | 15:00 | 23 | 36 | 444 |  | caution | 2020-09-14 | B25602¦Courtroom 4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 429 | [5 empty] | 23 | 45 | 468 |  | 2020-09-17 15:00 | 15:00 | 23 | 45 | 468 |  |  | 2020-09-14 | B70510¦Office 429¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 Waiting Area | [5 empty] | 22 | 31 | 435 |  | 2020-09-17 15:00 | 15:00 | 22 | 31 | 435 |  | low | 2020-09-14 | B12948¦Courtroom 2 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20893 | B20893 - 75 Mulcaster St. - Barrie | Courtroom 7,8,9 | [5 empty] | 23 | 38 | 527 |  | 2020-09-17 15:00 | 15:00 | 23 | 38 | 527 |  | caution | 2020-09-14 | B20893¦Courtroom 7,8,9¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 427 | [5 empty] | 23 | 44 | 458 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 458 |  |  | 2020-09-14 | B70510¦Office 427¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 Waiting Area | [5 empty] | 22 | 31 | 450 |  | 2020-09-17 15:00 | 15:00 | 22 | 31 | 450 |  | low | 2020-09-14 | B12948¦Courtroom 3 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 4 | [5 empty] | 23 | 35 | 420 |  | 2020-09-17 15:00 | 15:00 | 23 | 35 | 420 |  | caution | 2020-09-14 | B25602¦Courtroom 4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mail Room | [5 empty] | 23 | 44 | 460 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 460 |  |  | 2020-09-14 | B70510¦Mail Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92347 | B92347 - 75 Mulcaster Street - Barrie | Courtroom 15 | [5 empty] | 21 | 43 | 527 |  | 2020-09-17 15:00 | 15:00 | 21 | 43 | 527 |  |  | 2020-09-14 | B92347¦Courtroom 15¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 Waiting Area | [5 empty] | 22 | 31 | 447 |  | 2020-09-17 15:00 | 15:00 | 22 | 31 | 447 |  | low | 2020-09-14 | B12948¦Courtroom 5 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 6 | [5 empty] | 23 | 37 | 454 |  | 2020-09-17 15:00 | 15:00 | 23 | 37 | 454 |  | caution | 2020-09-14 | B25602¦Courtroom 6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 420 | [5 empty] | 23 | 44 | 460 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 460 |  |  | 2020-09-14 | B70510¦Office 420¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 and 6 Waiting Area | [5 empty] | 22 | 31 | 430 |  | 2020-09-17 15:00 | 15:00 | 22 | 31 | 430 |  | low | 2020-09-14 | B12948¦Courtroom 4 and 6 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 7 | [5 empty] | 23 | 35 | 450 |  | 2020-09-17 15:00 | 15:00 | 23 | 35 | 450 |  | caution | 2020-09-14 | B25602¦Courtroom 7¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 418 | [5 empty] | 23 | 44 | 465 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 465 |  |  | 2020-09-14 | B70510¦Office 418¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Crown Attorney Office | [5 empty] | 22 | 34 | 443 |  | 2020-09-17 12:00 | 12:00 | 22 | 34 | 443 |  | low | 2020-09-14 | B20016¦Crown Attorney Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | File Room | [5 empty] | 23 | 44 | 460 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 460 |  |  | 2020-09-14 | B70510¦File Room¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Legal Aid Ontario | [5 empty] | 22 | 33 | 442 |  | 2020-09-17 12:00 | 12:00 | 22 | 33 | 442 |  | low | 2020-09-14 | B20016¦Legal Aid Ontario¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Health Room | [5 empty] | 23 | 44 | 465 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 465 |  |  | 2020-09-14 | B70510¦Health Room¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel Waiting Area | [5 empty] | 23 | 32 | 441 |  | 2020-09-17 12:00 | 12:00 | 23 | 32 | 441 |  | low | 2020-09-14 | B20016¦Duty Counsel Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 | [5 empty] | 23 | 44 | 484 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 484 |  |  | 2020-09-14 | B70510¦Hearing Room 3¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Outdoors |  |  | 15 | 51 | 677 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B25602¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 Waiting Area | [5 empty] | 23 | 46 | 460 |  | 2020-09-17 15:00 | 15:00 | 23 | 46 | 460 |  |  | 2020-09-14 | B70510¦Hearing Room 3 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Elevator Lobby | [5 empty] | 22 | 45 | 456 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 456 |  |  | 2020-09-14 | B70510¦Elevator Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel | [5 empty] | 22 | 35 | 445 |  | 2020-09-17 12:00 | 12:00 | 22 | 35 | 445 |  | caution | 2020-09-14 | B20016¦Duty Counsel¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lobby Courtroom 1 - 2 | [5 empty] | 22 | 33 | 460 |  | 2020-09-17 12:00 | 12:00 | 22 | 33 | 460 |  | low | 2020-09-14 | B20016¦Lobby Courtroom 1 - 2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Main Lobby | [5 empty] | 22 | 34 | 498 |  | 2020-09-17 12:00 | 12:00 | 22 | 34 | 498 |  | low | 2020-09-14 | B20016¦Main Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lower Hallway | [5 empty] | 22 | 33 | 463 |  | 2020-09-17 12:00 | 12:00 | 22 | 33 | 463 |  | low | 2020-09-14 | B20016¦Lower Hallway¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | OTHER | [5 empty] | 21 | 33 | 472 | Courtroom 1-2-3 | 2020-09-17 12:00 | 12:00 | 21 | 33 | 472 |  | low | 2020-09-14 | B20016¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Outdoors |  |  | 23 | 35 | 448 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70510¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation | [5 empty] | 21 | 35 | 461 |  | 2020-09-17 12:00 | 12:00 | 21 | 35 | 461 |  | caution | 2020-09-14 | B20016¦Family Mediation¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation Across Stairs | [5 empty] | 20 | 34 | 491 |  | 2020-09-17 12:00 | 12:00 | 20 | 34 | 491 |  | low | 2020-09-14 | B20016¦Family Mediation Across Stairs¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Outdoors |  |  | 12 | 57 | 418 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B90838¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Main Lobby | [5 empty] | 19 | 45 | 458 |  | 2020-09-17 12:00 | 12:00 | 19 | 45 | 458 |  |  | 2020-09-14 | B19523¦Main Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Courtroom 101 Courtroom 102 | [5 empty] | 21 | 42 | 433 |  | 2020-09-17 15:00 | 15:00 | 21 | 42 | 433 |  |  | 2020-09-14 | B90838¦Courtroom 101 Courtroom 102¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Holding Cell | [5 empty] | 21 | 41 | 522 |  | 2020-09-17 12:00 | 12:00 | 21 | 41 | 522 |  |  | 2020-09-14 | B19523¦Holding Cell¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd fl lobby | [5 empty] | 21 | 33 | 718 |  | 2020-09-17 15:00 | 15:00 | 21 | 33 | 718 |  | low | 2020-09-14 | B20226¦2nd fl lobby¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 1 | [5 empty] | 21 | 41 | 440 |  | 2020-09-17 12:00 | 12:00 | 21 | 41 | 440 |  |  | 2020-09-14 | B19523¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Court Services | [5 empty] | 21 | 35 | 503 |  | 2020-09-17 12:00 | 12:00 | 21 | 35 | 503 |  | caution | 2020-09-14 | B19523¦Court Services¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | JP Office | [5 empty] | 21 | 39 | 455 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 455 |  | caution | 2020-09-14 | B19523¦JP Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 2 | [5 empty] | 21 | 32 | 660 |  | 2020-09-17 15:00 | 15:00 | 21 | 32 | 660 |  | low | 2020-09-14 | B20226¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | OPP Office | [5 empty] | 21 | 40 | 438 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 438 |  | caution | 2020-09-14 | B19523¦OPP Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Crown Attorney Office | [5 empty] | 21 | 42 | 447 |  | 2020-09-17 12:00 | 12:00 | 21 | 42 | 447 |  |  | 2020-09-14 | B19523¦Crown Attorney Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 42 | 468 |  | 2020-09-17 12:00 | 12:00 | 22 | 42 | 468 |  |  | 2020-09-14 | B19523¦VWAP Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 1 | [5 empty] | 21 | 34 | 814 |  | 2020-09-17 15:00 | 15:00 | 21 | 34 | 814 |  | low | 2020-09-14 | B20226¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 23 | 40 | 514 |  | 2020-09-17 12:00 | 12:00 | 23 | 40 | 514 |  | caution | 2020-09-14 | B19523¦VWAP Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 | [5 empty] | 23 | 48 | 481 |  | 2020-09-17 12:00 | 12:00 | 23 | 48 | 481 |  |  | 2020-09-14 | B14209¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 5 | [5 empty] | 21 | 38 | 429 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 429 |  | caution | 2020-09-14 | B19523¦Courtroom 5¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 - waiting area | [5 empty] | 22 | 48 | 490 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 490 |  |  | 2020-09-14 | B14209¦Courtroom 1 - waiting area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office North | [5 empty] | 24 | 31 | 755 |  | 2020-09-17 15:00 | 15:00 | 24 | 31 | 755 |  | low | 2020-09-14 | B14895¦Administration Office North¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 22 | 33 | 707 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 707 |  | low | 2020-09-14 | B20226¦2nd Floor Holding Cell¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 | [5 empty] | 22 | 46 | 471 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 471 |  |  | 2020-09-14 | B14209¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office South | [5 empty] | 23 | 26 | 570 |  | 2020-09-17 15:00 | 15:00 | 23 | 26 | 570 |  | low | 2020-09-14 | B14895¦Administration Office South¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 - waiting room | [5 empty] | 22 | 46 | 460 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 460 |  |  | 2020-09-14 | B14209¦Courtroom 2 - waiting room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Remote Testimony Room | [5 empty] | 21 | 39 | 435 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 435 |  | caution | 2020-09-14 | B19523¦Remote Testimony Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Conference Room 2 | [5 empty] | 21 | 41 | 434 |  | 2020-09-17 12:00 | 12:00 | 21 | 41 | 434 |  |  | 2020-09-14 | B19523¦Conference Room 2¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main entrance | [5 empty] | 22 | 37 | 587 |  | 2020-09-17 15:00 | 15:00 | 22 | 37 | 587 |  | caution | 2020-09-14 | B14895¦Main entrance¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 | [5 empty] | 21 | 40 | 429 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 429 |  | caution | 2020-09-14 | B19523¦Courtroom 3¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main Floor Waiting Area | [5 empty] | 24 | 27 | 588 |  | 2020-09-17 15:00 | 15:00 | 24 | 27 | 588 |  | low | 2020-09-14 | B14895¦Main Floor Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 Waiting Area | [5 empty] | 21 | 40 | 442 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 442 |  | caution | 2020-09-14 | B19523¦Courtroom 3 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom A | [5 empty] | 23 | 28 | 476 |  | 2020-09-17 15:00 | 15:00 | 23 | 28 | 476 |  | low | 2020-09-14 | B14895¦Courtroom A¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 40 | 464 |  | 2020-09-17 12:00 | 12:00 | 20 | 40 | 464 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom B | [5 empty] | 23 | 27 | 454 |  | 2020-09-17 15:00 | 15:00 | 23 | 27 | 454 |  | low | 2020-09-14 | B14895¦Courtroom B¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 21 | 40 | 476 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 476 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | 2nd Floor Waiting Area | [5 empty] | 24 | 28 | 605 |  | 2020-09-17 15:00 | 15:00 | 24 | 28 | 605 |  | low | 2020-09-14 | B14895¦2nd Floor Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 3 | [5 empty] | 22 | 28 | 547 |  | 2020-09-17 15:00 | 15:00 | 22 | 28 | 547 |  | low | 2020-09-14 | B20226¦Courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 40 | 492 |  | 2020-09-17 12:00 | 12:00 | 20 | 40 | 492 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Crown Attorney Office | [5 empty] | 24 | 34 | 695 |  | 2020-09-17 15:00 | 15:00 | 24 | 34 | 695 |  | low | 2020-09-14 | B14895¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 2 | [5 empty] | 21 | 41 | 468 |  | 2020-09-17 12:00 | 12:00 | 21 | 41 | 468 |  |  | 2020-09-14 | B19523¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Waiting Area | [5 empty] | 24 | 30 | 554 |  | 2020-09-17 15:00 | 15:00 | 24 | 30 | 554 |  | low | 2020-09-14 | B14895¦Basement Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Police Court Bureau | [5 empty] | 21 | 40 | 456 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 456 |  | caution | 2020-09-14 | B19523¦Police Court Bureau¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Boardroom | [5 empty] | 24 | 31 | 527 |  | 2020-09-17 15:00 | 15:00 | 24 | 31 | 527 |  | low | 2020-09-14 | B14895¦Basement Boardroom¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 Waiting Area | [5 empty] | 21 | 40 | 457 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 457 |  | caution | 2020-09-14 | B19523¦Courtroom 4 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Male Holding Cell | [5 empty] | 24 | 28 | 475 |  | 2020-09-17 15:00 | 15:00 | 24 | 28 | 475 |  | low | 2020-09-14 | B14895¦Male Holding Cell¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 | [5 empty] | 21 | 40 | 428 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 428 |  | caution | 2020-09-14 | B19523¦Courtroom 4¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Female Holding Cell | [5 empty] | 24 | 27 | 456 |  | 2020-09-17 15:00 | 15:00 | 24 | 27 | 456 |  | low | 2020-09-14 | B14895¦Female Holding Cell¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 40 | 478 |  | 2020-09-17 12:00 | 12:00 | 20 | 40 | 478 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Outdoors |  |  | 16 | 18 | 381 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B14895¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 41 | 462 |  | 2020-09-17 12:00 | 12:00 | 19 | 41 | 462 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 43 | 464 |  | 2020-09-17 12:00 | 12:00 | 19 | 43 | 464 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Jury Room | [5 empty] | 19 | 42 | 438 |  | 2020-09-17 12:00 | 12:00 | 19 | 42 | 438 |  |  | 2020-09-14 | B19523¦Jury Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Ontario Court | [5 empty] | 21 | 43 | 449 |  | 2020-09-17 12:00 | 12:00 | 21 | 43 | 449 |  |  | 2020-09-14 | B19523¦Ontario Court¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Judicial Library | [5 empty] | 21 | 40 | 435 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 435 |  | caution | 2020-09-14 | B19523¦Judicial Library¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 315 | [5 empty] | 21 | 39 | 430 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 430 |  | caution | 2020-09-14 | B19523¦Office Room 315¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Outdoors |  |  | 14 | 21 | 405 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20226¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 316 | [5 empty] | 21 | 39 | 427 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 427 |  | caution | 2020-09-14 | B19523¦Office Room 316¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 317 | [5 empty] | 21 | 39 | 429 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 429 |  | caution | 2020-09-14 | B19523¦Office Room 317¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Outdoors |  |  | 14 | 26 | 402 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70050¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Superior Court | [5 empty] | 21 | 39 | 439 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 439 |  | caution | 2020-09-14 | B19523¦Superior Court¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 313 | [5 empty] | 22 | 38 | 433 |  | 2020-09-17 12:00 | 12:00 | 22 | 38 | 433 |  | caution | 2020-09-14 | B19523¦Office Room 313¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 312 | [5 empty] | 22 | 39 | 441 |  | 2020-09-17 12:00 | 12:00 | 22 | 39 | 441 |  | caution | 2020-09-14 | B19523¦Office Room 312¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Main Lobby | [5 empty] | 20 | 45 | 556 |  | 2020-09-17 15:00 | 15:00 | 20 | 45 | 556 |  |  | 2020-09-14 | B70050¦Main Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 310 | [5 empty] | 22 | 39 | 479 |  | 2020-09-17 12:00 | 12:00 | 22 | 39 | 479 |  | caution | 2020-09-14 | B19523¦Office Room 310¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Law Association | [5 empty] | 21 | 38 | 448 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 448 |  | caution | 2020-09-14 | B19523¦Law Association¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room | [5 empty] | 22 | 47 | 428 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 428 |  |  | 2020-09-14 | B14209¦Hearing Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room, Judge’s Chamber | [5 empty] | 22 | 46 | 449 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 449 |  |  | 2020-09-14 | B14209¦Hearing Room, Judge’s Chamber¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room waiting Area | [5 empty] | 23 | 48 | 479 |  | 2020-09-17 12:00 | 12:00 | 23 | 48 | 479 |  |  | 2020-09-14 | B14209¦Hearing Room waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Front desk | [5 empty] | 22 | 49 | 475 |  | 2020-09-17 12:00 | 12:00 | 22 | 49 | 475 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Front desk¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 1 | [5 empty] | 20 | 42 | 517 |  | 2020-09-17 15:00 | 15:00 | 20 | 42 | 517 |  |  | 2020-09-14 | B70050¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown attorney admin area | [5 empty] | 23 | 49 | 484 |  | 2020-09-17 12:00 | 12:00 | 23 | 49 | 484 |  |  | 2020-09-14 | B14209¦Crown attorney admin area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 21 | 43 | 508 |  | 2020-09-17 15:00 | 15:00 | 21 | 43 | 508 |  |  | 2020-09-14 | B70050¦2nd Floor Holding Cell¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Meeting Room (232) | [5 empty] | 21 | 50 | 485 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 485 |  |  | 2020-09-14 | B14209¦Crown Attorney Meeting Room (232)¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Yannick Bedard Office - 2nd Floor | [5 empty] | 22 | 44 | 582 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 582 |  |  | 2020-09-14 | B70050¦Yannick Bedard Office - 2nd Floor¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office | [5 empty] | 22 | 50 | 440 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 440 |  |  | 2020-09-14 | B14209¦Crown Attorney Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 2 | [5 empty] | 21 | 44 | 537 |  | 2020-09-17 15:00 | 15:00 | 21 | 44 | 537 |  |  | 2020-09-14 | B70050¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd fl lobby | [5 empty] | 21 | 44 | 509 |  | 2020-09-17 15:00 | 15:00 | 21 | 44 | 509 |  |  | 2020-09-14 | B70050¦2nd fl lobby¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Assistant Crown Attorney Office (236) | [5 empty] | 22 | 50 | 452 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 452 |  |  | 2020-09-14 | B14209¦Assistant Crown Attorney Office (236)¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 101 | [5 empty] | 20 | 54 | 559 |  | 2020-09-17 15:00 | 15:00 | 20 | 54 | 559 |  |  | 2020-09-14 | B25671¦Courtroom 101¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 201 | [5 empty] | 21 | 54 | 601 |  | 2020-09-17 15:00 | 15:00 | 21 | 54 | 601 |  |  | 2020-09-14 | B25671¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 100 Courtroom 102 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203 | [5 empty] | 21 | 40 | 452 |  | 2020-09-17 15:00 | 15:00 | 21 | 40 | 452 |  | caution | 2020-09-14 | B20616¦Courtroom 100 Courtroom 102 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Lobby | [5 empty] | 23 | 50 | 491 |  | 2020-09-17 12:00 | 12:00 | 23 | 50 | 491 |  |  | 2020-09-14 | B14209¦Court Admin Office Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B25671 | B25671 - 425 Grand Ave W - Chatham | Courtroom 301 | [5 empty] | 20 | 53 | 538 | FYI I am off tomorrow September 18th | 2020-09-17 15:00 | 15:00 | 20 | 53 | 538 |  |  | 2020-09-14 | B25671¦Courtroom 301¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Cubicles | [5 empty] | 22 | 46 | 491 |  | 2020-09-17 12:00 | 12:00 | 22 | 46 | 491 |  |  | 2020-09-14 | B14209¦Court Admin Office Cubicles¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Holding Cell corridor | [5 empty] | 22 | 44 | 434 |  | 2020-09-17 12:00 | 12:00 | 22 | 44 | 434 |  |  | 2020-09-14 | B14209¦Holding Cell corridor¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 101 Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 401 Courtroom 402 Courtroom 403 | [5 empty] | 22 | 40 | 452 |  | 2020-09-17 15:00 | 15:00 | 22 | 40 | 452 |  | caution | 2020-09-14 | B20616¦Courtroom 101 Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 401 Courtroom 402 Courtroom 403¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Police Control Room | [5 empty] | 22 | 45 | 457 |  | 2020-09-17 12:00 | 12:00 | 22 | 45 | 457 |  |  | 2020-09-14 | B14209¦Police Control Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Intake Court | [5 empty] | 22 | 52 | 442 |  | 2020-09-17 12:00 | 12:00 | 22 | 52 | 442 |  |  | 2020-09-14 | B14209¦Intake Court¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 106 Courtroom 205 | [5 empty] | 20 | 45 | 451 |  | 2020-09-17 15:00 | 15:00 | 20 | 45 | 451 |  |  | 2020-09-14 | B20616¦Courtroom 106 Courtroom 205¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Level 1 Corridor by room 103 | [5 empty] | 23 | 49 | 465 |  | 2020-09-17 12:00 | 12:00 | 23 | 49 | 465 |  |  | 2020-09-14 | B14209¦Level 1 Corridor by room 103¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 204 Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 404 Courtroom 405 | [5 empty] | 21 | 45 | 451 |  | 2020-09-17 15:00 | 15:00 | 21 | 45 | 451 |  |  | 2020-09-14 | B20616¦Courtroom 204 Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 404 Courtroom 405¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Library | [5 empty] | 22 | 51 | 457 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 457 |  |  | 2020-09-14 | B14209¦Library¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Law Library Meeting Room (028B) | [5 empty] | 22 | 50 | 480 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 480 |  |  | 2020-09-14 | B14209¦Law Library Meeting Room (028B)¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Lunch Room | [5 empty] | 22 | 50 | 428 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 428 |  |  | 2020-09-14 | B14209¦Lunch Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Entrance by Stair G | [5 empty] | 22 | 44 | 445 |  | 2020-09-17 12:00 | 12:00 | 22 | 44 | 445 |  |  | 2020-09-14 | B14209¦Entrance by Stair G¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 304 Courtroom 305 | [5 empty] | 21 | 41 | 579 |  | 2020-09-17 15:00 | 15:00 | 21 | 41 | 579 |  |  | 2020-09-14 | B20616¦Courtroom 304 Courtroom 305¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 107 Courtroom 108 | [5 empty] | 21 | 40 | 417 |  | 2020-09-17 15:00 | 15:00 | 21 | 40 | 417 |  | caution | 2020-09-14 | B20616¦Courtroom 107 Courtroom 108¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Main Floor Entrance Lobby | [5 empty] | 23 | 43 | 639 |  | 2020-09-17 12:00 | 12:00 | 23 | 43 | 639 |  |  | 2020-09-14 | B14209¦Main Floor Entrance Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Outdoors |  |  | 19 | 35 | 391 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B14209¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Outdoors |  |  | 18 | 52 | 387 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B19652¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Social Benefits Tribunal Reception | [5 empty] | 21 | 43 | 463 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 463 |  |  | 2020-09-14 | B70485¦Social Benefits Tribunal Reception¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Outdoors |  |  | 18 | 46 | 479 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20289¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Print Room | [5 empty] | 22 | 41 | 468 |  | 2020-09-17 12:00 | 12:00 | 22 | 41 | 468 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Print Room¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | OTHER | [5 empty] | 21 | 43 | 448 | SBT Hearing Room #3 | 2020-09-17 09:00 | 9:00 | 21 | 43 | 448 |  |  | 2020-09-14 | B70485¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #4 | [5 empty] | 21 | 43 | 435 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 435 |  |  | 2020-09-14 | B70485¦SBT Hearing Room #4¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Center) | [5 empty] | 23 | 41 | 433 |  | 2020-09-17 15:00 | 15:00 | 23 | 41 | 433 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Center)¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | LTB Hearing Room #1 | [5 empty] | 21 | 43 | 418 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 418 |  |  | 2020-09-14 | B70485¦LTB Hearing Room #1¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 | [5 empty] | 23 | 42 | 453 |  | 2020-09-17 12:00 | 12:00 | 23 | 42 | 453 |  |  | 2020-09-14 | B14209¦Courtroom 1¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Regional Managers Office | [5 empty] | 20 | 44 | 432 |  | 2020-09-17 09:00 | 9:00 | 20 | 44 | 432 |  |  | 2020-09-14 | B70485¦Regional Managers Office¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 - waiting area | [5 empty] | 23 | 48 | 457 |  | 2020-09-17 15:00 | 15:00 | 23 | 48 | 457 |  |  | 2020-09-14 | B14209¦Courtroom 1 - waiting area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 | [5 empty] | 23 | 42 | 453 |  | 2020-09-17 15:00 | 15:00 | 23 | 42 | 453 |  |  | 2020-09-14 | B14209¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Judge Dias) | [5 empty] | 22 | 42 | 422 |  | 2020-09-17 15:00 | 15:00 | 22 | 42 | 422 |  |  | 2020-09-14 | B19652¦Courtroom 1 (Judge Dias)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 | [5 empty] | 23 | 46 | 462 |  | 2020-09-17 15:00 | 15:00 | 23 | 46 | 462 |  |  | 2020-09-14 | B14209¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 44 | 421 | superior judges chamber | 2020-09-17 15:00 | 15:00 | 22 | 44 | 421 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Cubes outside RM Office | [5 empty] | 20 | 43 | 416 |  | 2020-09-17 09:00 | 9:00 | 20 | 43 | 416 |  |  | 2020-09-14 | B70485¦Cubes outside RM Office¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 - waiting room | [5 empty] | 23 | 46 | 462 |  | 2020-09-17 15:00 | 15:00 | 23 | 46 | 462 |  |  | 2020-09-14 | B14209¦Courtroom 2 - waiting room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 45 | 452 | 3rd floor stair landing | 2020-09-17 15:00 | 15:00 | 22 | 45 | 452 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room | [5 empty] | 23 | 47 | 424 |  | 2020-09-17 15:00 | 15:00 | 23 | 47 | 424 |  |  | 2020-09-14 | B14209¦Hearing Room¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #1 | [5 empty] | 21 | 42 | 416 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 416 |  |  | 2020-09-14 | B70485¦Mediation Room #1¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room, Judge’s Chamber | [5 empty] | 23 | 46 | 423 |  | 2020-09-17 15:00 | 15:00 | 23 | 46 | 423 |  |  | 2020-09-14 | B14209¦Hearing Room, Judge’s Chamber¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room - Waiting area | [5 empty] | 23 | 47 | 448 |  | 2020-09-17 15:00 | 15:00 | 23 | 47 | 448 |  |  | 2020-09-14 | B14209¦Hearing Room - Waiting area¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #2 | [5 empty] | 21 | 42 | 417 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 417 |  |  | 2020-09-14 | B70485¦Mediation Room #2¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 3rd floor jury room | [5 empty] | 22 | 44 | 440 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 440 |  |  | 2020-09-14 | B19652¦3rd floor jury room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Outdoors |  |  | 21 | 50 | 508 |  |  |  | judge | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20289¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Front desk | [5 empty] | 23 | 42 | 479 |  | 2020-09-17 15:00 | 15:00 | 23 | 42 | 479 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Front desk¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Reception/ Administration LTB | [5 empty] | 21 | 42 | 425 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 425 |  |  | 2020-09-14 | B70485¦Reception/ Administration LTB¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | justice mcdonald chamber | [5 empty] | 22 | 46 | 564 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 564 |  |  | 2020-09-14 | B19652¦justice mcdonald chamber¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown attorney admin area | [5 empty] | 22 | 38 | 466 |  | 2020-09-17 15:00 | 15:00 | 22 | 38 | 466 |  | caution | 2020-09-14 | B14209¦Crown attorney admin area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 21 | 50 | 498 | public | 2020-09-17 15:00 | 15:00 | 21 | 50 | 498 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Print Room | [5 empty] | 22 | 45 | 481 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 481 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Print Room¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | OTHER | [5 empty] | 21 | 42 | 423 | Document Area | 2020-09-17 09:00 | 9:00 | 21 | 42 | 423 |  |  | 2020-09-14 | B70485¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | JUSTICE MCDONALD SECRETARY | [5 empty] | 22 | 47 | 570 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 570 |  |  | 2020-09-14 | B19652¦JUSTICE MCDONALD SECRETARY¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Assistant Crown Attorney Office (236) | [5 empty] | 22 | 47 | 452 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 452 |  |  | 2020-09-14 | B14209¦Assistant Crown Attorney Office (236)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 22 | 49 | 504 | judge | 2020-09-17 15:00 | 15:00 | 22 | 49 | 504 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 22 | 48 | 497 | public | 2020-09-17 15:00 | 15:00 | 22 | 48 | 497 |  |  | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Meeting Room (232) | [5 empty] | 21 | 47 | 449 |  | 2020-09-17 15:00 | 15:00 | 21 | 47 | 449 |  |  | 2020-09-14 | B14209¦Crown Attorney Meeting Room (232)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | SCJTC Office | [5 empty] | 22 | 47 | 561 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 561 |  |  | 2020-09-14 | B19652¦SCJTC Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 300 | [5 empty] | 22 | 58 | 496 |  | 2020-09-17 15:00 | 15:00 | 22 | 58 | 496 |  |  | 2020-09-14 | B20289¦Courtroom 300¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office | [5 empty] | 21 | 48 | 446 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 446 |  |  | 2020-09-14 | B14209¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Copy Room | [5 empty] | 21 | 42 | 412 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 412 |  |  | 2020-09-14 | B70485¦Copy Room¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | visiting justice chamber | [5 empty] | 22 | 47 | 556 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 556 |  |  | 2020-09-14 | B19652¦visiting justice chamber¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 301 | [5 empty] | 21 | 58 | 498 |  | 2020-09-17 15:00 | 15:00 | 21 | 58 | 498 |  |  | 2020-09-14 | B20289¦Courtroom 301¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Lobby | [5 empty] | 23 | 43 | 477 |  | 2020-09-17 15:00 | 15:00 | 23 | 43 | 477 |  |  | 2020-09-14 | B14209¦Court Admin Office Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 302 | [5 empty] | 22 | 59 | 507 |  | 2020-09-17 15:00 | 15:00 | 22 | 59 | 507 |  |  | 2020-09-14 | B20289¦Courtroom 302¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 303 | [5 empty] | 21 | 46 | 498 |  | 2020-09-17 15:00 | 15:00 | 21 | 46 | 498 |  |  | 2020-09-14 | B20289¦Courtroom 303¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Cubicles | [5 empty] | 22 | 46 | 512 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 512 |  |  | 2020-09-14 | B14209¦Court Admin Office Cubicles¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Center) | [5 empty] | 22 | 47 | 552 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 552 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Center)¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #3 | [5 empty] | 21 | 41 | 413 |  | 2020-09-17 09:00 | 9:00 | 21 | 41 | 413 |  |  | 2020-09-14 | B70485¦Mediation Room #3¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Holding Cell corridor | [5 empty] | 22 | 42 | 430 |  | 2020-09-17 15:00 | 15:00 | 22 | 42 | 430 |  |  | 2020-09-14 | B14209¦Holding Cell corridor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom A | [5 empty] | 22 | 58 | 519 |  | 2020-09-17 15:00 | 15:00 | 22 | 58 | 519 |  |  | 2020-09-14 | B20289¦Courtroom A¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Corner Office | [5 empty] | 21 | 43 | 414 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 414 |  |  | 2020-09-14 | B70485¦Corner Office¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Police Control Room | [5 empty] | 22 | 43 | 449 |  | 2020-09-17 15:00 | 15:00 | 22 | 43 | 449 |  |  | 2020-09-14 | B14209¦Police Control Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom B | [5 empty] | 21 | 59 | 549 |  | 2020-09-17 15:00 | 15:00 | 21 | 59 | 549 |  |  | 2020-09-14 | B20289¦Courtroom B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Judge Dias) | [5 empty] | 22 | 47 | 570 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 570 |  |  | 2020-09-14 | B19652¦Courtroom 2 (Judge Dias)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Intake Court | [5 empty] | 22 | 49 | 445 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 445 |  |  | 2020-09-14 | B14209¦Intake Court¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom C (North) | [5 empty] | 22 | 59 | 557 |  | 2020-09-17 15:00 | 15:00 | 22 | 59 | 557 |  |  | 2020-09-14 | B20289¦Courtroom C (North)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom D | [5 empty] | 22 | 59 | 569 |  | 2020-09-17 15:00 | 15:00 | 22 | 59 | 569 |  |  | 2020-09-14 | B20289¦Courtroom D¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Level 1 Corridor by room 103 | [5 empty] | 23 | 47 | 449 |  | 2020-09-17 15:00 | 15:00 | 23 | 47 | 449 |  |  | 2020-09-14 | B14209¦Level 1 Corridor by room 103¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 Waiting Area | [5 empty] | 22 | 47 | 586 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 586 |  |  | 2020-09-14 | B19652¦Courtroom 2 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom E | [5 empty] | 21 | 59 | 572 |  | 2020-09-17 15:00 | 15:00 | 21 | 59 | 572 |  |  | 2020-09-14 | B20289¦Courtroom E¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Center) | [5 empty] | 22 | 45 | 451 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 451 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Center)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom F | [5 empty] | 22 | 58 | 551 | in session; measurement taken outside courtroom | 2020-09-17 15:00 | 15:00 | 22 | 58 | 551 |  |  | 2020-09-14 | B20289¦Courtroom F¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Law Library Meeting Room (028B) | [5 empty] | 23 | 47 | 576 |  | 2020-09-17 15:00 | 15:00 | 23 | 47 | 576 |  |  | 2020-09-14 | B14209¦Law Library Meeting Room (028B)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Judge Dias) | [5 empty] | 22 | 44 | 461 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 461 |  |  | 2020-09-14 | B19652¦Courtroom 3 (Judge Dias)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Library | [5 empty] | 22 | 49 | 441 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 441 |  |  | 2020-09-14 | B14209¦Library¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | justice peace chamber | [5 empty] | 23 | 45 | 501 |  | 2020-09-17 15:00 | 15:00 | 23 | 45 | 501 |  |  | 2020-09-14 | B19652¦justice peace chamber¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Crown Attorney Office | [5 empty] | 22 | 26 | 434 |  | 2020-09-17 15:00 | 15:00 | 22 | 26 | 434 |  | low | 2020-09-14 | B20016¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Entrance by Stair G | [5 empty] | 24 | 33 | 510 |  | 2020-09-17 15:00 | 15:00 | 24 | 33 | 510 |  | low | 2020-09-14 | B14209¦Entrance by Stair G¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Legal Aid Ontario | [5 empty] | 23 | 24 | 442 |  | 2020-09-17 15:00 | 15:00 | 23 | 24 | 442 |  | low | 2020-09-14 | B20016¦Legal Aid Ontario¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | council chamber dias | [5 empty] | 22 | 48 | 598 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 598 |  |  | 2020-09-14 | B19652¦council chamber dias¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Main Floor Entrance Lobby | [5 empty] | 22 | 42 | 671 |  | 2020-09-17 15:00 | 15:00 | 22 | 42 | 671 |  |  | 2020-09-14 | B14209¦Main Floor Entrance Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel Waiting Area | [5 empty] | 23 | 24 | 460 |  | 2020-09-17 15:00 | 15:00 | 23 | 24 | 460 |  | low | 2020-09-14 | B20016¦Duty Counsel Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel | [5 empty] | 23 | 30 | 459 |  | 2020-09-17 15:00 | 15:00 | 23 | 30 | 459 |  | low | 2020-09-14 | B20016¦Duty Counsel¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | council chamber center | [5 empty] | 22 | 47 | 585 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 585 |  |  | 2020-09-14 | B19523¦council chamber center¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Side Entry Door | [5 empty] | 21 | 43 | 427 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 427 |  |  | 2020-09-14 | B70485¦Side Entry Door¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Outdoors |  |  | 19 | 21 | 396 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B14209¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-1, 16th Floor OTHER | [5 empty] | 22 | 44 | 718 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 718 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-1, 16th Floor OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Filing Area | [5 empty] | 21 | 43 | 430 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 430 |  |  | 2020-09-14 | B70485¦Filing Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 2nd Floor Lunchroom | [5 empty] | 22 | 42 | 553 |  | 2020-09-17 15:00 | 15:00 | 22 | 42 | 553 |  |  | 2020-09-14 | B19652¦2nd Floor Lunchroom¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Entrance by Stair G | [5 empty] | 24 | 33 | 510 |  | 2020-09-17 15:00 | 15:00 | 24 | 33 | 510 |  | low | 2020-09-14 | B14209¦Entrance by Stair G¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lobby Courtroom 1 - 2 | [5 empty] | 23 | 25 | 464 |  | 2020-09-17 15:00 | 15:00 | 23 | 25 | 464 |  | low | 2020-09-14 | B20016¦Lobby Courtroom 1 - 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-3, 16th Floor OTHER | [5 empty] | 21 | 45 | 711 |  | 2020-09-17 15:00 | 15:00 | 21 | 45 | 711 |  |  | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-3, 16th Floor OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 2nd floor stair landing | [5 empty] | 22 | 45 | 519 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 519 |  |  | 2020-09-14 | B19652¦2nd floor stair landing¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Staff Kitchen | [5 empty] | 21 | 43 | 434 |  | 2020-09-17 09:00 | 9:00 | 21 | 43 | 434 |  |  | 2020-09-14 | B70485¦Staff Kitchen¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Main Lobby | [5 empty] | 23 | 27 | 514 |  | 2020-09-17 15:00 | 15:00 | 23 | 27 | 514 |  | low | 2020-09-14 | B20016¦Main Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | court services kitchenette | [5 empty] | 22 | 42 | 502 |  | 2020-09-17 15:00 | 15:00 | 22 | 42 | 502 |  |  | 2020-09-14 | B19652¦court services kitchenette¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Washrooms, 16th Floor OTHER | [5 empty] | 21 | 45 | 706 |  | 2020-09-17 15:00 | 15:00 | 21 | 45 | 706 |  |  | 2020-09-14 | B25398¦Corridor adj. to Washrooms, 16th Floor OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | court services north | [5 empty] | 23 | 41 | 634 |  | 2020-09-17 15:00 | 15:00 | 23 | 41 | 634 |  |  | 2020-09-14 | B19652¦court services north¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Hearing Room #2 | [5 empty] | 21 | 42 | 427 |  | 2020-09-17 09:00 | 9:00 | 21 | 42 | 427 |  |  | 2020-09-14 | B70485¦Hearing Room #2¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lower Hallway | [5 empty] | 22 | 27 | 464 |  | 2020-09-17 15:00 | 15:00 | 22 | 27 | 464 |  | low | 2020-09-14 | B20016¦Lower Hallway¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Women's Washroom, 16th Floor | [5 empty] | 21 | 45 | 699 |  | 2020-09-17 15:00 | 15:00 | 21 | 45 | 699 |  |  | 2020-09-14 | B25398¦OTHER Women's Washroom, 16th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | OTHER | [5 empty] | 21 | 27 | 462 | Courtroom 1-2-3 | 2020-09-17 15:00 | 15:00 | 21 | 27 | 462 |  | low | 2020-09-14 | B20016¦OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | court service south | [5 empty] | 23 | 42 | 630 |  | 2020-09-17 15:00 | 15:00 | 23 | 42 | 630 |  |  | 2020-09-14 | B19652¦court service south¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER elevator Lobby, 16th Floor | [5 empty] | 22 | 45 | 703 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 703 |  |  | 2020-09-14 | B25398¦OTHER elevator Lobby, 16th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Elevators | [5 empty] | 22 | 41 | 412 |  | 2020-09-17 09:00 | 9:00 | 22 | 41 | 412 |  |  | 2020-09-14 | B70485¦Elevators¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation | [5 empty] | 21 | 28 | 472 |  | 2020-09-17 15:00 | 15:00 | 21 | 28 | 472 |  | low | 2020-09-14 | B20016¦Family Mediation¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | court service entrance vestibule | [5 empty] | 23 | 42 | 614 |  | 2020-09-17 15:00 | 15:00 | 23 | 42 | 614 |  |  | 2020-09-14 | B19652¦court service entrance vestibule¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation Across Stairs | [5 empty] | 20 | 27 | 484 |  | 2020-09-17 15:00 | 15:00 | 20 | 27 | 484 |  | low | 2020-09-14 | B20016¦Family Mediation Across Stairs¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, West, 15th Floor | [5 empty] | 21 | 49 | 720 |  | 2020-09-17 15:00 | 15:00 | 21 | 49 | 720 |  |  | 2020-09-14 | B25398¦OTHER Office Area, West, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 1st floor stair landing court service entrance vestibule | [5 empty] | 22 | 44 | 536 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 536 |  |  | 2020-09-14 | B19652¦1st floor stair landing court service entrance vestibule¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Justice of the Peace Office | [5 empty] | 22 | 30 | 632 |  | 2020-09-17 15:00 | 15:00 | 22 | 30 | 632 |  | low | 2020-09-14 | B20016¦Justice of the Peace Office¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Outdoors |  |  | 16 | 42 | 408 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70485¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North West, 15th Floor | [5 empty] | 21 | 48 | 723 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 723 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North West, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Holding Cell | [5 empty] | 21 | 28 | 463 |  | 2020-09-17 15:00 | 15:00 | 21 | 28 | 463 |  | low | 2020-09-14 | B20016¦Holding Cell¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North, 15th Floor | [5 empty] | 21 | 48 | 716 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 716 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Courtroom 1 | [5 empty] | 21 | 27 | 428 |  | 2020-09-17 15:00 | 15:00 | 21 | 27 | 428 |  | low | 2020-09-14 | B20016¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Main Lobby | [5 empty] | 20 | 40 | 453 |  | 2020-09-17 15:00 | 15:00 | 20 | 40 | 453 |  | caution | 2020-09-14 | B19523¦Main Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Front Security Desk | [5 empty] | 20 | 51 | 510 |  | 2020-09-17 09:00 | 9:00 | 20 | 51 | 510 |  |  | 2020-09-14 | B20705¦Front Security Desk¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North East, 15th Floor | [5 empty] | 21 | 47 | 715 |  | 2020-09-17 15:00 | 15:00 | 21 | 47 | 715 |  |  | 2020-09-14 | B25398¦OTHER Office Area, North East, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Holding Cell | [5 empty] | 21 | 37 | 455 |  | 2020-09-17 15:00 | 15:00 | 21 | 37 | 455 |  | caution | 2020-09-14 | B19523¦Holding Cell¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family Law Reception | [5 empty] | 22 | 40 | 445 |  | 2020-09-17 09:00 | 9:00 | 22 | 40 | 445 |  | caution | 2020-09-14 | B20705¦Family Law Reception¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 1 | [5 empty] | 21 | 39 | 440 |  | 2020-09-17 15:00 | 15:00 | 21 | 39 | 440 |  | caution | 2020-09-14 | B19523¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Are, East, 15th Floor | [5 empty] | 21 | 47 | 713 |  | 2020-09-17 15:00 | 15:00 | 21 | 47 | 713 |  |  | 2020-09-14 | B25398¦OTHER Office Are, East, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Court Services | [5 empty] | 21 | 40 | 487 |  | 2020-09-17 15:00 | 15:00 | 21 | 40 | 487 |  | caution | 2020-09-14 | B19523¦Court Services¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Criminal Court Inquiry | [5 empty] | 22 | 41 | 475 |  | 2020-09-17 09:00 | 9:00 | 22 | 41 | 475 |  |  | 2020-09-14 | B20705¦Criminal Court Inquiry¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South East, 15th Floor | [5 empty] | 21 | 46 | 720 |  | 2020-09-17 15:00 | 15:00 | 21 | 46 | 720 |  |  | 2020-09-14 | B25398¦OTHER Office Area, South East, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | JP Office | [5 empty] | 21 | 38 | 477 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 477 |  | caution | 2020-09-14 | B19523¦JP Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | OPP Office | [5 empty] | 21 | 38 | 435 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 435 |  | caution | 2020-09-14 | B19523¦OPP Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South, 15th Floor | [5 empty] | 21 | 46 | 720 |  | 2020-09-17 15:00 | 15:00 | 21 | 46 | 720 |  |  | 2020-09-14 | B25398¦OTHER Office Area, South, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Crown Attorney Office | [5 empty] | 22 | 40 | 467 |  | 2020-09-17 15:00 | 15:00 | 22 | 40 | 467 |  | caution | 2020-09-14 | B19523¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family/Civil Waiting Area | [5 empty] | 22 | 44 | 446 |  | 2020-09-17 09:00 | 9:00 | 22 | 44 | 446 |  |  | 2020-09-14 | B20705¦Family/Civil Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 41 | 478 |  | 2020-09-17 15:00 | 15:00 | 22 | 41 | 478 |  |  | 2020-09-14 | B19523¦VWAP Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Reception, 15th Floor | [5 empty] | 22 | 46 | 712 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 712 |  |  | 2020-09-14 | B25398¦OTHER Reception, 15th Floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 23 | 38 | 515 |  | 2020-09-17 15:00 | 15:00 | 23 | 38 | 515 |  | caution | 2020-09-14 | B19523¦VWAP Office¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Court Support Office | [5 empty] | 23 | 41 | 497 |  | 2020-09-17 09:00 | 9:00 | 23 | 41 | 497 |  |  | 2020-09-14 | B20705¦Court Support Office¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 5 | [5 empty] | 22 | 36 | 443 |  | 2020-09-17 15:00 | 15:00 | 22 | 36 | 443 |  | caution | 2020-09-14 | B19523¦Courtroom 5¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Mail Room, 15th Floor OTHER | [5 empty] | 21 | 48 | 720 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 720 |  |  | 2020-09-14 | B25398¦Corridor adj. to Mail Room, 15th Floor OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Remote Testimony Room | [5 empty] | 21 | 37 | 434 |  | 2020-09-17 15:00 | 15:00 | 21 | 37 | 434 |  | caution | 2020-09-14 | B19523¦Remote Testimony Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Conference Room 2 | [5 empty] | 21 | 39 | 429 |  | 2020-09-17 15:00 | 15:00 | 21 | 39 | 429 |  | caution | 2020-09-14 | B19523¦Conference Room 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 15th Floor OTHER | [5 empty] | 21 | 47 | 710 |  | 2020-09-17 15:00 | 15:00 | 21 | 47 | 710 |  |  | 2020-09-14 | B25398¦Elevator Lobby, 15th Floor OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 20-24 Waiting Area | [5 empty] | 23 | 40 | 453 |  | 2020-09-17 09:00 | 9:00 | 23 | 40 | 453 |  | caution | 2020-09-14 | B20705¦Courtroom 20-24 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 | [5 empty] | 21 | 39 | 433 |  | 2020-09-17 15:00 | 15:00 | 21 | 39 | 433 |  | caution | 2020-09-14 | B19523¦Courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | reception area | [5 empty] | 23 | 46 | 518 |  | 2020-09-17 12:00 | 12:00 | 23 | 46 | 518 |  |  | 2020-09-14 | B70003¦reception area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 Waiting Area | [5 empty] | 21 | 38 | 442 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 442 |  | caution | 2020-09-14 | B19523¦Courtroom 3 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 2 | [5 empty] | 19 | 52 | 507 |  | 2020-09-17 15:00 | 15:00 | 19 | 52 | 507 |  |  | 2020-09-14 | B11586¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Outdoors |  |  | 19 | 42 | 685 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B25398¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Front of main hallway | [5 empty] | 22 | 47 | 512 |  | 2020-09-17 12:00 | 12:00 | 22 | 47 | 512 |  |  | 2020-09-14 | B70003¦Front of main hallway¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 4-6 Waiting Area | [5 empty] | 23 | 39 | 450 |  | 2020-09-17 09:00 | 9:00 | 23 | 39 | 450 |  | caution | 2020-09-14 | B20705¦Courtroom 4-6 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 20 | 49 | 493 | Crown attorney beaton’s office | 2020-09-17 15:00 | 15:00 | 20 | 49 | 493 |  |  | 2020-09-14 | B11586¦OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 21 | 49 | 510 |  | 2020-09-17 15:00 | 15:00 | 21 | 49 | 510 |  |  | 2020-09-14 | B11586¦OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 1-3 Waiting Area | [5 empty] | 23 | 38 | 485 |  | 2020-09-17 09:00 | 9:00 | 23 | 38 | 485 |  | caution | 2020-09-14 | B20705¦Courtroom 1-3 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 22 | 49 | 491 | outside of 502 | 2020-09-17 12:00 | 12:00 | 22 | 49 | 491 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown attorney admin area | [5 empty] | 21 | 48 | 528 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 528 |  |  | 2020-09-14 | B11586¦Crown attorney admin area¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 50 | 469 | public area | 2020-09-17 12:00 | 12:00 | 21 | 50 | 469 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom waiting area | [5 empty] | 22 | 45 | 494 |  | 2020-09-17 15:00 | 15:00 | 22 | 45 | 494 |  |  | 2020-09-14 | B11586¦Courtroom waiting area¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 51 | 472 | judge area | 2020-09-17 12:00 | 12:00 | 21 | 51 | 472 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 52 | 500 | outside of 503 | 2020-09-17 12:00 | 12:00 | 21 | 52 | 500 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 38 | 459 |  | 2020-09-17 15:00 | 15:00 | 20 | 38 | 459 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 | [5 empty] | 21 | 40 | 517 |  | 2020-09-17 15:00 | 15:00 | 21 | 40 | 517 |  | caution | 2020-09-14 | B11586¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 52 | 493 | public area | 2020-09-17 12:00 | 12:00 | 21 | 52 | 493 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 | [5 empty] | 21 | 40 | 517 |  | 2020-09-17 15:00 | 15:00 | 21 | 40 | 517 |  | caution | 2020-09-14 | B11586¦Courtroom 1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 39 | 479 |  | 2020-09-17 15:00 | 15:00 | 20 | 39 | 479 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 53 | 492 | judge area | 2020-09-17 12:00 | 12:00 | 20 | 53 | 492 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | 2nd Floor Holding Cell | [5 empty] | 21 | 41 | 478 |  | 2020-09-17 15:00 | 15:00 | 21 | 41 | 478 |  |  | 2020-09-14 | B11586¦2nd Floor Holding Cell¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 | [5 empty] | 20 | 39 | 462 |  | 2020-09-17 15:00 | 15:00 | 20 | 39 | 462 |  | caution | 2020-09-14 | B19523¦Courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 54 | 526 | outside of 506 | 2020-09-17 12:00 | 12:00 | 20 | 54 | 526 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Police Court Bureau | [5 empty] | 21 | 39 | 462 |  | 2020-09-17 15:00 | 15:00 | 21 | 39 | 462 |  | caution | 2020-09-14 | B19523¦Police Court Bureau¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 54 | 563 | public area | 2020-09-17 12:00 | 12:00 | 20 | 54 | 563 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 Waiting Area | [5 empty] | 21 | 39 | 465 |  | 2020-09-17 15:00 | 15:00 | 21 | 39 | 465 |  | caution | 2020-09-14 | B19523¦Courtroom 4 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 55 | 572 | judge area | 2020-09-17 12:00 | 12:00 | 20 | 55 | 572 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Judge office | [5 empty] | 21 | 39 | 462 |  | 2020-09-17 15:00 | 15:00 | 21 | 39 | 462 |  | caution | 2020-09-14 | B11586¦Judge office¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 56 | 551 | outside of 509 | 2020-09-17 12:00 | 12:00 | 20 | 56 | 551 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 54 | 500 | public area | 2020-09-17 12:00 | 12:00 | 20 | 54 | 500 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | court admin office | [5 empty] | 19 | 55 | 534 |  | 2020-09-17 15:00 | 15:00 | 19 | 55 | 534 |  |  | 2020-09-14 | B11586¦court admin office¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 7-9 Waiting Room | [5 empty] | 23 | 39 | 461 |  | 2020-09-17 09:00 | 9:00 | 23 | 39 | 461 |  | caution | 2020-09-14 | B20705¦Courtroom 7-9 Waiting Room¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 | [5 empty] | 21 | 39 | 430 |  | 2020-09-17 15:00 | 15:00 | 21 | 39 | 430 |  | caution | 2020-09-14 | B19523¦Courtroom 4¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 55 | 506 | judge area | 2020-09-17 12:00 | 12:00 | 20 | 55 | 506 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Main Lobby | [5 empty] | 18 | 54 | 511 |  | 2020-09-17 15:00 | 15:00 | 18 | 54 | 511 |  |  | 2020-09-14 | B11586¦Main Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 39 | 477 |  | 2020-09-17 15:00 | 15:00 | 20 | 39 | 477 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 55 | 538 | outside of 510 | 2020-09-17 12:00 | 12:00 | 20 | 55 | 538 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 40 | 463 |  | 2020-09-17 15:00 | 15:00 | 19 | 40 | 463 |  | caution | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Outdoors |  |  | 16 | 32 | 412 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B11586¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 54 | 638 | public area | 2020-09-17 12:00 | 12:00 | 20 | 54 | 638 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 42 | 465 |  | 2020-09-17 15:00 | 15:00 | 19 | 42 | 465 |  |  | 2020-09-14 | B19523¦Interview Room¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 21 | 54 | 632 | judge area | 2020-09-17 12:00 | 12:00 | 21 | 54 | 632 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Jury Room | [5 empty] | 19 | 41 | 426 |  | 2020-09-17 15:00 | 15:00 | 19 | 41 | 426 |  |  | 2020-09-14 | B19523¦Jury Room¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 10-12 Waiting Area | [5 empty] | 23 | 39 | 472 |  | 2020-09-17 09:00 | 9:00 | 23 | 39 | 472 |  | caution | 2020-09-14 | B20705¦Courtroom 10-12 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Back of main hallway | [5 empty] | 20 | 54 | 558 |  | 2020-09-17 12:00 | 12:00 | 20 | 54 | 558 |  |  | 2020-09-14 | B70003¦Back of main hallway¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Ontario Court | [5 empty] | 21 | 42 | 449 |  | 2020-09-17 15:00 | 15:00 | 21 | 42 | 449 |  |  | 2020-09-14 | B19523¦Ontario Court¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Elevator area | [5 empty] | 20 | 54 | 523 |  | 2020-09-17 12:00 | 12:00 | 20 | 54 | 523 |  |  | 2020-09-14 | B70003¦Elevator area¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 13-14 Waiting Area | [5 empty] | 23 | 39 | 469 |  | 2020-09-17 09:00 | 9:00 | 23 | 39 | 469 |  | caution | 2020-09-14 | B20705¦Courtroom 13-14 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Main entrance | [5 empty] | 22 | 46 | 539 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 539 |  |  | 2020-09-14 | B20979¦Main entrance¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Outdoors |  |  | 19 | 52 | 419 |  |  |  | outside of 444 Yonge St. | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70003¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Judicial Library | [5 empty] | 21 | 40 | 449 |  | 2020-09-17 15:00 | 15:00 | 21 | 40 | 449 |  | caution | 2020-09-14 | B19523¦Judicial Library¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 34-36 Waiting Area | [5 empty] | 23 | 40 | 442 |  | 2020-09-17 09:00 | 9:00 | 23 | 40 | 442 |  | caution | 2020-09-14 | B20705¦Courtroom 34-36 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Front seating area | [5 empty] | 22 | 47 | 409 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 409 |  |  | 2020-09-14 | B18359¦Front seating area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 315 | [5 empty] | 21 | 38 | 440 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 440 |  | caution | 2020-09-14 | B19523¦Office Room 315¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Northwest corridor | [5 empty] | 22 | 47 | 413 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 413 |  |  | 2020-09-14 | B18359¦Northwest corridor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 316 | [5 empty] | 21 | 38 | 428 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 428 |  | caution | 2020-09-14 | B19523¦Office Room 316¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 30-33 Waiting Area | [5 empty] | 23 | 41 | 423 |  | 2020-09-17 09:00 | 9:00 | 23 | 41 | 423 |  |  | 2020-09-14 | B20705¦Courtroom 30-33 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 22 | 48 | 4033 | north side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 4033 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 317 | [5 empty] | 21 | 38 | 438 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 438 |  | caution | 2020-09-14 | B19523¦Office Room 317¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 22 | 48 | 404 | south side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Superior Court | [5 empty] | 21 | 38 | 428 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 428 |  | caution | 2020-09-14 | B19523¦Superior Court¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Crown Attorney Entrance | [5 empty] | 23 | 41 | 447 |  | 2020-09-17 09:00 | 9:00 | 23 | 41 | 447 |  |  | 2020-09-14 | B20705¦Crown Attorney Entrance¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 313 | [5 empty] | 22 | 38 | 429 |  | 2020-09-17 15:00 | 15:00 | 22 | 38 | 429 |  | caution | 2020-09-14 | B19523¦Office Room 313¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 23 | 47 | 407 | north side | 2020-09-17 15:00 | 15:00 | 23 | 47 | 407 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 312 | [5 empty] | 22 | 38 | 445 |  | 2020-09-17 15:00 | 15:00 | 22 | 38 | 445 |  | caution | 2020-09-14 | B19523¦Office Room 312¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 23 | 47 | 404 | south side | 2020-09-17 15:00 | 15:00 | 23 | 47 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Law Association | [5 empty] | 20 | 37 | 436 |  | 2020-09-17 15:00 | 15:00 | 20 | 37 | 436 |  | caution | 2020-09-14 | B19523¦Law Association¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 22 | 47 | 399 | north side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 399 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 22 | 46 | 616 | east | 2020-09-17 15:00 | 15:00 | 22 | 46 | 616 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 22 | 47 | 407 | south side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 407 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 22 | 47 | 406 | north side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 406 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 23 | 45 | 540 | west | 2020-09-17 15:00 | 15:00 | 23 | 45 | 540 |  |  | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 22 | 47 | 407 | south side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 407 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Probation/Parole Waiting Area | [5 empty] | 23 | 38 | 491 |  | 2020-09-17 09:00 | 9:00 | 23 | 38 | 491 |  | caution | 2020-09-14 | B20705¦Probation/Parole Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 22 | 47 | 404 | north side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 404 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 22 | 45 | 658 | south | 2020-09-17 15:00 | 15:00 | 22 | 45 | 658 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 22 | 47 | 401 | south side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 401 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Land Registry Office | [5 empty] | 23 | 38 | 475 |  | 2020-09-17 09:00 | 9:00 | 23 | 38 | 475 |  | caution | 2020-09-14 | B20705¦Land Registry Office¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 22 | 46 | 611 | north | 2020-09-17 15:00 | 15:00 | 22 | 46 | 611 |  |  | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 4th floor waiting area | [5 empty] | 23 | 38 | 445 |  | 2020-09-17 09:00 | 9:00 | 23 | 38 | 445 |  | caution | 2020-09-14 | B20705¦4th floor waiting area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 307 | [5 empty] | 22 | 48 | 731 | south | 2020-09-17 15:00 | 15:00 | 22 | 48 | 731 |  |  | 2020-09-14 | B20979¦Courtroom 307¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 53-55 Waiting Area | [5 empty] | 22 | 38 | 466 |  | 2020-09-17 09:00 | 9:00 | 22 | 38 | 466 |  | caution | 2020-09-14 | B20705¦Courtroom 53-55 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 51-52 Waiting Area | [5 empty] | 23 | 38 | 427 |  | 2020-09-17 09:00 | 9:00 | 23 | 38 | 427 |  | caution | 2020-09-14 | B20705¦Courtroom 51-52 Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 307 | [5 empty] | 22 | 48 | 755 | north | 2020-09-17 15:00 | 15:00 | 22 | 48 | 755 |  |  | 2020-09-14 | B20979¦Courtroom 307¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 6th Floor Waiting Area | [5 empty] | 22 | 37 | 434 |  | 2020-09-17 09:00 | 9:00 | 22 | 37 | 434 |  | caution | 2020-09-14 | B20705¦6th Floor Waiting Area¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 22 | 47 | 760 | east | 2020-09-17 15:00 | 15:00 | 22 | 47 | 760 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Outdoors |  |  | 15 | 44 | 402 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20705¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 23 | 47 | 741 | west | 2020-09-17 15:00 | 15:00 | 23 | 47 | 741 |  |  | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Hallway by courtroom 307 | [5 empty] | 22 | 43 | 556 |  | 2020-09-17 15:00 | 15:00 | 22 | 43 | 556 |  |  | 2020-09-14 | B20979¦Hallway by courtroom 307¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Hallway by courtroom 302 | [5 empty] | 22 | 44 | 525 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 525 |  |  | 2020-09-14 | B20979¦Hallway by courtroom 302¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Social Benefits Tribunal Reception | [5 empty] | 21 | 38 | 406 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 406 |  | caution | 2020-09-14 | B70485¦Social Benefits Tribunal Reception¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 43 | 459 | south | 2020-09-17 15:00 | 15:00 | 22 | 43 | 459 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #3 | [5 empty] | 21 | 38 | 401 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 401 |  | caution | 2020-09-14 | B70485¦SBT Hearing Room #3¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 23 | 43 | 492 | north | 2020-09-17 15:00 | 15:00 | 23 | 43 | 492 |  |  | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #4 | [5 empty] | 21 | 36 | 404 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 404 |  | caution | 2020-09-14 | B70485¦SBT Hearing Room #4¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Basement cells - hallway | [5 empty] | 23 | 41 | 432 |  | 2020-09-17 15:00 | 15:00 | 23 | 41 | 432 |  |  | 2020-09-14 | B20979¦Basement cells - hallway¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | LTB Hearing Room #1 | [5 empty] | 21 | 37 | 407 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 407 |  | caution | 2020-09-14 | B70485¦LTB Hearing Room #1¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Police Office | [5 empty] | 23 | 44 | 557 |  | 2020-09-17 15:00 | 15:00 | 23 | 44 | 557 |  |  | 2020-09-14 | B20979¦Police Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Outdoors |  |  | 20 | 40 | 411 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20979¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Regional Managers Office | [5 empty] | 21 | 37 | 396 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 396 |  | caution | 2020-09-14 | B70485¦Regional Managers Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Main entrance | [5 empty] | 22 | 43 | 458 |  | 2020-09-17 15:00 | 15:00 | 22 | 43 | 458 |  |  | 2020-09-14 | B90636¦Main entrance¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #1 | [5 empty] | 21 | 38 | 397 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 397 |  | caution | 2020-09-14 | B70485¦Mediation Room #1¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 22 | 43 | 428 | north | 2020-09-17 15:00 | 15:00 | 22 | 43 | 428 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Cubes outside RM Office | [5 empty] | 21 | 37 | 400 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 400 |  | caution | 2020-09-14 | B70485¦Cubes outside RM Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 22 | 43 | 433 | south | 2020-09-17 15:00 | 15:00 | 22 | 43 | 433 |  |  | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 22 | 48 | 406 | north side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 406 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 22 | 48 | 403 | south side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 403 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 22 | 43 | 444 | courtroom lobby | 2020-09-17 15:00 | 15:00 | 22 | 43 | 444 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 22 | 48 | 407 | north side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 407 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #2 | [5 empty] | 21 | 37 | 422 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 422 |  | caution | 2020-09-14 | B70485¦Mediation Room #2¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 22 | 48 | 406 | south side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 406 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 22 | 44 | 442 | south | 2020-09-17 15:00 | 15:00 | 22 | 44 | 442 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 22 | 48 | 423 | north side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 423 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Reception/ Administration LTB | [5 empty] | 21 | 36 | 403 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 403 |  | caution | 2020-09-14 | B70485¦Reception/ Administration LTB¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 22 | 44 | 440 | north | 2020-09-17 15:00 | 15:00 | 22 | 44 | 440 |  |  | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 22 | 48 | 412 | south side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 412 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 2nd fl lobby | [5 empty] | 22 | 44 | 441 |  | 2020-09-17 15:00 | 15:00 | 22 | 44 | 441 |  |  | 2020-09-14 | B90636¦2nd fl lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 3rd Floor Elevator Lobby | [5 empty] | 22 | 43 | 436 |  | 2020-09-17 15:00 | 15:00 | 22 | 43 | 436 |  |  | 2020-09-14 | B90636¦3rd Floor Elevator Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Document Area | [5 empty] | 21 | 37 | 416 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 416 |  | caution | 2020-09-14 | B70485¦Document Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 23 | 43 | 447 | west | 2020-09-17 15:00 | 15:00 | 23 | 43 | 447 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 23 | 42 | 433 | east | 2020-09-17 15:00 | 15:00 | 23 | 42 | 433 |  |  | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Copy Room | [5 empty] | 21 | 36 | 410 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 410 |  | caution | 2020-09-14 | B70485¦Copy Room¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 4th floor waiting area | [5 empty] | 23 | 39 | 427 |  | 2020-09-17 15:00 | 15:00 | 23 | 39 | 427 |  | caution | 2020-09-14 | B90636¦4th floor waiting area¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #3 | [5 empty] | 21 | 36 | 404 |  | 2020-09-17 12:00 | 12:00 | 21 | 36 | 404 |  | caution | 2020-09-14 | B70485¦Mediation Room #3¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 211 | [5 empty] | 22 | 43 | 415 | north | 2020-09-17 15:00 | 15:00 | 22 | 43 | 415 |  |  | 2020-09-14 | B90636¦Courtroom 211¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Corner Office | [5 empty] | 21 | 37 | 413 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 413 |  | caution | 2020-09-14 | B70485¦Corner Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 211 | [5 empty] | 22 | 43 | 411 | south | 2020-09-17 15:00 | 15:00 | 22 | 43 | 411 |  |  | 2020-09-14 | B90636¦Courtroom 211¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Hallway by courtroom 211 | [5 empty] | 21 | 42 | 424 |  | 2020-09-17 15:00 | 15:00 | 21 | 42 | 424 |  |  | 2020-09-14 | B90636¦Hallway by courtroom 211¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Side Entry Door | [5 empty] | 21 | 38 | 460 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 460 |  | caution | 2020-09-14 | B70485¦Side Entry Door¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Outdoors |  |  | 20 | 40 | 411 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B90636¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Filing Area | [5 empty] | 21 | 38 | 418 |  | 2020-09-17 12:00 | 12:00 | 21 | 38 | 418 |  | caution | 2020-09-14 | B70485¦Filing Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Staff Kitchen | [5 empty] | 21 | 37 | 420 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 420 |  | caution | 2020-09-14 | B70485¦Staff Kitchen¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Hearing Room #2 | [5 empty] | 20 | 41 | 412 |  | 2020-09-17 12:00 | 12:00 | 20 | 41 | 412 |  |  | 2020-09-14 | B70485¦Hearing Room #2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Elevators | [5 empty] | 20 | 44 | 413 |  | 2020-09-17 12:00 | 12:00 | 20 | 44 | 413 |  |  | 2020-09-14 | B70485¦Elevators¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Outdoors |  |  | 16 | 40 | 401 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70485¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Front Security Desk | [5 empty] | 21 | 43 | 478 |  | 2020-09-17 12:00 | 12:00 | 21 | 43 | 478 |  |  | 2020-09-14 | B20705¦Front Security Desk¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family Law Reception | [5 empty] | 21 | 40 | 485 |  | 2020-09-17 12:00 | 12:00 | 21 | 40 | 485 |  | caution | 2020-09-14 | B20705¦Family Law Reception¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Criminal Court Inquiry | [5 empty] | 22 | 40 | 479 |  | 2020-09-17 12:00 | 12:00 | 22 | 40 | 479 |  | caution | 2020-09-14 | B20705¦Criminal Court Inquiry¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family/Civil Waiting Area | [5 empty] | 22 | 42 | 493 |  | 2020-09-17 12:00 | 12:00 | 22 | 42 | 493 |  |  | 2020-09-14 | B20705¦Family/Civil Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 20-24 Waiting Area | [5 empty] | 22 | 39 | 474 |  | 2020-09-17 12:00 | 12:00 | 22 | 39 | 474 |  | caution | 2020-09-14 | B20705¦Courtroom 20-24 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Security Check In | [5 empty] | 20 | 52 | 437 |  | 2020-09-17 15:00 | 15:00 | 20 | 52 | 437 |  |  | 2020-09-14 | B92624¦Security Check In¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 20 | 54 | 456 | West | 2020-09-17 15:00 | 15:00 | 20 | 54 | 456 |  |  | 2020-09-14 | B92624¦Room 701¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Court Support Office | [5 empty] | 22 | 38 | 437 |  | 2020-09-17 12:00 | 12:00 | 22 | 38 | 437 |  | caution | 2020-09-14 | B20705¦Court Support Office¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 20 | 53 | 458 | East | 2020-09-17 15:00 | 15:00 | 20 | 53 | 458 |  |  | 2020-09-14 | B92624¦Room 701¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 20 | 53 | 457 | North | 2020-09-17 15:00 | 15:00 | 20 | 53 | 457 |  |  | 2020-09-14 | B92624¦Room 701¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 701 | [5 empty] | 20 | 51 | 431 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 431 |  |  | 2020-09-14 | B92624¦Hallway by Room 701¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 20 | 53 | 442 | East | 2020-09-17 15:00 | 15:00 | 20 | 53 | 442 |  |  | 2020-09-14 | B92624¦Room 718A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 20 | 52 | 440 | West | 2020-09-17 15:00 | 15:00 | 20 | 52 | 440 |  |  | 2020-09-14 | B92624¦Room 718A¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 25-26 Waiting Area | [5 empty] | 22 | 38 | 436 |  | 2020-09-17 12:00 | 12:00 | 22 | 38 | 436 |  | caution | 2020-09-14 | B20705¦Courtroom 25-26 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718B | [5 empty] | 20 | 51 | 447 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 447 |  |  | 2020-09-14 | B92624¦Room 718B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 718A | [5 empty] | 20 | 49 | 451 |  | 2020-09-17 15:00 | 15:00 | 20 | 49 | 451 |  |  | 2020-09-14 | B92624¦Hallway by Room 718A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717A | [5 empty] | 20 | 52 | 493 |  | 2020-09-17 15:00 | 15:00 | 20 | 52 | 493 |  |  | 2020-09-14 | B92624¦Room 717A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717B | [5 empty] | 20 | 52 | 486 |  | 2020-09-17 15:00 | 15:00 | 20 | 52 | 486 |  |  | 2020-09-14 | B92624¦Room 717B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716A | [5 empty] | 19 | 53 | 482 |  | 2020-09-17 15:00 | 15:00 | 19 | 53 | 482 |  |  | 2020-09-14 | B92624¦Room 716A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716B | [5 empty] | 19 | 53 | 478 |  | 2020-09-17 15:00 | 15:00 | 19 | 53 | 478 |  |  | 2020-09-14 | B92624¦Room 716B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715A | [5 empty] | 20 | 51 | 561 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 561 |  |  | 2020-09-14 | B92624¦Room 715A¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 4-6 Waiting Area | [5 empty] | 22 | 37 | 467 |  | 2020-09-17 12:00 | 12:00 | 22 | 37 | 467 |  | caution | 2020-09-14 | B20705¦Courtroom 4-6 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715B | [5 empty] | 20 | 51 | 481 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 481 |  |  | 2020-09-14 | B92624¦Room 715B¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 1-3 Waiting Area | [5 empty] | 22 | 38 | 465 |  | 2020-09-17 12:00 | 12:00 | 22 | 38 | 465 |  | caution | 2020-09-14 | B20705¦Courtroom 1-3 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 7-9 Waiting Area | [5 empty] | 22 | 37 | 457 |  | 2020-09-17 12:00 | 12:00 | 22 | 37 | 457 |  | caution | 2020-09-14 | B20705¦Courtroom 7-9 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714A | [5 empty] | 19 | 53 | 485 |  | 2020-09-17 15:00 | 15:00 | 19 | 53 | 485 |  |  | 2020-09-14 | B92624¦Room 714A¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 10-12 Waiting Area | [5 empty] | 23 | 37 | 435 |  | 2020-09-17 12:00 | 12:00 | 23 | 37 | 435 |  | caution | 2020-09-14 | B20705¦Courtroom 10-12 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714B | [5 empty] | 19 | 53 | 452 |  | 2020-09-17 15:00 | 15:00 | 19 | 53 | 452 |  |  | 2020-09-14 | B92624¦Room 714B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713A | [5 empty] | 20 | 53 | 481 |  | 2020-09-17 15:00 | 15:00 | 20 | 53 | 481 |  |  | 2020-09-14 | B92624¦Room 713A¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 13-14 Waiting Area | [5 empty] | 23 | 23 | 460 |  | 2020-09-17 12:00 | 12:00 | 23 | 23 | 460 |  | low | 2020-09-14 | B20705¦Courtroom 13-14 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713B | [5 empty] | 20 | 52 | 520 |  | 2020-09-17 15:00 | 15:00 | 20 | 52 | 520 |  |  | 2020-09-14 | B92624¦Room 713B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Escalator, 700 | [5 empty] | 20 | 52 | 438 |  | 2020-09-17 15:00 | 15:00 | 20 | 52 | 438 |  |  | 2020-09-14 | B92624¦Hallway by Escalator, 700¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801A | [5 empty] | 20 | 51 | 417 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 417 |  |  | 2020-09-14 | B92624¦Room 801A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801B | [5 empty] | 20 | 51 | 427 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 427 |  |  | 2020-09-14 | B92624¦Room 801B¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 801A | [5 empty] | 20 | 51 | 421 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 421 |  |  | 2020-09-14 | B92624¦Hallway by Room 801A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Lounge | [5 empty] | 21 | 48 | 439 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 439 |  |  | 2020-09-14 | B92624¦Lounge¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 34-36 Waiting Area | [5 empty] | 23 | 35 | 447 |  | 2020-09-17 12:00 | 12:00 | 23 | 35 | 447 |  | caution | 2020-09-14 | B20705¦Courtroom 34-36 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-1 | [5 empty] | 20.8 | 48.3 | 695 |  | 2020-09-17 15:00 | 15:00 | 20.8 | 48.3 | 695 |  |  | 2020-09-14 | B10644¦Courtroom 2-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Outdoors |  |  | 19 | 50 | 406 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B92624¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 30-33 Waiting Area | [5 empty] | 23 | 37 | 442 |  | 2020-09-17 12:00 | 12:00 | 23 | 37 | 442 |  | caution | 2020-09-14 | B20705¦Courtroom 30-33 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-2 | [5 empty] | 18.9 | 55.8 | 545 |  | 2020-09-17 15:00 | 15:00 | 18.9 | 55.8 | 545 |  |  | 2020-09-14 | B10644¦Courtroom 2-2¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 4th floor waiting area | [5 empty] | 23 | 36 | 454 |  | 2020-09-17 12:00 | 12:00 | 23 | 36 | 454 |  | caution | 2020-09-14 | B20705¦4th floor waiting area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-3 | [5 empty] | 20.5 | 73 | 419 |  | 2020-09-17 15:00 | 15:00 | 20.5 | 73 | 419 |  | high | 2020-09-14 | B10644¦Courtroom 2-3¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Crown Attorney Admin Waiting Area | [5 empty] | 23 | 36 | 446 |  | 2020-09-17 12:00 | 12:00 | 23 | 36 | 446 |  | caution | 2020-09-14 | B20705¦Crown Attorney Admin Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Probation/Parole Waiting Area | [5 empty] | 23 | 37 | 442 |  | 2020-09-17 12:00 | 12:00 | 23 | 37 | 442 |  | caution | 2020-09-14 | B20705¦Probation/Parole Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-4 | [5 empty] | 21.9 | 38.6 | 531 |  | 2020-09-17 15:00 | 15:00 | 21.9 | 38.6 | 531 |  | caution | 2020-09-14 | B10644¦Courtroom 2-4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-5 | [5 empty] | 20.3 | 48 | 390 |  | 2020-09-17 15:00 | 15:00 | 20.3 | 48 | 390 |  |  | 2020-09-14 | B10644¦Courtroom 2-5¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 53-55 Waiting Area | [5 empty] | 22 | 36 | 445 |  | 2020-09-17 12:00 | 12:00 | 22 | 36 | 445 |  | caution | 2020-09-14 | B20705¦Courtroom 53-55 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-6 | [5 empty] | 23.2 | 46.7 | 413 |  | 2020-09-17 15:00 | 15:00 | 23.2 | 46.7 | 413 |  |  | 2020-09-14 | B10644¦Courtroom 2-6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-8 | [5 empty] | 21.1 | 49.1 | 643 |  | 2020-09-17 15:00 | 15:00 | 21.1 | 49.1 | 643 |  |  | 2020-09-14 | B10644¦Courtroom 2-8¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 51-52 Waiting Area | [5 empty] | 22 | 36 | 437 |  | 2020-09-17 12:00 | 12:00 | 22 | 36 | 437 |  | caution | 2020-09-14 | B20705¦Courtroom 51-52 Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 6th Floor Waiting Area | [5 empty] | 22 | 35 | 433 |  | 2020-09-17 12:00 | 12:00 | 22 | 35 | 433 |  | caution | 2020-09-14 | B20705¦6th Floor Waiting Area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Outdoors |  |  | 18 | 31 | 403 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20705¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 3-2 | [5 empty] | 22.2 | 34.5 | 576 |  | 2020-09-17 15:00 | 15:00 | 22.2 | 34.5 | 576 |  | low | 2020-09-14 | B10644¦Courtroom 3-2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Outdoors |  |  | 15 | 34 | 410 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70485¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-1 | [5 empty] | 22.7 | 53.3 | 483 |  | 2020-09-17 15:00 | 15:00 | 22.7 | 53.3 | 483 |  |  | 2020-09-14 | B10644¦Courtroom 4-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-2 | [5 empty] | 20.8 | 50 | 419 |  | 2020-09-17 15:00 | 15:00 | 20.8 | 50 | 419 |  |  | 2020-09-14 | B10644¦Courtroom 4-2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Social Benefits Tribunal Reception | [5 empty] | 22 | 29 | 412 |  | 2020-09-17 15:00 | 15:00 | 22 | 29 | 412 |  | low | 2020-09-14 | B70485¦Social Benefits Tribunal Reception¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-3 | [5 empty] | 25.4 | 50.8 | 405 |  | 2020-09-17 15:00 | 15:00 | 25.4 | 50.8 | 405 |  |  | 2020-09-14 | B10644¦Courtroom 4-3¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #3 | [5 empty] | 22 | 29 | 397 |  | 2020-09-17 15:00 | 15:00 | 22 | 29 | 397 |  | low | 2020-09-14 | B70485¦SBT Hearing Room #3¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #4 | [5 empty] | 22 | 28 | 402 |  | 2020-09-17 15:00 | 15:00 | 22 | 28 | 402 |  | low | 2020-09-14 | B70485¦SBT Hearing Room #4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | LTB Hearing Room #1 | [5 empty] | 22 | 30 | 402 |  | 2020-09-17 15:00 | 15:00 | 22 | 30 | 402 |  | low | 2020-09-14 | B70485¦LTB Hearing Room #1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Regional Managers Office | [5 empty] | 22 | 30 | 405 |  | 2020-09-17 15:00 | 15:00 | 22 | 30 | 405 |  | low | 2020-09-14 | B70485¦Regional Managers Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Cubes outside RM Office | [5 empty] | 21 | 31 | 399 |  | 2020-09-17 15:00 | 15:00 | 21 | 31 | 399 |  | low | 2020-09-14 | B70485¦Cubes outside RM Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #1 | [5 empty] | 21 | 30 | 407 |  | 2020-09-17 15:00 | 15:00 | 21 | 30 | 407 |  | low | 2020-09-14 | B70485¦Mediation Room #1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-4 | [5 empty] | 22.1 | 51.6 | 504 |  | 2020-09-17 15:00 | 15:00 | 22.1 | 51.6 | 504 |  |  | 2020-09-14 | B10644¦Courtroom 4-4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #2 | [5 empty] | 21 | 31 | 405 |  | 2020-09-17 15:00 | 15:00 | 21 | 31 | 405 |  | low | 2020-09-14 | B70485¦Mediation Room #2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-6 | [5 empty] | 22.6 | 51.6 | 380 |  | 2020-09-17 15:00 | 15:00 | 22.6 | 51.6 | 380 |  |  | 2020-09-14 | B10644¦Courtroom 4-6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Reception/ Administration LTB | [5 empty] | 21 | 31 | 414 |  | 2020-09-17 15:00 | 15:00 | 21 | 31 | 414 |  | low | 2020-09-14 | B70485¦Reception/ Administration LTB¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-7 | [5 empty] | 22.4 | 51.1 | 382 |  | 2020-09-17 15:00 | 15:00 | 22.4 | 51.1 | 382 |  |  | 2020-09-14 | B10644¦Courtroom 4-7¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Document Area | [5 empty] | 21 | 31 | 409 |  | 2020-09-17 15:00 | 15:00 | 21 | 31 | 409 |  | low | 2020-09-14 | B70485¦Document Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-8 | [5 empty] | 22.8 | 51.2 | 396 |  | 2020-09-17 15:00 | 15:00 | 22.8 | 51.2 | 396 |  |  | 2020-09-14 | B10644¦Courtroom 4-8¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Copy Room | [5 empty] | 21 | 30 | 404 |  | 2020-09-17 15:00 | 15:00 | 21 | 30 | 404 |  | low | 2020-09-14 | B70485¦Copy Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22.6 | 42.5 | 694 |  | 2020-09-17 15:00 | 15:00 | 22.6 | 42.5 | 694 |  |  | 2020-09-14 | B10644¦Courtroom 5-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-1 | [5 empty] | 21.3 | 54.8 | 395 |  | 2020-09-17 15:00 | 15:00 | 21.3 | 54.8 | 395 |  |  | 2020-09-14 | B10644¦Courtroom 6-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #3 | [5 empty] | 21 | 30 | 408 |  | 2020-09-17 15:00 | 15:00 | 21 | 30 | 408 |  | low | 2020-09-14 | B70485¦Mediation Room #3¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Corner Office | [5 empty] | 20 | 34 | 413 |  | 2020-09-17 15:00 | 15:00 | 20 | 34 | 413 |  | low | 2020-09-14 | B70485¦Corner Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Side Entry Door | [5 empty] | 20 | 35 | 427 |  | 2020-09-17 15:00 | 15:00 | 20 | 35 | 427 |  | caution | 2020-09-14 | B70485¦Side Entry Door¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Filing Area | [5 empty] | 21 | 33 | 414 |  | 2020-09-17 15:00 | 15:00 | 21 | 33 | 414 |  | low | 2020-09-14 | B70485¦Filing Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Staff Kitchen | [5 empty] | 21 | 32 | 418 |  | 2020-09-17 15:00 | 15:00 | 21 | 32 | 418 |  | low | 2020-09-14 | B70485¦Staff Kitchen¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Hearing Room #2 | [5 empty] | 21 | 33 | 412 |  | 2020-09-17 15:00 | 15:00 | 21 | 33 | 412 |  | low | 2020-09-14 | B70485¦Hearing Room #2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Elevators | [5 empty] | 19 | 39 | 420 |  | 2020-09-17 15:00 | 15:00 | 19 | 39 | 420 |  | caution | 2020-09-14 | B70485¦Elevators¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Front Security Desk | [5 empty] | 22 | 33 | 444 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 444 |  | low | 2020-09-14 | B20705¦Front Security Desk¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family Law Reception Area | [5 empty] | 22 | 33 | 459 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 459 |  | low | 2020-09-14 | B20705¦Family Law Reception Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Criminal Court Inquiry Area | [5 empty] | 22 | 33 | 473 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 473 |  | low | 2020-09-14 | B20705¦Criminal Court Inquiry Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family/Civil Division Waiting Area | [5 empty] | 22 | 34 | 505 |  | 2020-09-17 15:00 | 15:00 | 22 | 34 | 505 |  | low | 2020-09-14 | B20705¦Family/Civil Division Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Court Support Office | [5 empty] | 22 | 33 | 457 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 457 |  | low | 2020-09-14 | B20705¦Court Support Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 20-24 Waiting Area | [5 empty] | 20 | 42 | 459 |  | 2020-09-17 15:00 | 15:00 | 20 | 42 | 459 |  |  | 2020-09-14 | B20705¦Courtroom 20-24 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 25-26 Waiting Area | [5 empty] | 22 | 35 | 443 |  | 2020-09-17 15:00 | 15:00 | 22 | 35 | 443 |  | caution | 2020-09-14 | B20705¦Courtroom 25-26 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 4-6 Waiting Area | [5 empty] | 22 | 32 | 467 |  | 2020-09-17 15:00 | 15:00 | 22 | 32 | 467 |  | low | 2020-09-14 | B20705¦Courtroom 4-6 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 1-3 Waiting Area | [5 empty] | 22 | 33 | 484 |  | 2020-09-17 15:00 | 15:00 | 22 | 33 | 484 |  | low | 2020-09-14 | B20705¦Courtroom 1-3 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 7-9 Waiting Area | [5 empty] | 22 | 32 | 447 |  | 2020-09-17 15:00 | 15:00 | 22 | 32 | 447 |  | low | 2020-09-14 | B20705¦Courtroom 7-9 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 10-12 Waiting Area | [5 empty] | 22 | 32 | 440 |  | 2020-09-17 15:00 | 15:00 | 22 | 32 | 440 |  | low | 2020-09-14 | B20705¦Courtroom 10-12 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 13-14 Waiting Area | [5 empty] | 22 | 32 | 423 |  | 2020-09-17 15:00 | 15:00 | 22 | 32 | 423 |  | low | 2020-09-14 | B20705¦Courtroom 13-14 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 34-36 Waiting Area | [5 empty] | 23 | 30 | 439 |  | 2020-09-17 15:00 | 15:00 | 23 | 30 | 439 |  | low | 2020-09-14 | B20705¦Courtroom 34-36 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 30-33 Waiting Area | [5 empty] | 23 | 32 | 432 |  | 2020-09-17 15:00 | 15:00 | 23 | 32 | 432 |  | low | 2020-09-14 | B20705¦Courtroom 30-33 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Crown Attorney Wing Entrance | [5 empty] | 23 | 33 | 444 |  | 2020-09-17 15:00 | 15:00 | 23 | 33 | 444 |  | low | 2020-09-14 | B20705¦Crown Attorney Wing Entrance¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Probation/Parole Waiting Area | [5 empty] | 23 | 31 | 572 |  | 2020-09-17 15:00 | 15:00 | 23 | 31 | 572 |  | low | 2020-09-14 | B20705¦Probation/Parole Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 4th floor waiting area | [5 empty] | 23 | 31 | 446 |  | 2020-09-17 15:00 | 15:00 | 23 | 31 | 446 |  | low | 2020-09-14 | B20705¦4th floor waiting area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 53-55 Waiting Area | [5 empty] | 23 | 30 | 441 |  | 2020-09-17 15:00 | 15:00 | 23 | 30 | 441 |  | low | 2020-09-14 | B20705¦Courtroom 53-55 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 51-52 Waiting Area | [5 empty] | 23 | 31 | 463 |  | 2020-09-17 15:00 | 15:00 | 23 | 31 | 463 |  | low | 2020-09-14 | B20705¦Courtroom 51-52 Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 6th Floor Waiting Area | [5 empty] | 23 | 31 | 436 |  | 2020-09-17 15:00 | 15:00 | 23 | 31 | 436 |  | low | 2020-09-14 | B20705¦6th Floor Waiting Area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Outdoors |  |  | 19 | 24 | 407 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20705¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 22 | 48 | 404 | north side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 404 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 22 | 47 | 411 | south side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 411 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 22 | 47 | 403 | north side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 403 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 22 | 47 | 407 | south side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 407 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 22 | 47 | 404 | north side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 404 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 22 | 47 | 399 | south side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 399 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 22 | 48 | 398 | north side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 398 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 22 | 48 | 400 | south side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 400 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | northeast corridor | [5 empty] | 22 | 48 | 408 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 408 |  |  | 2020-09-14 | B18359¦northeast corridor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 22 | 48 | 403 | north side | 2020-09-17 15:00 | 15:00 | 22 | 48 | 403 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 22 | 47 | 400 | south side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 400 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 22 | 44 | 400 | north side | 2020-09-17 15:00 | 15:00 | 22 | 44 | 400 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 22 | 47 | 401 | south side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 401 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 22 | 47 | 400 | north side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 400 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 22 | 47 | 400 | south side | 2020-09-17 15:00 | 15:00 | 22 | 47 | 400 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Outdoors |  |  | 18 | 46 | 390 |  |  |  | outside of 15 Grosvenor Ave. | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B18359¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | reception area | [5 empty] | 21 | 49 | 525 |  | 2020-09-17 15:00 | 15:00 | 21 | 49 | 525 |  |  | 2020-09-14 | B70003¦reception area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | front of main hallway | [5 empty] | 21 | 48 | 521 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 521 |  |  | 2020-09-14 | B70003¦front of main hallway¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 48 | 512 | outside of 502 | 2020-09-17 15:00 | 15:00 | 21 | 48 | 512 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 48 | 490 | public area | 2020-09-17 15:00 | 15:00 | 21 | 48 | 490 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 48 | 484 | judge area | 2020-09-17 15:00 | 15:00 | 21 | 48 | 484 |  |  | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 50 | 507 | outside of 503 | 2020-09-17 15:00 | 15:00 | 20 | 50 | 507 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 50 | 516 | public area | 2020-09-17 15:00 | 15:00 | 20 | 50 | 516 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 50 | 515 | judge area | 2020-09-17 15:00 | 15:00 | 20 | 50 | 515 |  |  | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 51 | 513 | outside of 506 | 2020-09-17 15:00 | 15:00 | 20 | 51 | 513 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 21 | 50 | 500 | public area | 2020-09-17 15:00 | 15:00 | 21 | 50 | 500 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 50 | 491 | judge area | 2020-09-17 15:00 | 15:00 | 20 | 50 | 491 |  |  | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 51 | 509 | outside of 509 | 2020-09-17 15:00 | 15:00 | 20 | 51 | 509 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 52 | 517 | public area | 2020-09-17 15:00 | 15:00 | 20 | 52 | 517 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 51 | 533 | judge area | 2020-09-17 15:00 | 15:00 | 20 | 51 | 533 |  |  | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 52 | 515 | outside of 510 | 2020-09-17 15:00 | 15:00 | 20 | 52 | 515 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 52 | 537 | public area | 2020-09-17 15:00 | 15:00 | 20 | 52 | 537 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 52 | 525 | judge area | 2020-09-17 15:00 | 15:00 | 20 | 52 | 525 |  |  | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Back of main hallway | [5 empty] | 20 | 51 | 519 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 519 |  |  | 2020-09-14 | B70003¦Back of main hallway¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | elevator area | [5 empty] | 20 | 51 | 527 |  | 2020-09-17 15:00 | 15:00 | 20 | 51 | 527 |  |  | 2020-09-14 | B70003¦elevator area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Outdoors |  |  | 18 | 48 | 400 |  |  |  | outside of 444 Yonge St. | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70003¦Outdoors¦¦Sep-17-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B20893 | B20893 - 75 Mulcaster St. - Barrie | Courtroom 7,8,9 | [5 empty] | 21.4 | 29 | 444 |  | 2020-09-18 09:00 | 9:00 | 21.4 | 29 | 444 |  | low | 2020-09-14 | B20893¦Courtroom 7,8,9¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B92347 | B92347 - 75 Mulcaster Street - Barrie | Courtroom 15 | [5 empty] | 20.8 | 33 | 461 |  | 2020-09-18 09:00 | 9:00 | 20.8 | 33 | 461 |  | low | 2020-09-14 | B92347¦Courtroom 15¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 101 | [5 empty] | 20 | 44 | 514 |  | 2020-09-18 09:00 | 9:00 | 20 | 44 | 514 |  |  | 2020-09-14 | B19512¦Courtroom 101¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 200 | [5 empty] | 21 | 45 | 524 |  | 2020-09-18 09:00 | 9:00 | 21 | 45 | 524 |  |  | 2020-09-14 | B19512¦Courtroom 200¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 201 | [5 empty] | 24 | 22 | 450 |  | 2020-09-18 09:00 | 9:00 | 24 | 22 | 450 |  | low | 2020-09-14 | B19512¦Courtroom 201¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Outdoors |  |  | 8 | 60 | [5 empty] | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B19512¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Outdoors |  |  | 7 | 66 | 680 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B25602¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 101 | [5 empty] | 22 | 41 |  |  | 2020-09-18 09:00 | 9:00 | 22 | 41 |  |  |  | 2020-09-14 | B20080¦Courtroom 101¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 3 | [5 empty] | 23 | 33 | 304 |  | 2020-09-18 09:00 | 9:00 | 23 | 33 | 304 |  | low | 2020-09-14 | B24638¦Courtroom 3¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 201 | [5 empty] | 22 | 34 | 428 |  | 2020-09-18 09:00 | 9:00 | 22 | 34 | 428 |  | low | 2020-09-14 | B20080¦Courtroom 201¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd fl lobby | [5 empty] | 20 | 34 | 553 |  | 2020-09-18 09:00 | 9:00 | 20 | 34 | 553 |  | low | 2020-09-14 | B20226¦2nd fl lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 1 | [5 empty] | 23 | 36 | 506 |  | 2020-09-18 09:00 | 9:00 | 23 | 36 | 506 |  | caution | 2020-09-14 | B24638¦Courtroom 1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 202 | [5 empty] | 23 | 34 | 443 |  | 2020-09-18 09:00 | 9:00 | 23 | 34 | 443 |  | low | 2020-09-14 | B20080¦Courtroom 202¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 2 | [5 empty] | 20 | 36 | 506 |  | 2020-09-18 09:00 | 9:00 | 20 | 36 | 506 |  | caution | 2020-09-14 | B20226¦Courtroom 2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 301 | [5 empty] | 23 | 34 | 413 |  | 2020-09-18 09:00 | 9:00 | 23 | 34 | 413 |  | low | 2020-09-14 | B20080¦Courtroom 301¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 1 | [5 empty] | 21 | 37 | 475 |  | 2020-09-18 09:00 | 9:00 | 21 | 37 | 475 |  | caution | 2020-09-14 | B20226¦Courtroom 1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 303 | [5 empty] | 22 | 34 | 487 |  | 2020-09-18 09:00 | 9:00 | 22 | 34 | 487 |  | low | 2020-09-14 | B20080¦Courtroom 303¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 21 | 38 | 618 |  | 2020-09-18 09:00 | 9:00 | 21 | 38 | 618 |  | caution | 2020-09-14 | B20226¦2nd Floor Holding Cell¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Outdoors |  |  | 21 | 30 | 308 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B24638¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom B01 | [5 empty] | 22 | 34 |  |  | 2020-09-18 09:00 | 9:00 | 22 | 34 |  |  | low | 2020-09-14 | B20080¦Courtroom B01¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 3 | [5 empty] | 21 | 28 | 447 |  | 2020-09-18 09:00 | 9:00 | 21 | 28 | 447 |  | low | 2020-09-14 | B20226¦Courtroom 3¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Outdoors |  |  | 11 | 67 | 420 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20080¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Outdoors |  |  | 6 | 80 | 426 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B12948¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 1 | [5 empty] | 19 | 41 | 431 |  | 2020-09-18 09:00 | 9:00 | 19 | 41 | 431 |  |  | 2020-09-14 | B12948¦Courtroom 1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 | [5 empty] | 20 | 36 | 429 |  | 2020-09-18 09:00 | 9:00 | 20 | 36 | 429 |  | caution | 2020-09-14 | B12948¦Courtroom 2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 | [5 empty] | 21 | 35 | 439 |  | 2020-09-18 09:00 | 9:00 | 21 | 35 | 439 |  | caution | 2020-09-14 | B12948¦Courtroom 3¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Outdoors |  |  | 3 | 60 | 428 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20226¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 | [5 empty] | 21 | 34 | 441 |  | 2020-09-18 09:00 | 9:00 | 21 | 34 | 441 |  | low | 2020-09-14 | B12948¦Courtroom 4¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 | [5 empty] | 21 | 35 | 450 |  | 2020-09-18 09:00 | 9:00 | 21 | 35 | 450 |  | caution | 2020-09-14 | B12948¦Courtroom 5¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Outdoors |  |  | 4 | 59 | 432 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70050¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 6 | [5 empty] | 20 | 34 | 440 |  | 2020-09-18 09:00 | 9:00 | 20 | 34 | 440 |  | low | 2020-09-14 | B12948¦Courtroom 6¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Cell Basement | [5 empty] | 22 | 35 | 450 |  | 2020-09-18 09:00 | 9:00 | 22 | 35 | 450 |  | caution | 2020-09-14 | B12948¦Cell Basement¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 | [5 empty] | 20 | 49 | 422 |  | 2020-09-18 09:00 | 9:00 | 20 | 49 | 422 |  |  | 2020-09-14 | B14209¦Courtroom 1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration Office Waiting Area | [5 empty] | 22 | 34 | 450 |  | 2020-09-18 09:00 | 9:00 | 22 | 34 | 450 |  | low | 2020-09-14 | B12948¦Administration Office Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration office | [5 empty] | 22 | 35 | 448 |  | 2020-09-18 09:00 | 9:00 | 22 | 35 | 448 |  | caution | 2020-09-14 | B12948¦Administration office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 - waiting area | [5 empty] | 22 | 40 | 413 |  | 2020-09-18 09:00 | 9:00 | 22 | 40 | 413 |  | caution | 2020-09-14 | B14209¦Courtroom 1 - waiting area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 | [5 empty] | 20 | 40 | 453 |  | 2020-09-18 09:00 | 9:00 | 20 | 40 | 453 |  | caution | 2020-09-14 | B14209¦Courtroom 2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Crown attorney admin area | [5 empty] | 22 | 35 | 548 |  | 2020-09-18 09:00 | 9:00 | 22 | 35 | 548 |  | caution | 2020-09-14 | B12948¦Crown attorney admin area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main entrance | [5 empty] | 21 | 34 | 448 |  | 2020-09-18 09:00 | 9:00 | 21 | 34 | 448 |  | low | 2020-09-14 | B12948¦Main entrance¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 - waiting room | [5 empty] | 21 | 37 | 425 |  | 2020-09-18 09:00 | 9:00 | 21 | 37 | 425 |  | caution | 2020-09-14 | B14209¦Courtroom 2 - waiting room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Main Lobby | [5 empty] | 19 | 44 | 533 |  | 2020-09-18 09:00 | 9:00 | 19 | 44 | 533 |  |  | 2020-09-14 | B70050¦Main Lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main Entrance Waiting Area | [5 empty] | 21 | 36 | 446 |  | 2020-09-18 09:00 | 9:00 | 21 | 36 | 446 |  | caution | 2020-09-14 | B12948¦Main Entrance Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Court Room 1 Waiting Area | [5 empty] | 21 | 35 | 448 |  | 2020-09-18 09:00 | 9:00 | 21 | 35 | 448 |  | caution | 2020-09-14 | B12948¦Court Room 1 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room | [5 empty] | 20 | 40 | 423 |  | 2020-09-18 09:00 | 9:00 | 20 | 40 | 423 |  | caution | 2020-09-14 | B14209¦Hearing Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 Waiting Area | [5 empty] | 22 | 33 | 437 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 437 |  | low | 2020-09-14 | B12948¦Courtroom 2 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 1 | [5 empty] | 20 | 47 | 473 |  | 2020-09-18 09:00 | 9:00 | 20 | 47 | 473 |  |  | 2020-09-14 | B70050¦Courtroom 1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 8 | [5 empty] | 22 | 43 | 427 |  | 2020-09-18 09:00 | 9:00 | 22 | 43 | 427 |  |  | 2020-09-14 | B25683¦Courtroom 8¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 Waiting Area | [5 empty] | 22 | 33 | 452 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 452 |  | low | 2020-09-14 | B12948¦Courtroom 3 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 11 | [5 empty] | 22 | 43 | 427 |  | 2020-09-18 09:00 | 9:00 | 22 | 43 | 427 |  |  | 2020-09-14 | B25683¦Courtroom 11¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 20 | 42 | 442 |  | 2020-09-18 09:00 | 9:00 | 20 | 42 | 442 |  |  | 2020-09-14 | B70050¦2nd Floor Holding Cell¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 9 | [5 empty] | 23 | 40 | 432 |  | 2020-09-18 09:00 | 9:00 | 23 | 40 | 432 |  | caution | 2020-09-14 | B25683¦Courtroom 9¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room, Judge’s Chamber | [5 empty] | 20 | 40 | 413 |  | 2020-09-18 09:00 | 9:00 | 20 | 40 | 413 |  | caution | 2020-09-14 | B14209¦Hearing Room, Judge’s Chamber¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 Waiting Area | [5 empty] | 22 | 33 | 439 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 439 |  | low | 2020-09-14 | B12948¦Courtroom 5 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Outdoors |  |  | 10 | 48 | 501 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B90838¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room - Waiting area | [5 empty] | 22 | 39 | 431 |  | 2020-09-18 09:00 | 9:00 | 22 | 39 | 431 |  | caution | 2020-09-14 | B14209¦Hearing Room - Waiting area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Yannick Bedard Office - 2nd Floor | [5 empty] | 21 | 43 | 497 |  | 2020-09-18 09:00 | 9:00 | 21 | 43 | 497 |  |  | 2020-09-14 | B70050¦Yannick Bedard Office - 2nd Floor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 2 | [5 empty] | 21 | 43 | 509 |  | 2020-09-18 09:00 | 9:00 | 21 | 43 | 509 |  |  | 2020-09-14 | B70050¦Courtroom 2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Courtroom 101 Courtroom 102 | [5 empty] | 21 | 32 | 431 | humidification not on yet | 2020-09-18 09:00 | 9:00 | 21 | 32 | 431 |  | low | 2020-09-14 | B90838¦Courtroom 101 Courtroom 102¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 and 6 Waiting Area | [5 empty] | 22 | 33 | 438 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 438 |  | low | 2020-09-14 | B12948¦Courtroom 4 and 6 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd fl lobby | [5 empty] | 20 | 40 | 440 |  | 2020-09-18 09:00 | 9:00 | 20 | 40 | 440 |  | caution | 2020-09-14 | B70050¦2nd fl lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Front desk | [5 empty] | 21 | 46 | 415 |  | 2020-09-18 09:00 | 9:00 | 21 | 46 | 415 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Front desk¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Main Lobby | [5 empty] | 17 | 45 | 485 |  | 2020-09-18 09:00 | 9:00 | 17 | 45 | 485 |  |  | 2020-09-14 | B19523¦Main Lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Holding Cell | [5 empty] | 18 | 38 | 468 |  | 2020-09-18 09:00 | 9:00 | 18 | 38 | 468 |  | caution | 2020-09-14 | B19523¦Holding Cell¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Front desk | [5 empty] | 21 | 46 | 415 |  | 2020-09-18 09:00 | 9:00 | 21 | 46 | 415 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Front desk¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 1 | [5 empty] | 20 | 36 | 465 |  | 2020-09-18 09:00 | 9:00 | 20 | 36 | 465 |  | caution | 2020-09-14 | B19523¦Courtroom 1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown attorney admin area | [5 empty] | 21 | 46 | 423 |  | 2020-09-18 09:00 | 9:00 | 21 | 46 | 423 |  |  | 2020-09-14 | B14209¦Crown attorney admin area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Court Services | [5 empty] | 20 | 34 | 486 |  | 2020-09-18 09:00 | 9:00 | 20 | 34 | 486 |  | low | 2020-09-14 | B19523¦Court Services¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Print Room | [5 empty] | 21 | 46 | 438 |  | 2020-09-18 09:00 | 9:00 | 21 | 46 | 438 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Print Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | JP Office | [5 empty] | 20 | 34 | 478 |  | 2020-09-18 09:00 | 9:00 | 20 | 34 | 478 |  | low | 2020-09-14 | B19523¦JP Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Assistant Crown Attorney Office (236) | [5 empty] | 21 | 47 | 413 |  | 2020-09-18 09:00 | 9:00 | 21 | 47 | 413 |  |  | 2020-09-14 | B14209¦Assistant Crown Attorney Office (236)¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | OPP Office | [5 empty] | 20 | 33 | 483 |  | 2020-09-18 09:00 | 9:00 | 20 | 33 | 483 |  | low | 2020-09-14 | B19523¦OPP Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office | [5 empty] | 21 | 46 | 407 |  | 2020-09-18 09:00 | 9:00 | 21 | 46 | 407 |  |  | 2020-09-14 | B14209¦Crown Attorney Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Entry/Waiting | [5 empty] | 22 | 33 | 478 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 478 |  | low | 2020-09-14 | B70510¦Entry/Waiting¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Meeting Room (232) | [5 empty] | 21 | 47 | 405 |  | 2020-09-18 09:00 | 9:00 | 21 | 47 | 405 |  |  | 2020-09-14 | B14209¦Crown Attorney Meeting Room (232)¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Lobby | [5 empty] | 22 | 41 | 412 |  | 2020-09-18 09:00 | 9:00 | 22 | 41 | 412 |  |  | 2020-09-14 | B14209¦Court Admin Office Lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room A | [5 empty] | 22 | 32 | 456 |  | 2020-09-18 09:00 | 9:00 | 22 | 32 | 456 |  | low | 2020-09-14 | B70510¦Mediation Room A¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Outdoors |  |  | 10 | 52 | 431 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B19652¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Outdoors |  |  | 15 | 23 | 489 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20289¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Crown Attorney Office | [5 empty] | 20 | 30 | 471 |  | 2020-09-18 09:00 | 9:00 | 20 | 30 | 471 |  | low | 2020-09-14 | B19523¦Crown Attorney Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Center) | [5 empty] | 21 | 35 | 483 |  | 2020-09-18 09:00 | 9:00 | 21 | 35 | 483 |  | caution | 2020-09-14 | B19652¦Courtroom 1 (Center)¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 20 | 40 | 525 | judge | 2020-09-18 09:00 | 9:00 | 20 | 40 | 525 |  | caution | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 21 | 31 | 492 |  | 2020-09-18 09:00 | 9:00 | 21 | 31 | 492 |  | low | 2020-09-14 | B19523¦VWAP Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 20 | 41 | 517 | public | 2020-09-18 09:00 | 9:00 | 20 | 41 | 517 |  |  | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Cubicles | [5 empty] | 21 | 44 | 410 |  | 2020-09-18 09:00 | 9:00 | 21 | 44 | 410 |  |  | 2020-09-14 | B14209¦Court Admin Office Cubicles¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 21 | 29 | 504 |  | 2020-09-18 09:00 | 9:00 | 21 | 29 | 504 |  | low | 2020-09-14 | B19523¦VWAP Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 20 | 40 | 530 | judge | 2020-09-18 09:00 | 9:00 | 20 | 40 | 530 |  | caution | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Judge Dias) | [5 empty] | 21 | 36 | 449 |  | 2020-09-18 09:00 | 9:00 | 21 | 36 | 449 |  | caution | 2020-09-14 | B19652¦Courtroom 1 (Judge Dias)¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 5 | [5 empty] | 20 | 32 | 484 |  | 2020-09-18 09:00 | 9:00 | 20 | 32 | 484 |  | low | 2020-09-14 | B19523¦Courtroom 5¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 21 | 40 | 522 | public | 2020-09-18 09:00 | 9:00 | 21 | 40 | 522 |  | caution | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Remote Testimony Room | [5 empty] | 20 | 33 | 469 |  | 2020-09-18 09:00 | 9:00 | 20 | 33 | 469 |  | low | 2020-09-14 | B19523¦Remote Testimony Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 37 | 466 | Superior judges chamber | 2020-09-18 09:00 | 9:00 | 21 | 37 | 466 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Holding Cell corridor | [5 empty] | 22 | 41 | 407 |  | 2020-09-18 09:00 | 9:00 | 22 | 41 | 407 |  |  | 2020-09-14 | B14209¦Holding Cell corridor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Conference Room 2 | [5 empty] | 20 | 35 | 480 |  | 2020-09-18 09:00 | 9:00 | 20 | 35 | 480 |  | caution | 2020-09-14 | B19523¦Conference Room 2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Police Control Room | [5 empty] | 22 | 44 | 407 |  | 2020-09-18 09:00 | 9:00 | 22 | 44 | 407 |  |  | 2020-09-14 | B14209¦Police Control Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 100 Courtroom 101 Courtroom 102 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203 Courtroom 402 Courtroom 403 | [5 empty] | 21 | 31 | 461 |  | 2020-09-18 09:00 | 9:00 | 21 | 31 | 461 |  | low | 2020-09-14 | B20616¦Courtroom 100 Courtroom 101 Courtroom 102 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203 Courtroom 402 Courtroom 403¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Information Desk | [5 empty] | 22 | 33 | 466 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 466 |  | low | 2020-09-14 | B70510¦Information Desk¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Intake Court | [5 empty] | 22 | 46 | 416 |  | 2020-09-18 09:00 | 9:00 | 22 | 46 | 416 |  |  | 2020-09-14 | B14209¦Intake Court¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 38 | 550 | 3rd floor stair landing | 2020-09-18 09:00 | 9:00 | 21 | 38 | 550 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Entrance by Stair G | [5 empty] | 25 | 33 | 417 |  | 2020-09-18 09:00 | 9:00 | 25 | 33 | 417 |  | low | 2020-09-14 | B14209¦Entrance by Stair G¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 | [5 empty] | 21 | 32 | 464 |  | 2020-09-18 09:00 | 9:00 | 21 | 32 | 464 |  | low | 2020-09-14 | B19523¦Courtroom 3¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 38 | 445 | 3rd floor Jury room | 2020-09-18 09:00 | 9:00 | 21 | 38 | 445 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Library | [5 empty] | 23 | 41 | 410 |  | 2020-09-18 09:00 | 9:00 | 23 | 41 | 410 |  |  | 2020-09-14 | B14209¦Library¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Lunch Room 454 | [5 empty] | 22 | 32 | 461 |  | 2020-09-18 09:00 | 9:00 | 22 | 32 | 461 |  | low | 2020-09-14 | B70510¦Lunch Room 454¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 300 | [5 empty] | 22 | 31 | 534 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 534 |  | low | 2020-09-14 | B20289¦Courtroom 300¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 20 | 39 | 452 | Justice McDonald chamber | 2020-09-18 09:00 | 9:00 | 20 | 39 | 452 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 401 | [5 empty] | 22 | 31 | 461 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 461 |  | low | 2020-09-14 | B20616¦Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 401¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 Waiting Area | [5 empty] | 21 | 31 | 483 |  | 2020-09-18 09:00 | 9:00 | 21 | 31 | 483 |  | low | 2020-09-14 | B19523¦Courtroom 3 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Law Library Meeting Room (028B) | [5 empty] | 22 | 43 | 431 |  | 2020-09-18 09:00 | 9:00 | 22 | 43 | 431 |  |  | 2020-09-14 | B14209¦Law Library Meeting Room (028B)¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 301 | [5 empty] | 22 | 31 | 525 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 525 |  | low | 2020-09-14 | B20289¦Courtroom 301¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 20 | 39 | 471 | Justice McDonald secretary | 2020-09-18 09:00 | 9:00 | 20 | 39 | 471 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 302 | [5 empty] | 22 | 31 | 538 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 538 |  | low | 2020-09-14 | B20289¦Courtroom 302¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 303 | [5 empty] | 22 | 31 | 530 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 530 |  | low | 2020-09-14 | B20289¦Courtroom 303¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 21 | 31 | 486 |  | 2020-09-18 09:00 | 9:00 | 21 | 31 | 486 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 20 | 39 | 472 | SCJTC office | 2020-09-18 09:00 | 9:00 | 20 | 39 | 472 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Copy Room 455 | [5 empty] | 22 | 33 | 450 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 450 |  | low | 2020-09-14 | B70510¦Copy Room 455¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom A | [5 empty] | 21 | 31 | 552 | in session; measurement taken outside courtroom | 2020-09-18 09:00 | 9:00 | 21 | 31 | 552 |  | low | 2020-09-14 | B20289¦Courtroom A¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 204 Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 404 Courtroom 405 | [5 empty] | 21 | 37 | 458 |  | 2020-09-18 09:00 | 9:00 | 21 | 37 | 458 |  | caution | 2020-09-14 | B20616¦Courtroom 204 Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 404 Courtroom 405¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 20 | 39 | 462 | Visiting justice chamber | 2020-09-18 09:00 | 9:00 | 20 | 39 | 462 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room B | [5 empty] | 22 | 34 | 460 |  | 2020-09-18 09:00 | 9:00 | 22 | 34 | 460 |  | low | 2020-09-14 | B70510¦Mediation Room B¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom B | [5 empty] | 21 | 27 | 543 |  | 2020-09-18 09:00 | 9:00 | 21 | 27 | 543 |  | low | 2020-09-14 | B20289¦Courtroom B¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Lunch Room | [5 empty] | 22 | 43 | 414 |  | 2020-09-18 09:00 | 9:00 | 22 | 43 | 414 |  |  | 2020-09-14 | B14209¦Lunch Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Center) | [5 empty] | 20 | 39 | 494 |  | 2020-09-18 09:00 | 9:00 | 20 | 39 | 494 |  | caution | 2020-09-14 | B19652¦Courtroom 2 (Center)¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 31 | 488 |  | 2020-09-18 09:00 | 9:00 | 20 | 31 | 488 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom C (North) | [5 empty] | 22 | 31 | 551 | in session; measurement taken outside courtroom | 2020-09-18 09:00 | 9:00 | 22 | 31 | 551 |  | low | 2020-09-14 | B20289¦Courtroom C (North)¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 459 | [5 empty] | 22 | 33 | 452 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 452 |  | low | 2020-09-14 | B70510¦Office 459¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Judge Dias) | [5 empty] | 20 | 39 | 503 |  | 2020-09-18 09:00 | 9:00 | 20 | 39 | 503 |  | caution | 2020-09-14 | B19652¦Courtroom 2 (Judge Dias)¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Level 1 Corridor by room 103 | [5 empty] | 22 | 42 | 431 |  | 2020-09-18 09:00 | 9:00 | 22 | 42 | 431 |  |  | 2020-09-14 | B14209¦Level 1 Corridor by room 103¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 106 Courtroom 205 | [5 empty] | 20 | 37 | 458 |  | 2020-09-18 09:00 | 9:00 | 20 | 37 | 458 |  | caution | 2020-09-14 | B20616¦Courtroom 106 Courtroom 205¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom D | [5 empty] | 22 | 29 | 536 |  | 2020-09-18 09:00 | 9:00 | 22 | 29 | 536 |  | low | 2020-09-14 | B20289¦Courtroom D¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Main Floor Entrance Lobby | [5 empty] | 22 | 38 | 416 |  | 2020-09-18 09:00 | 9:00 | 22 | 38 | 416 |  | caution | 2020-09-14 | B14209¦Main Floor Entrance Lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | office 467 | [5 empty] | 22 | 33 | 470 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 470 |  | low | 2020-09-14 | B70510¦office 467¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom E | [5 empty] | 22 | 33 | 553 | in session; measurement taken outside courtroom | 2020-09-18 09:00 | 9:00 | 22 | 33 | 553 |  | low | 2020-09-14 | B20289¦Courtroom E¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Outdoors |  |  | 13 | 30 | 404 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B14209¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom F | [5 empty] | 22 | 33 | 558 | in session; measurement taken outside courtroom | 2020-09-18 09:00 | 9:00 | 22 | 33 | 558 |  | low | 2020-09-14 | B20289¦Courtroom F¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 Waiting Area | [5 empty] | 20 | 40 | 491 |  | 2020-09-18 09:00 | 9:00 | 20 | 40 | 491 |  | caution | 2020-09-14 | B19652¦Courtroom 2 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 469 | [5 empty] | 22 | 33 | 461 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 461 |  | low | 2020-09-14 | B70510¦Office 469¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 304 Courtroom 305 | [5 empty] | 21 | 31 | 565 |  | 2020-09-18 09:00 | 9:00 | 21 | 31 | 565 |  | low | 2020-09-14 | B20616¦Courtroom 304 Courtroom 305¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Room 473 | [5 empty] | 22 | 33 | 457 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 457 |  | low | 2020-09-14 | B70510¦Room 473¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Center) | [5 empty] | 21 | 33 | 458 |  | 2020-09-18 09:00 | 9:00 | 21 | 33 | 458 |  | low | 2020-09-14 | B19652¦Courtroom 3 (Center)¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 32 | 523 |  | 2020-09-18 09:00 | 9:00 | 20 | 32 | 523 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 107 Courtroom 108 | [5 empty] | 21 | 37 | 472 |  | 2020-09-18 09:00 | 9:00 | 21 | 37 | 472 |  | caution | 2020-09-14 | B20616¦Courtroom 107 Courtroom 108¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Judge Dias) | [5 empty] | 21 | 33 | 462 |  | 2020-09-18 09:00 | 9:00 | 21 | 33 | 462 |  | low | 2020-09-14 | B19652¦Courtroom 3 (Judge Dias)¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hall 475 or 466 | [5 empty] | 22 | 33 | 459 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 459 |  | low | 2020-09-14 | B70510¦Hall 475 or 466¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 1 | [5 empty] | 22 | 33 | 454 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 454 |  | low | 2020-09-14 | B70510¦Hearing Room 1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 2 | [5 empty] | 20 | 31 | 474 |  | 2020-09-18 09:00 | 9:00 | 20 | 31 | 474 |  | low | 2020-09-14 | B19523¦Courtroom 2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 34 | 471 | Justice peace chamber | 2020-09-18 09:00 | 9:00 | 22 | 34 | 471 |  | low | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Meeting Rooms 1/2 | [5 empty] | 22 | 35 | 454 |  | 2020-09-18 09:00 | 9:00 | 22 | 35 | 454 |  | caution | 2020-09-14 | B70510¦Vestibule at Meeting Rooms 1/2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Police Court Bureau | [5 empty] | 20 | 32 | 488 |  | 2020-09-18 09:00 | 9:00 | 20 | 32 | 488 |  | low | 2020-09-14 | B19523¦Police Court Bureau¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 35 | 461 | Council chamber dias | 2020-09-18 09:00 | 9:00 | 21 | 35 | 461 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Hearing Room 1 | [5 empty] | 22 | 35 | 458 |  | 2020-09-18 09:00 | 9:00 | 22 | 35 | 458 |  | caution | 2020-09-14 | B70510¦Vestibule at Hearing Room 1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom Waiting Area | [5 empty] | 20 | 33 | 496 |  | 2020-09-18 09:00 | 9:00 | 20 | 33 | 496 |  | low | 2020-09-14 | B19523¦Courtroom Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 2 | [5 empty] | 22 | 35 | 456 |  | 2020-09-18 09:00 | 9:00 | 22 | 35 | 456 |  | caution | 2020-09-14 | B70510¦Hearing Room 2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 | [5 empty] | 20 | 34 | 466 |  | 2020-09-18 09:00 | 9:00 | 20 | 34 | 466 |  | low | 2020-09-14 | B19523¦Courtroom 4¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 35 | 445 | Council chamber center | 2020-09-18 09:00 | 9:00 | 21 | 35 | 445 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 439 | [5 empty] | 22 | 33 | 466 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 466 |  | low | 2020-09-14 | B70510¦Office 439¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 2nd Floor Lunchroom | [5 empty] | 21 | 38 | 512 |  | 2020-09-18 09:00 | 9:00 | 21 | 38 | 512 |  | caution | 2020-09-14 | B19652¦2nd Floor Lunchroom¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 32 | 496 |  | 2020-09-18 09:00 | 9:00 | 20 | 32 | 496 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | First Aid Desk | [5 empty] | 22 | 33 | 464 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 464 |  | low | 2020-09-14 | B70510¦First Aid Desk¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 31 | 490 |  | 2020-09-18 09:00 | 9:00 | 19 | 31 | 490 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 36 | 547 | 2nd floor stair landing | 2020-09-18 09:00 | 9:00 | 22 | 36 | 547 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 436 | [5 empty] | 22 | 34 | 466 |  | 2020-09-18 09:00 | 9:00 | 22 | 34 | 466 |  | low | 2020-09-14 | B70510¦Office 436¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 33 | 503 |  | 2020-09-18 09:00 | 9:00 | 19 | 33 | 503 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 432 | [5 empty] | 22 | 34 | 462 |  | 2020-09-18 09:00 | 9:00 | 22 | 34 | 462 |  | low | 2020-09-14 | B70510¦Office 432¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Jury Room | [5 empty] | 20 | 33 | 470 |  | 2020-09-18 09:00 | 9:00 | 20 | 33 | 470 |  | low | 2020-09-14 | B19523¦Jury Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 36 | 502 | Court services kitchenette | 2020-09-18 09:00 | 9:00 | 21 | 36 | 502 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 429 | [5 empty] | 22 | 34 | 465 |  | 2020-09-18 09:00 | 9:00 | 22 | 34 | 465 |  | low | 2020-09-14 | B70510¦Office 429¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 427 | [5 empty] | 22 | 34 | 473 |  | 2020-09-18 09:00 | 9:00 | 22 | 34 | 473 |  | low | 2020-09-14 | B70510¦Office 427¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 18 | 53 | 687 | Court service north | 2020-09-18 09:00 | 9:00 | 18 | 53 | 687 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Ontario Court | [5 empty] | 21 | 35 | 478 |  | 2020-09-18 09:00 | 9:00 | 21 | 35 | 478 |  | caution | 2020-09-14 | B19523¦Ontario Court¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mail Room | [5 empty] | 22 | 35 | 465 |  | 2020-09-18 09:00 | 9:00 | 22 | 35 | 465 |  | caution | 2020-09-14 | B70510¦Mail Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 19 | 52 | 670 | Court service south | 2020-09-18 09:00 | 9:00 | 19 | 52 | 670 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Judicial Library | [5 empty] | 21 | 34 | 490 |  | 2020-09-18 09:00 | 9:00 | 21 | 34 | 490 |  | low | 2020-09-14 | B19523¦Judicial Library¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 420 | [5 empty] | 22 | 34 | 469 |  | 2020-09-18 09:00 | 9:00 | 22 | 34 | 469 |  | low | 2020-09-14 | B70510¦Office 420¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 19 | 48 | 675 | Court service entrance vestibule | 2020-09-18 09:00 | 9:00 | 19 | 48 | 675 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 315 | [5 empty] | 21 | 34 | 476 |  | 2020-09-18 09:00 | 9:00 | 21 | 34 | 476 |  | low | 2020-09-14 | B19523¦Office Room 315¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 20 | 42 | 654 | 1st floor stair landing | 2020-09-18 09:00 | 9:00 | 20 | 42 | 654 |  |  | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 316 | [5 empty] | 21 | 35 | 474 |  | 2020-09-18 09:00 | 9:00 | 21 | 35 | 474 |  | caution | 2020-09-14 | B19523¦Office Room 316¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 418 | [5 empty] | 22 | 34 | 474 |  | 2020-09-18 09:00 | 9:00 | 22 | 34 | 474 |  | low | 2020-09-14 | B70510¦Office 418¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 317 | [5 empty] | 22 | 34 | 469 |  | 2020-09-18 09:00 | 9:00 | 22 | 34 | 469 |  | low | 2020-09-14 | B19523¦Office Room 317¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | File Room | [5 empty] | 22 | 35 | 469 |  | 2020-09-18 09:00 | 9:00 | 22 | 35 | 469 |  | caution | 2020-09-14 | B70510¦File Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Health Room | [5 empty] | 22 | 35 | 467 |  | 2020-09-18 09:00 | 9:00 | 22 | 35 | 467 |  | caution | 2020-09-14 | B70510¦Health Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Superior Court | [5 empty] | 22 | 33 | 519 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 519 |  | low | 2020-09-14 | B19523¦Superior Court¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 | [5 empty] | 21 | 34 | 460 |  | 2020-09-18 09:00 | 9:00 | 21 | 34 | 460 |  | low | 2020-09-14 | B70510¦Hearing Room 3¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 313 | [5 empty] | 22 | 33 | 533 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 533 |  | low | 2020-09-14 | B19523¦Office Room 313¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 Waiting Area | [5 empty] | 21 | 39 | 452 |  | 2020-09-18 09:00 | 9:00 | 21 | 39 | 452 |  | caution | 2020-09-14 | B70510¦Hearing Room 3 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Elevator Lobby | [5 empty] | 21 | 37 | 445 |  | 2020-09-18 09:00 | 9:00 | 21 | 37 | 445 |  | caution | 2020-09-14 | B70510¦Elevator Lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Front seating area | [5 empty] | 20 | 40 | 417 |  | 2020-09-18 09:00 | 9:00 | 20 | 40 | 417 |  | caution | 2020-09-14 | B18359¦Front seating area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Outdoors |  |  | 12 | 38 | 447 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70510¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 312 | [5 empty] | 22 | 33 | 494 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 494 |  | low | 2020-09-14 | B19523¦Office Room 312¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Northwest corridor | [5 empty] | 20 | 39 | 414 |  | 2020-09-18 09:00 | 9:00 | 20 | 39 | 414 |  | caution | 2020-09-14 | B18359¦Northwest corridor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 310 | [5 empty] | 22 | 33 | 503 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 503 |  | low | 2020-09-14 | B19523¦Office Room 310¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Main entrance | [5 empty] | 21 | 32 | 501 |  | 2020-09-18 09:00 | 9:00 | 21 | 32 | 501 |  | low | 2020-09-14 | B20979¦Main entrance¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Law Association | [5 empty] | 20 | 31 | 492 |  | 2020-09-18 09:00 | 9:00 | 20 | 31 | 492 |  | low | 2020-09-14 | B19523¦Law Association¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Outdoors |  |  | 13 | 42 | [5 empty] | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20619¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 21 | 36 | 409 | north side | 2020-09-18 09:00 | 9:00 | 21 | 36 | 409 |  | caution | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Courtroom 1-14 | [5 empty] | 22 | 36 | 465 |  | 2020-09-18 09:00 | 9:00 | 22 | 36 | 465 |  | caution | 2020-09-14 | B20619¦Courtroom 1-14¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 21 | 34 | 455 | east | 2020-09-18 09:00 | 9:00 | 21 | 34 | 455 |  | low | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 21 | 36 | 402 | south side | 2020-09-18 09:00 | 9:00 | 21 | 36 | 402 |  | caution | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 21 | 33 | 465 | west | 2020-09-18 09:00 | 9:00 | 21 | 33 | 465 |  | low | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 21 | 36 | 402 | south side | 2020-09-18 09:00 | 9:00 | 21 | 36 | 402 |  | caution | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 21 | 33 | 520 | south | 2020-09-18 09:00 | 9:00 | 21 | 33 | 520 |  | low | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 21 | 36 | 420 | north side | 2020-09-18 09:00 | 9:00 | 21 | 36 | 420 |  | caution | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 21 | 36 | 408 | south side | 2020-09-18 09:00 | 9:00 | 21 | 36 | 408 |  | caution | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 21 | 34 | 460 | north | 2020-09-18 09:00 | 9:00 | 21 | 34 | 460 |  | low | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 21 | 36 | 412 | north side | 2020-09-18 09:00 | 9:00 | 21 | 36 | 412 |  | caution | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 307 | [5 empty] | 20 | 34 | 445 | south | 2020-09-18 09:00 | 9:00 | 20 | 34 | 445 |  | low | 2020-09-14 | B20979¦Courtroom 307¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 21 | 35 | 419 | south side | 2020-09-18 09:00 | 9:00 | 21 | 35 | 419 |  | caution | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 307 | [5 empty] | 21 | 34 | 437 | north | 2020-09-18 09:00 | 9:00 | 21 | 34 | 437 |  | low | 2020-09-14 | B20979¦Courtroom 307¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 34 | 410 | north side | 2020-09-18 09:00 | 9:00 | 21 | 34 | 410 |  | low | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 34 | 405 | south side | 2020-09-18 09:00 | 9:00 | 21 | 34 | 405 |  | low | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 21 | 34 | 451 | east | 2020-09-18 09:00 | 9:00 | 21 | 34 | 451 |  | low | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 34 | 410 | north side | 2020-09-18 09:00 | 9:00 | 21 | 34 | 410 |  | low | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 21 | 34 | 442 | west | 2020-09-18 09:00 | 9:00 | 21 | 34 | 442 |  | low | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 34 | 418 | south side | 2020-09-18 09:00 | 9:00 | 21 | 34 | 418 |  | low | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 21 | 34 | 420 | north side | 2020-09-18 09:00 | 9:00 | 21 | 34 | 420 |  | low | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Hallway by Courtroom 307 | [5 empty] | 21 | 32 | 450 |  | 2020-09-18 09:00 | 9:00 | 21 | 32 | 450 |  | low | 2020-09-14 | B20979¦Hallway by Courtroom 307¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 21 | 34 | 410 | south side | 2020-09-18 09:00 | 9:00 | 21 | 34 | 410 |  | low | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Hallway by courtroom 302 | [5 empty] | 20 | 32 | 449 |  | 2020-09-18 09:00 | 9:00 | 20 | 32 | 449 |  | low | 2020-09-14 | B20979¦Hallway by courtroom 302¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Outdoors |  |  | 11 | 48 | 313 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B25165¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 21 | 34 | 408 | north side | 2020-09-18 09:00 | 9:00 | 21 | 34 | 408 |  | low | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 21 | 30 | 480 | south | 2020-09-18 09:00 | 9:00 | 21 | 30 | 480 |  | low | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | OTHER | [5 empty] | 21 | 35 | 431 |  | 2020-09-18 09:00 | 9:00 | 21 | 35 | 431 |  | caution | 2020-09-14 | B25165¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 21 | 34 | 404 | south side | 2020-09-18 09:00 | 9:00 | 21 | 34 | 404 |  | low | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 21 | 29 | 448 | north | 2020-09-18 09:00 | 9:00 | 21 | 29 | 448 |  | low | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 600 | [5 empty] | 20 | 35 | 436 |  | 2020-09-18 09:00 | 9:00 | 20 | 35 | 436 |  | caution | 2020-09-14 | B25165¦Courtroom 600¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 308 | [5 empty] | 21 | 35 | 439 |  | 2020-09-18 09:00 | 9:00 | 21 | 35 | 439 |  | caution | 2020-09-14 | B25165¦Courtroom 308¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Basement cells - hallway | [5 empty] | 21 | 28 | 445 |  | 2020-09-18 09:00 | 9:00 | 21 | 28 | 445 |  | low | 2020-09-14 | B20979¦Basement cells - hallway¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 306 | [5 empty] | 21 | 35 | 427 |  | 2020-09-18 09:00 | 9:00 | 21 | 35 | 427 |  | caution | 2020-09-14 | B25165¦Courtroom 306¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 304 | [5 empty] | 22 | 35 | 432 |  | 2020-09-18 09:00 | 9:00 | 22 | 35 | 432 |  | caution | 2020-09-14 | B25165¦Courtroom 304¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Police Office | [5 empty] | 22 | 33 | 540 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 540 |  | low | 2020-09-14 | B20979¦Police Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Outdoors |  |  | 15 | 29 | 447 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20979¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 304 | [5 empty] | 22 | 35 | 432 |  | 2020-09-18 09:00 | 9:00 | 22 | 35 | 432 |  | caution | 2020-09-14 | B25165¦Courtroom 304¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office North | [5 empty] | 21 | 38 | 430 |  | 2020-09-18 09:00 | 9:00 | 21 | 38 | 430 |  | caution | 2020-09-14 | B14895¦Administration Office North¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Main entrance | [5 empty] | 20 | 35 | 515 |  | 2020-09-18 09:00 | 9:00 | 20 | 35 | 515 |  | caution | 2020-09-14 | B90636¦Main entrance¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office South | [5 empty] | 23 | 35 | 450 |  | 2020-09-18 09:00 | 9:00 | 23 | 35 | 450 |  | caution | 2020-09-14 | B14895¦Administration Office South¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 302 | [5 empty] | 20 | 35 | 431 |  | 2020-09-18 09:00 | 9:00 | 20 | 35 | 431 |  | caution | 2020-09-14 | B25165¦Courtroom 302¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 21 | 31 | 460 | north | 2020-09-18 09:00 | 9:00 | 21 | 31 | 460 |  | low | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main entrance | [5 empty] | 21 | 36 | 463 |  | 2020-09-18 09:00 | 9:00 | 21 | 36 | 463 |  | caution | 2020-09-14 | B14895¦Main entrance¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 208 | [5 empty] | 20 | 35 | 421 |  | 2020-09-18 09:00 | 9:00 | 20 | 35 | 421 |  | caution | 2020-09-14 | B25165¦Courtroom 208¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 21 | 31 | 451 | south | 2020-09-18 09:00 | 9:00 | 21 | 31 | 451 |  | low | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main Floor Waiting Area | [5 empty] | 23 | 31 | 419 |  | 2020-09-18 09:00 | 9:00 | 23 | 31 | 419 |  | low | 2020-09-14 | B14895¦Main Floor Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 206 | [5 empty] | 20 | 35 | 430 |  | 2020-09-18 09:00 | 9:00 | 20 | 35 | 430 |  | caution | 2020-09-14 | B25165¦Courtroom 206¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom A | [5 empty] | 22 | 37 | 441 |  | 2020-09-18 09:00 | 9:00 | 22 | 37 | 441 |  | caution | 2020-09-14 | B14895¦Courtroom A¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 204 | [5 empty] | 21 | 35 | 445 |  | 2020-09-18 09:00 | 9:00 | 21 | 35 | 445 |  | caution | 2020-09-14 | B25165¦Courtroom 204¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 21 | 31 | 466 | Lobby entrance | 2020-09-18 09:00 | 9:00 | 21 | 31 | 466 |  | low | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 202 | [5 empty] | 20 | 35 | 419 |  | 2020-09-18 09:00 | 9:00 | 20 | 35 | 419 |  | caution | 2020-09-14 | B25165¦Courtroom 202¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 21 | 30 | 454 | south | 2020-09-18 09:00 | 9:00 | 21 | 30 | 454 |  | low | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 200 | [5 empty] | 21 | 35 | 429 |  | 2020-09-18 09:00 | 9:00 | 21 | 35 | 429 |  | caution | 2020-09-14 | B25165¦Courtroom 200¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-1, 16th Floor OTHER | [5 empty] | 19 | 31 | 651 |  | 2020-09-18 09:00 | 9:00 | 19 | 31 | 651 |  | low | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-1, 16th Floor OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | 2nd Floor Waiting Area | [5 empty] | 23 | 33 | 508 |  | 2020-09-18 09:00 | 9:00 | 23 | 33 | 508 |  | low | 2020-09-14 | B14895¦2nd Floor Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 21 | 30 | 446 | north | 2020-09-18 09:00 | 9:00 | 21 | 30 | 446 |  | low | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 100 | [5 empty] | 21 | 35 | 436 |  | 2020-09-18 09:00 | 9:00 | 21 | 35 | 436 |  | caution | 2020-09-14 | B25165¦Courtroom 100¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Crown Attorney Office | [5 empty] | 23 | 36 | 431 |  | 2020-09-18 09:00 | 9:00 | 23 | 36 | 431 |  | caution | 2020-09-14 | B14895¦Crown Attorney Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-3, 16th Floor OTHER | [5 empty] | 19 | 31 | 632 |  | 2020-09-18 09:00 | 9:00 | 19 | 31 | 632 |  | low | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-3, 16th Floor OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 2nd fl lobby | [5 empty] | 22 | 29 | 548 |  | 2020-09-18 09:00 | 9:00 | 22 | 29 | 548 |  | low | 2020-09-14 | B90636¦2nd fl lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Waiting Area | [5 empty] | 23 | 37 | 516 |  | 2020-09-18 09:00 | 9:00 | 23 | 37 | 516 |  | caution | 2020-09-14 | B14895¦Basement Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 101 | [5 empty] | 20 | 37 | 528 |  | 2020-09-18 12:00 | 12:00 | 20 | 37 | 528 |  | caution | 2020-09-14 | B19512¦Courtroom 101¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 3rd Floor Elevator Lobby | [5 empty] | 21 | 27 | 440 |  | 2020-09-18 09:00 | 9:00 | 21 | 27 | 440 |  | low | 2020-09-14 | B90636¦3rd Floor Elevator Lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Boardroom | [5 empty] | 24 | 27 | 442 |  | 2020-09-18 09:00 | 9:00 | 24 | 27 | 442 |  | low | 2020-09-14 | B14895¦Basement Boardroom¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 16th Floor OTHER | [5 empty] | 20 | 29 | 631 |  | 2020-09-18 09:00 | 9:00 | 20 | 29 | 631 |  | low | 2020-09-14 | B25398¦Elevator Lobby, 16th Floor OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | OTHER | [5 empty] | 21 | 35 | 431 | submitted "other" with out filling in comments section, this is for courtroom 700, Please add courtroom 700 to drop down list, thank you | 2020-09-18 09:00 | 9:00 | 21 | 35 | 431 |  | caution | 2020-09-14 | B25165¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Male Holding Cell | [5 empty] | 24 | 34 | 486 |  | 2020-09-18 09:00 | 9:00 | 24 | 34 | 486 |  | low | 2020-09-14 | B14895¦Male Holding Cell¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 21 | 28 | 443 | west | 2020-09-18 09:00 | 9:00 | 21 | 28 | 443 |  | low | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 200 | [5 empty] | 21 | 37 | 528 |  | 2020-09-18 12:00 | 12:00 | 21 | 37 | 528 |  | caution | 2020-09-14 | B19512¦Courtroom 200¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Washrooms, 16th Floor OTHER | [5 empty] | 20 | 30 | 637 |  | 2020-09-18 09:00 | 9:00 | 20 | 30 | 637 |  | low | 2020-09-14 | B25398¦Corridor adj. to Washrooms, 16th Floor OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 21 | 28 | 441 | east | 2020-09-18 09:00 | 9:00 | 21 | 28 | 441 |  | low | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Female Holding Cell | [5 empty] | 24 | 39 | 499 |  | 2020-09-18 09:00 | 9:00 | 24 | 39 | 499 |  | caution | 2020-09-14 | B14895¦Female Holding Cell¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 4th floor waiting area | [5 empty] | 21 | 25 | 461 |  | 2020-09-18 09:00 | 9:00 | 21 | 25 | 461 |  | low | 2020-09-14 | B90636¦4th floor waiting area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Women's Washroom, 16th Floor | [5 empty] | 20 | 31 | 631 |  | 2020-09-18 09:00 | 9:00 | 20 | 31 | 631 |  | low | 2020-09-14 | B25398¦OTHER Women's Washroom, 16th Floor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 210 | [5 empty] | 21 | 25 | 429 | north | 2020-09-18 09:00 | 9:00 | 21 | 25 | 429 |  | low | 2020-09-14 | B90636¦Courtroom 210¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Outdoors |  |  | 13 | 17 | 384 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B14895¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, West, 15th Floor | [5 empty] | 19 | 35 | 655 |  | 2020-09-18 09:00 | 9:00 | 19 | 35 | 655 |  | caution | 2020-09-14 | B25398¦OTHER Office Area, West, 15th Floor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 210 | [5 empty] | 21 | 25 | 432 | south | 2020-09-18 09:00 | 9:00 | 21 | 25 | 432 |  | low | 2020-09-14 | B90636¦Courtroom 210¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Office Area, North West, 15th Floor | [5 empty] | 20 | 34 | 654 |  | 2020-09-18 09:00 | 9:00 | 20 | 34 | 654 |  | low | 2020-09-14 | B25398¦Office Area, North West, 15th Floor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Hallway by courtroom 211 | [5 empty] | 21 | 26 | 530 |  | 2020-09-18 09:00 | 9:00 | 21 | 26 | 530 |  | low | 2020-09-14 | B90636¦Hallway by courtroom 211¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Outdoors |  |  | 15 | 29 | 447 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B90636¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 2 | [5 empty] | 20 | 43 | 481 |  | 2020-09-18 09:00 | 9:00 | 20 | 43 | 481 |  |  | 2020-09-14 | B11586¦Courtroom 2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North, 15th Floor | [5 empty] | 20 | 35 | 658 |  | 2020-09-18 09:00 | 9:00 | 20 | 35 | 658 |  | caution | 2020-09-14 | B25398¦OTHER Office Area, North, 15th Floor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 20 | 48 | 484 | Crown attorney beatons office | 2020-09-18 09:00 | 9:00 | 20 | 48 | 484 |  |  | 2020-09-14 | B11586¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 21 | 46 | 476 | Crown attorney henault’s office | 2020-09-18 09:00 | 9:00 | 21 | 46 | 476 |  |  | 2020-09-14 | B11586¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown attorney admin area | [5 empty] | 21 | 47 | 522 |  | 2020-09-18 09:00 | 9:00 | 21 | 47 | 522 |  |  | 2020-09-14 | B11586¦Crown attorney admin area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North East, 15th Floor | [5 empty] | 20 | 35 | 660 |  | 2020-09-18 09:00 | 9:00 | 20 | 35 | 660 |  | caution | 2020-09-14 | B25398¦OTHER Office Area, North East, 15th Floor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom waiting area | [5 empty] | 22 | 44 | 473 |  | 2020-09-18 09:00 | 9:00 | 22 | 44 | 473 |  |  | 2020-09-14 | B11586¦Courtroom waiting area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 | [5 empty] | 21 | 38 | 441 |  | 2020-09-18 09:00 | 9:00 | 21 | 38 | 441 |  | caution | 2020-09-14 | B11586¦Courtroom 1¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 200 | [5 empty] | 21 | 36 | 528 |  | 2020-09-18 12:00 | 12:00 | 21 | 36 | 528 |  | caution | 2020-09-14 | B19512¦Courtroom 200¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, East, 15th Floor | [5 empty] | 20 | 35 | 653 |  | 2020-09-18 09:00 | 9:00 | 20 | 35 | 653 |  | caution | 2020-09-14 | B25398¦OTHER Office Area, East, 15th Floor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 21 | 33 | 405 | north side | 2020-09-18 09:00 | 9:00 | 21 | 33 | 405 |  | low | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | 2nd Floor Holding Cell | [5 empty] | 21 | 30 | 441 |  | 2020-09-18 09:00 | 9:00 | 21 | 30 | 441 |  | low | 2020-09-14 | B11586¦2nd Floor Holding Cell¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 21 | 33 | 402 | south side | 2020-09-18 09:00 | 9:00 | 21 | 33 | 402 |  | low | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 201 | [5 empty] | 23 | 43 | 622 |  | 2020-09-18 12:00 | 12:00 | 23 | 43 | 622 |  |  | 2020-09-14 | B19512¦Courtroom 201¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Judge office | [5 empty] | 21 | 38 | 521 |  | 2020-09-18 09:00 | 9:00 | 21 | 38 | 521 |  | caution | 2020-09-14 | B11586¦Judge office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South East, 15th Floor | [5 empty] | 20 | 34 | 656 |  | 2020-09-18 09:00 | 9:00 | 20 | 34 | 656 |  | low | 2020-09-14 | B25398¦OTHER Office Area, South East, 15th Floor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 21 | 34 | 410 | north side | 2020-09-18 09:00 | 9:00 | 21 | 34 | 410 |  | low | 2020-09-14 | B18359¦courtroom 209¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Outdoors |  |  | 14 | 38 | [5 empty] | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B19512¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | court admin | [5 empty] | 19 | 59 | 680 |  | 2020-09-18 09:00 | 9:00 | 19 | 59 | 680 |  |  | 2020-09-14 | B11586¦court admin¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 21 | 33 | 418 | south side | 2020-09-18 09:00 | 9:00 | 21 | 33 | 418 |  | low | 2020-09-14 | B18359¦courtroom 209¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Main Lobby | [5 empty] | 20 | 47 | 551 |  | 2020-09-18 09:00 | 9:00 | 20 | 47 | 551 |  |  | 2020-09-14 | B11586¦Main Lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South, 15th Floor | [5 empty] | 20 | 34 | 649 |  | 2020-09-18 09:00 | 9:00 | 20 | 34 | 649 |  | low | 2020-09-14 | B25398¦OTHER Office Area, South, 15th Floor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Outdoors |  |  | 18 | 74 | 328 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B11586¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Northeast corridor | [5 empty] | 22 | 33 | 415 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 415 |  | low | 2020-09-14 | B18359¦Northeast corridor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Reception, 15th Floor | [5 empty] | 20 | 34 | 643 |  | 2020-09-18 09:00 | 9:00 | 20 | 34 | 643 |  | low | 2020-09-14 | B25398¦OTHER Reception, 15th Floor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Mail Room, 15th Floor OTHER | [5 empty] | 20 | 33 | 653 |  | 2020-09-18 09:00 | 9:00 | 20 | 33 | 653 |  | low | 2020-09-14 | B25398¦Corridor adj. to Mail Room, 15th Floor OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 22 | 34 | 465 | north side | 2020-09-18 09:00 | 9:00 | 22 | 34 | 465 |  | low | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 22 | 33 | 438 | south side | 2020-09-18 09:00 | 9:00 | 22 | 33 | 438 |  | low | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 15th Floor OTHER | [5 empty] | 20 | 32 | 650 |  | 2020-09-18 09:00 | 9:00 | 20 | 32 | 650 |  | low | 2020-09-14 | B25398¦Elevator Lobby, 15th Floor OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 22 | 32 | 409 | north side | 2020-09-18 09:00 | 9:00 | 22 | 32 | 409 |  | low | 2020-09-14 | B18359¦courtroom 211¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Outdoors |  |  | 12 | 25 | 629 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B25398¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Outdoors |  |  | 5 | 56 | 531 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10000¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 22 | 32 | 402 | south side | 2020-09-18 09:00 | 9:00 | 22 | 32 | 402 |  | low | 2020-09-14 | B18359¦courtroom 211¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Outdoors |  |  | 10 | 41 | 509 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10000¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 22 | 32 | 403 | north side | 2020-09-18 09:00 | 9:00 | 22 | 32 | 403 |  | low | 2020-09-14 | B18359¦courtroom 212¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 22 | 32 | 400 | south side | 2020-09-18 09:00 | 9:00 | 22 | 32 | 400 |  | low | 2020-09-14 | B18359¦courtroom 212¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 1 | [5 empty] | 21.6667 | 31 | 464 |  | 2020-09-18 09:00 | 9:00 | 21.6667 | 31 | 464 |  | low | 2020-09-14 | B10000¦Courtroom 1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 1 | [5 empty] | 21.6667 | 31 | 464 |  | 2020-09-18 09:00 | 9:00 | 21.6667 | 31 | 464 |  | low | 2020-09-14 | B10000¦Courtroom 1¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 1 | [5 empty] | 21.1111 | 31 | 488 |  | 2020-09-18 12:00 | 12:00 | 21.1111 | 31 | 488 |  | low | 2020-09-14 | B10000¦Courtroom 1¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd fl lobby | [5 empty] | 20 | 33 | 553 |  | 2020-09-18 12:00 | 12:00 | 20 | 33 | 553 |  | low | 2020-09-14 | B20226¦2nd fl lobby¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 22 | 32 | 406 | north side | 2020-09-18 09:00 | 9:00 | 22 | 32 | 406 |  | low | 2020-09-14 | B18359¦courtroom 213¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 2 | [5 empty] | 23.3333 | 29 | 428 |  | 2020-09-18 09:00 | 9:00 | 23.3333 | 29 | 428 |  | low | 2020-09-14 | B10000¦Courtroom 2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 22 | 32 | 401 | south side | 2020-09-18 09:00 | 9:00 | 22 | 32 | 401 |  | low | 2020-09-14 | B18359¦courtroom 213¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 2 | [5 empty] | 20 | 33 | 559 |  | 2020-09-18 12:00 | 12:00 | 20 | 33 | 559 |  | low | 2020-09-14 | B20226¦Courtroom 2¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 2 | [5 empty] | 22.7778 | 26 | 493 |  | 2020-09-18 12:00 | 12:00 | 22.7778 | 26 | 493 |  | low | 2020-09-14 | B10000¦Courtroom 2¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 3 | [5 empty] | 21.1111 | 18 | 431 |  | 2020-09-18 09:00 | 9:00 | 21.1111 | 18 | 431 |  | low | 2020-09-14 | B10000¦Courtroom 3¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 1 | [5 empty] | 21 | 37 | 656 |  | 2020-09-18 12:00 | 12:00 | 21 | 37 | 656 |  | caution | 2020-09-14 | B20226¦Courtroom 1¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 3 | [5 empty] | 21.6667 | 17 | 450 |  | 2020-09-18 12:00 | 12:00 | 21.6667 | 17 | 450 |  | low | 2020-09-14 | B10000¦Courtroom 3¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 3 | [5 empty] | 22 | 27 | 316 |  | 2020-09-18 12:00 | 12:00 | 22 | 27 | 316 |  | low | 2020-09-14 | B24638¦Courtroom 3¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 22 | 32 | 411 | north side | 2020-09-18 09:00 | 9:00 | 22 | 32 | 411 |  | low | 2020-09-14 | B18359¦courtroom 214¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 22 | 31 | 406 | south side | 2020-09-18 09:00 | 9:00 | 22 | 31 | 406 |  | low | 2020-09-14 | B18359¦courtroom 214¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 4 | [5 empty] | 21.1111 | 18 | 456 |  | 2020-09-18 09:00 | 9:00 | 21.1111 | 18 | 456 |  | low | 2020-09-14 | B10000¦Courtroom 4¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 1 | [5 empty] | 23 | 30 | 399 |  | 2020-09-18 12:00 | 12:00 | 23 | 30 | 399 |  | low | 2020-09-14 | B24638¦Courtroom 1¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 22 | 32 | 408 | north side | 2020-09-18 09:00 | 9:00 | 22 | 32 | 408 |  | low | 2020-09-14 | B18359¦courtroom 215¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 4 | [5 empty] | 21.6667 | 17 | 499 |  | 2020-09-18 12:00 | 12:00 | 21.6667 | 17 | 499 |  | low | 2020-09-14 | B10000¦Courtroom 4¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 101 | [5 empty] | 22 | 37 |  |  | 2020-09-18 12:00 | 12:00 | 22 | 37 |  |  | caution | 2020-09-14 | B20080¦Courtroom 101¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 22 | 32 | 643 |  | 2020-09-18 12:00 | 12:00 | 22 | 32 | 643 |  | low | 2020-09-14 | B20226¦2nd Floor Holding Cell¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 22 | 32 | 406 | south side | 2020-09-18 09:00 | 9:00 | 22 | 32 | 406 |  | low | 2020-09-14 | B18359¦courtroom 215¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 201 | [5 empty] | 22 | 32 | 453 |  | 2020-09-18 12:00 | 12:00 | 22 | 32 | 453 |  | low | 2020-09-14 | B20080¦Courtroom 201¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Outdoors |  |  | 22 | 27 | 336 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B24638¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Outdoors |  |  | 12 | 34 | 441 |  |  |  | outside of 15 Grosvenor Ave. | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B18359¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 202 | [5 empty] | 23 | 32 | 482 |  | 2020-09-18 12:00 | 12:00 | 23 | 32 | 482 |  | low | 2020-09-14 | B20080¦Courtroom 202¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 5 | [5 empty] | 21.6667 | 29 | 439 |  | 2020-09-18 09:00 | 9:00 | 21.6667 | 29 | 439 |  | low | 2020-09-14 | B10000¦Courtroom 5¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 3 | [5 empty] | 22 | 29 | 556 |  | 2020-09-18 12:00 | 12:00 | 22 | 29 | 556 |  | low | 2020-09-14 | B20226¦Courtroom 3¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 5 | [5 empty] | 22.7778 | 29 | 494 |  | 2020-09-18 12:00 | 12:00 | 22.7778 | 29 | 494 |  | low | 2020-09-14 | B10000¦Courtroom 5¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 301 | [5 empty] | 24 | 34 | 497 |  | 2020-09-18 12:00 | 12:00 | 24 | 34 | 497 |  | low | 2020-09-14 | B20080¦Courtroom 301¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 303 | [5 empty] | 22 | 34 | 538 |  | 2020-09-18 12:00 | 12:00 | 22 | 34 | 538 |  | low | 2020-09-14 | B20080¦Courtroom 303¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 6 | [5 empty] | 21.1111 | 29 | 439 |  | 2020-09-18 09:00 | 9:00 | 21.1111 | 29 | 439 |  | low | 2020-09-14 | B10000¦Courtroom 6¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom B01 | [5 empty] | 22 | 32 |  |  | 2020-09-18 12:00 | 12:00 | 22 | 32 |  |  | low | 2020-09-14 | B20080¦Courtroom B01¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 6 | [5 empty] | 22.2222 | 29 | 439 |  | 2020-09-18 12:00 | 12:00 | 22.2222 | 29 | 439 |  | low | 2020-09-14 | B10000¦Courtroom 6¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Outdoors |  |  | 14 | 53 | 412 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20080¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 7 | [5 empty] | 21.6667 | 24 | 474 |  | 2020-09-18 09:00 | 9:00 | 21.6667 | 24 | 474 |  | low | 2020-09-14 | B10000¦Courtroom 7¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Outdoors |  |  | 14 | 30 | 400 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20226¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 7 | [5 empty] | 22.2222 | 24 | 453 |  | 2020-09-18 12:00 | 12:00 | 22.2222 | 24 | 453 |  | low | 2020-09-14 | B10000¦Courtroom 7¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Outdoors |  |  | 11 | 38 | 404 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70050¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 8 | [5 empty] | 21.1111 | 22 | 428 |  | 2020-09-18 09:00 | 9:00 | 21.1111 | 22 | 428 |  | low | 2020-09-14 | B10000¦Courtroom 8¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20893 | B20893 - 75 Mulcaster St. - Barrie | Courtroom 7,8,9 | [5 empty] | 21.5 | 28 | 503 |  | 2020-09-18 12:00 | 12:00 | 21.5 | 28 | 503 |  | low | 2020-09-14 | B20893¦Courtroom 7,8,9¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 8 | [5 empty] | 22.2222 | 25 | 493 |  | 2020-09-18 12:00 | 12:00 | 22.2222 | 25 | 493 |  | low | 2020-09-14 | B10000¦Courtroom 8¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Outdoors |  |  | 16 | 34 | 405 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B12948¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B92347 | B92347 - 75 Mulcaster Street - Barrie | Courtroom 15 | [5 empty] | 20.9 | 31 | 483 |  | 2020-09-18 12:00 | 12:00 | 20.9 | 31 | 483 |  | low | 2020-09-14 | B92347¦Courtroom 15¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 9 | [5 empty] | 21.1111 | 29 | 439 |  | 2020-09-18 09:00 | 9:00 | 21.1111 | 29 | 439 |  | low | 2020-09-14 | B10000¦Courtroom 9¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 1 | [5 empty] | 21 | 31 | 415 |  | 2020-09-18 12:00 | 12:00 | 21 | 31 | 415 |  | low | 2020-09-14 | B12948¦Courtroom 1¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 9 | [5 empty] | 22.2222 | 29 | 494 |  | 2020-09-18 12:00 | 12:00 | 22.2222 | 29 | 494 |  | low | 2020-09-14 | B10000¦Courtroom 9¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 | [5 empty] | 21 | 32 | 438 |  | 2020-09-18 12:00 | 12:00 | 21 | 32 | 438 |  | low | 2020-09-14 | B12948¦Courtroom 2¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Main Lobby | [5 empty] | 19 | 46 | 504 |  | 2020-09-18 12:00 | 12:00 | 19 | 46 | 504 |  |  | 2020-09-14 | B70050¦Main Lobby¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 | [5 empty] | 21 | 30 | 415 |  | 2020-09-18 12:00 | 12:00 | 21 | 30 | 415 |  | low | 2020-09-14 | B12948¦Courtroom 4¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 | [5 empty] | 21 | 31 | 420 |  | 2020-09-18 12:00 | 12:00 | 21 | 31 | 420 |  | low | 2020-09-14 | B12948¦Courtroom 5¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 1 | [5 empty] | 20 | 44 | 485 |  | 2020-09-18 12:00 | 12:00 | 20 | 44 | 485 |  |  | 2020-09-14 | B70050¦Courtroom 1¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 6 | [5 empty] | 20 | 30 | 419 |  | 2020-09-18 12:00 | 12:00 | 20 | 30 | 419 |  | low | 2020-09-14 | B12948¦Courtroom 6¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Cell Basement | [5 empty] | 22 | 31 | 440 |  | 2020-09-18 12:00 | 12:00 | 22 | 31 | 440 |  | low | 2020-09-14 | B12948¦Cell Basement¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 20 | 41 | 482 |  | 2020-09-18 12:00 | 12:00 | 20 | 41 | 482 |  |  | 2020-09-14 | B70050¦2nd Floor Holding Cell¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration Office Waiting Area | [5 empty] | 22 | 31 | 433 |  | 2020-09-18 12:00 | 12:00 | 22 | 31 | 433 |  | low | 2020-09-14 | B12948¦Administration Office Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration office | [5 empty] | 22 | 32 | 430 |  | 2020-09-18 12:00 | 12:00 | 22 | 32 | 430 |  | low | 2020-09-14 | B12948¦Administration office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Crown attorney admin area | [5 empty] | 22 | 33 | 541 |  | 2020-09-18 12:00 | 12:00 | 22 | 33 | 541 |  | low | 2020-09-14 | B12948¦Crown attorney admin area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Yannick Bedard Office - 2nd Floor | [5 empty] | 21 | 42 | 545 |  | 2020-09-18 12:00 | 12:00 | 21 | 42 | 545 |  |  | 2020-09-14 | B70050¦Yannick Bedard Office - 2nd Floor¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main entrance | [5 empty] | 22 | 30 | 435 |  | 2020-09-18 12:00 | 12:00 | 22 | 30 | 435 |  | low | 2020-09-14 | B12948¦Main entrance¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Entry/Waiting | [5 empty] | 23 | 30 | 486 |  | 2020-09-18 12:00 | 12:00 | 23 | 30 | 486 |  | low | 2020-09-14 | B70510¦Entry/Waiting¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main Entrance Waiting Area | [5 empty] | 22 | 31 | 435 |  | 2020-09-18 12:00 | 12:00 | 22 | 31 | 435 |  | low | 2020-09-14 | B12948¦Main Entrance Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room A | [5 empty] | 23 | 29 | 474 |  | 2020-09-18 12:00 | 12:00 | 23 | 29 | 474 |  | low | 2020-09-14 | B70510¦Mediation Room A¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Court Room 1 Waiting Area | [5 empty] | 21 | 30 | 428 |  | 2020-09-18 12:00 | 12:00 | 21 | 30 | 428 |  | low | 2020-09-14 | B12948¦Court Room 1 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Information Desk | [5 empty] | 23 | 29 | 476 |  | 2020-09-18 12:00 | 12:00 | 23 | 29 | 476 |  | low | 2020-09-14 | B70510¦Information Desk¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 Waiting Area | [5 empty] | 22 | 30 | 431 |  | 2020-09-18 12:00 | 12:00 | 22 | 30 | 431 |  | low | 2020-09-14 | B12948¦Courtroom 2 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Lunch Room 454 | [5 empty] | 23 | 29 | 465 |  | 2020-09-18 12:00 | 12:00 | 23 | 29 | 465 |  | low | 2020-09-14 | B70510¦Lunch Room 454¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 Waiting Area | [5 empty] | 22 | 30 | 450 |  | 2020-09-18 12:00 | 12:00 | 22 | 30 | 450 |  | low | 2020-09-14 | B12948¦Courtroom 3 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 2 | [5 empty] | 21 | 42 | 527 |  | 2020-09-18 12:00 | 12:00 | 21 | 42 | 527 |  |  | 2020-09-14 | B70050¦Courtroom 2¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 Waiting Area | [5 empty] | 22 | 30 | 429 |  | 2020-09-18 12:00 | 12:00 | 22 | 30 | 429 |  | low | 2020-09-14 | B12948¦Courtroom 5 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Copy Room 455 | [5 empty] | 23 | 30 | 470 |  | 2020-09-18 12:00 | 12:00 | 23 | 30 | 470 |  | low | 2020-09-14 | B70510¦Copy Room 455¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 and 6 Waiting Area | [5 empty] | 22 | 30 | 425 |  | 2020-09-18 12:00 | 12:00 | 22 | 30 | 425 |  | low | 2020-09-14 | B12948¦Courtroom 4 and 6 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd fl lobby | [5 empty] | 20 | 42 | 500 |  | 2020-09-18 12:00 | 12:00 | 20 | 42 | 500 |  |  | 2020-09-14 | B70050¦2nd fl lobby¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room B | [5 empty] | 23 | 30 | 462 |  | 2020-09-18 12:00 | 12:00 | 23 | 30 | 462 |  | low | 2020-09-14 | B70510¦Mediation Room B¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 459 | [5 empty] | 23 | 30 | 472 |  | 2020-09-18 12:00 | 12:00 | 23 | 30 | 472 |  | low | 2020-09-14 | B70510¦Office 459¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 467 | [5 empty] | 23 | 29 | 469 |  | 2020-09-18 12:00 | 12:00 | 23 | 29 | 469 |  | low | 2020-09-14 | B70510¦Office 467¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Crown Attorney Office | [5 empty] | 21 | 26 | 473 |  | 2020-09-18 12:00 | 12:00 | 21 | 26 | 473 |  | low | 2020-09-14 | B20016¦Crown Attorney Office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 469 | [5 empty] | 23 | 30 | 475 |  | 2020-09-18 12:00 | 12:00 | 23 | 30 | 475 |  | low | 2020-09-14 | B70510¦Office 469¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 | [5 empty] | 23 | 39 | 475 |  | 2020-09-18 12:00 | 12:00 | 23 | 39 | 475 |  | caution | 2020-09-14 | B14209¦Courtroom 1¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Room 473 | [5 empty] | 22 | 30 | 472 |  | 2020-09-18 12:00 | 12:00 | 22 | 30 | 472 |  | low | 2020-09-14 | B70510¦Room 473¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 - waiting area | [5 empty] | 18 | 50 | 481 |  | 2020-09-18 12:00 | 12:00 | 18 | 50 | 481 |  |  | 2020-09-14 | B14209¦Courtroom 1 - waiting area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Outdoors |  |  | 13 | 28 | 390 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B19652¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hall 475 or 466 | [5 empty] | 22 | 30 | 487 |  | 2020-09-18 12:00 | 12:00 | 22 | 30 | 487 |  | low | 2020-09-14 | B70510¦Hall 475 or 466¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Outdoors |  |  | 14 | 37 | [5 empty] | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20619¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 | [5 empty] | 22 | 36 | 468 |  | 2020-09-18 12:00 | 12:00 | 22 | 36 | 468 |  | caution | 2020-09-14 | B14209¦Courtroom 2¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Center) | [5 empty] | 18 | 38 | 530 |  | 2020-09-18 12:00 | 12:00 | 18 | 38 | 530 |  | caution | 2020-09-14 | B19652¦Courtroom 1 (Center)¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Legal Aid Ontario | [5 empty] | 21 | 27 | 454 |  | 2020-09-18 12:00 | 12:00 | 21 | 27 | 454 |  | low | 2020-09-14 | B20016¦Legal Aid Ontario¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 1 | [5 empty] | 22 | 30 | 503 |  | 2020-09-18 12:00 | 12:00 | 22 | 30 | 503 |  | low | 2020-09-14 | B70510¦Hearing Room 1¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20619 | B20619 - 59 Church St - St. Catharines | Courtroom 1-14 | [5 empty] | 22 | 33 | 458 |  | 2020-09-18 12:00 | 12:00 | 22 | 33 | 458 |  | low | 2020-09-14 | B20619¦Courtroom 1-14¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 - waiting room | [5 empty] | 20 | 43 | 467 |  | 2020-09-18 12:00 | 12:00 | 20 | 43 | 467 |  |  | 2020-09-14 | B14209¦Courtroom 2 - waiting room¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel Waiting Area | [5 empty] | 22 | 24 | 450 |  | 2020-09-18 12:00 | 12:00 | 22 | 24 | 450 |  | low | 2020-09-14 | B20016¦Duty Counsel Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Judge Dias) | [5 empty] | 18 | 38 | 450 |  | 2020-09-18 12:00 | 12:00 | 18 | 38 | 450 |  | caution | 2020-09-14 | B19652¦Courtroom 1 (Judge Dias)¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room | [5 empty] | 22 | 38 | 439 |  | 2020-09-18 12:00 | 12:00 | 22 | 38 | 439 |  | caution | 2020-09-14 | B14209¦Hearing Room¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Meeting Rooms 1/2 | [5 empty] | 22 | 32 | 469 |  | 2020-09-18 12:00 | 12:00 | 22 | 32 | 469 |  | low | 2020-09-14 | B70510¦Vestibule at Meeting Rooms 1/2¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 18 | 39 | 471 | Superior judges chamber | 2020-09-18 12:00 | 12:00 | 18 | 39 | 471 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel | [5 empty] | 22 | 28 | 452 |  | 2020-09-18 12:00 | 12:00 | 22 | 28 | 452 |  | low | 2020-09-14 | B20016¦Duty Counsel¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Hearing Room 1 | [5 empty] | 22 | 32 | 474 |  | 2020-09-18 12:00 | 12:00 | 22 | 32 | 474 |  | low | 2020-09-14 | B70510¦Vestibule at Hearing Room 1¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 19 | 38 | 545 | 3rd floor stair landing | 2020-09-18 12:00 | 12:00 | 19 | 38 | 545 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Outdoors |  |  | 11 | 39 | 429 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B90838¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lobby Courtroom 1 - 2 | [5 empty] | 22 | 26 | 456 |  | 2020-09-18 12:00 | 12:00 | 22 | 26 | 456 |  | low | 2020-09-14 | B20016¦Lobby Courtroom 1 - 2¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 19 | 39 | 459 | 3rd floor Jury room | 2020-09-18 12:00 | 12:00 | 19 | 39 | 459 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Courtroom 101 Courtroom 102 | [5 empty] | 21 | 39 | 432 |  | 2020-09-18 12:00 | 12:00 | 21 | 39 | 432 |  | caution | 2020-09-14 | B90838¦Courtroom 101 Courtroom 102¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 2 | [5 empty] | 22 | 33 | 471 |  | 2020-09-18 12:00 | 12:00 | 22 | 33 | 471 |  | low | 2020-09-14 | B70510¦Hearing Room 2¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 35 | 492 | Justice McDonald chamber | 2020-09-18 12:00 | 12:00 | 21 | 35 | 492 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 439 | [5 empty] | 22 | 31 | 474 |  | 2020-09-18 12:00 | 12:00 | 22 | 31 | 474 |  | low | 2020-09-14 | B70510¦Office 439¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 20 | 35 | 505 | Justice McDonald secretary | 2020-09-18 12:00 | 12:00 | 20 | 35 | 505 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Main Lobby | [5 empty] | 22 | 26 | 479 |  | 2020-09-18 12:00 | 12:00 | 22 | 26 | 479 |  | low | 2020-09-14 | B20016¦Main Lobby¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 36 | 525 | SCJTC office | 2020-09-18 12:00 | 12:00 | 21 | 36 | 525 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | First Aid Desk | [5 empty] | 22 | 31 | 465 |  | 2020-09-18 12:00 | 12:00 | 22 | 31 | 465 |  | low | 2020-09-14 | B70510¦First Aid Desk¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 21 | 35 | 506 | Visiting justice chamber | 2020-09-18 12:00 | 12:00 | 21 | 35 | 506 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Main Lobby | [5 empty] | 22 | 26 | 479 |  | 2020-09-18 12:00 | 12:00 | 22 | 26 | 479 |  | low | 2020-09-14 | B20016¦Main Lobby¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lower Hallway | [5 empty] | 22 | 26 | 514 |  | 2020-09-18 12:00 | 12:00 | 22 | 26 | 514 |  | low | 2020-09-14 | B20016¦Lower Hallway¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Center) | [5 empty] | 21 | 39 | 909 |  | 2020-09-18 12:00 | 12:00 | 21 | 39 | 909 |  | caution | 2020-09-14 | B19652¦Courtroom 2 (Center)¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 2 | [5 empty] | 21 | 49 | 599 |  | 2020-09-18 12:00 | 12:00 | 21 | 49 | 599 |  |  | 2020-09-14 | B11586¦Courtroom 2¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 436 | [5 empty] | 23 | 31 | 474 |  | 2020-09-18 12:00 | 12:00 | 23 | 31 | 474 |  | low | 2020-09-14 | B70510¦Office 436¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Judge Dias) | [5 empty] | 21 | 40 | 920 |  | 2020-09-18 12:00 | 12:00 | 21 | 40 | 920 |  | caution | 2020-09-14 | B19652¦Courtroom 2 (Judge Dias)¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | OTHER | [5 empty] | 21 | 25 | 517 | Courtroom 1-2-3 | 2020-09-18 12:00 | 12:00 | 21 | 25 | 517 |  | low | 2020-09-14 | B20016¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 21 | 43 | 558 | Crown attorney Beatons office | 2020-09-18 12:00 | 12:00 | 21 | 43 | 558 |  |  | 2020-09-14 | B11586¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 Waiting Area | [5 empty] | 21 | 37 | 688 |  | 2020-09-18 12:00 | 12:00 | 21 | 37 | 688 |  | caution | 2020-09-14 | B19652¦Courtroom 2 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 432 | [5 empty] | 23 | 31 | 481 |  | 2020-09-18 12:00 | 12:00 | 23 | 31 | 481 |  | low | 2020-09-14 | B70510¦Office 432¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | OTHER | [5 empty] | 21 | 42 | 566 | Crown attorney henault’s office | 2020-09-18 12:00 | 12:00 | 21 | 42 | 566 |  |  | 2020-09-14 | B11586¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Center) | [5 empty] | 22 | 33 | 457 |  | 2020-09-18 12:00 | 12:00 | 22 | 33 | 457 |  | low | 2020-09-14 | B19652¦Courtroom 3 (Center)¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation | [5 empty] | 21 | 27 | 499 |  | 2020-09-18 12:00 | 12:00 | 21 | 27 | 499 |  | low | 2020-09-14 | B20016¦Family Mediation¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown attorney admin area | [5 empty] | 22 | 43 | 598 |  | 2020-09-18 12:00 | 12:00 | 22 | 43 | 598 |  |  | 2020-09-14 | B11586¦Crown attorney admin area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 432 | [5 empty] | 23 | 31 | 481 |  | 2020-09-18 12:00 | 12:00 | 23 | 31 | 481 |  | low | 2020-09-14 | B70510¦Office 432¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation Across Stairs | [5 empty] | 20 | 25 | 553 |  | 2020-09-18 12:00 | 12:00 | 20 | 25 | 553 |  | low | 2020-09-14 | B20016¦Family Mediation Across Stairs¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom waiting area | [5 empty] | 22 | 40 | 564 |  | 2020-09-18 12:00 | 12:00 | 22 | 40 | 564 |  | caution | 2020-09-14 | B11586¦Courtroom waiting area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Judge Dias) | [5 empty] | 22 | 29 | 471 |  | 2020-09-18 12:00 | 12:00 | 22 | 29 | 471 |  | low | 2020-09-14 | B19652¦Courtroom 3 (Judge Dias)¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 | [5 empty] | 21 | 36 | 640 |  | 2020-09-18 12:00 | 12:00 | 21 | 36 | 640 |  | caution | 2020-09-14 | B11586¦Courtroom 1¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 429 | [5 empty] | 23 | 31 | 470 |  | 2020-09-18 12:00 | 12:00 | 23 | 31 | 470 |  | low | 2020-09-14 | B70510¦Office 429¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 32 | 561 | Justice peace chamber | 2020-09-18 12:00 | 12:00 | 22 | 32 | 561 |  | low | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | 2nd Floor Holding Cell | [5 empty] | 21 | 37 | 507 |  | 2020-09-18 12:00 | 12:00 | 21 | 37 | 507 |  | caution | 2020-09-14 | B11586¦2nd Floor Holding Cell¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Main entrance | [5 empty] | 19 | 30 | 460 |  | 2020-09-18 12:00 | 12:00 | 19 | 30 | 460 |  | low | 2020-09-14 | B90636¦Main entrance¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Judge office | [5 empty] | 22 | 40 | 552 |  | 2020-09-18 12:00 | 12:00 | 22 | 40 | 552 |  | caution | 2020-09-14 | B11586¦Judge office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 427 | [5 empty] | 23 | 31 | 478 |  | 2020-09-18 12:00 | 12:00 | 23 | 31 | 478 |  | low | 2020-09-14 | B70510¦Office 427¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 32 | 473 | Council chamber dias | 2020-09-18 12:00 | 12:00 | 22 | 32 | 473 |  | low | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 8 | [5 empty] | 22 | 43 | 427 |  | 2020-09-18 12:00 | 12:00 | 22 | 43 | 427 |  |  | 2020-09-14 | B25683¦Courtroom 8¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | court admin | [5 empty] | 18 | 54 | 610 |  | 2020-09-18 12:00 | 12:00 | 18 | 54 | 610 |  |  | 2020-09-14 | B11586¦court admin¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mail Room | [5 empty] | 23 | 31 | 477 |  | 2020-09-18 12:00 | 12:00 | 23 | 31 | 477 |  | low | 2020-09-14 | B70510¦Mail Room¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 32 | 477 | Council chamber center | 2020-09-18 12:00 | 12:00 | 22 | 32 | 477 |  | low | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 11 | [5 empty] | 22 | 43 | 427 |  | 2020-09-18 12:00 | 12:00 | 22 | 43 | 427 |  |  | 2020-09-14 | B25683¦Courtroom 11¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Main Lobby | [5 empty] | 19 | 51 | 584 |  | 2020-09-18 12:00 | 12:00 | 19 | 51 | 584 |  |  | 2020-09-14 | B11586¦Main Lobby¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 420 | [5 empty] | 22 | 31 | 511 |  | 2020-09-18 12:00 | 12:00 | 22 | 31 | 511 |  | low | 2020-09-14 | B70510¦Office 420¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25683 | B25683 - 200 Chatham St - Windsor | Courtroom 9 | [5 empty] | 22 | 40 | 432 |  | 2020-09-18 12:00 | 12:00 | 22 | 40 | 432 |  | caution | 2020-09-14 | B25683¦Courtroom 9¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 2nd Floor Lunchroom | [5 empty] | 21 | 33 | 572 |  | 2020-09-18 12:00 | 12:00 | 21 | 33 | 572 |  | low | 2020-09-14 | B19652¦2nd Floor Lunchroom¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Outdoors |  |  | 15 | 29 | 387 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B11586¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 418 | [5 empty] | 22 | 31 | 490 |  | 2020-09-18 12:00 | 12:00 | 22 | 31 | 490 |  | low | 2020-09-14 | B70510¦Office 418¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 30 | 517 | 2nd floor stair landing | 2020-09-18 12:00 | 12:00 | 22 | 30 | 517 |  | low | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | File Room | [5 empty] | 22 | 31 | 489 |  | 2020-09-18 12:00 | 12:00 | 22 | 31 | 489 |  | low | 2020-09-14 | B70510¦File Room¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 19 | 27 | 453 | north | 2020-09-18 12:00 | 12:00 | 19 | 27 | 453 |  | low | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 32 | 484 | Court services kitchenette | 2020-09-18 12:00 | 12:00 | 22 | 32 | 484 |  | low | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Health Room | [5 empty] | 22 | 32 | 485 |  | 2020-09-18 12:00 | 12:00 | 22 | 32 | 485 |  | low | 2020-09-14 | B70510¦Health Room¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 20 | 27 | 436 | south | 2020-09-18 12:00 | 12:00 | 20 | 27 | 436 |  | low | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 | [5 empty] | 22 | 31 | 474 |  | 2020-09-18 12:00 | 12:00 | 22 | 31 | 474 |  | low | 2020-09-14 | B70510¦Hearing Room 3¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 37 | 720 | Court service north | 2020-09-18 12:00 | 12:00 | 23 | 37 | 720 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 21 | 28 | 457 | lobby | 2020-09-18 12:00 | 12:00 | 21 | 28 | 457 |  | low | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 Waiting Area | [5 empty] | 22 | 33 | 462 |  | 2020-09-18 12:00 | 12:00 | 22 | 33 | 462 |  | low | 2020-09-14 | B70510¦Hearing Room 3 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 37 | 744 | Court service south | 2020-09-18 12:00 | 12:00 | 23 | 37 | 744 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Elevator Lobby | [5 empty] | 22 | 32 | 483 |  | 2020-09-18 12:00 | 12:00 | 22 | 32 | 483 |  | low | 2020-09-14 | B70510¦Elevator Lobby¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 22 | 35 | 608 | Court service entrance vestibule | 2020-09-18 12:00 | 12:00 | 22 | 35 | 608 |  | caution | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 21 | 29 | 474 | entrance | 2020-09-18 12:00 | 12:00 | 21 | 29 | 474 |  | low | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Outdoors |  |  | 15 | 28 | 454 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70510¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | front seating area | [5 empty] | 21 | 42 | 438 |  | 2020-09-18 09:00 | 9:00 | 21 | 42 | 438 |  |  | 2020-09-14 | B18359¦front seating area¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | OTHER | [5 empty] | 23 | 31 | 605 | 1st floor stair landing | 2020-09-18 12:00 | 12:00 | 23 | 31 | 605 |  | low | 2020-09-14 | B19652¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Hallway by courtroom 203 | [5 empty] | 22 | 25 | 473 |  | 2020-09-18 12:00 | 12:00 | 22 | 25 | 473 |  | low | 2020-09-14 | B90636¦Hallway by courtroom 203¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 100 Courtroom 101 Courtroom 102 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203 Courtroom 402 Courtroom 403 | [5 empty] | 21 | 28 | 445 |  | 2020-09-18 12:00 | 12:00 | 21 | 28 | 445 |  | low | 2020-09-14 | B20616¦Courtroom 100 Courtroom 101 Courtroom 102 Courtroom 200 Courtroom 201 Courtroom 202 Courtroom 203 Courtroom 402 Courtroom 403¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Outdoors |  |  | 13 | 19 | 489 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20289¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 2nd fl lobby | [5 empty] | 22 | 26 | 472 |  | 2020-09-18 12:00 | 12:00 | 22 | 26 | 472 |  | low | 2020-09-14 | B90636¦2nd fl lobby¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 19 | 30 | 520 | judge | 2020-09-18 12:00 | 12:00 | 19 | 30 | 520 |  | low | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 19 | 29 | 510 | public | 2020-09-18 12:00 | 12:00 | 19 | 29 | 510 |  | low | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 3rd floor waiting area | [5 empty] | 21 | 26 | 453 |  | 2020-09-18 12:00 | 12:00 | 21 | 26 | 453 |  | low | 2020-09-14 | B90636¦3rd floor waiting area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room, Judge’s Chamber | [5 empty] | 21 | 38 | 426 |  | 2020-09-18 12:00 | 12:00 | 21 | 38 | 426 |  | caution | 2020-09-14 | B14209¦Hearing Room, Judge’s Chamber¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 20 | 27 | 509 | judge | 2020-09-18 12:00 | 12:00 | 20 | 27 | 509 |  | low | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 401 | [5 empty] | 22 | 28 | 445 |  | 2020-09-18 12:00 | 12:00 | 22 | 28 | 445 |  | low | 2020-09-14 | B20616¦Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 401¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room - Waiting area | [5 empty] | 20 | 48 | 474 |  | 2020-09-18 12:00 | 12:00 | 20 | 48 | 474 |  |  | 2020-09-14 | B14209¦Hearing Room - Waiting area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 20 | 27 | 508 | public | 2020-09-18 12:00 | 12:00 | 20 | 27 | 508 |  | low | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 21 | 26 | 464 | west | 2020-09-18 12:00 | 12:00 | 21 | 26 | 464 |  | low | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 300 | [5 empty] | 16 | 21 | 500 |  | 2020-09-18 12:00 | 12:00 | 16 | 21 | 500 |  | low | 2020-09-14 | B20289¦Courtroom 300¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Lobby | [5 empty] | 22 | 46 | 521 |  | 2020-09-18 12:00 | 12:00 | 22 | 46 | 521 |  |  | 2020-09-14 | B14209¦Court Admin Office Lobby¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 106 Courtroom 205 | [5 empty] | 20 | 34 | 446 |  | 2020-09-18 12:00 | 12:00 | 20 | 34 | 446 |  | low | 2020-09-14 | B20616¦Courtroom 106 Courtroom 205¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 301 | [5 empty] | 17 | 21 | 506 |  | 2020-09-18 12:00 | 12:00 | 17 | 21 | 506 |  | low | 2020-09-14 | B20289¦Courtroom 301¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 207 | [5 empty] | 21 | 26 | 460 | east | 2020-09-18 12:00 | 12:00 | 21 | 26 | 460 |  | low | 2020-09-14 | B90636¦Courtroom 207¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 302 | [5 empty] | 18 | 21 | 507 |  | 2020-09-18 12:00 | 12:00 | 18 | 21 | 507 |  | low | 2020-09-14 | B20289¦Courtroom 302¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 303 | [5 empty] | 17 | 22 | 492 |  | 2020-09-18 12:00 | 12:00 | 17 | 22 | 492 |  | low | 2020-09-14 | B20289¦Courtroom 303¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Cubicles | [5 empty] | 22 | 45 | 510 |  | 2020-09-18 12:00 | 12:00 | 22 | 45 | 510 |  |  | 2020-09-14 | B14209¦Court Admin Office Cubicles¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 3rd floor waiting area | [5 empty] | 21 | 22 | 438 |  | 2020-09-18 12:00 | 12:00 | 21 | 22 | 438 |  | low | 2020-09-14 | B90636¦3rd floor waiting area¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | northwest corridor | [5 empty] | 21 | 41 | 418 |  | 2020-09-18 09:00 | 9:00 | 21 | 41 | 418 |  |  | 2020-09-14 | B18359¦northwest corridor¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom A | [5 empty] | 17 | 21 | 525 | in session; measurement taken outside courtroom | 2020-09-18 12:00 | 12:00 | 17 | 21 | 525 |  | low | 2020-09-14 | B20289¦Courtroom A¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 405 | [5 empty] | 21 | 34 | 446 |  | 2020-09-18 12:00 | 12:00 | 21 | 34 | 446 |  | low | 2020-09-14 | B20616¦Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 405¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Front desk | [5 empty] | 21 | 48 | 480 |  | 2020-09-18 12:00 | 12:00 | 21 | 48 | 480 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Front desk¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom B | [5 empty] | 18 | 22 | 527 | in session; measurement taken outside courtroom | 2020-09-18 12:00 | 12:00 | 18 | 22 | 527 |  | low | 2020-09-14 | B20289¦Courtroom B¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 21 | 41 | 413 | north | 2020-09-18 09:00 | 9:00 | 21 | 41 | 413 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 211 | [5 empty] | 21 | 24 | 411 | north | 2020-09-18 12:00 | 12:00 | 21 | 24 | 411 |  | low | 2020-09-14 | B90636¦Courtroom 211¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown attorney admin area | [5 empty] | 22 | 44 | 466 |  | 2020-09-18 12:00 | 12:00 | 22 | 44 | 466 |  |  | 2020-09-14 | B14209¦Crown attorney admin area¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 21 | 42 | 421 | south | 2020-09-18 09:00 | 9:00 | 21 | 42 | 421 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 204 Courtroom 404 | [5 empty] | 22 | 34 | 446 |  | 2020-09-18 12:00 | 12:00 | 22 | 34 | 446 |  | low | 2020-09-14 | B20616¦Courtroom 204 Courtroom 404¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom C (North) | [5 empty] | 17 | 23 | 562 |  | 2020-09-18 12:00 | 12:00 | 17 | 23 | 562 |  | low | 2020-09-14 | B20289¦Courtroom C (North)¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 20 | 42 | 420 | north | 2020-09-18 09:00 | 9:00 | 20 | 42 | 420 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-1 | [5 empty] | 20.1 | 35.2 | 706 |  | 2020-09-18 09:00 | 9:00 | 20.1 | 35.2 | 706 |  | caution | 2020-09-14 | B10644¦Courtroom 2-1¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office North | [5 empty] | 23 | 32 | 610 |  | 2020-09-18 12:00 | 12:00 | 23 | 32 | 610 |  | low | 2020-09-14 | B14895¦Administration Office North¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom D | [5 empty] | 17 | 24 | 574 |  | 2020-09-18 12:00 | 12:00 | 17 | 24 | 574 |  | low | 2020-09-14 | B20289¦Courtroom D¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Print Room | [5 empty] | 22 | 44 | 457 |  | 2020-09-18 12:00 | 12:00 | 22 | 44 | 457 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Print Room¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 20 | 42 | 423 | south | 2020-09-18 09:00 | 9:00 | 20 | 42 | 423 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom E | [5 empty] | 17 | 23 | 576 |  | 2020-09-18 12:00 | 12:00 | 17 | 23 | 576 |  | low | 2020-09-14 | B20289¦Courtroom E¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 107 Courtroom 108 | [5 empty] | 21 | 29 | 431 |  | 2020-09-18 12:00 | 12:00 | 21 | 29 | 431 |  | low | 2020-09-14 | B20616¦Courtroom 107 Courtroom 108¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 211 | [5 empty] | 22 | 24 | 415 | south | 2020-09-18 12:00 | 12:00 | 22 | 24 | 415 |  | low | 2020-09-14 | B90636¦Courtroom 211¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom F | [5 empty] | 17 | 23 | 560 | in session; measurement taken outside courtroom | 2020-09-18 12:00 | 12:00 | 17 | 23 | 560 |  | low | 2020-09-14 | B20289¦Courtroom F¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 20 | 43 | 426 | north | 2020-09-18 09:00 | 9:00 | 20 | 43 | 426 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 304 Courtroom 305 | [5 empty] | 21 | 27 | 554 |  | 2020-09-18 12:00 | 12:00 | 21 | 27 | 554 |  | low | 2020-09-14 | B20616¦Courtroom 304 Courtroom 305¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office South | [5 empty] | 23 | 30 | 595 |  | 2020-09-18 12:00 | 12:00 | 23 | 30 | 595 |  | low | 2020-09-14 | B14895¦Administration Office South¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 20 | 43 | 428 | south | 2020-09-18 09:00 | 9:00 | 20 | 43 | 428 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Hallway by 211 | [5 empty] | 21 | 26 | 483 |  | 2020-09-18 12:00 | 12:00 | 21 | 26 | 483 |  | low | 2020-09-14 | B90636¦Hallway by 211¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Assistant Crown Attorney Office (236) | [5 empty] | 22 | 45 | 441 |  | 2020-09-18 12:00 | 12:00 | 22 | 45 | 441 |  |  | 2020-09-14 | B14209¦Assistant Crown Attorney Office (236)¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 20 | 43 | 422 | north | 2020-09-18 09:00 | 9:00 | 20 | 43 | 422 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main entrance | [5 empty] | 21 | 35 | 572 |  | 2020-09-18 12:00 | 12:00 | 21 | 35 | 572 |  | caution | 2020-09-14 | B14895¦Main entrance¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-8 | [5 empty] | 20.8 | 36.8 | 671 |  | 2020-09-18 09:00 | 9:00 | 20.8 | 36.8 | 671 |  | caution | 2020-09-14 | B10644¦Courtroom 2-8¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office | [5 empty] | 22 | 44 | 429 |  | 2020-09-18 12:00 | 12:00 | 22 | 44 | 429 |  |  | 2020-09-14 | B14209¦Crown Attorney Office¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 43 | 416 | south | 2020-09-18 09:00 | 9:00 | 21 | 43 | 416 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Outdoors |  |  | 18 | 23 | 461 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B90636¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main Floor Waiting Area | [5 empty] | 23 | 31 | 552 |  | 2020-09-18 12:00 | 12:00 | 23 | 31 | 552 |  | low | 2020-09-14 | B14895¦Main Floor Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 43 | 423 | north | 2020-09-18 09:00 | 9:00 | 21 | 43 | 423 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom A | [5 empty] | 22 | 29 | 443 |  | 2020-09-18 12:00 | 12:00 | 22 | 29 | 443 |  | low | 2020-09-14 | B14895¦Courtroom A¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 43 | 423 | south | 2020-09-18 09:00 | 9:00 | 21 | 43 | 423 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-3 | [5 empty] | 20.5 | 56.1 | 430 |  | 2020-09-18 09:00 | 9:00 | 20.5 | 56.1 | 430 |  |  | 2020-09-14 | B10644¦Courtroom 2-3¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Main entrance | [5 empty] | 23 | 25 | 514 |  | 2020-09-18 12:00 | 12:00 | 23 | 25 | 514 |  | low | 2020-09-14 | B20979¦Main entrance¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 20 | 43 | 416 | north | 2020-09-18 09:00 | 9:00 | 20 | 43 | 416 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Meeting Room (232) | [5 empty] | 21 | 44 | 434 |  | 2020-09-18 12:00 | 12:00 | 21 | 44 | 434 |  |  | 2020-09-14 | B14209¦Crown Attorney Meeting Room (232)¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom A | [5 empty] | 22 | 29 | 443 |  | 2020-09-18 12:00 | 12:00 | 22 | 29 | 443 |  | low | 2020-09-14 | B14895¦Courtroom A¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 20 | 43 | 426 | south | 2020-09-18 09:00 | 9:00 | 20 | 43 | 426 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 23 | 26 | 500 | east | 2020-09-18 12:00 | 12:00 | 23 | 26 | 500 |  | low | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom B | [5 empty] | 22 | 28 | 474 |  | 2020-09-18 12:00 | 12:00 | 22 | 28 | 474 |  | low | 2020-09-14 | B14895¦Courtroom B¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-4 | [5 empty] | 21.4 | 32.6 | 546 |  | 2020-09-18 09:00 | 9:00 | 21.4 | 32.6 | 546 |  | low | 2020-09-14 | B10644¦Courtroom 2-4¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 20 | 43 | 422 | north | 2020-09-18 09:00 | 9:00 | 20 | 43 | 422 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | 2nd Floor Waiting Area | [5 empty] | 23 | 30 | 637 |  | 2020-09-18 12:00 | 12:00 | 23 | 30 | 637 |  | low | 2020-09-14 | B14895¦2nd Floor Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 23 | 26 | 503 | west | 2020-09-18 12:00 | 12:00 | 23 | 26 | 503 |  | low | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Holding Cell corridor | [5 empty] | 22 | 40 | 447 |  | 2020-09-18 12:00 | 12:00 | 22 | 40 | 447 |  | caution | 2020-09-14 | B14209¦Holding Cell corridor¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 20 | 43 | 427 | south | 2020-09-18 09:00 | 9:00 | 20 | 43 | 427 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Police Control Room | [5 empty] | 22 | 40 | 442 |  | 2020-09-18 12:00 | 12:00 | 22 | 40 | 442 |  | caution | 2020-09-14 | B14209¦Police Control Room¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 22 | 28 | 620 | south | 2020-09-18 12:00 | 12:00 | 22 | 28 | 620 |  | low | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-5 | [5 empty] | 20.8 | 38.6 | 404 |  | 2020-09-18 09:00 | 9:00 | 20.8 | 38.6 | 404 |  | caution | 2020-09-14 | B10644¦Courtroom 2-5¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Intake Court | [5 empty] | 22 | 45 | 449 |  | 2020-09-18 12:00 | 12:00 | 22 | 45 | 449 |  |  | 2020-09-14 | B14209¦Intake Court¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 20 | 44 | 429 | north | 2020-09-18 09:00 | 9:00 | 20 | 44 | 429 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Crown Attorney Office | [5 empty] | 23 | 33 | 556 |  | 2020-09-18 12:00 | 12:00 | 23 | 33 | 556 |  | low | 2020-09-14 | B14895¦Crown Attorney Office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 22 | 29 | 553 | north | 2020-09-18 12:00 | 12:00 | 22 | 29 | 553 |  | low | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-3, 16th Floor OTHER | [5 empty] | 21 | 22.5 | 657 |  | 2020-09-18 12:00 | 12:00 | 21 | 22.5 | 657 |  | low | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-3, 16th Floor OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 20 | 44 | 430 | south | 2020-09-18 09:00 | 9:00 | 20 | 44 | 430 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Outdoors |  |  | 15 | 32 | 325 |  |  |  | Base readings | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B25165¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Boardroom | [5 empty] | 24 | 32 | 590 |  | 2020-09-18 12:00 | 12:00 | 24 | 32 | 590 |  | low | 2020-09-14 | B14895¦Basement Boardroom¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 307 | [5 empty] | 21 | 32 | 773 | south | 2020-09-18 12:00 | 12:00 | 21 | 32 | 773 |  | low | 2020-09-14 | B20979¦Courtroom 307¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Coutroom 16-3, 16th Floor OTHER | [5 empty] | 21 | 22 | 660 |  | 2020-09-18 12:00 | 12:00 | 21 | 22 | 660 |  | low | 2020-09-14 | B25398¦Corridor adj. to Coutroom 16-3, 16th Floor OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Male Holding Cell | [5 empty] | 24 | 28 | 492 |  | 2020-09-18 12:00 | 12:00 | 24 | 28 | 492 |  | low | 2020-09-14 | B14895¦Male Holding Cell¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 20 | 43 | 425 | north | 2020-09-18 09:00 | 9:00 | 20 | 43 | 425 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | OTHER | [5 empty] | 21 | 33 | 430 | Courtroom 700, please add to drop down box, thank you | 2020-09-18 12:00 | 12:00 | 21 | 33 | 430 |  | low | 2020-09-14 | B25165¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 307 | [5 empty] | 22 | 33 | 849 | north | 2020-09-18 12:00 | 12:00 | 22 | 33 | 849 |  | low | 2020-09-14 | B20979¦Courtroom 307¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 16th Floor OTHER | [5 empty] | 21 | 22 | 641 |  | 2020-09-18 12:00 | 12:00 | 21 | 22 | 641 |  | low | 2020-09-14 | B25398¦Elevator Lobby, 16th Floor OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 20 | 43 | 425 | south | 2020-09-18 09:00 | 9:00 | 20 | 43 | 425 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 600 | [5 empty] | 21 | 33 | 467 |  | 2020-09-18 12:00 | 12:00 | 21 | 33 | 467 |  | low | 2020-09-14 | B25165¦Courtroom 600¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-2 | [5 empty] | 19.9 | 45.8 | 562 |  | 2020-09-18 09:00 | 9:00 | 19.9 | 45.8 | 562 |  |  | 2020-09-14 | B10644¦Courtroom 2-2¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Outdoors |  |  | 14 | 25 | 430 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B14895¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Washrooms, 16th Floor OTHER | [5 empty] | 21 | 22 | 653 |  | 2020-09-18 12:00 | 12:00 | 21 | 22 | 653 |  | low | 2020-09-14 | B25398¦Corridor adj. to Washrooms, 16th Floor OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 22 | 32 | 694 | east | 2020-09-18 12:00 | 12:00 | 22 | 32 | 694 |  | low | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Intake Court | [5 empty] | 22 | 45 | 449 |  | 2020-09-18 12:00 | 12:00 | 22 | 45 | 449 |  |  | 2020-09-14 | B14209¦Intake Court¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 308 | [5 empty] | 21 | 33 | 457 |  | 2020-09-18 12:00 | 12:00 | 21 | 33 | 457 |  | low | 2020-09-14 | B25165¦Courtroom 308¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 20 | 43 | 420 | north | 2020-09-18 09:00 | 9:00 | 20 | 43 | 420 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 3-2 | [5 empty] | 21.5 | 30.9 | 614 |  | 2020-09-18 09:00 | 9:00 | 21.5 | 30.9 | 614 |  | low | 2020-09-14 | B10644¦Courtroom 3-2¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Women's Washroom, 16th Floor | [5 empty] | 21 | 23 | 648 |  | 2020-09-18 12:00 | 12:00 | 21 | 23 | 648 |  | low | 2020-09-14 | B25398¦OTHER Women's Washroom, 16th Floor¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Level 1 Corridor by room 103 | [5 empty] | 23 | 43 | 453 |  | 2020-09-18 12:00 | 12:00 | 23 | 43 | 453 |  |  | 2020-09-14 | B14209¦Level 1 Corridor by room 103¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 20 | 44 | 425 | south | 2020-09-18 09:00 | 9:00 | 20 | 44 | 425 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 306 | [5 empty] | 21 | 33 | 490 |  | 2020-09-18 12:00 | 12:00 | 21 | 33 | 490 |  | low | 2020-09-14 | B25165¦Courtroom 306¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 22 | 32 | 737 | west | 2020-09-18 12:00 | 12:00 | 22 | 32 | 737 |  | low | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 20 | 43 | 420 | north | 2020-09-18 09:00 | 9:00 | 20 | 43 | 420 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 304 | [5 empty] | 21 | 33 | 444 |  | 2020-09-18 12:00 | 12:00 | 21 | 33 | 444 |  | low | 2020-09-14 | B25165¦Courtroom 304¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Entrance by Stair G | [5 empty] | 25 | 31 | 447 |  | 2020-09-18 12:00 | 12:00 | 25 | 31 | 447 |  | low | 2020-09-14 | B14209¦Entrance by Stair G¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Reception, 15th Floor | [5 empty] | 21 | 26 | 676 |  | 2020-09-18 12:00 | 12:00 | 21 | 26 | 676 |  | low | 2020-09-14 | B25398¦OTHER Reception, 15th Floor¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 20 | 43 | 423 | south | 2020-09-18 09:00 | 9:00 | 20 | 43 | 423 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Hallway by courtroom 307 | [5 empty] | 21 | 28 | 519 |  | 2020-09-18 12:00 | 12:00 | 21 | 28 | 519 |  | low | 2020-09-14 | B20979¦Hallway by courtroom 307¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 302 | [5 empty] | 21 | 33 | 440 |  | 2020-09-18 12:00 | 12:00 | 21 | 33 | 440 |  | low | 2020-09-14 | B25165¦Courtroom 302¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 20 | 43 | 425 | north | 2020-09-18 09:00 | 9:00 | 20 | 43 | 425 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South, 15th Floor | [5 empty] | 21 | 29 | 672 |  | 2020-09-18 12:00 | 12:00 | 21 | 29 | 672 |  | low | 2020-09-14 | B25398¦OTHER Office Area, South, 15th Floor¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Hallway by courtroom 302 | [5 empty] | 21 | 28 | 512 |  | 2020-09-18 12:00 | 12:00 | 21 | 28 | 512 |  | low | 2020-09-14 | B20979¦Hallway by courtroom 302¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 208 | [5 empty] | 21 | 33 | 446 |  | 2020-09-18 12:00 | 12:00 | 21 | 33 | 446 |  | low | 2020-09-14 | B25165¦Courtroom 208¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 20 | 43 | 420 | south | 2020-09-18 09:00 | 9:00 | 20 | 43 | 420 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Library | [5 empty] | 22 | 43 | 448 |  | 2020-09-18 12:00 | 12:00 | 22 | 43 | 448 |  |  | 2020-09-14 | B14209¦Library¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 206 | [5 empty] | 21 | 33 | 428 |  | 2020-09-18 12:00 | 12:00 | 21 | 33 | 428 |  | low | 2020-09-14 | B25165¦Courtroom 206¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South East, 15th Floor | [5 empty] | 21 | 29 | 673 |  | 2020-09-18 12:00 | 12:00 | 21 | 29 | 673 |  | low | 2020-09-14 | B25398¦OTHER Office Area, South East, 15th Floor¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | 213 | [5 empty] | 20 | 43 | 424 | north | 2020-09-18 09:00 | 9:00 | 20 | 43 | 424 |  |  | 2020-09-14 | B18359¦213¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 26 | 560 | south | 2020-09-18 12:00 | 12:00 | 22 | 26 | 560 |  | low | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 204 | [5 empty] | 21 | 33 | 448 |  | 2020-09-18 12:00 | 12:00 | 21 | 33 | 448 |  | low | 2020-09-14 | B25165¦Courtroom 204¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | 213 | [5 empty] | 20 | 44 | 421 | south | 2020-09-18 09:00 | 9:00 | 20 | 44 | 421 |  |  | 2020-09-14 | B18359¦213¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-1 | [5 empty] | 19.9 | 49.4 | 407 |  | 2020-09-18 09:00 | 9:00 | 19.9 | 49.4 | 407 |  |  | 2020-09-14 | B10644¦Courtroom 6-1¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Law Library Meeting Room (028B) | [5 empty] | 24 | 40 | 467 |  | 2020-09-18 12:00 | 12:00 | 24 | 40 | 467 |  | caution | 2020-09-14 | B14209¦Law Library Meeting Room (028B)¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | 214 | [5 empty] | 20 | 44 | 425 | north | 2020-09-18 09:00 | 9:00 | 20 | 44 | 425 |  |  | 2020-09-14 | B18359¦214¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 25 | 457 | north | 2020-09-18 12:00 | 12:00 | 22 | 25 | 457 |  | low | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 202 | [5 empty] | 21 | 33 | 436 |  | 2020-09-18 12:00 | 12:00 | 21 | 33 | 436 |  | low | 2020-09-14 | B25165¦Courtroom 202¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Lunch Room | [5 empty] | 22 | 44 | 451 |  | 2020-09-18 12:00 | 12:00 | 22 | 44 | 451 |  |  | 2020-09-14 | B14209¦Lunch Room¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, East, 15th Floor | [5 empty] | 21 | 29 | 673 |  | 2020-09-18 12:00 | 12:00 | 21 | 29 | 673 |  | low | 2020-09-14 | B25398¦OTHER Office Area, East, 15th Floor¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | 214 | [5 empty] | 20 | 44 | 419 | south | 2020-09-18 09:00 | 9:00 | 20 | 44 | 419 |  |  | 2020-09-14 | B18359¦214¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 200 | [5 empty] | 21 | 33 | 449 |  | 2020-09-18 12:00 | 12:00 | 21 | 33 | 449 |  | low | 2020-09-14 | B25165¦Courtroom 200¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Basement cells - hallway | [5 empty] | 22 | 21 | 431 |  | 2020-09-18 12:00 | 12:00 | 22 | 21 | 431 |  | low | 2020-09-14 | B20979¦Basement cells - hallway¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | 215 | [5 empty] | 20 | 44 | 423 | north | 2020-09-18 09:00 | 9:00 | 20 | 44 | 423 |  |  | 2020-09-14 | B18359¦215¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Main Floor Entrance Lobby | [5 empty] | 15 | 47 | 488 |  | 2020-09-18 12:00 | 12:00 | 15 | 47 | 488 |  |  | 2020-09-14 | B14209¦Main Floor Entrance Lobby¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North East, 15th Floor | [5 empty] | 21 | 29 | 674 |  | 2020-09-18 12:00 | 12:00 | 21 | 29 | 674 |  | low | 2020-09-14 | B25398¦OTHER Office Area, North East, 15th Floor¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 100 | [5 empty] | 21 | 33 | 441 |  | 2020-09-18 12:00 | 12:00 | 21 | 33 | 441 |  | low | 2020-09-14 | B25165¦Courtroom 100¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Police office | [5 empty] | 22 | 27 | 530 |  | 2020-09-18 12:00 | 12:00 | 22 | 27 | 530 |  | low | 2020-09-14 | B20979¦Police office¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | 215 | [5 empty] | 20 | 44 | 419 | south | 2020-09-18 09:00 | 9:00 | 20 | 44 | 419 |  |  | 2020-09-14 | B18359¦215¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Outdoors |  |  | 14 | 32 | 393 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B14209¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North, 15th Floor | [5 empty] | 21 | 29 | 674 |  | 2020-09-18 12:00 | 12:00 | 21 | 29 | 674 |  | low | 2020-09-14 | B25398¦OTHER Office Area, North, 15th Floor¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | northeast corridor | [5 empty] | 20 | 43 | 420 |  | 2020-09-18 09:00 | 9:00 | 20 | 43 | 420 |  |  | 2020-09-14 | B18359¦northeast corridor¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Outdoors |  |  | 18 | 23 | 461 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20979¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | outside | [5 empty] | 16 | 53 | 432 |  | 2020-09-18 09:00 | 9:00 | 16 | 53 | 432 |  |  | 2020-09-14 | B18359¦outside¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North West, 15th Floor | [5 empty] | 20 | 29 | 671 |  | 2020-09-18 12:00 | 12:00 | 20 | 29 | 671 |  | low | 2020-09-14 | B25398¦OTHER Office Area, North West, 15th Floor¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, West, 15th Floor | [5 empty] | 20 | 29 | 673 |  | 2020-09-18 12:00 | 12:00 | 20 | 29 | 673 |  | low | 2020-09-14 | B25398¦OTHER Office Area, West, 15th Floor¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Mail Room, 15th Floor OTHER | [5 empty] | 20 | 27 | 667 |  | 2020-09-18 12:00 | 12:00 | 20 | 27 | 667 |  | low | 2020-09-14 | B25398¦Corridor adj. to Mail Room, 15th Floor OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 15th Floor OTHER | [5 empty] | 21 | 26 | 678 |  | 2020-09-18 12:00 | 12:00 | 21 | 26 | 678 |  | low | 2020-09-14 | B25398¦Elevator Lobby, 15th Floor OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Outdoors |  |  | 16 | 26 | 648 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B25398¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | front seating area | [5 empty] | 21 | 43 | 418 |  | 2020-09-18 12:00 | 12:00 | 21 | 43 | 418 |  |  | 2020-09-14 | B18359¦front seating area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | northwest corridor | [5 empty] | 21 | 43 | 420 |  | 2020-09-18 12:00 | 12:00 | 21 | 43 | 420 |  |  | 2020-09-14 | B18359¦northwest corridor¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 22 | 40 | 431 | north | 2020-09-18 12:00 | 12:00 | 22 | 40 | 431 |  | caution | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 22 | 40 | 429 | south | 2020-09-18 12:00 | 12:00 | 22 | 40 | 429 |  | caution | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 22 | 41 | 422 | north | 2020-09-18 12:00 | 12:00 | 22 | 41 | 422 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 21 | 41 | 429 | south | 2020-09-18 12:00 | 12:00 | 21 | 41 | 429 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 21 | 41 | 425 | north | 2020-09-18 12:00 | 12:00 | 21 | 41 | 425 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 21 | 41 | 424 | south | 2020-09-18 12:00 | 12:00 | 21 | 41 | 424 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 42 | 418 | north | 2020-09-18 12:00 | 12:00 | 21 | 42 | 418 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 42 | 421 | south | 2020-09-18 12:00 | 12:00 | 21 | 42 | 421 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 42 | 444 | north | 2020-09-18 12:00 | 12:00 | 21 | 42 | 444 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 42 | 421 | south | 2020-09-18 12:00 | 12:00 | 21 | 42 | 421 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 21 | 42 | 415 | north | 2020-09-18 12:00 | 12:00 | 21 | 42 | 415 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 21 | 42 | 421 | south | 2020-09-18 12:00 | 12:00 | 21 | 42 | 421 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 21 | 43 | 419 | north | 2020-09-18 12:00 | 12:00 | 21 | 43 | 419 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 21 | 43 | 423 | south | 2020-09-18 12:00 | 12:00 | 21 | 43 | 423 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 | [5 empty] | 23 | 40 | 460 |  | 2020-09-18 15:00 | 15:00 | 23 | 40 | 460 |  | caution | 2020-09-14 | B14209¦Courtroom 1¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 21 | 43 | 420 | north | 2020-09-18 12:00 | 12:00 | 21 | 43 | 420 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 21 | 43 | 416 | south | 2020-09-18 12:00 | 12:00 | 21 | 43 | 416 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 21 | 43 | 419 | north | 2020-09-18 12:00 | 12:00 | 21 | 43 | 419 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 1 | [5 empty] | 22 | 36 | 455 |  | 2020-09-18 09:00 | 9:00 | 22 | 36 | 455 |  | caution | 2020-09-14 | B25602¦Courtroom 1¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 21 | 43 | 427 | south | 2020-09-18 12:00 | 12:00 | 21 | 43 | 427 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 2 | [5 empty] | 22 | 38 | 466 |  | 2020-09-18 09:00 | 9:00 | 22 | 38 | 466 |  | caution | 2020-09-14 | B25602¦Courtroom 2¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 21 | 43 | 419 | north | 2020-09-18 12:00 | 12:00 | 21 | 43 | 419 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 21 | 43 | 423 | south | 2020-09-18 12:00 | 12:00 | 21 | 43 | 423 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 21 | 43 | 427 | north | 2020-09-18 12:00 | 12:00 | 21 | 43 | 427 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 21 | 43 | 415 | south | 2020-09-18 12:00 | 12:00 | 21 | 43 | 415 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 21 | 43 | 414 | north | 2020-09-18 12:00 | 12:00 | 21 | 43 | 414 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 3 | [5 empty] | 22 | 34 | 440 |  | 2020-09-18 09:00 | 9:00 | 22 | 34 | 440 |  | low | 2020-09-14 | B25602¦Courtroom 3¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 21 | 43 | 418 | south | 2020-09-18 12:00 | 12:00 | 21 | 43 | 418 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Outdoors |  |  | 13 | 34 | 483 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10000¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 21 | 42 | 418 | north | 2020-09-18 12:00 | 12:00 | 21 | 42 | 418 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 21 | 43 | 416 | south | 2020-09-18 12:00 | 12:00 | 21 | 43 | 416 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 21 | 43 | 429 | north | 2020-09-18 12:00 | 12:00 | 21 | 43 | 429 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 4 | [5 empty] | 23 | 33 | 435 |  | 2020-09-18 09:00 | 9:00 | 23 | 33 | 435 |  | low | 2020-09-14 | B25602¦Courtroom 4¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 21 | 43 | 417 | south | 2020-09-18 12:00 | 12:00 | 21 | 43 | 417 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 21 | 43 | 447 | north | 2020-09-18 12:00 | 12:00 | 21 | 43 | 447 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 5 | [5 empty] | 23 | 31 | 440 |  | 2020-09-18 09:00 | 9:00 | 23 | 31 | 440 |  | low | 2020-09-14 | B25602¦Courtroom 5¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 21 | 43 | 415 | south | 2020-09-18 12:00 | 12:00 | 21 | 43 | 415 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 6 | [5 empty] | 23 | 31 | 441 |  | 2020-09-18 09:00 | 9:00 | 23 | 31 | 441 |  | low | 2020-09-14 | B25602¦Courtroom 6¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | northeast corridor | [5 empty] | 21 | 43 | 422 |  | 2020-09-18 12:00 | 12:00 | 21 | 43 | 422 |  |  | 2020-09-14 | B18359¦northeast corridor¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 7 | [5 empty] | 23 | 38 | 455 |  | 2020-09-18 09:00 | 9:00 | 23 | 38 | 455 |  | caution | 2020-09-14 | B25602¦Courtroom 7¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | outside | [5 empty] | 17 | 50 | 408 |  | 2020-09-18 12:00 | 12:00 | 17 | 50 | 408 |  |  | 2020-09-14 | B18359¦outside¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 1 | [5 empty] | 22 | 31 | 480 |  | 2020-09-18 12:00 | 12:00 | 22 | 31 | 480 |  | low | 2020-09-14 | B25602¦Courtroom 1¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | front seating area | [5 empty] | 22 | 43 | 434 |  | 2020-09-18 15:00 | 15:00 | 22 | 43 | 434 |  |  | 2020-09-14 | B18359¦front seating area¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 2 | [5 empty] | 22 | 32 | 466 |  | 2020-09-18 12:00 | 12:00 | 22 | 32 | 466 |  | low | 2020-09-14 | B25602¦Courtroom 2¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | northwest corridor | [5 empty] | 22 | 42 | 421 |  | 2020-09-18 15:00 | 15:00 | 22 | 42 | 421 |  |  | 2020-09-14 | B18359¦northwest corridor¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 3 | [5 empty] | 22 | 32 | 468 |  | 2020-09-18 12:00 | 12:00 | 22 | 32 | 468 |  | low | 2020-09-14 | B25602¦Courtroom 3¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 22 | 42 | 415 | north | 2020-09-18 15:00 | 15:00 | 22 | 42 | 415 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 201 | [5 empty] | 22 | 42 | 416 | south | 2020-09-18 15:00 | 15:00 | 22 | 42 | 416 |  |  | 2020-09-14 | B18359¦Courtroom 201¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 4 | [5 empty] | 22 | 33 | 440 |  | 2020-09-18 12:00 | 12:00 | 22 | 33 | 440 |  | low | 2020-09-14 | B25602¦Courtroom 4¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 21 | 43 | 416 | north | 2020-09-18 15:00 | 15:00 | 21 | 43 | 416 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 5 | [5 empty] | 23 | 32 | 474 |  | 2020-09-18 12:00 | 12:00 | 23 | 32 | 474 |  | low | 2020-09-14 | B25602¦Courtroom 5¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Outdoors |  |  | 13 | 34 | 483 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10000¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 6 | [5 empty] | 23 | 31 | 438 |  | 2020-09-18 12:00 | 12:00 | 23 | 31 | 438 |  | low | 2020-09-14 | B25602¦Courtroom 6¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 7 | [5 empty] | 23 | 32 | 475 |  | 2020-09-18 12:00 | 12:00 | 23 | 32 | 475 |  | low | 2020-09-14 | B25602¦Courtroom 7¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 - waiting room | [5 empty] | 22 | 38 | 440 |  | 2020-09-18 15:00 | 15:00 | 22 | 38 | 440 |  | caution | 2020-09-14 | B14209¦Courtroom 2 - waiting room¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 1 | [5 empty] | 21.1111 | 28 | 515 |  | 2020-09-18 15:00 | 15:00 | 21.1111 | 28 | 515 |  | low | 2020-09-14 | B10000¦Courtroom 1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 202 | [5 empty] | 21 | 43 | 423 | south | 2020-09-18 15:00 | 15:00 | 21 | 43 | 423 |  |  | 2020-09-14 | B18359¦Courtroom 202¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Outdoors |  |  | 11 | 33 | 678 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B25602¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 2 | [5 empty] | 22 | 37 | 451 |  | 2020-09-18 15:00 | 15:00 | 22 | 37 | 451 |  | caution | 2020-09-14 | B14209¦Courtroom 2¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 21 | 43 | 428 | north | 2020-09-18 15:00 | 15:00 | 21 | 43 | 428 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd fl lobby | [5 empty] | 21 | 27 | 493 |  | 2020-09-18 15:00 | 15:00 | 21 | 27 | 493 |  | low | 2020-09-14 | B20226¦2nd fl lobby¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 2 | [5 empty] | 21.6667 | 28 | 444 |  | 2020-09-18 15:00 | 15:00 | 21.6667 | 28 | 444 |  | low | 2020-09-14 | B10000¦Courtroom 2¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Courtroom 1 - waiting area | [5 empty] | 23 | 40 | 464 |  | 2020-09-18 15:00 | 15:00 | 23 | 40 | 464 |  | caution | 2020-09-14 | B14209¦Courtroom 1 - waiting area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 203 | [5 empty] | 21 | 43 | 420 | south | 2020-09-18 15:00 | 15:00 | 21 | 43 | 420 |  |  | 2020-09-14 | B18359¦Courtroom 203¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 3 | [5 empty] | 22.2222 | 23 | 477 |  | 2020-09-18 15:00 | 15:00 | 22.2222 | 23 | 477 |  | low | 2020-09-14 | B10000¦Courtroom 3¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room | [5 empty] | 22 | 39 | 422 |  | 2020-09-18 15:00 | 15:00 | 22 | 39 | 422 |  | caution | 2020-09-14 | B14209¦Hearing Room¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 43 | 423 | north | 2020-09-18 15:00 | 15:00 | 21 | 43 | 423 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 2 | [5 empty] | 21 | 26 | 466 |  | 2020-09-18 15:00 | 15:00 | 21 | 26 | 466 |  | low | 2020-09-14 | B20226¦Courtroom 2¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 204 | [5 empty] | 21 | 43 | 414 | south | 2020-09-18 15:00 | 15:00 | 21 | 43 | 414 |  |  | 2020-09-14 | B18359¦Courtroom 204¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room, Judge’s Chamber | [5 empty] | 22 | 39 | 423 |  | 2020-09-18 15:00 | 15:00 | 22 | 39 | 423 |  | caution | 2020-09-14 | B14209¦Hearing Room, Judge’s Chamber¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 43 | 411 | north | 2020-09-18 15:00 | 15:00 | 21 | 43 | 411 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 4 | [5 empty] | 20.5556 | 23 | 477 |  | 2020-09-18 15:00 | 15:00 | 20.5556 | 23 | 477 |  | low | 2020-09-14 | B10000¦Courtroom 4¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 101 | [5 empty] | 21 | 34 |  |  | 2020-09-18 15:00 | 15:00 | 21 | 34 |  |  | low | 2020-09-14 | B20080¦Courtroom 101¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 205 | [5 empty] | 21 | 43 | 416 | south | 2020-09-18 15:00 | 15:00 | 21 | 43 | 416 |  |  | 2020-09-14 | B18359¦Courtroom 205¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 1 | [5 empty] | 21 | 29 | 488 |  | 2020-09-18 15:00 | 15:00 | 21 | 29 | 488 |  | low | 2020-09-14 | B20226¦Courtroom 1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Hearing Room - Waiting area | [5 empty] | 23 | 40 | 475 |  | 2020-09-18 15:00 | 15:00 | 23 | 40 | 475 |  | caution | 2020-09-14 | B14209¦Hearing Room - Waiting area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 5 | [5 empty] | 21.6667 | 25 | 490 |  | 2020-09-18 15:00 | 15:00 | 21.6667 | 25 | 490 |  | low | 2020-09-14 | B10000¦Courtroom 5¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 21 | 43 | 418 | north | 2020-09-18 15:00 | 15:00 | 21 | 43 | 418 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Front desk | [5 empty] | 23 | 42 | 478 |  | 2020-09-18 15:00 | 15:00 | 23 | 42 | 478 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Front desk¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 6 | [5 empty] | 21.6667 | 25 | 490 |  | 2020-09-18 15:00 | 15:00 | 21.6667 | 25 | 490 |  | low | 2020-09-14 | B10000¦Courtroom 6¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 206 | [5 empty] | 21 | 43 | 414 | south | 2020-09-18 15:00 | 15:00 | 21 | 43 | 414 |  |  | 2020-09-14 | B18359¦Courtroom 206¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 201 | [5 empty] | 22 | 30 | 448 |  | 2020-09-18 15:00 | 15:00 | 22 | 30 | 448 |  | low | 2020-09-14 | B20080¦Courtroom 201¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown attorney admin area | [5 empty] | 21 | 42 | 475 |  | 2020-09-18 15:00 | 15:00 | 21 | 42 | 475 |  |  | 2020-09-14 | B14209¦Crown attorney admin area¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Security Check In | [5 empty] | 20 | 34 | 419 |  | 2020-09-18 09:00 | 9:00 | 20 | 34 | 419 |  | low | 2020-09-14 | B92624¦Security Check In¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 21 | 44 | 420 | north | 2020-09-18 15:00 | 15:00 | 21 | 44 | 420 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 7 | [5 empty] | 22.2222 | 23 | 437 |  | 2020-09-18 15:00 | 15:00 | 22.2222 | 23 | 437 |  | low | 2020-09-14 | B10000¦Courtroom 7¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office Print Room | [5 empty] | 21 | 42 | 475 |  | 2020-09-18 15:00 | 15:00 | 21 | 42 | 475 |  |  | 2020-09-14 | B14209¦Crown Attorney Office Print Room¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 207 | [5 empty] | 21 | 44 | 415 | south | 2020-09-18 15:00 | 15:00 | 21 | 44 | 415 |  |  | 2020-09-14 | B18359¦Courtroom 207¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 1 | [5 empty] | 22 | 22 | 462 |  | 2020-09-18 15:00 | 15:00 | 22 | 22 | 462 |  | low | 2020-09-14 | B25602¦Courtroom 1¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 21 | 35 | 414 | West | 2020-09-18 09:00 | 9:00 | 21 | 35 | 414 |  | caution | 2020-09-14 | B92624¦Room 701¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 21 | 44 | 416 | north | 2020-09-18 15:00 | 15:00 | 21 | 44 | 416 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office North | [5 empty] | 22 | 39 | 746 |  | 2020-09-18 15:00 | 15:00 | 22 | 39 | 746 |  | caution | 2020-09-14 | B14895¦Administration Office North¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 2 | [5 empty] | 22 | 23 | 471 |  | 2020-09-18 15:00 | 15:00 | 22 | 23 | 471 |  | low | 2020-09-14 | B25602¦Courtroom 2¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 208 | [5 empty] | 21 | 44 | 419 | south | 2020-09-18 15:00 | 15:00 | 21 | 44 | 419 |  |  | 2020-09-14 | B18359¦Courtroom 208¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 202 | [5 empty] | 23 | 30 | 563 |  | 2020-09-18 15:00 | 15:00 | 23 | 30 | 563 |  | low | 2020-09-14 | B20080¦Courtroom 202¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 21 | 34 | 411 | East | 2020-09-18 09:00 | 9:00 | 21 | 34 | 411 |  | low | 2020-09-14 | B92624¦Room 701¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Administration Office South | [5 empty] | 22 | 31 | 640 |  | 2020-09-18 15:00 | 15:00 | 22 | 31 | 640 |  | low | 2020-09-14 | B14895¦Administration Office South¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 21 | 44 | 420 | north | 2020-09-18 15:00 | 15:00 | 21 | 44 | 420 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 21 | 35 | 411 | North | 2020-09-18 09:00 | 9:00 | 21 | 35 | 411 |  | caution | 2020-09-14 | B92624¦Room 701¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Assistant Crown Attorney Office (236) | [5 empty] | 21 | 43 | 448 |  | 2020-09-18 15:00 | 15:00 | 21 | 43 | 448 |  |  | 2020-09-14 | B14209¦Assistant Crown Attorney Office (236)¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 22 | 23 | 487 |  | 2020-09-18 15:00 | 15:00 | 22 | 23 | 487 |  | low | 2020-09-14 | B20226¦2nd Floor Holding Cell¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 301 | [5 empty] | 24 | 30 | 438 |  | 2020-09-18 15:00 | 15:00 | 24 | 30 | 438 |  | low | 2020-09-14 | B20080¦Courtroom 301¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 21 | 44 | 428 | south | 2020-09-18 15:00 | 15:00 | 21 | 44 | 428 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Entry/Waiting | [5 empty] | 23 | 31 | 492 |  | 2020-09-18 15:00 | 15:00 | 23 | 31 | 492 |  | low | 2020-09-14 | B70510¦Entry/Waiting¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room A | [5 empty] | 23 | 30 | 480 |  | 2020-09-18 15:00 | 15:00 | 23 | 30 | 480 |  | low | 2020-09-14 | B70510¦Mediation Room A¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 101 | [5 empty] | 20 | 33 | 506 |  | 2020-09-18 15:00 | 15:00 | 20 | 33 | 506 |  | low | 2020-09-14 | B19512¦Courtroom 101¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Courtroom 3 | [5 empty] | 21 | 27 | 548 |  | 2020-09-18 15:00 | 15:00 | 21 | 27 | 548 |  | low | 2020-09-14 | B20226¦Courtroom 3¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 701 | [5 empty] | 20 | 33 | 417 |  | 2020-09-18 09:00 | 9:00 | 20 | 33 | 417 |  | low | 2020-09-14 | B92624¦Hallway by Room 701¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 22 | 29 | 415 | East | 2020-09-18 09:00 | 9:00 | 22 | 29 | 415 |  | low | 2020-09-14 | B92624¦Room 718A¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Information Desk | [5 empty] | 23 | 30 | 488 |  | 2020-09-18 15:00 | 15:00 | 23 | 30 | 488 |  | low | 2020-09-14 | B70510¦Information Desk¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20226 | B20226 - 38 Pine St N - Timmins | Outdoors |  |  | 12 | 22 | 399 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20226¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 200 | [5 empty] | 22 | 40 | 594 |  | 2020-09-18 15:00 | 15:00 | 22 | 40 | 594 |  | caution | 2020-09-14 | B19512¦Courtroom 200¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 22 | 28 | 520 | West | 2020-09-18 09:00 | 9:00 | 22 | 28 | 520 |  | low | 2020-09-14 | B92624¦Room 718A¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718B | [5 empty] | 22 | 32 | 430 |  | 2020-09-18 09:00 | 9:00 | 22 | 32 | 430 |  | low | 2020-09-14 | B92624¦Room 718B¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Main Lobby | [5 empty] | 20 | 42 | 522 |  | 2020-09-18 15:00 | 15:00 | 20 | 42 | 522 |  |  | 2020-09-14 | B70050¦Main Lobby¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Courtroom 201 | [5 empty] | 22 | 40 | 594 |  | 2020-09-18 15:00 | 15:00 | 22 | 40 | 594 |  | caution | 2020-09-14 | B19512¦Courtroom 201¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Lunch Room 454 | [5 empty] | 23 | 30 | 458 |  | 2020-09-18 15:00 | 15:00 | 23 | 30 | 458 |  | low | 2020-09-14 | B70510¦Lunch Room 454¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 718A | [5 empty] | 22 | 27 | 418 |  | 2020-09-18 09:00 | 9:00 | 22 | 27 | 418 |  | low | 2020-09-14 | B92624¦Hallway by Room 718A¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Copy Room 455 | [5 empty] | 23 | 30 | 455 |  | 2020-09-18 15:00 | 15:00 | 23 | 30 | 455 |  | low | 2020-09-14 | B70510¦Copy Room 455¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717A | [5 empty] | 21 | 39 | 402 |  | 2020-09-18 09:00 | 9:00 | 21 | 39 | 402 |  | caution | 2020-09-14 | B92624¦Room 717A¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Office | [5 empty] | 21 | 42 | 433 |  | 2020-09-18 15:00 | 15:00 | 21 | 42 | 433 |  |  | 2020-09-14 | B14209¦Crown Attorney Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 1 | [5 empty] | 20 | 42 | 516 |  | 2020-09-18 15:00 | 15:00 | 20 | 42 | 516 |  |  | 2020-09-14 | B70050¦Courtroom 1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mediation Room B | [5 empty] | 23 | 31 | 469 |  | 2020-09-18 15:00 | 15:00 | 23 | 31 | 469 |  | low | 2020-09-14 | B70510¦Mediation Room B¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717B | [5 empty] | 21 | 38 | 407 |  | 2020-09-18 09:00 | 9:00 | 21 | 38 | 407 |  | caution | 2020-09-14 | B92624¦Room 717B¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Crown Attorney Meeting Room (232) | [5 empty] | 21 | 42 | 434 |  | 2020-09-18 15:00 | 15:00 | 21 | 42 | 434 |  |  | 2020-09-14 | B14209¦Crown Attorney Meeting Room (232)¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 459 | [5 empty] | 23 | 30 | 466 |  | 2020-09-18 15:00 | 15:00 | 23 | 30 | 466 |  | low | 2020-09-14 | B70510¦Office 459¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716A | [5 empty] | 21 | 34 | 403 |  | 2020-09-18 09:00 | 9:00 | 21 | 34 | 403 |  | low | 2020-09-14 | B92624¦Room 716A¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B19512 | B19512 - 70 Wellington St - Brantford | Outdoors |  |  | 16 | 33 | [5 empty] | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B19512¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Outdoors |  |  | 11 | 28 | 396 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70050¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Lobby | [5 empty] | 22 | 42 | 468 |  | 2020-09-18 15:00 | 15:00 | 22 | 42 | 468 |  |  | 2020-09-14 | B14209¦Court Admin Office Lobby¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716B | [5 empty] | 21 | 34 | 411 |  | 2020-09-18 09:00 | 9:00 | 21 | 34 | 411 |  | low | 2020-09-14 | B92624¦Room 716B¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 467 | [5 empty] | 22 | 30 | 443 |  | 2020-09-18 15:00 | 15:00 | 22 | 30 | 443 |  | low | 2020-09-14 | B70510¦Office 467¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Court Admin Office Cubicles | [5 empty] | 22 | 43 | 494 |  | 2020-09-18 15:00 | 15:00 | 22 | 43 | 494 |  |  | 2020-09-14 | B14209¦Court Admin Office Cubicles¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Romo 715A | [5 empty] | 22 | 30 | 409 |  | 2020-09-18 09:00 | 9:00 | 22 | 30 | 409 |  | low | 2020-09-14 | B92624¦Romo 715A¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 469 | [5 empty] | 22 | 30 | 465 |  | 2020-09-18 15:00 | 15:00 | 22 | 30 | 465 |  | low | 2020-09-14 | B70510¦Office 469¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Holding Cell corridor | [5 empty] | 22 | 34 | 424 |  | 2020-09-18 15:00 | 15:00 | 22 | 34 | 424 |  | low | 2020-09-14 | B14209¦Holding Cell corridor¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715B | [5 empty] | 22 | 29 | 413 |  | 2020-09-18 09:00 | 9:00 | 22 | 29 | 413 |  | low | 2020-09-14 | B92624¦Room 715B¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714A | [5 empty] | 21 | 34 | 409 |  | 2020-09-18 09:00 | 9:00 | 21 | 34 | 409 |  | low | 2020-09-14 | B92624¦Room 714A¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Police Control Room | [5 empty] | 22 | 36 | 436 |  | 2020-09-18 15:00 | 15:00 | 22 | 36 | 436 |  | caution | 2020-09-14 | B14209¦Police Control Room¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Room 473 | [5 empty] | 22 | 31 | 466 |  | 2020-09-18 15:00 | 15:00 | 22 | 31 | 466 |  | low | 2020-09-14 | B70510¦Room 473¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 1 | [5 empty] | 23 | 27 |  |  | 2020-09-18 15:00 | 15:00 | 23 | 27 |  |  | low | 2020-09-14 | B24638¦Courtroom 1¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714B | [5 empty] | 22 | 33 | 414 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 414 |  | low | 2020-09-14 | B92624¦Room 714B¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd Floor Holding Cell | [5 empty] | 20 | 41 | 506 |  | 2020-09-18 15:00 | 15:00 | 20 | 41 | 506 |  |  | 2020-09-14 | B70050¦2nd Floor Holding Cell¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713A | [5 empty] | 21 | 28 | 397 |  | 2020-09-18 09:00 | 9:00 | 21 | 28 | 397 |  | low | 2020-09-14 | B92624¦Room 713A¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Intake Court | [5 empty] | 22 | 48 | 448 |  | 2020-09-18 15:00 | 15:00 | 22 | 48 | 448 |  |  | 2020-09-14 | B14209¦Intake Court¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hall 475 or 466 | [5 empty] | 22 | 31 | 460 |  | 2020-09-18 15:00 | 15:00 | 22 | 31 | 460 |  | low | 2020-09-14 | B70510¦Hall 475 or 466¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Courtroom 3 | [5 empty] | 23 | 28 | 391 |  | 2020-09-18 15:00 | 15:00 | 23 | 28 | 391 |  | low | 2020-09-14 | B24638¦Courtroom 3¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713B | [5 empty] | 22 | 28 | 411 |  | 2020-09-18 09:00 | 9:00 | 22 | 28 | 411 |  | low | 2020-09-14 | B92624¦Room 713B¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Level 1 Corridor by room 103 | [5 empty] | 23 | 41 | 453 |  | 2020-09-18 15:00 | 15:00 | 23 | 41 | 453 |  |  | 2020-09-14 | B14209¦Level 1 Corridor by room 103¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 1 | [5 empty] | 22 | 30 | 476 |  | 2020-09-18 15:00 | 15:00 | 22 | 30 | 476 |  | low | 2020-09-14 | B70510¦Hearing Room 1¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Escalator, 700 | [5 empty] | 22 | 29 | 414 |  | 2020-09-18 09:00 | 9:00 | 22 | 29 | 414 |  | low | 2020-09-14 | B92624¦Hallway by Escalator, 700¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Yannick Bedard Office - 2nd Floor | [5 empty] | 21 | 42 | 520 |  | 2020-09-18 15:00 | 15:00 | 21 | 42 | 520 |  |  | 2020-09-14 | B70050¦Yannick Bedard Office - 2nd Floor¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Entrance by Stair G | [5 empty] | 23 | 32 | 467 |  | 2020-09-18 15:00 | 15:00 | 23 | 32 | 467 |  | low | 2020-09-14 | B14209¦Entrance by Stair G¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B24638 | B24638 - 55 Main St W - Hamilton | Outdoors |  |  | 22 | 25 | 319 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B24638¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801A | [5 empty] | 21 | 31 | 403 |  | 2020-09-18 09:00 | 9:00 | 21 | 31 | 403 |  | low | 2020-09-14 | B92624¦Room 801A¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Meeting Rooms 1/2 | [5 empty] | 22 | 32 | 461 |  | 2020-09-18 15:00 | 15:00 | 22 | 32 | 461 |  | low | 2020-09-14 | B70510¦Vestibule at Meeting Rooms 1/2¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Library | [5 empty] | 22 | 46 | 459 |  | 2020-09-18 15:00 | 15:00 | 22 | 46 | 459 |  |  | 2020-09-14 | B14209¦Library¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801B | [5 empty] | 21 | 28 | 404 |  | 2020-09-18 09:00 | 9:00 | 21 | 28 | 404 |  | low | 2020-09-14 | B92624¦Room 801B¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 801A | [5 empty] | 20 | 25 | 403 |  | 2020-09-18 09:00 | 9:00 | 20 | 25 | 403 |  | low | 2020-09-14 | B92624¦Hallway by Room 801A¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Law Library Meeting Room (028B) | [5 empty] | 22 | 42 | 495 |  | 2020-09-18 09:00 | 9:00 | 22 | 42 | 495 |  |  | 2020-09-14 | B14209¦Law Library Meeting Room (028B)¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Vestibule at Hearing Room 1 | [5 empty] | 22 | 32 | 465 |  | 2020-09-18 15:00 | 15:00 | 22 | 32 | 465 |  | low | 2020-09-14 | B70510¦Vestibule at Hearing Room 1¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Lounge | [5 empty] | 21 | 31 | 434 |  | 2020-09-18 09:00 | 9:00 | 21 | 31 | 434 |  | low | 2020-09-14 | B92624¦Lounge¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Lunch Room | [5 empty] | 21 | 45 | 450 |  | 2020-09-18 15:00 | 15:00 | 21 | 45 | 450 |  |  | 2020-09-14 | B14209¦Lunch Room¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 2 | [5 empty] | 22 | 32 | 464 |  | 2020-09-18 15:00 | 15:00 | 22 | 32 | 464 |  | low | 2020-09-14 | B70510¦Hearing Room 2¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Outdoors |  |  | 12 | 33 | 431 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B92624¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 3 | [5 empty] | 22 | 40 | 522 |  | 2020-09-18 15:00 | 15:00 | 22 | 40 | 522 |  | caution | 2020-09-14 | B70050¦Courtroom 3¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Main Floor Entrance Lobby | [5 empty] | 23 | 38 | 648 |  | 2020-09-18 15:00 | 15:00 | 23 | 38 | 648 |  | caution | 2020-09-14 | B14209¦Main Floor Entrance Lobby¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Security Check In | [5 empty] | 20 | 34 | 420 |  | 2020-09-18 12:00 | 12:00 | 20 | 34 | 420 |  | low | 2020-09-14 | B92624¦Security Check In¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B14209 | B14209 - 89 James St - Parry Sound | Outdoors |  |  | 17 | 21 | 390 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B14209¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 439 | [5 empty] | 22 | 31 | 464 |  | 2020-09-18 15:00 | 15:00 | 22 | 31 | 464 |  | low | 2020-09-14 | B70510¦Office 439¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | Courtroom 2 | [5 empty] | 22 | 40 | 516 |  | 2020-09-18 15:00 | 15:00 | 22 | 40 | 516 |  | caution | 2020-09-14 | B70050¦Courtroom 2¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 21 | 34 | 394 | West | 2020-09-18 12:00 | 12:00 | 21 | 34 | 394 |  | low | 2020-09-14 | B92624¦Room 701¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | First Aid Desk | [5 empty] | 22 | 32 | 458 |  | 2020-09-18 15:00 | 15:00 | 22 | 32 | 458 |  | low | 2020-09-14 | B70510¦First Aid Desk¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 21 | 34 | 402 | East | 2020-09-18 12:00 | 12:00 | 21 | 34 | 402 |  | low | 2020-09-14 | B92624¦Room 701¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B70050 | B70050 - 48 Spruce St N - Timmins | 2nd fl lobby | [5 empty] | 21 | 40 | 497 |  | 2020-09-18 15:00 | 15:00 | 21 | 40 | 497 |  | caution | 2020-09-14 | B70050¦2nd fl lobby¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 436 | [5 empty] | 22 | 31 | 459 |  | 2020-09-18 15:00 | 15:00 | 22 | 31 | 459 |  | low | 2020-09-14 | B70510¦Office 436¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 21 | 35 | 396 | North | 2020-09-18 12:00 | 12:00 | 21 | 35 | 396 |  | caution | 2020-09-14 | B92624¦Room 701¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | COrridor Adj. to Courtroom 16-1, 16th Floor OTHER | [5 empty] | 21 | 23 | 677 |  | 2020-09-18 15:00 | 15:00 | 21 | 23 | 677 |  | low | 2020-09-14 | B25398¦COrridor Adj. to Courtroom 16-1, 16th Floor OTHER¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 701 | [5 empty] | 21 | 26 | 397 |  | 2020-09-18 12:00 | 12:00 | 21 | 26 | 397 |  | low | 2020-09-14 | B92624¦Hallway by Room 701¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 432 | [5 empty] | 22 | 31 | 467 |  | 2020-09-18 15:00 | 15:00 | 22 | 31 | 467 |  | low | 2020-09-14 | B70510¦Office 432¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20893 | B20893 - 75 Mulcaster St. - Barrie | Courtroom 7,8,9 | [5 empty] | 21.7 | 30 | 529 |  | 2020-09-18 15:00 | 15:00 | 21.7 | 30 | 529 |  | low | 2020-09-14 | B20893¦Courtroom 7,8,9¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 429 | [5 empty] | 23 | 31 | 467 |  | 2020-09-18 15:00 | 15:00 | 23 | 31 | 467 |  | low | 2020-09-14 | B70510¦Office 429¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 427 | [5 empty] | 23 | 31 | 463 |  | 2020-09-18 15:00 | 15:00 | 23 | 31 | 463 |  | low | 2020-09-14 | B70510¦Office 427¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92347 | B92347 - 75 Mulcaster Street - Barrie | Courtroom 15 | [5 empty] | 21.2 | 31 | 508 |  | 2020-09-18 15:00 | 15:00 | 21.2 | 31 | 508 |  | low | 2020-09-14 | B92347¦Courtroom 15¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Courtroom 16-3, 16th Floor OTHER | [5 empty] | 21 | 23 | 667 |  | 2020-09-18 15:00 | 15:00 | 21 | 23 | 667 |  | low | 2020-09-14 | B25398¦Corridor adj. to Courtroom 16-3, 16th Floor OTHER¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Mail Room | [5 empty] | 23 | 31 | 478 |  | 2020-09-18 15:00 | 15:00 | 23 | 31 | 478 |  | low | 2020-09-14 | B70510¦Mail Room¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 21 | 29 | 419 | East | 2020-09-18 12:00 | 12:00 | 21 | 29 | 419 |  | low | 2020-09-14 | B92624¦Room 718A¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 420 | [5 empty] | 23 | 31 | 495 |  | 2020-09-18 15:00 | 15:00 | 23 | 31 | 495 |  | low | 2020-09-14 | B70510¦Office 420¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 16th Floor OTHER | [5 empty] | 21 | 23 | 662 |  | 2020-09-18 15:00 | 15:00 | 21 | 23 | 662 |  | low | 2020-09-14 | B25398¦Elevator Lobby, 16th Floor OTHER¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Office 418 | [5 empty] | 23 | 31 | 511 |  | 2020-09-18 15:00 | 15:00 | 23 | 31 | 511 |  | low | 2020-09-14 | B70510¦Office 418¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | File Room | [5 empty] | 23 | 32 | 502 |  | 2020-09-18 15:00 | 15:00 | 23 | 32 | 502 |  | low | 2020-09-14 | B70510¦File Room¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 21 | 30 | 404 | West | 2020-09-18 12:00 | 12:00 | 21 | 30 | 404 |  | low | 2020-09-14 | B92624¦Room 718A¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Washrooms, 16th Floor OTHER | [5 empty] | 21 | 23 | 661 |  | 2020-09-18 15:00 | 15:00 | 21 | 23 | 661 |  | low | 2020-09-14 | B25398¦Corridor adj. to Washrooms, 16th Floor OTHER¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 8 | [5 empty] | 22.2222 | 22 | 444 |  | 2020-09-18 15:00 | 15:00 | 22.2222 | 22 | 444 |  | low | 2020-09-14 | B10000¦Courtroom 8¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718B | [5 empty] | 21 | 31 | 415 |  | 2020-09-18 12:00 | 12:00 | 21 | 31 | 415 |  | low | 2020-09-14 | B92624¦Room 718B¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Health Room | [5 empty] | 22 | 31 | 502 |  | 2020-09-18 15:00 | 15:00 | 22 | 31 | 502 |  | low | 2020-09-14 | B70510¦Health Room¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10000 | B10000 - 426 Queen St E - Sault Ste. Marie | Courtroom 9 | [5 empty] | 21.1111 | 25 | 490 |  | 2020-09-18 15:00 | 15:00 | 21.1111 | 25 | 490 |  | low | 2020-09-14 | B10000¦Courtroom 9¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 718A | [5 empty] | 22 | 26 | 407 |  | 2020-09-18 12:00 | 12:00 | 22 | 26 | 407 |  | low | 2020-09-14 | B92624¦Hallway by Room 718A¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 | [5 empty] | 22 | 31 | 474 |  | 2020-09-18 15:00 | 15:00 | 22 | 31 | 474 |  | low | 2020-09-14 | B70510¦Hearing Room 3¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717A | [5 empty] | 22 | 27 | 402 |  | 2020-09-18 12:00 | 12:00 | 22 | 27 | 402 |  | low | 2020-09-14 | B92624¦Room 717A¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Women's Washroom, 16th Floor | [5 empty] | 21 | 24 | 681 |  | 2020-09-18 15:00 | 15:00 | 21 | 24 | 681 |  | low | 2020-09-14 | B25398¦OTHER Women's Washroom, 16th Floor¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717B | [5 empty] | 22 | 27 | 399 |  | 2020-09-18 12:00 | 12:00 | 22 | 27 | 399 |  | low | 2020-09-14 | B92624¦Room 717B¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Hearing Room 3 Waiting Area | [5 empty] | 22 | 33 | 464 |  | 2020-09-18 15:00 | 15:00 | 22 | 33 | 464 |  | low | 2020-09-14 | B70510¦Hearing Room 3 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716A | [5 empty] | 22 | 28 | 394 |  | 2020-09-18 12:00 | 12:00 | 22 | 28 | 394 |  | low | 2020-09-14 | B92624¦Room 716A¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Elevator Lobby | [5 empty] | 22 | 31 | 462 |  | 2020-09-18 15:00 | 15:00 | 22 | 31 | 462 |  | low | 2020-09-14 | B70510¦Elevator Lobby¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Reception, 15th Floor | [5 empty] | 21 | 25 | 683 |  | 2020-09-18 15:00 | 15:00 | 21 | 25 | 683 |  | low | 2020-09-14 | B25398¦OTHER Reception, 15th Floor¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716B | [5 empty] | 22 | 29 | 419 |  | 2020-09-18 12:00 | 12:00 | 22 | 29 | 419 |  | low | 2020-09-14 | B92624¦Room 716B¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 3 | [5 empty] | 22 | 21 | 429 |  | 2020-09-18 15:00 | 15:00 | 22 | 21 | 429 |  | low | 2020-09-14 | B25602¦Courtroom 3¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715A | [5 empty] | 22 | 27 | 401 |  | 2020-09-18 12:00 | 12:00 | 22 | 27 | 401 |  | low | 2020-09-14 | B92624¦Room 715A¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B70510 | B70510 - 150 Dufferin Ave - London | Outdoors |  |  | 21 | 37 | 445 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70510¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South, 15th Floor | [5 empty] | 21 | 28 | 698 |  | 2020-09-18 15:00 | 15:00 | 21 | 28 | 698 |  | low | 2020-09-14 | B25398¦OTHER Office Area, South, 15th Floor¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715B | [5 empty] | 22 | 27 | 409 |  | 2020-09-18 12:00 | 12:00 | 22 | 27 | 409 |  | low | 2020-09-14 | B92624¦Room 715B¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 4 | [5 empty] | 23 | 22 | 414 |  | 2020-09-18 15:00 | 15:00 | 23 | 22 | 414 |  | low | 2020-09-14 | B25602¦Courtroom 4¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714A | [5 empty] | 22 | 28 | 395 |  | 2020-09-18 12:00 | 12:00 | 22 | 28 | 395 |  | low | 2020-09-14 | B92624¦Room 714A¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, South East, 15th Floor | [5 empty] | 21 | 28 | 695 |  | 2020-09-18 15:00 | 15:00 | 21 | 28 | 695 |  | low | 2020-09-14 | B25398¦OTHER Office Area, South East, 15th Floor¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 5 | [5 empty] | 23 | 20 | 422 |  | 2020-09-18 15:00 | 15:00 | 23 | 20 | 422 |  | low | 2020-09-14 | B25602¦Courtroom 5¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714B | [5 empty] | 22 | 28 | 399 |  | 2020-09-18 12:00 | 12:00 | 22 | 28 | 399 |  | low | 2020-09-14 | B92624¦Room 714B¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713A | [5 empty] | 22 | 28 | 402 |  | 2020-09-18 12:00 | 12:00 | 22 | 28 | 402 |  | low | 2020-09-14 | B92624¦Room 713A¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, East, 15th Floor | [5 empty] | 21 | 29 | 690 |  | 2020-09-18 15:00 | 15:00 | 21 | 29 | 690 |  | low | 2020-09-14 | B25398¦OTHER Office Area, East, 15th Floor¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713B | [5 empty] | 22 | 27 | 394 |  | 2020-09-18 12:00 | 12:00 | 22 | 27 | 394 |  | low | 2020-09-14 | B92624¦Room 713B¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 6 | [5 empty] | 23 | 22 | 428 |  | 2020-09-18 15:00 | 15:00 | 23 | 22 | 428 |  | low | 2020-09-14 | B25602¦Courtroom 6¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Escalator, 700 | [5 empty] | 21 | 27 | 393 |  | 2020-09-18 12:00 | 12:00 | 21 | 27 | 393 |  | low | 2020-09-14 | B92624¦Hallway by Escalator, 700¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North East, 15th Floor | [5 empty] | 20 | 28 | 668 |  | 2020-09-18 15:00 | 15:00 | 20 | 28 | 668 |  | low | 2020-09-14 | B25398¦OTHER Office Area, North East, 15th Floor¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801A | [5 empty] | 21 | 27 | 388 |  | 2020-09-18 12:00 | 12:00 | 21 | 27 | 388 |  | low | 2020-09-14 | B92624¦Room 801A¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Courtroom 7 | [5 empty] | 23 | 21 | 477 |  | 2020-09-18 15:00 | 15:00 | 23 | 21 | 477 |  | low | 2020-09-14 | B25602¦Courtroom 7¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801B | [5 empty] | 21 | 25 | 399 |  | 2020-09-18 12:00 | 12:00 | 21 | 25 | 399 |  | low | 2020-09-14 | B92624¦Room 801B¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North, 15th Floor | [5 empty] | 20 | 28 | 688 |  | 2020-09-18 15:00 | 15:00 | 20 | 28 | 688 |  | low | 2020-09-14 | B25398¦OTHER Office Area, North, 15th Floor¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 801A | [5 empty] | 21 | 25 | 399 |  | 2020-09-18 12:00 | 12:00 | 21 | 25 | 399 |  | low | 2020-09-14 | B92624¦Hallway by Room 801A¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B25602 | B25602 - 29 Second St W - Cornwall | Outdoors |  |  | 12 | 31 | 678 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B25602¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Lounge | [5 empty] | 21 | 27 | 402 |  | 2020-09-18 12:00 | 12:00 | 21 | 27 | 402 |  | low | 2020-09-14 | B92624¦Lounge¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, North West, 15th Floor | [5 empty] | 20 | 29 | 695 |  | 2020-09-18 15:00 | 15:00 | 20 | 29 | 695 |  | low | 2020-09-14 | B25398¦OTHER Office Area, North West, 15th Floor¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Outdoors |  |  | 16 | 32 | 325 |  |  |  | Base Readings | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B25165¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | OTHER Office Area, West, 15th Floor | [5 empty] | 20 | 29 | 699 |  | 2020-09-18 15:00 | 15:00 | 20 | 29 | 699 |  | low | 2020-09-14 | B25398¦OTHER Office Area, West, 15th Floor¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | OTHER | [5 empty] | 21 | 30 | 448 | Courtroom 700, Please add courtroom 700 to drop down box, thank you | 2020-09-18 15:00 | 15:00 | 21 | 30 | 448 |  | low | 2020-09-14 | B25165¦OTHER¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Outdoors |  |  | 16 | 34 | 419 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B92624¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Corridor adj. to Mail Room, 15th Floor OTHER | [5 empty] | 20 | 27 | 689 |  | 2020-09-18 15:00 | 15:00 | 20 | 27 | 689 |  | low | 2020-09-14 | B25398¦Corridor adj. to Mail Room, 15th Floor OTHER¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 600 | [5 empty] | 21 | 32 | 437 |  | 2020-09-18 15:00 | 15:00 | 21 | 32 | 437 |  | low | 2020-09-14 | B25165¦Courtroom 600¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Elevator Lobby, 15th Floor OTHER | [5 empty] | 21 | 26 | 680 |  | 2020-09-18 15:00 | 15:00 | 21 | 26 | 680 |  | low | 2020-09-14 | B25398¦Elevator Lobby, 15th Floor OTHER¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 308 | [5 empty] | 21 | 32 | 452 |  | 2020-09-18 15:00 | 15:00 | 21 | 32 | 452 |  | low | 2020-09-14 | B25165¦Courtroom 308¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25398 | B25398 - 655 BAY ST - Toronto | Outdoors |  |  | 16 | 21 | 667 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B25398¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 306 | [5 empty] | 21 | 30 | 424 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 424 |  | low | 2020-09-14 | B25165¦Courtroom 306¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 304 | [5 empty] | 21 | 30 | 423 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 423 |  | low | 2020-09-14 | B25165¦Courtroom 304¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Outdoors |  |  | 10 | 33 | 418 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B90838¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 304 | [5 empty] | 21 | 30 | 424 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 424 |  | low | 2020-09-14 | B25165¦Courtroom 304¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90838 | B90838 - 611 9th Ave E - Owen Sound | Courtroom 101 | [5 empty] | 21 | 39 | 419 |  | 2020-09-18 15:00 | 15:00 | 21 | 39 | 419 |  | caution | 2020-09-14 | B90838¦Courtroom 101¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 302 | [5 empty] | 21 | 30 | 423 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 423 |  | low | 2020-09-14 | B25165¦Courtroom 302¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 208 | [5 empty] | 21 | 30 | 431 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 431 |  | low | 2020-09-14 | B25165¦Courtroom 208¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 206 | [5 empty] | 21 | 30 | 434 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 434 |  | low | 2020-09-14 | B25165¦Courtroom 206¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 204 | [5 empty] | 21 | 30 | 508 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 508 |  | low | 2020-09-14 | B25165¦Courtroom 204¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 202 | [5 empty] | 21 | 30 | 454 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 454 |  | low | 2020-09-14 | B25165¦Courtroom 202¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 200 | [5 empty] | 21 | 30 | 480 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 480 |  | low | 2020-09-14 | B25165¦Courtroom 200¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B25165 | B25165 - 45 Main Street East - Hamilton | Courtroom 100 | [5 empty] | 21 | 30 | 437 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 437 |  | low | 2020-09-14 | B25165¦Courtroom 100¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 100 Courtroom 101 Courtroom 102 Courtroom 200 Courtroom 202 Courtroom 203 Courtroom 401 Courtroom 402 Courtroom 403 | [5 empty] | 21 | 26 | 472 |  | 2020-09-18 15:00 | 15:00 | 21 | 26 | 472 |  | low | 2020-09-14 | B20616¦Courtroom 100 Courtroom 101 Courtroom 102 Courtroom 200 Courtroom 202 Courtroom 203 Courtroom 401 Courtroom 402 Courtroom 403¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 201 | [5 empty] | 22 | 26 | 472 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 472 |  | low | 2020-09-14 | B20616¦Courtroom 103 Courtroom 104 Courtroom 105 Courtroom 201¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 106 Courtroom 205 Courtroom 405 | [5 empty] | 20 | 32 | 470 |  | 2020-09-18 15:00 | 15:00 | 20 | 32 | 470 |  | low | 2020-09-14 | B20616¦Courtroom 106 Courtroom 205 Courtroom 405¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 404 | [5 empty] | 21 | 32 | 470 |  | 2020-09-18 15:00 | 15:00 | 21 | 32 | 470 |  | low | 2020-09-14 | B20616¦Courtroom 301 Courtroom 302 Courtroom 303 Courtroom 404¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 204 | [5 empty] | 22 | 32 | 470 |  | 2020-09-18 15:00 | 15:00 | 22 | 32 | 470 |  | low | 2020-09-14 | B20616¦Courtroom 204¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 107 Courtroom 108 | [5 empty] | 21 | 26 | 417 |  | 2020-09-18 15:00 | 15:00 | 21 | 26 | 417 |  | low | 2020-09-14 | B20616¦Courtroom 107 Courtroom 108¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20616 | B20616 - 50 Eagle St W - Newmarket | Courtroom 304 Courtroom 305 | [5 empty] | 22 | 28 | 550 |  | 2020-09-18 15:00 | 15:00 | 22 | 28 | 550 |  | low | 2020-09-14 | B20616¦Courtroom 304 Courtroom 305¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Outdoors |  |  | 17 | 25 | 394 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B19652¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Center) | [5 empty] | 21 | 30 | 455 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 455 |  | low | 2020-09-14 | B19652¦Courtroom 1 (Center)¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 1 (Judge Dias) | [5 empty] | 21 | 30 | 454 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 454 |  | low | 2020-09-14 | B19652¦Courtroom 1 (Judge Dias)¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Superior Judge's Chambers | [5 empty] | 21 | 34 | 454 |  | 2020-09-18 15:00 | 15:00 | 21 | 34 | 454 |  | low | 2020-09-14 | B19652¦Superior Judge's Chambers¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 3rd floor stair landing | [5 empty] | 21 | 34 | 561 |  | 2020-09-18 15:00 | 15:00 | 21 | 34 | 561 |  | low | 2020-09-14 | B19652¦3rd floor stair landing¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 301 | [5 empty] | 24 | 30 | 438 |  | 2020-09-18 15:00 | 15:00 | 24 | 30 | 438 |  | low | 2020-09-14 | B20080¦Courtroom 301¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 3rd floor jury room | [5 empty] | 21 | 34 | 445 |  | 2020-09-18 15:00 | 15:00 | 21 | 34 | 445 |  | low | 2020-09-14 | B19652¦3rd floor jury room¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom 303 | [5 empty] | 22 | 30 | 449 |  | 2020-09-18 15:00 | 15:00 | 22 | 30 | 449 |  | low | 2020-09-14 | B20080¦Courtroom 303¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Justice Macdonald Chambers | [5 empty] | 21 | 32 | 460 |  | 2020-09-18 15:00 | 15:00 | 21 | 32 | 460 |  | low | 2020-09-14 | B19652¦Justice Macdonald Chambers¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Courtroom B01 | [5 empty] | 22 | 30 |  |  | 2020-09-18 15:00 | 15:00 | 22 | 30 |  |  | low | 2020-09-14 | B20080¦Courtroom B01¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Justice Macdonald Secretary | [5 empty] | 21 | 32 | 436 |  | 2020-09-18 15:00 | 15:00 | 21 | 32 | 436 |  | low | 2020-09-14 | B19652¦Justice Macdonald Secretary¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | SCJTC Office | [5 empty] | 21 | 32 | 524 |  | 2020-09-18 15:00 | 15:00 | 21 | 32 | 524 |  | low | 2020-09-14 | B19652¦SCJTC Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20080 | B20080 - 700 Christina Street North - Sarnia | Outdoors |  |  | 14 | 45 | 411 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20080¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Visitin Justice's Chambers | [5 empty] | 21 | 32 | 486 |  | 2020-09-18 15:00 | 15:00 | 21 | 32 | 486 |  | low | 2020-09-14 | B19652¦Visitin Justice's Chambers¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Center) | [8 empty] | Court in session | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B19652¦Courtroom 2 (Center)¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 (Judge Dias) | [8 empty] | Court in session | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B19652¦Courtroom 2 (Judge Dias)¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 2 Waiting Area | [5 empty] | 21 | 34 | 594 |  | 2020-09-18 15:00 | 15:00 | 21 | 34 | 594 |  | low | 2020-09-14 | B19652¦Courtroom 2 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Center) | [5 empty] | 22 | 27 | 517 |  | 2020-09-18 15:00 | 15:00 | 22 | 27 | 517 |  | low | 2020-09-14 | B19652¦Courtroom 3 (Center)¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Courtroom 3 (Judge Dias) | [5 empty] | 22 | 26 | 438 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 438 |  | low | 2020-09-14 | B19652¦Courtroom 3 (Judge Dias)¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | Justice of the peace chambers | [5 empty] | 22 | 30 | 494 |  | 2020-09-18 15:00 | 15:00 | 22 | 30 | 494 |  | low | 2020-09-14 | B19652¦Justice of the peace chambers¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | council chambers dias | [5 empty] | 22 | 30 | 489 |  | 2020-09-18 15:00 | 15:00 | 22 | 30 | 489 |  | low | 2020-09-14 | B19652¦council chambers dias¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | council chambers center | [5 empty] | 22 | 30 | 450 |  | 2020-09-18 15:00 | 15:00 | 22 | 30 | 450 |  | low | 2020-09-14 | B19652¦council chambers center¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 2nd Floor Lunchroom | [5 empty] | 21 | 30 | 471 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 471 |  | low | 2020-09-14 | B19652¦2nd Floor Lunchroom¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 2nd floor stair landing | [5 empty] | 22 | 30 | 512 |  | 2020-09-18 15:00 | 15:00 | 22 | 30 | 512 |  | low | 2020-09-14 | B19652¦2nd floor stair landing¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | court services kitchenette | [5 empty] | 21 | 30 | 470 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 470 |  | low | 2020-09-14 | B19652¦court services kitchenette¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | court services north | [5 empty] | 23 | 36 | 744 |  | 2020-09-18 15:00 | 15:00 | 23 | 36 | 744 |  | caution | 2020-09-14 | B19652¦court services north¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | court services south | [5 empty] | 23 | 36 | 771 |  | 2020-09-18 15:00 | 15:00 | 23 | 36 | 771 |  | caution | 2020-09-14 | B19652¦court services south¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | court services entrance vestibule | [5 empty] | 22 | 33 | 643 |  | 2020-09-18 15:00 | 15:00 | 22 | 33 | 643 |  | low | 2020-09-14 | B19652¦court services entrance vestibule¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Outdoors |  |  | 17 | 23 | 490 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20289¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19652 | B19652 - 1 Courthouse Sq - Goderich | 1st floor stair landing | [5 empty] | 22 | 29 | 547 |  | 2020-09-18 15:00 | 15:00 | 22 | 29 | 547 |  | low | 2020-09-14 | B19652¦1st floor stair landing¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 20 | 30 | 551 | judge | 2020-09-18 15:00 | 15:00 | 20 | 30 | 551 |  | low | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 110 | [5 empty] | 20 | 30 | 510 | public | 2020-09-18 15:00 | 15:00 | 20 | 30 | 510 |  | low | 2020-09-14 | B20289¦Courtroom 110¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 21 | 29 | 525 | judge | 2020-09-18 15:00 | 15:00 | 21 | 29 | 525 |  | low | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 111 | [5 empty] | 21 | 28 | 509 | public | 2020-09-18 15:00 | 15:00 | 21 | 28 | 509 |  | low | 2020-09-14 | B20289¦Courtroom 111¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 300 | [5 empty] | 21 | 25 | 523 |  | 2020-09-18 15:00 | 15:00 | 21 | 25 | 523 |  | low | 2020-09-14 | B20289¦Courtroom 300¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 301 | [5 empty] | 22 | 24 | 518 |  | 2020-09-18 15:00 | 15:00 | 22 | 24 | 518 |  | low | 2020-09-14 | B20289¦Courtroom 301¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom 303 | [5 empty] | 22 | 25 | 499 |  | 2020-09-18 15:00 | 15:00 | 22 | 25 | 499 |  | low | 2020-09-14 | B20289¦Courtroom 303¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom A | [5 empty] | 22 | 25 | 577 | in session; measurement taken outside courtroom | 2020-09-18 15:00 | 15:00 | 22 | 25 | 577 |  | low | 2020-09-14 | B20289¦Courtroom A¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom B | [5 empty] | 22 | 25 | 572 | in session; measurement taken outside courtroom | 2020-09-18 15:00 | 15:00 | 22 | 25 | 572 |  | low | 2020-09-14 | B20289¦Courtroom B¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom C (North) | [5 empty] | 22 | 26 | 595 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 595 |  | low | 2020-09-14 | B20289¦Courtroom C (North)¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom D | [5 empty] | 21 | 25 | 584 |  | 2020-09-18 15:00 | 15:00 | 21 | 25 | 584 |  | low | 2020-09-14 | B20289¦Courtroom D¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom E | [5 empty] | 22 | 25 | 572 |  | 2020-09-18 15:00 | 15:00 | 22 | 25 | 572 |  | low | 2020-09-14 | B20289¦Courtroom E¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20289 | B20289 - 47 SHEPPARD AVE E - Willowdale | Courtroom F | [5 empty] | 22 | 25 | 538 | in session; measurement taken outside courtroom | 2020-09-18 15:00 | 15:00 | 22 | 25 | 538 |  | low | 2020-09-14 | B20289¦Courtroom F¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Outdoors |  |  | 16 | 28 | 420 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20265¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 north side | [5 empty] | 22 | 28 | 580 |  | 2020-09-18 15:00 | 15:00 | 22 | 28 | 580 |  | low | 2020-09-14 | B20265¦courtroom M1 north side¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 south side | [5 empty] | 22 | 28 | 551 |  | 2020-09-18 15:00 | 15:00 | 22 | 28 | 551 |  | low | 2020-09-14 | B20265¦courtroom M1 south side¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by Courtroom M1 | [5 empty] | 22 | 27 | 538 |  | 2020-09-18 15:00 | 15:00 | 22 | 27 | 538 |  | low | 2020-09-14 | B20265¦hallway by Courtroom M1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom J | [5 empty] | 21 | 27 | 570 | south | 2020-09-18 15:00 | 15:00 | 21 | 27 | 570 |  | low | 2020-09-14 | B20265¦Courtroom J¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom J | [5 empty] | 21 | 26 | 494 | north | 2020-09-18 15:00 | 15:00 | 21 | 26 | 494 |  | low | 2020-09-14 | B20265¦Courtroom J¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom J | [5 empty] | 21 | 31 | 513 |  | 2020-09-18 15:00 | 15:00 | 21 | 31 | 513 |  | low | 2020-09-14 | B20265¦hallway by courtroom J¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G south side | [5 empty] | 21 | 30 | 565 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 565 |  | low | 2020-09-14 | B20265¦courtroom G south side¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G north side | [5 empty] | 22 | 31 | 538 |  | 2020-09-18 15:00 | 15:00 | 22 | 31 | 538 |  | low | 2020-09-14 | B20265¦courtroom G north side¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 121 | [5 empty] | 22 | 33 | 519 | west | 2020-09-18 15:00 | 15:00 | 22 | 33 | 519 |  | low | 2020-09-14 | B20265¦Courtroom 121¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 121 | [5 empty] | 22 | 32 | 516 | east | 2020-09-18 15:00 | 15:00 | 22 | 32 | 516 |  | low | 2020-09-14 | B20265¦Courtroom 121¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 123 | [5 empty] | 22 | 26 | 447 | east | 2020-09-18 15:00 | 15:00 | 22 | 26 | 447 |  | low | 2020-09-14 | B20265¦Courtroom 123¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 123 | [5 empty] | 22 | 26 | 438 | west | 2020-09-18 15:00 | 15:00 | 22 | 26 | 438 |  | low | 2020-09-14 | B20265¦Courtroom 123¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 east side | [5 empty] | 22 | 31 | 505 |  | 2020-09-18 15:00 | 15:00 | 22 | 31 | 505 |  | low | 2020-09-14 | B20265¦courtroom 124 east side¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 west side | [5 empty] | 22 | 33 | 513 |  | 2020-09-18 15:00 | 15:00 | 22 | 33 | 513 |  | low | 2020-09-14 | B20265¦courtroom 124 west side¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 125 | [5 empty] | 22 | 29 | 500 | south | 2020-09-18 15:00 | 15:00 | 22 | 29 | 500 |  | low | 2020-09-14 | B20265¦Courtroom 125¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 125 | [5 empty] | 22 | 30 | 476 | north | 2020-09-18 15:00 | 15:00 | 22 | 30 | 476 |  | low | 2020-09-14 | B20265¦Courtroom 125¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 126 south side | [5 empty] | 22 | 26 | 581 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 581 |  | low | 2020-09-14 | B20265¦courtroom 126 south side¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom 126 | [5 empty] | 22 | 26 | 510 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 510 |  | low | 2020-09-14 | B20265¦hallway by courtroom 126¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Hallway | [5 empty] | 22 | 27 | 499 | by recieving | 2020-09-18 15:00 | 15:00 | 22 | 27 | 499 |  | low | 2020-09-14 | B20265¦Hallway¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Outdoors |  |  | 18 | 26 | 431 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10639¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 6 | [5 empty] | 20 | 23 | 441 | north | 2020-09-18 15:00 | 15:00 | 20 | 23 | 441 |  | low | 2020-09-14 | B10639¦Courtroom 6¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 6 | [5 empty] | 20 | 23 | 430 | south | 2020-09-18 15:00 | 15:00 | 20 | 23 | 430 |  | low | 2020-09-14 | B10639¦Courtroom 6¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 6 | [5 empty] | 20 | 25 | 454 |  | 2020-09-18 15:00 | 15:00 | 20 | 25 | 454 |  | low | 2020-09-14 | B10639¦Hallway by courtroom 6¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 5 | [5 empty] | 20 | 28 | 428 | north | 2020-09-18 15:00 | 15:00 | 20 | 28 | 428 |  | low | 2020-09-14 | B10639¦Courtroom 5¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 5 | [5 empty] | 20 | 29 | 434 | south | 2020-09-18 15:00 | 15:00 | 20 | 29 | 434 |  | low | 2020-09-14 | B10639¦Courtroom 5¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 5 | [5 empty] | 20 | 26 | 430 |  | 2020-09-18 15:00 | 15:00 | 20 | 26 | 430 |  | low | 2020-09-14 | B10639¦Hallway by courtroom 5¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 3 | [5 empty] | 20 | 27 | 510 | southeast | 2020-09-18 15:00 | 15:00 | 20 | 27 | 510 |  | low | 2020-09-14 | B10639¦Courtroom 3¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 3 | [5 empty] | 20 | 27 | 448 | northwest | 2020-09-18 15:00 | 15:00 | 20 | 27 | 448 |  | low | 2020-09-14 | B10639¦Courtroom 3¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | hallway by courtroom 3 | [5 empty] | 21 | 25 | 445 |  | 2020-09-18 15:00 | 15:00 | 21 | 25 | 445 |  | low | 2020-09-14 | B10639¦hallway by courtroom 3¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby East Side | [5 empty] | 21 | 26 | 443 |  | 2020-09-18 15:00 | 15:00 | 21 | 26 | 443 |  | low | 2020-09-14 | B10639¦Entrance Lobby East Side¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby West Side | [5 empty] | 21 | 26 | 446 |  | 2020-09-18 15:00 | 15:00 | 21 | 26 | 446 |  | low | 2020-09-14 | B10639¦Entrance Lobby West Side¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | lobby by statue | [5 empty] | 21 | 25 | 435 |  | 2020-09-18 15:00 | 15:00 | 21 | 25 | 435 |  | low | 2020-09-14 | B10639¦lobby by statue¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by COA intake office | [5 empty] | 21 | 27 | 450 |  | 2020-09-18 15:00 | 15:00 | 21 | 27 | 450 |  | low | 2020-09-14 | B10639¦Hallway by COA intake office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by Law Society of Ontario | [5 empty] | 21 | 25 | 430 |  | 2020-09-18 15:00 | 15:00 | 21 | 25 | 430 |  | low | 2020-09-14 | B10639¦Hallway by Law Society of Ontario¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Main entrance | [5 empty] | 19 | 32 | 412 |  | 2020-09-18 15:00 | 15:00 | 19 | 32 | 412 |  | low | 2020-09-14 | B90636¦Main entrance¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 20 | 28 | 404 | north | 2020-09-18 15:00 | 15:00 | 20 | 28 | 404 |  | low | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 201 | [5 empty] | 20 | 27 | 389 | south | 2020-09-18 15:00 | 15:00 | 20 | 27 | 389 |  | low | 2020-09-14 | B90636¦Courtroom 201¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 21 | 28 | 413 | Courtroom lobby | 2020-09-18 15:00 | 15:00 | 21 | 28 | 413 |  | low | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 203 | [5 empty] | 22 | 28 | 421 | entrance | 2020-09-18 15:00 | 15:00 | 22 | 28 | 421 |  | low | 2020-09-14 | B90636¦Courtroom 203¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Hallway by courtroom 203 | [5 empty] | 22 | 26 | 426 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 426 |  | low | 2020-09-14 | B90636¦Hallway by courtroom 203¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 2nd fl lobby | [5 empty] | 22 | 26 | 407 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 407 |  | low | 2020-09-14 | B90636¦2nd fl lobby¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 3rd Floor Elevator Lobby | [5 empty] | 22 | 25 | 412 |  | 2020-09-18 15:00 | 15:00 | 22 | 25 | 412 |  | low | 2020-09-14 | B90636¦3rd Floor Elevator Lobby¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 208 | [5 empty] | 21 | 26 | 402 | west | 2020-09-18 15:00 | 15:00 | 21 | 26 | 402 |  | low | 2020-09-14 | B90636¦Courtroom 208¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 208 | [5 empty] | 21 | 26 | 401 | east | 2020-09-18 15:00 | 15:00 | 21 | 26 | 401 |  | low | 2020-09-14 | B90636¦Courtroom 208¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 211 | [5 empty] | 21 | 26 | 366 | north | 2020-09-18 15:00 | 15:00 | 21 | 26 | 366 |  | low | 2020-09-14 | B90636¦Courtroom 211¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Courtroom 211 | [5 empty] | 22 | 25 | 367 | south | 2020-09-18 15:00 | 15:00 | 22 | 25 | 367 |  | low | 2020-09-14 | B90636¦Courtroom 211¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | 4th floor waiting area | [5 empty] | 21 | 23 | 385 |  | 2020-09-18 15:00 | 15:00 | 21 | 23 | 385 |  | low | 2020-09-14 | B90636¦4th floor waiting area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Hallway by courtroom 211 | [5 empty] | 21 | 24 | 395 |  | 2020-09-18 15:00 | 15:00 | 21 | 24 | 395 |  | low | 2020-09-14 | B90636¦Hallway by courtroom 211¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B90636 | B90636 - 2201 Finch Ave W - Toronto | Outdoors |  |  | 16 | 23 | 388 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B90636¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Main entrance | [5 empty] | 20 | 32 | 536 |  | 2020-09-18 15:00 | 15:00 | 20 | 32 | 536 |  | low | 2020-09-14 | B20979¦Main entrance¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 21 | 31 | 510 | east | 2020-09-18 15:00 | 15:00 | 21 | 31 | 510 |  | low | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 301 | [5 empty] | 21 | 31 | 540 | west | 2020-09-18 15:00 | 15:00 | 21 | 31 | 540 |  | low | 2020-09-14 | B20979¦Courtroom 301¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 306 | [5 empty] | 21 | 31 | 576 | south | 2020-09-18 15:00 | 15:00 | 21 | 31 | 576 |  | low | 2020-09-14 | B20979¦Courtroom 306¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 100 | [5 empty] | 22 | 31 | 561 | north | 2020-09-18 15:00 | 15:00 | 22 | 31 | 561 |  | low | 2020-09-14 | B20979¦Courtroom 100¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 307 | [5 empty] | 22 | 32 | 781 | south | 2020-09-18 15:00 | 15:00 | 22 | 32 | 781 |  | low | 2020-09-14 | B20979¦Courtroom 307¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 307 | [5 empty] | 23 | 32 | 828 | north | 2020-09-18 15:00 | 15:00 | 23 | 32 | 828 |  | low | 2020-09-14 | B20979¦Courtroom 307¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 22 | 31 | 727 | east | 2020-09-18 15:00 | 15:00 | 22 | 31 | 727 |  | low | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 304 | [5 empty] | 23 | 30 | 622 | west | 2020-09-18 15:00 | 15:00 | 23 | 30 | 622 |  | low | 2020-09-14 | B20979¦Courtroom 304¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Hallway by courtroom 307 | [5 empty] | 22 | 28 | 533 |  | 2020-09-18 15:00 | 15:00 | 22 | 28 | 533 |  | low | 2020-09-14 | B20979¦Hallway by courtroom 307¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Hallway by courtroom 302 | [5 empty] | 22 | 28 | 529 |  | 2020-09-18 15:00 | 15:00 | 22 | 28 | 529 |  | low | 2020-09-14 | B20979¦Hallway by courtroom 302¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 27 | 466 | south | 2020-09-18 15:00 | 15:00 | 22 | 27 | 466 |  | low | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Courtroom 309 | [5 empty] | 22 | 26 | 453 | north | 2020-09-18 15:00 | 15:00 | 22 | 26 | 453 |  | low | 2020-09-14 | B20979¦Courtroom 309¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Basement cells - hallway | [5 empty] | 22 | 24 | 415 |  | 2020-09-18 15:00 | 15:00 | 22 | 24 | 415 |  | low | 2020-09-14 | B20979¦Basement cells - hallway¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Police Office | [5 empty] | 23 | 28 | 509 |  | 2020-09-18 15:00 | 15:00 | 23 | 28 | 509 |  | low | 2020-09-14 | B20979¦Police Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20979 | B20979 - 1000 Finch Ave W - Toronto | Outdoors |  |  | 16 | 23 | 386 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20979¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Outdoors |  |  | 7 | 66 | 474 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70485¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Social Benefits Tribunal Reception | [5 empty] | 21 | 31 | 409 |  | 2020-09-18 09:00 | 9:00 | 21 | 31 | 409 |  | low | 2020-09-14 | B70485¦Social Benefits Tribunal Reception¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #3 | [5 empty] | 21 | 31 | 409 |  | 2020-09-18 09:00 | 9:00 | 21 | 31 | 409 |  | low | 2020-09-14 | B70485¦SBT Hearing Room #3¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #4 | [5 empty] | 21 | 30 | 413 |  | 2020-09-18 09:00 | 9:00 | 21 | 30 | 413 |  | low | 2020-09-14 | B70485¦SBT Hearing Room #4¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #4 | [5 empty] | 21 | 30 | 413 |  | 2020-09-18 09:00 | 9:00 | 21 | 30 | 413 |  | low | 2020-09-14 | B70485¦SBT Hearing Room #4¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | LTB Hearing Room #1 | [5 empty] | 18 | 40 | 456 |  | 2020-09-18 09:00 | 9:00 | 18 | 40 | 456 |  | caution | 2020-09-14 | B70485¦LTB Hearing Room #1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Regional Managers Office | [5 empty] | 19 | 37 | 457 |  | 2020-09-18 09:00 | 9:00 | 19 | 37 | 457 |  | caution | 2020-09-14 | B70485¦Regional Managers Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Cubes outside RM Office | [5 empty] | 19 | 36 | 447 |  | 2020-09-18 09:00 | 9:00 | 19 | 36 | 447 |  | caution | 2020-09-14 | B70485¦Cubes outside RM Office¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Security Check In | [5 empty] | 21 | 34 | 411 |  | 2020-09-18 15:00 | 15:00 | 21 | 34 | 411 |  | low | 2020-09-14 | B92624¦Security Check In¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 21 | 36 | 404 | West | 2020-09-18 15:00 | 15:00 | 21 | 36 | 404 |  | caution | 2020-09-14 | B92624¦Room 701¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #1 | [5 empty] | 20 | 35 | 442 |  | 2020-09-18 09:00 | 9:00 | 20 | 35 | 442 |  | caution | 2020-09-14 | B70485¦Mediation Room #1¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 21 | 34 | 406 | East | 2020-09-18 15:00 | 15:00 | 21 | 34 | 406 |  | low | 2020-09-14 | B92624¦Room 701¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #2 | [5 empty] | 20 | 34 | 456 |  | 2020-09-18 09:00 | 9:00 | 20 | 34 | 456 |  | low | 2020-09-14 | B70485¦Mediation Room #2¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 701 | [5 empty] | 21 | 34 | 404 | North | 2020-09-18 15:00 | 15:00 | 21 | 34 | 404 |  | low | 2020-09-14 | B92624¦Room 701¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 701 | [5 empty] | 20 | 26 | 400 |  | 2020-09-18 15:00 | 15:00 | 20 | 26 | 400 |  | low | 2020-09-14 | B92624¦Hallway by Room 701¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 22 | 28 | 403 | East | 2020-09-18 15:00 | 15:00 | 22 | 28 | 403 |  | low | 2020-09-14 | B92624¦Room 718A¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718A | [5 empty] | 22 | 26 | 402 | West | 2020-09-18 15:00 | 15:00 | 22 | 26 | 402 |  | low | 2020-09-14 | B92624¦Room 718A¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 718B | [5 empty] | 22 | 26 | 408 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 408 |  | low | 2020-09-14 | B92624¦Room 718B¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Reception/ Administration LTB | [5 empty] | 20 | 33 | 447 |  | 2020-09-18 09:00 | 9:00 | 20 | 33 | 447 |  | low | 2020-09-14 | B70485¦Reception/ Administration LTB¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 718A | [5 empty] | 22 | 25 | 401 |  | 2020-09-18 15:00 | 15:00 | 22 | 25 | 401 |  | low | 2020-09-14 | B92624¦Hallway by Room 718A¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717A | [5 empty] | 22 | 35 | 400 |  | 2020-09-18 15:00 | 15:00 | 22 | 35 | 400 |  | caution | 2020-09-14 | B92624¦Room 717A¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 717B | [5 empty] | 22 | 35 | 400 |  | 2020-09-18 15:00 | 15:00 | 22 | 35 | 400 |  | caution | 2020-09-14 | B92624¦Room 717B¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716A | [5 empty] | 22 | 33 | 399 |  | 2020-09-18 15:00 | 15:00 | 22 | 33 | 399 |  | low | 2020-09-14 | B92624¦Room 716A¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 716B | [5 empty] | 22 | 33 | 403 |  | 2020-09-18 15:00 | 15:00 | 22 | 33 | 403 |  | low | 2020-09-14 | B92624¦Room 716B¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715A | [5 empty] | 22 | 27 | 410 |  | 2020-09-18 15:00 | 15:00 | 22 | 27 | 410 |  | low | 2020-09-14 | B92624¦Room 715A¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 715B | [5 empty] | 22 | 26 | 400 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 400 |  | low | 2020-09-14 | B92624¦Room 715B¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Document Area | [5 empty] | 20 | 32 | 442 |  | 2020-09-18 09:00 | 9:00 | 20 | 32 | 442 |  | low | 2020-09-14 | B70485¦Document Area¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714A | [5 empty] | 22 | 36 | 398 |  | 2020-09-18 15:00 | 15:00 | 22 | 36 | 398 |  | caution | 2020-09-14 | B92624¦Room 714A¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-1 | [5 empty] | 21 | 30.9 | 695 |  | 2020-09-18 15:00 | 15:00 | 21 | 30.9 | 695 |  | low | 2020-09-14 | B10644¦Courtroom 2-1¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Copy Room | [5 empty] | 20 | 32 | 441 |  | 2020-09-18 09:00 | 9:00 | 20 | 32 | 441 |  | low | 2020-09-14 | B70485¦Copy Room¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 714B | [5 empty] | 22 | 38 | 399 |  | 2020-09-18 15:00 | 15:00 | 22 | 38 | 399 |  | caution | 2020-09-14 | B92624¦Room 714B¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713A | [5 empty] | 22 | 26 | 402 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 402 |  | low | 2020-09-14 | B92624¦Room 713A¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #3 | [5 empty] | 20 | 33 | 433 |  | 2020-09-18 09:00 | 9:00 | 20 | 33 | 433 |  | low | 2020-09-14 | B70485¦Mediation Room #3¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 713B | [5 empty] | 22 | 26 | 408 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 408 |  | low | 2020-09-14 | B92624¦Room 713B¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-2 | [5 empty] | 18.7 | 40.9 | 544 |  | 2020-09-18 15:00 | 15:00 | 18.7 | 40.9 | 544 |  |  | 2020-09-14 | B10644¦Courtroom 2-2¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Escalator, 700 | [5 empty] | 21 | 25 | 402 |  | 2020-09-18 15:00 | 15:00 | 21 | 25 | 402 |  | low | 2020-09-14 | B92624¦Hallway by Escalator, 700¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Corner Office | [5 empty] | 20 | 32 | 433 |  | 2020-09-18 09:00 | 9:00 | 20 | 32 | 433 |  | low | 2020-09-14 | B70485¦Corner Office¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801A | [5 empty] | 21 | 27 | 398 |  | 2020-09-18 15:00 | 15:00 | 21 | 27 | 398 |  | low | 2020-09-14 | B92624¦Room 801A¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Room 801B | [5 empty] | 21 | 25 | 401 |  | 2020-09-18 15:00 | 15:00 | 21 | 25 | 401 |  | low | 2020-09-14 | B92624¦Room 801B¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-3 | [5 empty] | 20.4 | 72.8 | 418 |  | 2020-09-18 15:00 | 15:00 | 20.4 | 72.8 | 418 |  | high | 2020-09-14 | B10644¦Courtroom 2-3¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Side Entry Door | [5 empty] | 20 | 33 | 446 |  | 2020-09-18 09:00 | 9:00 | 20 | 33 | 446 |  | low | 2020-09-14 | B70485¦Side Entry Door¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Hallway by Room 801A | [5 empty] | 21 | 22 | 399 |  | 2020-09-18 15:00 | 15:00 | 21 | 22 | 399 |  | low | 2020-09-14 | B92624¦Hallway by Room 801A¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Lounge | [5 empty] | 21 | 28 | 393 |  | 2020-09-18 15:00 | 15:00 | 21 | 28 | 393 |  | low | 2020-09-14 | B92624¦Lounge¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Filing Area | [5 empty] | 20 | 33 | 528 |  | 2020-09-18 09:00 | 9:00 | 20 | 33 | 528 |  | low | 2020-09-14 | B70485¦Filing Area¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B92624 | B92624 - 222 Bremner Blvd - Toronto | Outdoors |  |  | 17 | 26 | 394 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B92624¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Staff Kitchen | [5 empty] | 20 | 32 | 451 |  | 2020-09-18 09:00 | 9:00 | 20 | 32 | 451 |  | low | 2020-09-14 | B70485¦Staff Kitchen¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-4 | [5 empty] | 21.2 | 30.2 | 533 |  | 2020-09-18 15:00 | 15:00 | 21.2 | 30.2 | 533 |  | low | 2020-09-14 | B10644¦Courtroom 2-4¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Hearing Room 2 | [5 empty] | 21 | 33 | 449 |  | 2020-09-18 09:00 | 9:00 | 21 | 33 | 449 |  | low | 2020-09-14 | B70485¦Hearing Room 2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Elevators | [5 empty] | 21 | 30 | 415 |  | 2020-09-18 09:00 | 9:00 | 21 | 30 | 415 |  | low | 2020-09-14 | B70485¦Elevators¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-5 | [5 empty] | 19.4 | 33.4 | 391 |  | 2020-09-18 15:00 | 15:00 | 19.4 | 33.4 | 391 |  | low | 2020-09-14 | B10644¦Courtroom 2-5¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Outdoors |  |  | 15 | 33 | 427 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70485¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-8 | [5 empty] | 20.6 | 33.1 | 647 |  | 2020-09-18 15:00 | 15:00 | 20.6 | 33.1 | 647 |  | low | 2020-09-14 | B10644¦Courtroom 2-8¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Front Security Desk | [5 empty] | 23 | 31 | 473 |  | 2020-09-18 09:00 | 9:00 | 23 | 31 | 473 |  | low | 2020-09-14 | B20705¦Front Security Desk¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family Law Reception | [5 empty] | 22 | 31 | 471 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 471 |  | low | 2020-09-14 | B20705¦Family Law Reception¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-6 | [5 empty] | 23 | 32.8 | 418 |  | 2020-09-18 15:00 | 15:00 | 23 | 32.8 | 418 |  | low | 2020-09-14 | B10644¦Courtroom 2-6¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Criminal Inquiry Waiting Area | [5 empty] | 22 | 39 | 470 |  | 2020-09-18 09:00 | 9:00 | 22 | 39 | 470 |  | caution | 2020-09-14 | B20705¦Criminal Inquiry Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 3-2 | [5 empty] | 21.8 | 34.9 | 633 |  | 2020-09-18 15:00 | 15:00 | 21.8 | 34.9 | 633 |  | low | 2020-09-14 | B10644¦Courtroom 3-2¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family/Civil Waiting Area | [5 empty] | 22 | 32 | 505 |  | 2020-09-18 09:00 | 9:00 | 22 | 32 | 505 |  | low | 2020-09-14 | B20705¦Family/Civil Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Court Support Waiting Area | [5 empty] | 22 | 31 | 475 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 475 |  | low | 2020-09-14 | B20705¦Court Support Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-1 | [5 empty] | 22.5 | 37.1 | 480 |  | 2020-09-18 15:00 | 15:00 | 22.5 | 37.1 | 480 |  | caution | 2020-09-14 | B10644¦Courtroom 4-1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-2 | [5 empty] | 20.1 | 33.1 | 419 |  | 2020-09-18 15:00 | 15:00 | 20.1 | 33.1 | 419 |  | low | 2020-09-14 | B10644¦Courtroom 4-2¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 19.9 | 46.5 | 478 |  | 2020-09-18 09:00 | 9:00 | 19.9 | 46.5 | 478 |  |  | 2020-09-14 | B10644¦Courtroom 5-1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 20-24 Waiting Area | [5 empty] | 22 | 32 | 460 |  | 2020-09-18 09:00 | 9:00 | 22 | 32 | 460 |  | low | 2020-09-14 | B20705¦Courtroom 20-24 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-3 | [5 empty] | 24.2 | 39.2 | 405 |  | 2020-09-18 15:00 | 15:00 | 24.2 | 39.2 | 405 |  | caution | 2020-09-14 | B10644¦Courtroom 4-3¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-1 | [5 empty] | 22.3 | 41 | 489 |  | 2020-09-18 09:00 | 9:00 | 22.3 | 41 | 489 |  |  | 2020-09-14 | B10644¦Courtroom 4-1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-2 | [5 empty] | 20.1 | 37.9 | 431 |  | 2020-09-18 09:00 | 9:00 | 20.1 | 37.9 | 431 |  | caution | 2020-09-14 | B10644¦Courtroom 4-2¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-4 | [5 empty] | 21.5 | 38.9 | 504 |  | 2020-09-18 15:00 | 15:00 | 21.5 | 38.9 | 504 |  | caution | 2020-09-14 | B10644¦Courtroom 4-4¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 25-26 Waiting Area | [5 empty] | 22 | 31 | 458 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 458 |  | low | 2020-09-14 | B20705¦Courtroom 25-26 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-3 | [5 empty] | 22.8 | 42.2 | 405 |  | 2020-09-18 09:00 | 9:00 | 22.8 | 42.2 | 405 |  |  | 2020-09-14 | B10644¦Courtroom 4-3¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 4-6 Waiting Area | [5 empty] | 22 | 31 | 485 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 485 |  | low | 2020-09-14 | B20705¦Courtroom 4-6 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-6 | [5 empty] | 21.7 | 37.5 | 379 |  | 2020-09-18 15:00 | 15:00 | 21.7 | 37.5 | 379 |  | caution | 2020-09-14 | B10644¦Courtroom 4-6¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-9 | [5 empty] | 19.7 | 48.3 | 422 |  | 2020-09-18 09:00 | 9:00 | 19.7 | 48.3 | 422 |  |  | 2020-09-14 | B10644¦Courtroom 4-9¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 1-3 Waiting Area | [5 empty] | 22 | 32 | 537 |  | 2020-09-18 09:00 | 9:00 | 22 | 32 | 537 |  | low | 2020-09-14 | B20705¦Courtroom 1-3 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-7 | [5 empty] | 21.3 | 37.3 | 384 |  | 2020-09-18 15:00 | 15:00 | 21.3 | 37.3 | 384 |  | caution | 2020-09-14 | B10644¦Courtroom 4-7¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 7-9 Waiting Area | [5 empty] | 22 | 31 | 479 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 479 |  | low | 2020-09-14 | B20705¦Courtroom 7-9 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-8 | [5 empty] | 22 | 35.5 | 395 |  | 2020-09-18 15:00 | 15:00 | 22 | 35.5 | 395 |  | caution | 2020-09-14 | B10644¦Courtroom 4-8¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-4 | [6 empty] | 43.7 | 513 |  | 2020-09-18 09:00 | 9:00 |  | 43.7 | 513 |  |  | 2020-09-14 | B10644¦Courtroom 4-4¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 10-12 Waiting Area | [5 empty] | 22 | 30 | 464 |  | 2020-09-18 09:00 | 9:00 | 22 | 30 | 464 |  | low | 2020-09-14 | B20705¦Courtroom 10-12 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-9 | [5 empty] | 18.7 | 42.9 | 408 |  | 2020-09-18 15:00 | 15:00 | 18.7 | 42.9 | 408 |  |  | 2020-09-14 | B10644¦Courtroom 4-9¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-10 | [5 empty] | 24.7 | 43.1 | 413 |  | 2020-09-18 15:00 | 15:00 | 24.7 | 43.1 | 413 |  |  | 2020-09-14 | B10644¦Courtroom 4-10¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-4 | [5 empty] | 21.2 | 41.7 | 403 |  | 2020-09-18 09:00 | 9:00 | 21.2 | 41.7 | 403 |  |  | 2020-09-14 | B10644¦Courtroom 4-4¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 13-14 Waiting Area | [5 empty] | 22 | 30 | 454 |  | 2020-09-18 09:00 | 9:00 | 22 | 30 | 454 |  | low | 2020-09-14 | B20705¦Courtroom 13-14 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22.7 | 32.2 | 455 |  | 2020-09-18 15:00 | 15:00 | 22.7 | 32.2 | 455 |  | low | 2020-09-14 | B10644¦Courtroom 5-1¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 34-36 Waiting Area | [5 empty] | 22 | 31 | 464 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 464 |  | low | 2020-09-14 | B20705¦Courtroom 34-36 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-1 | [5 empty] | 20.6 | 38.3 | 392 |  | 2020-09-18 15:00 | 15:00 | 20.6 | 38.3 | 392 |  | caution | 2020-09-14 | B10644¦Courtroom 6-1¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 30-33 Waiting Area | [5 empty] | 22 | 31 | 468 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 468 |  | low | 2020-09-14 | B20705¦Courtroom 30-33 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-3 | [5 empty] | 22.4 | 29.8 | 634 |  | 2020-09-18 15:00 | 15:00 | 22.4 | 29.8 | 634 |  | low | 2020-09-14 | B10644¦Courtroom 6-3¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-8 | [5 empty] | 21.9 | 40 | 390 |  | 2020-09-18 09:00 | 9:00 | 21.9 | 40 | 390 |  | caution | 2020-09-14 | B10644¦Courtroom 4-8¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Crown Attorney Entrance | [5 empty] | 22 | 34 | 480 |  | 2020-09-18 09:00 | 9:00 | 22 | 34 | 480 |  | low | 2020-09-14 | B20705¦Crown Attorney Entrance¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-10 | [5 empty] | 20.4 | 46.8 | 425 |  | 2020-09-18 09:00 | 9:00 | 20.4 | 46.8 | 425 |  |  | 2020-09-14 | B10644¦Courtroom 4-10¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Probation/Parole Waiting Area | [5 empty] | 22 | 31 | 471 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 471 |  | low | 2020-09-14 | B20705¦Probation/Parole Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Land Registry Office | [5 empty] | 22 | 30 | 471 |  | 2020-09-18 09:00 | 9:00 | 22 | 30 | 471 |  | low | 2020-09-14 | B20705¦Land Registry Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 4th floor waiting area | [5 empty] | 22 | 30 | 460 |  | 2020-09-18 09:00 | 9:00 | 22 | 30 | 460 |  | low | 2020-09-14 | B20705¦4th floor waiting area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 53-55 Waiting Area | [5 empty] | 22 | 30 | 472 |  | 2020-09-18 09:00 | 9:00 | 22 | 30 | 472 |  | low | 2020-09-14 | B20705¦Courtroom 53-55 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-1 | [5 empty] | 21.5 | 40.2 | 690 |  | 2020-09-18 15:00 | 15:00 | 21.5 | 40.2 | 690 |  |  | 2020-09-14 | B10644¦Courtroom 2-1¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 51-52 Waiting Area | [5 empty] | 22 | 32 | 452 |  | 2020-09-18 09:00 | 9:00 | 22 | 32 | 452 |  | low | 2020-09-14 | B20705¦Courtroom 51-52 Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-2 | [5 empty] | 20.1 | 46.2 | 410 |  | 2020-09-18 15:00 | 15:00 | 20.1 | 46.2 | 410 |  |  | 2020-09-14 | B10644¦Courtroom 2-2¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 6th floor Waiting Area | [5 empty] | 22 | 30 | 453 |  | 2020-09-18 09:00 | 9:00 | 22 | 30 | 453 |  | low | 2020-09-14 | B20705¦6th floor Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-3 | [5 empty] | 20.9 | 65.4 | 440 |  | 2020-09-18 15:00 | 15:00 | 20.9 | 65.4 | 440 |  | high | 2020-09-14 | B10644¦Courtroom 2-3¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-4 | [5 empty] | 22.3 | 35.5 | 542 |  | 2020-09-18 15:00 | 15:00 | 22.3 | 35.5 | 542 |  | caution | 2020-09-14 | B10644¦Courtroom 2-4¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-5 | [5 empty] | 21.2 | 39.2 | 415 |  | 2020-09-18 15:00 | 15:00 | 21.2 | 39.2 | 415 |  | caution | 2020-09-14 | B10644¦Courtroom 2-5¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-6 | [5 empty] | 23 | 39.5 | 430 |  | 2020-09-18 15:00 | 15:00 | 23 | 39.5 | 430 |  | caution | 2020-09-14 | B10644¦Courtroom 2-6¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Outdoors |  |  | 15 | 31 | 412 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20705¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 2-8 | [5 empty] | 22 | 40 | 690 |  | 2020-09-18 15:00 | 15:00 | 22 | 40 | 690 |  | caution | 2020-09-14 | B10644¦Courtroom 2-8¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Outdoors |  |  | 16 | 20 | 357 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70485¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 3-2 | [5 empty] | 21.8 | 32.3 | 618 |  | 2020-09-18 15:00 | 15:00 | 21.8 | 32.3 | 618 |  | low | 2020-09-14 | B10644¦Courtroom 3-2¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Social Benefits Tribunal Reception | [5 empty] | 22 | 29 | 437 |  | 2020-09-18 12:00 | 12:00 | 22 | 29 | 437 |  | low | 2020-09-14 | B70485¦Social Benefits Tribunal Reception¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-1 | [5 empty] | 23.9 | 43 | 419 |  | 2020-09-18 15:00 | 15:00 | 23.9 | 43 | 419 |  |  | 2020-09-14 | B10644¦Courtroom 4-1¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #3 | [5 empty] | 22 | 27 | 408 |  | 2020-09-18 12:00 | 12:00 | 22 | 27 | 408 |  | low | 2020-09-14 | B70485¦SBT Hearing Room #3¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | 4-2 | [5 empty] | 20.3 | 39.2 | 436 |  | 2020-09-18 15:00 | 15:00 | 20.3 | 39.2 | 436 |  | caution | 2020-09-14 | B10644¦4-2¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #4 | [5 empty] | 21 | 25 | 412 |  | 2020-09-18 12:00 | 12:00 | 21 | 25 | 412 |  | low | 2020-09-14 | B70485¦SBT Hearing Room #4¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-4 | [5 empty] | 22.1 | 44.2 | 520 |  | 2020-09-18 15:00 | 15:00 | 22.1 | 44.2 | 520 |  |  | 2020-09-14 | B10644¦Courtroom 4-4¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | LTB Hearing Room #1 | [5 empty] | 21 | 25 | 361 |  | 2020-09-18 12:00 | 12:00 | 21 | 25 | 361 |  | low | 2020-09-14 | B70485¦LTB Hearing Room #1¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-6 | [5 empty] | 21.9 | 42.3 | 410 |  | 2020-09-18 15:00 | 15:00 | 21.9 | 42.3 | 410 |  |  | 2020-09-14 | B10644¦Courtroom 4-6¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Regional Managers Office | [5 empty] | 21 | 26 | 404 |  | 2020-09-18 12:00 | 12:00 | 21 | 26 | 404 |  | low | 2020-09-14 | B70485¦Regional Managers Office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Cubes outside RM Office | [5 empty] | 21 | 25 | 400 |  | 2020-09-18 12:00 | 12:00 | 21 | 25 | 400 |  | low | 2020-09-14 | B70485¦Cubes outside RM Office¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-7 | [5 empty] | 22.5 | 43 | 412 |  | 2020-09-18 15:00 | 15:00 | 22.5 | 43 | 412 |  |  | 2020-09-14 | B10644¦Courtroom 4-7¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-8 | [5 empty] | 22.3 | 41.2 | 405 |  | 2020-09-18 15:00 | 15:00 | 22.3 | 41.2 | 405 |  |  | 2020-09-14 | B10644¦Courtroom 4-8¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 4-10 | [5 empty] | 20.9 | 47.9 | 429 |  | 2020-09-18 15:00 | 15:00 | 20.9 | 47.9 | 429 |  |  | 2020-09-14 | B10644¦Courtroom 4-10¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #1 | [5 empty] | 22 | 25 | 404 |  | 2020-09-18 12:00 | 12:00 | 22 | 25 | 404 |  | low | 2020-09-14 | B70485¦Mediation Room #1¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 23.9 | 46.9 | 481 |  | 2020-09-18 15:00 | 15:00 | 23.9 | 46.9 | 481 |  |  | 2020-09-14 | B10644¦Courtroom 5-1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10644 | B10644 - 361 University Ave - Toronto | Courtroom 6-1 | [5 empty] | 22.5 | 43.9 | 412 |  | 2020-09-18 15:00 | 15:00 | 22.5 | 43.9 | 412 |  |  | 2020-09-14 | B10644¦Courtroom 6-1¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #2 | [5 empty] | 22 | 24 | 406 |  | 2020-09-18 12:00 | 12:00 | 22 | 24 | 406 |  | low | 2020-09-14 | B70485¦Mediation Room #2¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Reception/ Administration LTB | [5 empty] | 21 | 24 | 369 |  | 2020-09-18 12:00 | 12:00 | 21 | 24 | 369 |  | low | 2020-09-14 | B70485¦Reception/ Administration LTB¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Document Area | [5 empty] | 21 | 25 | 358 |  | 2020-09-18 12:00 | 12:00 | 21 | 25 | 358 |  | low | 2020-09-14 | B70485¦Document Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Copy Room | [5 empty] | 21 | 23 | 349 |  | 2020-09-18 12:00 | 12:00 | 21 | 23 | 349 |  | low | 2020-09-14 | B70485¦Copy Room¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #3 | [5 empty] | 21 | 24 | 352 |  | 2020-09-18 12:00 | 12:00 | 21 | 24 | 352 |  | low | 2020-09-14 | B70485¦Mediation Room #3¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Corner Office | [5 empty] | 20 | 26 | 373 |  | 2020-09-18 12:00 | 12:00 | 20 | 26 | 373 |  | low | 2020-09-14 | B70485¦Corner Office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Side Entry Door | [5 empty] | 20 | 25 | 423 |  | 2020-09-18 12:00 | 12:00 | 20 | 25 | 423 |  | low | 2020-09-14 | B70485¦Side Entry Door¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Filing Area | [5 empty] | 21 | 26 | 384 |  | 2020-09-18 12:00 | 12:00 | 21 | 26 | 384 |  | low | 2020-09-14 | B70485¦Filing Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Staff Kitchen | [5 empty] | 20 | 26 | 376 |  | 2020-09-18 12:00 | 12:00 | 20 | 26 | 376 |  | low | 2020-09-14 | B70485¦Staff Kitchen¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Hearing Room 2 | [5 empty] | 21 | 24 | 362 |  | 2020-09-18 12:00 | 12:00 | 21 | 24 | 362 |  | low | 2020-09-14 | B70485¦Hearing Room 2¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Elevators | [5 empty] | 21 | 23 | 361 |  | 2020-09-18 12:00 | 12:00 | 21 | 23 | 361 |  | low | 2020-09-14 | B70485¦Elevators¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Front Security Desk | [5 empty] | 22 | 22 | 388 |  | 2020-09-18 12:00 | 12:00 | 22 | 22 | 388 |  | low | 2020-09-14 | B20705¦Front Security Desk¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family Law Reception | [5 empty] | 22 | 22 | 403 |  | 2020-09-18 12:00 | 12:00 | 22 | 22 | 403 |  | low | 2020-09-14 | B20705¦Family Law Reception¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Criminal Court Inquiry | [5 empty] | 22 | 21 | 409 |  | 2020-09-18 12:00 | 12:00 | 22 | 21 | 409 |  | low | 2020-09-14 | B20705¦Criminal Court Inquiry¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family/Civil Waiting Area | [5 empty] | 22 | 23 | 416 |  | 2020-09-18 12:00 | 12:00 | 22 | 23 | 416 |  | low | 2020-09-14 | B20705¦Family/Civil Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Court Support Services | [5 empty] | 22 | 21 | 409 |  | 2020-09-18 12:00 | 12:00 | 22 | 21 | 409 |  | low | 2020-09-14 | B20705¦Court Support Services¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 20-24 Waiting Area | [5 empty] | 23 | 22 | 370 |  | 2020-09-18 12:00 | 12:00 | 23 | 22 | 370 |  | low | 2020-09-14 | B20705¦Courtroom 20-24 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 25-26 Waiting Area | [5 empty] | 23 | 21 | 384 |  | 2020-09-18 12:00 | 12:00 | 23 | 21 | 384 |  | low | 2020-09-14 | B20705¦Courtroom 25-26 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 4-6 Waiting Area | [5 empty] | 22 | 22 | 437 |  | 2020-09-18 12:00 | 12:00 | 22 | 22 | 437 |  | low | 2020-09-14 | B20705¦Courtroom 4-6 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 1-3 Waiting Area | [5 empty] | 22 | 22 | 437 |  | 2020-09-18 12:00 | 12:00 | 22 | 22 | 437 |  | low | 2020-09-14 | B20705¦Courtroom 1-3 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 7-9 Waiting Area | [5 empty] | 22 | 21 | 391 |  | 2020-09-18 12:00 | 12:00 | 22 | 21 | 391 |  | low | 2020-09-14 | B20705¦Courtroom 7-9 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 10-12 Waiting Area | [5 empty] | 22 | 21 | 375 |  | 2020-09-18 12:00 | 12:00 | 22 | 21 | 375 |  | low | 2020-09-14 | B20705¦Courtroom 10-12 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 13-14 Waiting Area | [5 empty] | 22 | 22 | 363 |  | 2020-09-18 12:00 | 12:00 | 22 | 22 | 363 |  | low | 2020-09-14 | B20705¦Courtroom 13-14 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 34-36 Waiting Area | [5 empty] | 23 | 21 | 394 |  | 2020-09-18 12:00 | 12:00 | 23 | 21 | 394 |  | low | 2020-09-14 | B20705¦Courtroom 34-36 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 30-33 Waiting Area | [5 empty] | 22 | 22 | 379 |  | 2020-09-18 12:00 | 12:00 | 22 | 22 | 379 |  | low | 2020-09-14 | B20705¦Courtroom 30-33 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Crown Attorney Entrance | [5 empty] | 22 | 21 | 384 |  | 2020-09-18 12:00 | 12:00 | 22 | 21 | 384 |  | low | 2020-09-14 | B20705¦Crown Attorney Entrance¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Probation/Parole Waiting Area | [5 empty] | 22 | 21 | 410 |  | 2020-09-18 12:00 | 12:00 | 22 | 21 | 410 |  | low | 2020-09-14 | B20705¦Probation/Parole Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 4th floor waiting area | [5 empty] | 23 | 22 | 399 |  | 2020-09-18 12:00 | 12:00 | 23 | 22 | 399 |  | low | 2020-09-14 | B20705¦4th floor waiting area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 53-55 Waiting Area | [5 empty] | 22 | 21 | 387 |  | 2020-09-18 12:00 | 12:00 | 22 | 21 | 387 |  | low | 2020-09-14 | B20705¦Courtroom 53-55 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 51-52 Waiting Area | [5 empty] | 22 | 23 | 372 |  | 2020-09-18 12:00 | 12:00 | 22 | 23 | 372 |  | low | 2020-09-14 | B20705¦Courtroom 51-52 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 6th Floor Waiting Area | [5 empty] | 22 | 20 | 387 |  | 2020-09-18 12:00 | 12:00 | 22 | 20 | 387 |  | low | 2020-09-14 | B20705¦6th Floor Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Outdoors |  |  | 15 | 25 | 380 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20705¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Social Benefits Tribunal Reception | [5 empty] | 20 | 22 | 371 |  | 2020-09-18 15:00 | 15:00 | 20 | 22 | 371 |  | low | 2020-09-14 | B70485¦Social Benefits Tribunal Reception¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #3 | [5 empty] | 21 | 22 | 364 |  | 2020-09-18 15:00 | 15:00 | 21 | 22 | 364 |  | low | 2020-09-14 | B70485¦SBT Hearing Room #3¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | SBT Hearing Room #4 | [5 empty] | 21 | 19 | 348 |  | 2020-09-18 15:00 | 15:00 | 21 | 19 | 348 |  | low | 2020-09-14 | B70485¦SBT Hearing Room #4¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | LTB Hearing Room #1 | [5 empty] | 22 | 18 | 355 |  | 2020-09-18 15:00 | 15:00 | 22 | 18 | 355 |  | low | 2020-09-14 | B70485¦LTB Hearing Room #1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | LTB Hearing Room #1 | [5 empty] | 22 | 19 | 366 |  | 2020-09-18 15:00 | 15:00 | 22 | 19 | 366 |  | low | 2020-09-14 | B70485¦LTB Hearing Room #1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Regional Managers Office | [5 empty] | 22 | 19 | 366 | Please disregard previous response | 2020-09-18 15:00 | 15:00 | 22 | 19 | 366 |  | low | 2020-09-14 | B70485¦Regional Managers Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Cubes outside RM Office | [5 empty] | 21 | 20 | 358 |  | 2020-09-18 15:00 | 15:00 | 21 | 20 | 358 |  | low | 2020-09-14 | B70485¦Cubes outside RM Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #1 | [5 empty] | 22 | 18 | 361 |  | 2020-09-18 15:00 | 15:00 | 22 | 18 | 361 |  | low | 2020-09-14 | B70485¦Mediation Room #1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #2 | [5 empty] | 21 | 20 | 362 |  | 2020-09-18 15:00 | 15:00 | 21 | 20 | 362 |  | low | 2020-09-14 | B70485¦Mediation Room #2¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Reception/ Administration LTB | [5 empty] | 21 | 20 | 364 |  | 2020-09-18 15:00 | 15:00 | 21 | 20 | 364 |  | low | 2020-09-14 | B70485¦Reception/ Administration LTB¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Document Area | [5 empty] | 21 | 21 | 359 |  | 2020-09-18 15:00 | 15:00 | 21 | 21 | 359 |  | low | 2020-09-14 | B70485¦Document Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Copy Room | [5 empty] | 21 | 20 | 359 |  | 2020-09-18 15:00 | 15:00 | 21 | 20 | 359 |  | low | 2020-09-14 | B70485¦Copy Room¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Mediation Room #3 | [5 empty] | 21 | 20 | 355 |  | 2020-09-18 15:00 | 15:00 | 21 | 20 | 355 |  | low | 2020-09-14 | B70485¦Mediation Room #3¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Corner Office | [5 empty] | 21 | 21 | 364 |  | 2020-09-18 15:00 | 15:00 | 21 | 21 | 364 |  | low | 2020-09-14 | B70485¦Corner Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Side Entry Door | [5 empty] | 21 | 20 | 369 |  | 2020-09-18 15:00 | 15:00 | 21 | 20 | 369 |  | low | 2020-09-14 | B70485¦Side Entry Door¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Filing Area | [5 empty] | 21 | 21 | 360 |  | 2020-09-18 15:00 | 15:00 | 21 | 21 | 360 |  | low | 2020-09-14 | B70485¦Filing Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Staff Kitchen | [5 empty] | 21 | 20 | 364 |  | 2020-09-18 15:00 | 15:00 | 21 | 20 | 364 |  | low | 2020-09-14 | B70485¦Staff Kitchen¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Hearing Room #2 | [5 empty] | 21 | 20 | 362 |  | 2020-09-18 15:00 | 15:00 | 21 | 20 | 362 |  | low | 2020-09-14 | B70485¦Hearing Room #2¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Elevators | [5 empty] | 22 | 18 | 383 |  | 2020-09-18 15:00 | 15:00 | 22 | 18 | 383 |  | low | 2020-09-14 | B70485¦Elevators¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70485 | B70485 - 255 Albert St - Ottawa | Outdoors |  |  | 15 | 17 | 371 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70485¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Front Security Entrance | [5 empty] | 21 | 24 | 441 |  | 2020-09-18 15:00 | 15:00 | 21 | 24 | 441 |  | low | 2020-09-14 | B20705¦Front Security Entrance¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family Law Reception | [5 empty] | 21 | 24 | 482 |  | 2020-09-18 15:00 | 15:00 | 21 | 24 | 482 |  | low | 2020-09-14 | B20705¦Family Law Reception¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Criminal Court Inquiry | [5 empty] | 21 | 24 | 505 |  | 2020-09-18 15:00 | 15:00 | 21 | 24 | 505 |  | low | 2020-09-14 | B20705¦Criminal Court Inquiry¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Family/Civil Waiting Area | [5 empty] | 22 | 25 | 565 |  | 2020-09-18 15:00 | 15:00 | 22 | 25 | 565 |  | low | 2020-09-14 | B20705¦Family/Civil Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Court Support Waiting Area | [5 empty] | 22 | 26 | 491 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 491 |  | low | 2020-09-14 | B20705¦Court Support Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 20-24 Waiting Area | [5 empty] | 23 | 21 | 444 |  | 2020-09-18 15:00 | 15:00 | 23 | 21 | 444 |  | low | 2020-09-14 | B20705¦Courtroom 20-24 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 25-26 Waiting Area | [5 empty] | 23 | 22 | 450 |  | 2020-09-18 15:00 | 15:00 | 23 | 22 | 450 |  | low | 2020-09-14 | B20705¦Courtroom 25-26 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 4-6 Waiting Area | [5 empty] | 22 | 21 | 469 |  | 2020-09-18 15:00 | 15:00 | 22 | 21 | 469 |  | low | 2020-09-14 | B20705¦Courtroom 4-6 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 1-3 Waiting Area | [5 empty] | 22 | 21 | 487 |  | 2020-09-18 15:00 | 15:00 | 22 | 21 | 487 |  | low | 2020-09-14 | B20705¦Courtroom 1-3 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 7-9 Waiting Area | [5 empty] | 22 | 22 | 459 |  | 2020-09-18 15:00 | 15:00 | 22 | 22 | 459 |  | low | 2020-09-14 | B20705¦Courtroom 7-9 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 10-12 Waiting Area | [5 empty] | 22 | 22 | 431 |  | 2020-09-18 15:00 | 15:00 | 22 | 22 | 431 |  | low | 2020-09-14 | B20705¦Courtroom 10-12 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 13-14 Waiting Area | [5 empty] | 22 | 22 | 446 |  | 2020-09-18 15:00 | 15:00 | 22 | 22 | 446 |  | low | 2020-09-14 | B20705¦Courtroom 13-14 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 34-36 Waiting Area | [5 empty] | 22 | 21 | 449 |  | 2020-09-18 15:00 | 15:00 | 22 | 21 | 449 |  | low | 2020-09-14 | B20705¦Courtroom 34-36 Waiting Area¦¦Sep-18-2020 15:00
2020-09-19 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 30-33 Waiting Area | [5 empty] | 22 | 22 | 424 |  | 2020-09-19 15:00 | 15:00 | 22 | 22 | 424 |  | low | 2020-09-14 | B20705¦Courtroom 30-33 Waiting Area¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Crown Attorney Entrance | [5 empty] | 20 | 23 | 455 |  | 2020-09-19 15:00 | 15:00 | 20 | 23 | 455 |  | low | 2020-09-14 | B20705¦Crown Attorney Entrance¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Probation/Parole Waiting Area | [5 empty] | 22 | 20 | 480 |  | 2020-09-19 15:00 | 15:00 | 22 | 20 | 480 |  | low | 2020-09-14 | B20705¦Probation/Parole Waiting Area¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 4th floor waiting area | [5 empty] | 22 | 21 | 455 |  | 2020-09-19 15:00 | 15:00 | 22 | 21 | 455 |  | low | 2020-09-14 | B20705¦4th floor waiting area¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 53-55 Waiting Area | [5 empty] | 22 | 22 | 465 |  | 2020-09-19 15:00 | 15:00 | 22 | 22 | 465 |  | low | 2020-09-14 | B20705¦Courtroom 53-55 Waiting Area¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Courtroom 51-52 Waiting Area | [5 empty] | 22 | 22 | 439 |  | 2020-09-19 15:00 | 15:00 | 22 | 22 | 439 |  | low | 2020-09-14 | B20705¦Courtroom 51-52 Waiting Area¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | 6th Floor Waiting Area | [5 empty] | 22 | 19 | 451 |  | 2020-09-19 15:00 | 15:00 | 22 | 19 | 451 |  | low | 2020-09-14 | B20705¦6th Floor Waiting Area¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE - BAS | B20705 | B20705 - 161 Elgin St - Ottawa | Outdoors |  |  | 16 | 17 | 403 |  |  |  |  | 2020-09-19 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20705¦Outdoors¦¦Sep-19-2020 15:00
2020-09-18 | 0:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 13.5417 | 48.125 | 440.5917 | Average of the hour | 2020-09-18 | 0:00 | 13.5417 | 48.125 | 440.5917 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 9.8167 | 55.6667 | 533.6667 | Average of the hour | 2020-09-18 | 0:00 | 9.8167 | 55.6667 | 533.6667 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 16.8733 | 49.6167 | 395.6667 | Average of the hour | 2020-09-18 | 0:00 | 16.8733 | 49.6167 | 395.6667 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 21.27 | 40.6917 | 385.5833 | Average of the hour | 2020-09-18 | 0:00 | 21.27 | 40.6917 | 385.5833 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 17.8458 | 53.0442 | 431.4167 | Average of the hour | 2020-09-18 | 0:00 | 17.8458 | 53.0442 | 431.4167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.9842 | 47.3325 | 460.75 | Average of the hour | 2020-09-18 | 0:00 | 22.9842 | 47.3325 | 460.75 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.4717 | 35.9592 | 429.5 | Average of the hour | 2020-09-18 | 0:00 | 24.4717 | 35.9592 | 429.5 |  | caution | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.5925 | 45.2379 | 416 | Average of the hour | 2020-09-18 | 0:00 | 22.5925 | 45.2379 | 416 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.613 | 40.0608 | 484.4925 | Average of the hour | 2020-09-18 | 0:00 | 22.613 | 40.0608 | 484.4925 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 26.1043 | 28.754 | 305.1323 | Average of the hour | 2020-09-18 | 0:00 | 26.1043 | 28.754 | 305.1323 | caution | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.5034 | 30.9487 | 379.138 | Average of the hour | 2020-09-18 | 0:00 | 23.5034 | 30.9487 | 379.138 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.3475 | 44.1317 | 619.5 | Average of the hour | 2020-09-18 | 0:00 | 21.3475 | 44.1317 | 619.5 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.9917 | 45.9225 | 408.25 | Average of the hour | 2020-09-18 | 0:00 | 20.9917 | 45.9225 | 408.25 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.2725 | 49.6012 | 412 | Average of the hour | 2020-09-18 | 0:00 | 21.2725 | 49.6012 | 412 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 14.3917 | 36.0833 | 442.3167 | Average of the hour | 2020-09-18 | 0:00 | 14.3917 | 36.0833 | 442.3167 |  | caution | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 12.5167 | 44.9858 | 416.775 | Average of the hour | 2020-09-18 | 0:00 | 12.5167 | 44.9858 | 416.775 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 9.8083 |  |  | Average of the hour | 2020-09-18 | 0:00 | 9.8083 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 12.6917 |  |  | Average of the hour | 2020-09-18 | 0:00 | 12.6917 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 11.1332 |  | 442.1167 | Average of the hour | 2020-09-18 | 0:00 | 11.1332 |  | 442.1167 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 11.0295 |  | 379.6667 | Average of the hour | 2020-09-18 | 0:00 | 11.0295 |  | 379.6667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 43 |  | Average of the hour | 2020-09-18 | 0:00 |  | 43 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 38.5667 |  | Average of the hour | 2020-09-18 | 0:00 |  | 38.5667 |  |  | caution | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.2127 | 25.8279 | 435.7759 | Average of the hour | 2020-09-18 | 0:00 | 22.2127 | 25.8279 | 435.7759 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 41.3463 | 687.7734 | Average of the hour | 2020-09-18 | 0:00 |  | 41.3463 | 687.7734 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.0993 | 28.6769 |  | Average of the hour | 2020-09-18 | 0:00 | 21.0993 | 28.6769 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 00:00
2020-09-18 | 0:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 | 0:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 00:00
2020-09-18 | 1:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 12.725 | 50.4583 | 432.8833 | Average of the hour | 2020-09-18 01:00 | 1:00 | 12.725 | 50.4583 | 432.8833 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 9.1833 | 59.0833 | 532.5833 | Average of the hour | 2020-09-18 01:00 | 1:00 | 9.1833 | 59.0833 | 532.5833 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 16.5375 | 45.7042 | 396.8333 | Average of the hour | 2020-09-18 01:00 | 1:00 | 16.5375 | 45.7042 | 396.8333 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 20.9608 | 37.2208 | 386.75 | Average of the hour | 2020-09-18 01:00 | 1:00 | 20.9608 | 37.2208 | 386.75 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 17.705 | 48.5758 | 429.75 | Average of the hour | 2020-09-18 01:00 | 1:00 | 17.705 | 48.5758 | 429.75 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 23.0742 | 47.1683 | 460.25 | Average of the hour | 2020-09-18 01:00 | 1:00 | 23.0742 | 47.1683 | 460.25 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.5008 | 35.6763 | 427.1667 | Average of the hour | 2020-09-18 01:00 | 1:00 | 24.5008 | 35.6763 | 427.1667 |  | caution | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.55 | 45.205 | 417.5 | Average of the hour | 2020-09-18 01:00 | 1:00 | 22.55 | 45.205 | 417.5 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.613 | 40.2278 | 482.3557 | Average of the hour | 2020-09-18 01:00 | 1:00 | 22.613 | 40.2278 | 482.3557 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 26.02 | 27.5964 | 307.2279 | Average of the hour | 2020-09-18 01:00 | 1:00 | 26.02 | 27.5964 | 307.2279 | caution | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.7235 | 29.7279 | 378.1262 | Average of the hour | 2020-09-18 01:00 | 1:00 | 22.7235 | 29.7279 | 378.1262 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.4125 | 44.4554 | 618.1667 | Average of the hour | 2020-09-18 01:00 | 1:00 | 21.4125 | 44.4554 | 618.1667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.9983 | 45.6971 | 409.25 | Average of the hour | 2020-09-18 01:00 | 1:00 | 20.9983 | 45.6971 | 409.25 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.2775 | 49.4862 | 414.6667 | Average of the hour | 2020-09-18 01:00 | 1:00 | 21.2775 | 49.4862 | 414.6667 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 13.7167 | 40.125 | 438.6167 | Average of the hour | 2020-09-18 01:00 | 1:00 | 13.7167 | 40.125 | 438.6167 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 19 | 42.39 | 414.3083 | Average of the hour | 2020-09-18 01:00 | 1:00 | 19 | 42.39 | 414.3083 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 9.2167 |  |  | Average of the hour | 2020-09-18 01:00 | 1:00 | 9.2167 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 12.1417 |  |  | Average of the hour | 2020-09-18 01:00 | 1:00 | 12.1417 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 10.3276 |  | 438.1417 | Average of the hour | 2020-09-18 01:00 | 1:00 | 10.3276 |  | 438.1417 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 10.2657 |  | 380.25 | Average of the hour | 2020-09-18 01:00 | 1:00 | 10.2657 |  | 380.25 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 39.7417 |  | Average of the hour | 2020-09-18 01:00 | 1:00 |  | 39.7417 |  |  | caution | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 35.6833 |  | Average of the hour | 2020-09-18 01:00 | 1:00 |  | 35.6833 |  |  | caution | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.2309 | 25.889 | 431.2647 | Average of the hour | 2020-09-18 01:00 | 1:00 | 22.2309 | 25.889 | 431.2647 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 41.4474 | 687.4079 | Average of the hour | 2020-09-18 01:00 | 1:00 |  | 41.4474 | 687.4079 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.1464 | 28.9767 |  | Average of the hour | 2020-09-18 01:00 | 1:00 | 21.1464 | 28.9767 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 01:00
2020-09-18 | 1:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 01:00 | 1:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 01:00
2020-09-18 | 2:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 12.125 | 52.7917 | 432.7917 | Average of the hour | 2020-09-18 02:00 | 2:00 | 12.125 | 52.7917 | 432.7917 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 9.25 | 59.3333 | 530.25 | Average of the hour | 2020-09-18 02:00 | 2:00 | 9.25 | 59.3333 | 530.25 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 16.2783 | 41.225 | 392.0833 | Average of the hour | 2020-09-18 02:00 | 2:00 | 16.2783 | 41.225 | 392.0833 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 20.6933 | 33.4642 | 383.25 | Average of the hour | 2020-09-18 02:00 | 2:00 | 20.6933 | 33.4642 | 383.25 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 17.4908 | 44.3642 | 427.4167 | Average of the hour | 2020-09-18 02:00 | 2:00 | 17.4908 | 44.3642 | 427.4167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 23.0542 | 46.9733 | 459.5833 | Average of the hour | 2020-09-18 02:00 | 2:00 | 23.0542 | 46.9733 | 459.5833 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.48 | 35.1837 | 423 | Average of the hour | 2020-09-18 02:00 | 2:00 | 24.48 | 35.1837 | 423 |  | caution | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.5217 | 45.2429 | 415.4167 | Average of the hour | 2020-09-18 02:00 | 2:00 | 22.5217 | 45.2429 | 415.4167 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.613 | 40.3953 | 481.7518 | Average of the hour | 2020-09-18 02:00 | 2:00 | 22.613 | 40.3953 | 481.7518 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 26.0423 | 25.4733 | 304.8599 | Average of the hour | 2020-09-18 02:00 | 2:00 | 26.0423 | 25.4733 | 304.8599 | caution | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.4005 | 26.5461 | 375.4454 | Average of the hour | 2020-09-18 02:00 | 2:00 | 22.4005 | 26.5461 | 375.4454 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.43 | 44.2437 | 621.5 | Average of the hour | 2020-09-18 02:00 | 2:00 | 21.43 | 44.2437 | 621.5 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.0358 | 44.6367 | 407.6667 | Average of the hour | 2020-09-18 02:00 | 2:00 | 21.0358 | 44.6367 | 407.6667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.395 | 49.2542 | 416.3333 | Average of the hour | 2020-09-18 02:00 | 2:00 | 21.395 | 49.2542 | 416.3333 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 13.2833 | 41.625 | 437.25 | Average of the hour | 2020-09-18 02:00 | 2:00 | 13.2833 | 41.625 | 437.25 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 16.1917 | 42.8175 | 413.175 | Average of the hour | 2020-09-18 02:00 | 2:00 | 16.1917 | 42.8175 | 413.175 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 8.8833 |  |  | Average of the hour | 2020-09-18 02:00 | 2:00 | 8.8833 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 12 |  |  | Average of the hour | 2020-09-18 02:00 | 2:00 | 12 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 10.1226 |  | 436.0167 | Average of the hour | 2020-09-18 02:00 | 2:00 | 10.1226 |  | 436.0167 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 10.0328 |  | 380.4167 | Average of the hour | 2020-09-18 02:00 | 2:00 | 10.0328 |  | 380.4167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 38.9917 |  | Average of the hour | 2020-09-18 02:00 | 2:00 |  | 38.9917 |  |  | caution | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 34.6917 |  | Average of the hour | 2020-09-18 02:00 | 2:00 |  | 34.6917 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.2471 | 25.8222 | 429.7906 | Average of the hour | 2020-09-18 02:00 | 2:00 | 22.2471 | 25.8222 | 429.7906 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 41.688 | 687.3202 | Average of the hour | 2020-09-18 02:00 | 2:00 |  | 41.688 | 687.3202 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.0948 | 29.2731 |  | Average of the hour | 2020-09-18 02:00 | 2:00 | 21.0948 | 29.2731 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 02:00
2020-09-18 | 2:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 02:00 | 2:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 02:00
2020-09-18 | 3:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 12.0083 | 52.9583 | 434.025 | Average of the hour | 2020-09-18 03:00 | 3:00 | 12.0083 | 52.9583 | 434.025 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 9.2667 | 59.0417 | 531.9583 | Average of the hour | 2020-09-18 03:00 | 3:00 | 9.2667 | 59.0417 | 531.9583 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 16.2858 | 39.4933 | 390.5 | Average of the hour | 2020-09-18 03:00 | 3:00 | 16.2858 | 39.4933 | 390.5 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 20.6675 | 32.1675 | 380.9167 | Average of the hour | 2020-09-18 03:00 | 3:00 | 20.6675 | 32.1675 | 380.9167 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 17.4542 | 42.9742 | 426.5833 | Average of the hour | 2020-09-18 03:00 | 3:00 | 17.4542 | 42.9742 | 426.5833 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 23.185 | 46.3742 | 458.4167 | Average of the hour | 2020-09-18 03:00 | 3:00 | 23.185 | 46.3742 | 458.4167 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.4925 | 34.5133 | 420.8333 | Average of the hour | 2020-09-18 03:00 | 3:00 | 24.4925 | 34.5133 | 420.8333 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.505 | 45.1246 | 414.8333 | Average of the hour | 2020-09-18 03:00 | 3:00 | 22.505 | 45.1246 | 414.8333 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.613 | 40.5146 | 486.9192 | Average of the hour | 2020-09-18 03:00 | 3:00 | 22.613 | 40.5146 | 486.9192 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 26.1062 | 24.9239 | 304.3354 | Average of the hour | 2020-09-18 03:00 | 3:00 | 26.1062 | 24.9239 | 304.3354 | caution | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.5226 | 25.4301 | 377.3181 | Average of the hour | 2020-09-18 03:00 | 3:00 | 22.5226 | 25.4301 | 377.3181 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.4408 | 44.5979 | 614 | Average of the hour | 2020-09-18 03:00 | 3:00 | 21.4408 | 44.5979 | 614 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.0608 | 44.0404 | 412.8333 | Average of the hour | 2020-09-18 03:00 | 3:00 | 21.0608 | 44.0404 | 412.8333 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.3967 | 49.185 | 410.0833 | Average of the hour | 2020-09-18 03:00 | 3:00 | 21.3967 | 49.185 | 410.0833 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 12.775 | 42.9583 | 434.8417 | Average of the hour | 2020-09-18 03:00 | 3:00 | 12.775 | 42.9583 | 434.8417 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 19.425 | 40.7342 | 412.3167 | Average of the hour | 2020-09-18 03:00 | 3:00 | 19.425 | 40.7342 | 412.3167 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 8.3667 |  |  | Average of the hour | 2020-09-18 03:00 | 3:00 | 8.3667 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 11.6083 |  |  | Average of the hour | 2020-09-18 03:00 | 3:00 | 11.6083 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 9.6992 |  | 435.1333 | Average of the hour | 2020-09-18 03:00 | 3:00 | 9.6992 |  | 435.1333 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 9.5524 |  | 380.4167 | Average of the hour | 2020-09-18 03:00 | 3:00 | 9.5524 |  | 380.4167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 38.2417 |  | Average of the hour | 2020-09-18 03:00 | 3:00 |  | 38.2417 |  |  | caution | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 33.8917 |  | Average of the hour | 2020-09-18 03:00 | 3:00 |  | 33.8917 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.2607 | 25.7664 | 430.7045 | Average of the hour | 2020-09-18 03:00 | 3:00 | 22.2607 | 25.7664 | 430.7045 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 41.8975 | 687.1633 | Average of the hour | 2020-09-18 03:00 | 3:00 |  | 41.8975 | 687.1633 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.1077 | 29.2837 |  | Average of the hour | 2020-09-18 03:00 | 3:00 | 21.1077 | 29.2837 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 03:00
2020-09-18 | 3:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 03:00 | 3:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 03:00
2020-09-18 | 4:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 13.8833 | 50.1667 | 442.0667 | Average of the hour | 2020-09-18 04:00 | 4:00 | 13.8833 | 50.1667 | 442.0667 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 13 | 53.4583 | 534.2083 | Average of the hour | 2020-09-18 04:00 | 4:00 | 13 | 53.4583 | 534.2083 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 18.6308 | 41.15 | 391.75 | Average of the hour | 2020-09-18 04:00 | 4:00 | 18.6308 | 41.15 | 391.75 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.9067 | 34.4258 | 383.0833 | Average of the hour | 2020-09-18 04:00 | 4:00 | 23.9067 | 34.4258 | 383.0833 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.1875 | 44.875 | 430 | Average of the hour | 2020-09-18 04:00 | 4:00 | 22.1875 | 44.875 | 430 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 23.1892 | 42.7792 | 458.6667 | Average of the hour | 2020-09-18 04:00 | 4:00 | 23.1892 | 42.7792 | 458.6667 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.5242 | 33.8208 | 418 | Average of the hour | 2020-09-18 04:00 | 4:00 | 24.5242 | 33.8208 | 418 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.4967 | 44.9017 | 414.1667 | Average of the hour | 2020-09-18 04:00 | 4:00 | 22.4967 | 44.9017 | 414.1667 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.613 | 40.6472 | 488.9075 | Average of the hour | 2020-09-18 04:00 | 4:00 | 22.613 | 40.6472 | 488.9075 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 24.0237 | 37.0534 | 302.7604 | Average of the hour | 2020-09-18 04:00 | 4:00 | 24.0237 | 37.0534 | 302.7604 |  | caution | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.2045 | 32.4409 | 375.7017 | Average of the hour | 2020-09-18 04:00 | 4:00 | 23.2045 | 32.4409 | 375.7017 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.4592 | 44.6638 | 617.5 | Average of the hour | 2020-09-18 04:00 | 4:00 | 21.4592 | 44.6638 | 617.5 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.0408 | 44.0854 | 409.3333 | Average of the hour | 2020-09-18 04:00 | 4:00 | 21.0408 | 44.0854 | 409.3333 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.3925 | 49.3358 | 411.9167 | Average of the hour | 2020-09-18 04:00 | 4:00 | 21.3925 | 49.3358 | 411.9167 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 12.3583 | 42.3333 | 435.1333 | Average of the hour | 2020-09-18 04:00 | 4:00 | 12.3583 | 42.3333 | 435.1333 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 14.2667 | 42.9792 | 414.2417 | Average of the hour | 2020-09-18 04:00 | 4:00 | 14.2667 | 42.9792 | 414.2417 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 7.8667 |  |  | Average of the hour | 2020-09-18 04:00 | 4:00 | 7.8667 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 11.35 |  |  | Average of the hour | 2020-09-18 04:00 | 4:00 | 11.35 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 9.2769 |  | 435.4 | Average of the hour | 2020-09-18 04:00 | 4:00 | 9.2769 |  | 435.4 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 9.1848 |  | 379.25 | Average of the hour | 2020-09-18 04:00 | 4:00 | 9.1848 |  | 379.25 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 38.925 |  | Average of the hour | 2020-09-18 04:00 | 4:00 |  | 38.925 |  |  | caution | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 34.175 |  | Average of the hour | 2020-09-18 04:00 | 4:00 |  | 34.175 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.2926 | 25.8651 | 430.4367 | Average of the hour | 2020-09-18 04:00 | 4:00 | 22.2926 | 25.8651 | 430.4367 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 42.1375 | 687.1589 | Average of the hour | 2020-09-18 04:00 | 4:00 |  | 42.1375 | 687.1589 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.1161 | 28.9496 |  | Average of the hour | 2020-09-18 04:00 | 4:00 | 21.1161 | 28.9496 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 04:00
2020-09-18 | 4:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 04:00 | 4:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 04:00
2020-09-18 | 5:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.0417 | 39.9167 | 436.1917 | Average of the hour | 2020-09-18 05:00 | 5:00 | 19.0417 | 39.9167 | 436.1917 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.3917 | 44.3333 | 536.375 | Average of the hour | 2020-09-18 05:00 | 5:00 | 20.3917 | 44.3333 | 536.375 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.0475 | 41.9792 | 391.75 | Average of the hour | 2020-09-18 05:00 | 5:00 | 21.0475 | 41.9792 | 391.75 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.82 | 38.7308 | 390.3333 | Average of the hour | 2020-09-18 05:00 | 5:00 | 22.82 | 38.7308 | 390.3333 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.1183 | 41.2792 | 431.5 | Average of the hour | 2020-09-18 05:00 | 5:00 | 22.1183 | 41.2792 | 431.5 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.5517 | 40.2442 | 458.0833 | Average of the hour | 2020-09-18 05:00 | 5:00 | 22.5517 | 40.2442 | 458.0833 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.7992 | 34.0346 | 412.5833 | Average of the hour | 2020-09-18 05:00 | 5:00 | 23.7992 | 34.0346 | 412.5833 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.2217 | 42.5042 | 411.5 | Average of the hour | 2020-09-18 05:00 | 5:00 | 22.2217 | 42.5042 | 411.5 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.7687 | 40.7145 | 501.9917 | Average of the hour | 2020-09-18 05:00 | 5:00 | 21.7687 | 40.7145 | 501.9917 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.1628 | 39.7709 | 299.2242 | Average of the hour | 2020-09-18 05:00 | 5:00 | 23.1628 | 39.7709 | 299.2242 |  | caution | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.8736 | 35.2803 | 376.662 | Average of the hour | 2020-09-18 05:00 | 5:00 | 23.8736 | 35.2803 | 376.662 |  | caution | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.4875 | 44.5029 | 613.6667 | Average of the hour | 2020-09-18 05:00 | 5:00 | 21.4875 | 44.5029 | 613.6667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.0025 | 44.0321 | 408.6667 | Average of the hour | 2020-09-18 05:00 | 5:00 | 21.0025 | 44.0321 | 408.6667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.59 | 50.0142 | 412.25 | Average of the hour | 2020-09-18 05:00 | 5:00 | 21.59 | 50.0142 | 412.25 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 13.35 | 42.0833 | 440.1083 | Average of the hour | 2020-09-18 05:00 | 5:00 | 13.35 | 42.0833 | 440.1083 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 18.8667 | 40.0317 | 416.3917 | Average of the hour | 2020-09-18 05:00 | 5:00 | 18.8667 | 40.0317 | 416.3917 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 7.1667 |  |  | Average of the hour | 2020-09-18 05:00 | 5:00 | 7.1667 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 10.7833 |  |  | Average of the hour | 2020-09-18 05:00 | 5:00 | 10.7833 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 8.6356 |  | 440.4333 | Average of the hour | 2020-09-18 05:00 | 5:00 | 8.6356 |  | 440.4333 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 8.6273 |  | 378.9167 | Average of the hour | 2020-09-18 05:00 | 5:00 | 8.6273 |  | 378.9167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 37.8417 |  | Average of the hour | 2020-09-18 05:00 | 5:00 |  | 37.8417 |  |  | caution | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 33.0583 |  | Average of the hour | 2020-09-18 05:00 | 5:00 |  | 33.0583 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.485 | 26.3142 | 431.077 | Average of the hour | 2020-09-18 05:00 | 5:00 | 22.485 | 26.3142 | 431.077 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 42.6767 | 687.4253 | Average of the hour | 2020-09-18 05:00 | 5:00 |  | 42.6767 | 687.4253 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.0753 | 28.7037 |  | Average of the hour | 2020-09-18 05:00 | 5:00 | 21.0753 | 28.7037 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 05:00
2020-09-18 | 5:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 05:00 | 5:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 05:00
2020-09-18 | 6:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 18.925 | 38.5417 | 433.7 | Average of the hour | 2020-09-18 06:00 | 6:00 | 18.925 | 38.5417 | 433.7 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 19.8667 | 41.5833 | 539.2917 | Average of the hour | 2020-09-18 06:00 | 6:00 | 19.8667 | 41.5833 | 539.2917 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.1633 | 38.5483 | 394.9167 | Average of the hour | 2020-09-18 06:00 | 6:00 | 21.1633 | 38.5483 | 394.9167 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.7967 | 41.9867 | 395.5 | Average of the hour | 2020-09-18 06:00 | 6:00 | 22.7967 | 41.9867 | 395.5 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.0708 | 40.135 | 433.4167 | Average of the hour | 2020-09-18 06:00 | 6:00 | 22.0708 | 40.135 | 433.4167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.3092 | 39.195 | 458.75 | Average of the hour | 2020-09-18 06:00 | 6:00 | 22.3092 | 39.195 | 458.75 |  | caution | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.3358 | 32.5263 | 413.0833 | Average of the hour | 2020-09-18 06:00 | 6:00 | 23.3358 | 32.5263 | 413.0833 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 20.8125 | 37.4138 | 414.5 | Average of the hour | 2020-09-18 06:00 | 6:00 | 20.8125 | 37.4138 | 414.5 |  | caution | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.8059 | 39.112 | 514.7577 | Average of the hour | 2020-09-18 06:00 | 6:00 | 20.8059 | 39.112 | 514.7577 |  | caution | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.9081 | 37.1485 | 301.4038 | Average of the hour | 2020-09-18 06:00 | 6:00 | 22.9081 | 37.1485 | 301.4038 |  | caution | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.0995 | 36.4553 | 366.262 | Average of the hour | 2020-09-18 06:00 | 6:00 | 23.0995 | 36.4553 | 366.262 |  | caution | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.43 | 44.7592 | 618.25 | Average of the hour | 2020-09-18 06:00 | 6:00 | 21.43 | 44.7592 | 618.25 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.9642 | 44.1237 | 410 | Average of the hour | 2020-09-18 06:00 | 6:00 | 20.9642 | 44.1237 | 410 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.5333 | 49.4829 | 413.6667 | Average of the hour | 2020-09-18 06:00 | 6:00 | 21.5333 | 49.4829 | 413.6667 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21 | 33.375 | 443.8917 | Average of the hour | 2020-09-18 06:00 | 6:00 | 21 | 33.375 | 443.8917 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 20.9917 | 35.3033 | 435.9917 | Average of the hour | 2020-09-18 06:00 | 6:00 | 20.9917 | 35.3033 | 435.9917 |  | caution | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.6417 |  |  | Average of the hour | 2020-09-18 06:00 | 6:00 | 22.6417 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 19.7667 |  |  | Average of the hour | 2020-09-18 06:00 | 6:00 | 19.7667 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 15.8878 |  | 444.6333 | Average of the hour | 2020-09-18 06:00 | 6:00 | 15.8878 |  | 444.6333 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 14.5154 |  | 379.6667 | Average of the hour | 2020-09-18 06:00 | 6:00 | 14.5154 |  | 379.6667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 36.9833 |  | Average of the hour | 2020-09-18 06:00 | 6:00 |  | 36.9833 |  |  | caution | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 33.275 |  | Average of the hour | 2020-09-18 06:00 | 6:00 |  | 33.275 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.3744 | 26.202 | 457.4997 | Average of the hour | 2020-09-18 06:00 | 6:00 | 22.3744 | 26.202 | 457.4997 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 42.4383 | 687.8639 | Average of the hour | 2020-09-18 06:00 | 6:00 |  | 42.4383 | 687.8639 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.7135 | 28.0024 |  | Average of the hour | 2020-09-18 06:00 | 6:00 | 20.7135 | 28.0024 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 06:00
2020-09-18 | 6:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 06:00 | 6:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 06:00
2020-09-18 | 7:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 18.8 | 38.0833 | 440.3333 | Average of the hour | 2020-09-18 07:00 | 7:00 | 18.8 | 38.0833 | 440.3333 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 19.8583 | 40.5 | 546.1667 | Average of the hour | 2020-09-18 07:00 | 7:00 | 19.8583 | 40.5 | 546.1667 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.2667 | 38.11 | 401.25 | Average of the hour | 2020-09-18 07:00 | 7:00 | 21.2667 | 38.11 | 401.25 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.9233 | 40.3742 | 397.75 | Average of the hour | 2020-09-18 07:00 | 7:00 | 22.9233 | 40.3742 | 397.75 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.3283 | 39.8017 | 435.5 | Average of the hour | 2020-09-18 07:00 | 7:00 | 22.3283 | 39.8017 | 435.5 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.355 | 38.6667 | 460.0833 | Average of the hour | 2020-09-18 07:00 | 7:00 | 22.355 | 38.6667 | 460.0833 |  | caution | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.26 | 31.9258 | 416.8333 | Average of the hour | 2020-09-18 07:00 | 7:00 | 23.26 | 31.9258 | 416.8333 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 20.1358 | 38.585 | 415.8333 | Average of the hour | 2020-09-18 07:00 | 7:00 | 20.1358 | 38.585 | 415.8333 |  | caution | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.8456 | 38.3447 | 517.8315 | Average of the hour | 2020-09-18 07:00 | 7:00 | 20.8456 | 38.3447 | 517.8315 |  | caution | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.8152 | 36.3926 | 303.084 | Average of the hour | 2020-09-18 07:00 | 7:00 | 22.8152 | 36.3926 | 303.084 |  | caution | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.9128 | 34.2041 | 367.8231 | Average of the hour | 2020-09-18 07:00 | 7:00 | 22.9128 | 34.2041 | 367.8231 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.3158 | 44.8117 | 623 | Average of the hour | 2020-09-18 07:00 | 7:00 | 21.3158 | 44.8117 | 623 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.9058 | 44.1671 | 413.75 | Average of the hour | 2020-09-18 07:00 | 7:00 | 20.9058 | 44.1671 | 413.75 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.48 | 49.2308 | 416 | Average of the hour | 2020-09-18 07:00 | 7:00 | 21.48 | 49.2308 | 416 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 20.8917 | 32.7083 | 442.2833 | Average of the hour | 2020-09-18 07:00 | 7:00 | 20.8917 | 32.7083 | 442.2833 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.1583 | 33.8942 | 435.05 | Average of the hour | 2020-09-18 07:00 | 7:00 | 21.1583 | 33.8942 | 435.05 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.9917 |  |  | Average of the hour | 2020-09-18 07:00 | 7:00 | 23.9917 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 19.7 |  |  | Average of the hour | 2020-09-18 07:00 | 7:00 | 19.7 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 17.1243 |  | 441.925 | Average of the hour | 2020-09-18 07:00 | 7:00 | 17.1243 |  | 441.925 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 16.148 |  | 379.6667 | Average of the hour | 2020-09-18 07:00 | 7:00 | 16.148 |  | 379.6667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 37.4083 |  | Average of the hour | 2020-09-18 07:00 | 7:00 |  | 37.4083 |  |  | caution | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 33.3167 |  | Average of the hour | 2020-09-18 07:00 | 7:00 |  | 33.3167 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.9561 | 25.2363 | 451.363 | Average of the hour | 2020-09-18 07:00 | 7:00 | 21.9561 | 25.2363 | 451.363 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 41.6452 | 687.9296 | Average of the hour | 2020-09-18 07:00 | 7:00 |  | 41.6452 | 687.9296 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.6635 | 27.7867 |  | Average of the hour | 2020-09-18 07:00 | 7:00 | 20.6635 | 27.7867 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 07:00
2020-09-18 | 7:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 07:00 | 7:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 07:00
2020-09-18 | 8:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 18.925 | 38 | 438.7917 | Average of the hour | 2020-09-18 08:00 | 8:00 | 18.925 | 38 | 438.7917 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 19.8333 | 40 | 548.7917 | Average of the hour | 2020-09-18 08:00 | 8:00 | 19.8333 | 40 | 548.7917 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.3017 | 37.5417 | 420.9167 | Average of the hour | 2020-09-18 08:00 | 8:00 | 21.3017 | 37.5417 | 420.9167 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.9258 | 39.4383 | 404.3333 | Average of the hour | 2020-09-18 08:00 | 8:00 | 22.9258 | 39.4383 | 404.3333 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.3692 | 39.4 | 438.5833 | Average of the hour | 2020-09-18 08:00 | 8:00 | 22.3692 | 39.4 | 438.5833 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.27 | 38.3275 | 460.8333 | Average of the hour | 2020-09-18 08:00 | 8:00 | 22.27 | 38.3275 | 460.8333 |  | caution | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.2058 | 30.71 | 422.1667 | Average of the hour | 2020-09-18 08:00 | 8:00 | 23.2058 | 30.71 | 422.1667 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 19.595 | 37.3875 | 419.4167 | Average of the hour | 2020-09-18 08:00 | 8:00 | 19.595 | 37.3875 | 419.4167 |  | caution | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.7765 | 37.3897 | 526.7319 | Average of the hour | 2020-09-18 08:00 | 8:00 | 20.7765 | 37.3897 | 526.7319 |  | caution | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.7986 | 32.8942 | 306.0567 | Average of the hour | 2020-09-18 08:00 | 8:00 | 22.7986 | 32.8942 | 306.0567 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.7097 | 32.7078 | 368.7733 | Average of the hour | 2020-09-18 08:00 | 8:00 | 22.7097 | 32.7078 | 368.7733 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.2433 | 44.4704 | 629.6667 | Average of the hour | 2020-09-18 08:00 | 8:00 | 21.2433 | 44.4704 | 629.6667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.835 | 44.0888 | 411.5 | Average of the hour | 2020-09-18 08:00 | 8:00 | 20.835 | 44.0888 | 411.5 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.485 | 49.185 | 417 | Average of the hour | 2020-09-18 08:00 | 8:00 | 21.485 | 49.185 | 417 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 20.8 | 32.0833 | 447.5583 | Average of the hour | 2020-09-18 08:00 | 8:00 | 20.8 | 32.0833 | 447.5583 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.2667 | 33.2483 | 432.0917 | Average of the hour | 2020-09-18 08:00 | 8:00 | 21.2667 | 33.2483 | 432.0917 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.5083 |  |  | Average of the hour | 2020-09-18 08:00 | 8:00 | 23.5083 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 19.7667 |  |  | Average of the hour | 2020-09-18 08:00 | 8:00 | 19.7667 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 17.4342 |  | 447.7167 | Average of the hour | 2020-09-18 08:00 | 8:00 | 17.4342 |  | 447.7167 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 16.4623 |  | 380.5833 | Average of the hour | 2020-09-18 08:00 | 8:00 | 16.4623 |  | 380.5833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 37.5417 |  | Average of the hour | 2020-09-18 08:00 | 8:00 |  | 37.5417 |  |  | caution | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 33.5917 |  | Average of the hour | 2020-09-18 08:00 | 8:00 |  | 33.5917 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.8342 | 24.7551 | 454.3805 | Average of the hour | 2020-09-18 08:00 | 8:00 | 21.8342 | 24.7551 | 454.3805 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 40.5532 | 688.0093 | Average of the hour | 2020-09-18 08:00 | 8:00 |  | 40.5532 | 688.0093 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.6607 | 27.3818 |  | Average of the hour | 2020-09-18 08:00 | 8:00 | 20.6607 | 27.3818 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 08:00
2020-09-18 | 8:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 08:00 | 8:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 08:00
2020-09-18 | 9:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.2167 | 37.25 | 431.3583 | Average of the hour | 2020-09-18 09:00 | 9:00 | 19.2167 | 37.25 | 431.3583 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20 | 39.0417 | 552.5833 | Average of the hour | 2020-09-18 09:00 | 9:00 | 20 | 39.0417 | 552.5833 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.3908 | 37.1258 | 446.5 | Average of the hour | 2020-09-18 09:00 | 9:00 | 21.3908 | 37.1258 | 446.5 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.0817 | 38.6458 | 422.5833 | Average of the hour | 2020-09-18 09:00 | 9:00 | 23.0817 | 38.6458 | 422.5833 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.3875 | 39.1942 | 444.5833 | Average of the hour | 2020-09-18 09:00 | 9:00 | 22.3875 | 39.1942 | 444.5833 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.1175 | 38.2925 | 462.25 | Average of the hour | 2020-09-18 09:00 | 9:00 | 22.1175 | 38.2925 | 462.25 |  | caution | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.1833 | 29.5196 | 425.9167 | Average of the hour | 2020-09-18 09:00 | 9:00 | 23.1833 | 29.5196 | 425.9167 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 20.3883 | 34.9063 | 421.5833 | Average of the hour | 2020-09-18 09:00 | 9:00 | 20.3883 | 34.9063 | 421.5833 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.7765 | 35.9204 | 543.8367 | Average of the hour | 2020-09-18 09:00 | 9:00 | 20.7765 | 35.9204 | 543.8367 |  | caution | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.6733 | 30.743 | 303.2715 | Average of the hour | 2020-09-18 09:00 | 9:00 | 22.6733 | 30.743 | 303.2715 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.5993 | 31.1221 | 374.0305 | Average of the hour | 2020-09-18 09:00 | 9:00 | 22.5993 | 31.1221 | 374.0305 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.3158 | 44.2813 | 655.5 | Average of the hour | 2020-09-18 09:00 | 9:00 | 21.3158 | 44.2813 | 655.5 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.87 | 44.0988 | 413.3333 | Average of the hour | 2020-09-18 09:00 | 9:00 | 20.87 | 44.0988 | 413.3333 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.6117 | 49.15 | 423 | Average of the hour | 2020-09-18 09:00 | 9:00 | 21.6117 | 49.15 | 423 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 20.8667 | 31.1667 | 468.9167 | Average of the hour | 2020-09-18 09:00 | 9:00 | 20.8667 | 31.1667 | 468.9167 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.6667 | 32.84 | 428.1917 | Average of the hour | 2020-09-18 09:00 | 9:00 | 21.6667 | 32.84 | 428.1917 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.6167 |  |  | Average of the hour | 2020-09-18 09:00 | 9:00 | 23.6167 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 19.9833 |  |  | Average of the hour | 2020-09-18 09:00 | 9:00 | 19.9833 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 19.0971 |  | 468.1833 | Average of the hour | 2020-09-18 09:00 | 9:00 | 19.0971 |  | 468.1833 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 16.8645 |  | 379.75 | Average of the hour | 2020-09-18 09:00 | 9:00 | 16.8645 |  | 379.75 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 37.6417 |  | Average of the hour | 2020-09-18 09:00 | 9:00 |  | 37.6417 |  |  | caution | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 33.6083 |  | Average of the hour | 2020-09-18 09:00 | 9:00 |  | 33.6083 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.8159 | 24.378 | 458.6095 | Average of the hour | 2020-09-18 09:00 | 9:00 | 21.8159 | 24.378 | 458.6095 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 39.5759 | 690.4562 | Average of the hour | 2020-09-18 09:00 | 9:00 |  | 39.5759 | 690.4562 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.7636 | 27.1012 |  | Average of the hour | 2020-09-18 09:00 | 9:00 | 20.7636 | 27.1012 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 09:00
2020-09-18 | 10:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 18.9167 | 33.5833 | 420.6083 | Average of the hour | 2020-09-18 10:00 | 10:00 | 18.9167 | 33.5833 | 420.6083 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20 | 37.2917 | 551.2917 | Average of the hour | 2020-09-18 10:00 | 10:00 | 20 | 37.2917 | 551.2917 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.5333 | 36.5258 | 443.4167 | Average of the hour | 2020-09-18 10:00 | 10:00 | 21.5333 | 36.5258 | 443.4167 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.0792 | 37.8958 | 423.1667 | Average of the hour | 2020-09-18 10:00 | 10:00 | 23.0792 | 37.8958 | 423.1667 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.4583 | 38.7908 | 450.5833 | Average of the hour | 2020-09-18 10:00 | 10:00 | 22.4583 | 38.7908 | 450.5833 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.04 | 37.9125 | 466.6667 | Average of the hour | 2020-09-18 10:00 | 10:00 | 22.04 | 37.9125 | 466.6667 |  | caution | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.1925 | 28.4042 | 427.5 | Average of the hour | 2020-09-18 10:00 | 10:00 | 23.1925 | 28.4042 | 427.5 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.2958 | 32.4396 | 424 | Average of the hour | 2020-09-18 10:00 | 10:00 | 21.2958 | 32.4396 | 424 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.785 | 34.5104 | 557.034 | Average of the hour | 2020-09-18 10:00 | 10:00 | 20.785 | 34.5104 | 557.034 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.5888 | 32.0628 | 300.7025 | Average of the hour | 2020-09-18 10:00 | 10:00 | 22.5888 | 32.0628 | 300.7025 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.5993 | 30.2988 | 374.038 | Average of the hour | 2020-09-18 10:00 | 10:00 | 22.5993 | 30.2988 | 374.038 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.4242 | 44.2521 | 658.8333 | Average of the hour | 2020-09-18 10:00 | 10:00 | 21.4242 | 44.2521 | 658.8333 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.9267 | 44.0862 | 418.25 | Average of the hour | 2020-09-18 10:00 | 10:00 | 20.9267 | 44.0862 | 418.25 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.6558 | 49.1058 | 414.9167 | Average of the hour | 2020-09-18 10:00 | 10:00 | 21.6558 | 49.1058 | 414.9167 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.0167 | 29.4167 | 486.5833 | Average of the hour | 2020-09-18 10:00 | 10:00 | 21.0167 | 29.4167 | 486.5833 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.85 | 31.8692 | 433.0083 | Average of the hour | 2020-09-18 10:00 | 10:00 | 21.85 | 31.8692 | 433.0083 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.2917 |  |  | Average of the hour | 2020-09-18 10:00 | 10:00 | 23.2917 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.175 |  |  | Average of the hour | 2020-09-18 10:00 | 10:00 | 20.175 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.0615 |  | 486.425 | Average of the hour | 2020-09-18 10:00 | 10:00 | 20.0615 |  | 486.425 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 17.9113 |  | 379.5 | Average of the hour | 2020-09-18 10:00 | 10:00 | 17.9113 |  | 379.5 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 36.625 |  | Average of the hour | 2020-09-18 10:00 | 10:00 |  | 36.625 |  |  | caution | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 33.1 |  | Average of the hour | 2020-09-18 10:00 | 10:00 |  | 33.1 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.8166 | 23.9222 | 459.3994 | Average of the hour | 2020-09-18 10:00 | 10:00 | 21.8166 | 23.9222 | 459.3994 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 38.4775 | 692.7147 | Average of the hour | 2020-09-18 10:00 | 10:00 |  | 38.4775 | 692.7147 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9026 | 25.9525 |  | Average of the hour | 2020-09-18 10:00 | 10:00 | 20.9026 | 25.9525 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 10:00
2020-09-18 | 10:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 10:00 | 10:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 10:00
2020-09-18 | 11:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 18.85 | 31.5417 | 416.525 | Average of the hour | 2020-09-18 11:00 | 11:00 | 18.85 | 31.5417 | 416.525 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20 | 35.5 | 546.25 | Average of the hour | 2020-09-18 11:00 | 11:00 | 20 | 35.5 | 546.25 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.4392 | 38.1317 | 463.1667 | Average of the hour | 2020-09-18 11:00 | 11:00 | 21.4392 | 38.1317 | 463.1667 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.9342 | 38.51 | 417.9167 | Average of the hour | 2020-09-18 11:00 | 11:00 | 22.9342 | 38.51 | 417.9167 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.2258 | 40.0733 | 470.0833 | Average of the hour | 2020-09-18 11:00 | 11:00 | 22.2258 | 40.0733 | 470.0833 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.9658 | 38.4142 | 467.3333 | Average of the hour | 2020-09-18 11:00 | 11:00 | 21.9658 | 38.4142 | 467.3333 |  | caution | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.1767 | 27.06 | 424.3333 | Average of the hour | 2020-09-18 11:00 | 11:00 | 23.1767 | 27.06 | 424.3333 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.7808 | 30.1546 | 421.5 | Average of the hour | 2020-09-18 11:00 | 11:00 | 21.7808 | 30.1546 | 421.5 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.878 | 32.7954 | 554.5095 | Average of the hour | 2020-09-18 11:00 | 11:00 | 20.878 | 32.7954 | 554.5095 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.4718 | 27.6691 | 298.6134 | Average of the hour | 2020-09-18 11:00 | 11:00 | 22.4718 | 27.6691 | 298.6134 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.5498 | 29.0207 | 373.8794 | Average of the hour | 2020-09-18 11:00 | 11:00 | 22.5498 | 29.0207 | 373.8794 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.5575 | 44.86 | 655 | Average of the hour | 2020-09-18 11:00 | 11:00 | 21.5575 | 44.86 | 655 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.02 | 44.4013 | 416.8333 | Average of the hour | 2020-09-18 11:00 | 11:00 | 21.02 | 44.4013 | 416.8333 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.7225 | 49.4487 | 413 | Average of the hour | 2020-09-18 11:00 | 11:00 | 21.7225 | 49.4487 | 413 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.0917 | 27.5417 | 482.8833 | Average of the hour | 2020-09-18 11:00 | 11:00 | 21.0917 | 27.5417 | 482.8833 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.95 | 30.9792 | 433.8917 | Average of the hour | 2020-09-18 11:00 | 11:00 | 21.95 | 30.9792 | 433.8917 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.1583 |  |  | Average of the hour | 2020-09-18 11:00 | 11:00 | 23.1583 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.275 |  |  | Average of the hour | 2020-09-18 11:00 | 11:00 | 20.275 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.5113 |  | 483.9083 | Average of the hour | 2020-09-18 11:00 | 11:00 | 20.5113 |  | 483.9083 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 18.1932 |  | 379.4167 | Average of the hour | 2020-09-18 11:00 | 11:00 | 18.1932 |  | 379.4167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 34.425 |  | Average of the hour | 2020-09-18 11:00 | 11:00 |  | 34.425 |  |  | low | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 32.1833 |  | Average of the hour | 2020-09-18 11:00 | 11:00 |  | 32.1833 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.7665 | 22.9766 | 450.4613 | Average of the hour | 2020-09-18 11:00 | 11:00 | 21.7665 | 22.9766 | 450.4613 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 36.9984 | 692.8481 | Average of the hour | 2020-09-18 11:00 | 11:00 |  | 36.9984 | 692.8481 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.0285 | 24.3678 |  | Average of the hour | 2020-09-18 11:00 | 11:00 | 21.0285 | 24.3678 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 11:00
2020-09-18 | 11:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 11:00 | 11:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 11:00
2020-09-18 | 12:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 18.825 | 31.8333 | 414.9167 | Average of the hour | 2020-09-18 12:00 | 12:00 | 18.825 | 31.8333 | 414.9167 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20 | 34.5 | 538.875 | Average of the hour | 2020-09-18 12:00 | 12:00 | 20 | 34.5 | 538.875 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.2275 | 39.47 | 475.6667 | Average of the hour | 2020-09-18 12:00 | 12:00 | 21.2275 | 39.47 | 475.6667 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.9808 | 39.1917 | 429.9167 | Average of the hour | 2020-09-18 12:00 | 12:00 | 22.9808 | 39.1917 | 429.9167 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.1308 | 40.9233 | 471.75 | Average of the hour | 2020-09-18 12:00 | 12:00 | 22.1308 | 40.9233 | 471.75 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.9542 | 39.43 | 466.5833 | Average of the hour | 2020-09-18 12:00 | 12:00 | 21.9542 | 39.43 | 466.5833 |  | caution | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.16 | 26.1375 | 422.9167 | Average of the hour | 2020-09-18 12:00 | 12:00 | 23.16 | 26.1375 | 422.9167 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.1408 | 28.7438 | 417.4167 | Average of the hour | 2020-09-18 12:00 | 12:00 | 22.1408 | 28.7438 | 417.4167 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.8521 | 31.5778 | 546.7506 | Average of the hour | 2020-09-18 12:00 | 12:00 | 20.8521 | 31.5778 | 546.7506 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.414 | 26.0143 | 298.3335 | Average of the hour | 2020-09-18 12:00 | 12:00 | 22.414 | 26.0143 | 298.3335 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.5002 | 30.0583 | 368.397 | Average of the hour | 2020-09-18 12:00 | 12:00 | 22.5002 | 30.0583 | 368.397 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.6617 | 44.7692 | 651.75 | Average of the hour | 2020-09-18 12:00 | 12:00 | 21.6617 | 44.7692 | 651.75 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.1008 | 44.5679 | 407.6667 | Average of the hour | 2020-09-18 12:00 | 12:00 | 21.1008 | 44.5679 | 407.6667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.7367 | 49.2033 | 415.9167 | Average of the hour | 2020-09-18 12:00 | 12:00 | 21.7367 | 49.2033 | 415.9167 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.0583 | 27 | 489.5 | Average of the hour | 2020-09-18 12:00 | 12:00 | 21.0583 | 27 | 489.5 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.05 | 30.7058 | 437.2417 | Average of the hour | 2020-09-18 12:00 | 12:00 | 22.05 | 30.7058 | 437.2417 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.25 |  |  | Average of the hour | 2020-09-18 12:00 | 12:00 | 23.25 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.4333 |  |  | Average of the hour | 2020-09-18 12:00 | 12:00 | 20.4333 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.9773 |  | 487.775 | Average of the hour | 2020-09-18 12:00 | 12:00 | 20.9773 |  | 487.775 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 18.5289 |  | 380.1667 | Average of the hour | 2020-09-18 12:00 | 12:00 | 18.5289 |  | 380.1667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 33.825 |  | Average of the hour | 2020-09-18 12:00 | 12:00 |  | 33.825 |  |  | low | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 31.825 |  | Average of the hour | 2020-09-18 12:00 | 12:00 |  | 31.825 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.6928 | 21.9236 | 441.5208 | Average of the hour | 2020-09-18 12:00 | 12:00 | 21.6928 | 21.9236 | 441.5208 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 36.0952 | 692.8673 | Average of the hour | 2020-09-18 12:00 | 12:00 |  | 36.0952 | 692.8673 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.0727 | 24.3931 |  | Average of the hour | 2020-09-18 12:00 | 12:00 | 21.0727 | 24.3931 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 12:00
2020-09-18 | 13:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 18.85 | 31.625 | 414.5333 | Average of the hour | 2020-09-18 13:00 | 13:00 | 18.85 | 31.625 | 414.5333 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 19.9833 | 33.5417 | 534.9167 | Average of the hour | 2020-09-18 13:00 | 13:00 | 19.9833 | 33.5417 | 534.9167 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.2075 | 39.6283 | 480.25 | Average of the hour | 2020-09-18 13:00 | 13:00 | 21.2075 | 39.6283 | 480.25 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.0433 | 39.1225 | 433.4167 | Average of the hour | 2020-09-18 13:00 | 13:00 | 23.0433 | 39.1225 | 433.4167 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.1217 | 41.0408 | 466.9167 | Average of the hour | 2020-09-18 13:00 | 13:00 | 22.1217 | 41.0408 | 466.9167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.9783 | 38.7375 | 464.3333 | Average of the hour | 2020-09-18 13:00 | 13:00 | 21.9783 | 38.7375 | 464.3333 |  | caution | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.075 | 25.845 | 420.3333 | Average of the hour | 2020-09-18 13:00 | 13:00 | 23.075 | 25.845 | 420.3333 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.3858 | 30.1887 | 422.6667 | Average of the hour | 2020-09-18 13:00 | 13:00 | 22.3858 | 30.1887 | 422.6667 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.7743 | 30.9445 | 535.807 | Average of the hour | 2020-09-18 13:00 | 13:00 | 20.7743 | 30.9445 | 535.807 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.414 | 25.6273 | 299.0595 | Average of the hour | 2020-09-18 13:00 | 13:00 | 22.414 | 25.6273 | 299.0595 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.5002 | 29.9791 | 365.9125 | Average of the hour | 2020-09-18 13:00 | 13:00 | 22.5002 | 29.9791 | 365.9125 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.4792 | 44.6062 | 640.75 | Average of the hour | 2020-09-18 13:00 | 13:00 | 21.4792 | 44.6062 | 640.75 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.9108 | 44.9513 | 409.9167 | Average of the hour | 2020-09-18 13:00 | 13:00 | 20.9108 | 44.9513 | 409.9167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.3142 | 49.905 | 419.75 | Average of the hour | 2020-09-18 13:00 | 13:00 | 21.3142 | 49.905 | 419.75 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.1917 | 26.625 | 488.5667 | Average of the hour | 2020-09-18 13:00 | 13:00 | 21.1917 | 26.625 | 488.5667 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.1 | 30.1742 | 438.2167 | Average of the hour | 2020-09-18 13:00 | 13:00 | 22.1 | 30.1742 | 438.2167 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.4667 |  |  | Average of the hour | 2020-09-18 13:00 | 13:00 | 22.4667 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.5 |  |  | Average of the hour | 2020-09-18 13:00 | 13:00 | 20.5 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.8011 |  | 489.1417 | Average of the hour | 2020-09-18 13:00 | 13:00 | 20.8011 |  | 489.1417 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 19.0594 |  | 379.5833 | Average of the hour | 2020-09-18 13:00 | 13:00 | 19.0594 |  | 379.5833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-18 13:00 | 13:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-18 13:00 | 13:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.7048 | 21.0544 | 438.0532 | Average of the hour | 2020-09-18 13:00 | 13:00 | 21.7048 | 21.0544 | 438.0532 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 36.6126 | 692.8671 | Average of the hour | 2020-09-18 13:00 | 13:00 |  | 36.6126 | 692.8671 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.1001 | 25.7739 |  | Average of the hour | 2020-09-18 13:00 | 13:00 | 21.1001 | 25.7739 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 13:00
2020-09-18 | 13:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 13:00 | 13:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 13:00
2020-09-18 | 14:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 18.8 | 30.5833 | 415 | Average of the hour | 2020-09-18 14:00 | 14:00 | 18.8 | 30.5833 | 415 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 19.9917 | 32.8333 | 535.2917 | Average of the hour | 2020-09-18 14:00 | 14:00 | 19.9917 | 32.8333 | 535.2917 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.1667 | 38.2908 | 487.9167 | Average of the hour | 2020-09-18 14:00 | 14:00 | 21.1667 | 38.2908 | 487.9167 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.0733 | 37.995 | 434.3333 | Average of the hour | 2020-09-18 14:00 | 14:00 | 23.0733 | 37.995 | 434.3333 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.1525 | 40.0967 | 470.8333 | Average of the hour | 2020-09-18 14:00 | 14:00 | 22.1525 | 40.0967 | 470.8333 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.9875 | 36.2125 | 464.25 | Average of the hour | 2020-09-18 14:00 | 14:00 | 21.9875 | 36.2125 | 464.25 |  | caution | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.0167 | 25.4371 | 425.3333 | Average of the hour | 2020-09-18 14:00 | 14:00 | 23.0167 | 25.4371 | 425.3333 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.0917 | 32.4317 | 426.1667 | Average of the hour | 2020-09-18 14:00 | 14:00 | 22.0917 | 32.4317 | 426.1667 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.7001 | 30.3889 | 528.2396 | Average of the hour | 2020-09-18 14:00 | 14:00 | 20.7001 | 30.3889 | 528.2396 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.5186 | 25.6404 | 299.1328 | Average of the hour | 2020-09-18 14:00 | 14:00 | 22.5186 | 25.6404 | 299.1328 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.5002 | 30.007 | 363.5232 | Average of the hour | 2020-09-18 14:00 | 14:00 | 22.5002 | 30.007 | 363.5232 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.5592 | 45.4354 | 662 | Average of the hour | 2020-09-18 14:00 | 14:00 | 21.5592 | 45.4354 | 662 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.03 | 45.6983 | 427.0833 | Average of the hour | 2020-09-18 14:00 | 14:00 | 21.03 | 45.6983 | 427.0833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.4633 | 50.7813 | 424 | Average of the hour | 2020-09-18 14:00 | 14:00 | 21.4633 | 50.7813 | 424 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.3583 | 26.5 | 495.625 | Average of the hour | 2020-09-18 14:00 | 14:00 | 21.3583 | 26.5 | 495.625 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.0583 | 29.6592 | 433.15 | Average of the hour | 2020-09-18 14:00 | 14:00 | 22.0583 | 29.6592 | 433.15 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.7583 |  |  | Average of the hour | 2020-09-18 14:00 | 14:00 | 22.7583 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.4 |  |  | Average of the hour | 2020-09-18 14:00 | 14:00 | 20.4 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.3433 |  | 494.3083 | Average of the hour | 2020-09-18 14:00 | 14:00 | 20.3433 |  | 494.3083 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 19.5413 |  | 379.3333 | Average of the hour | 2020-09-18 14:00 | 14:00 | 19.5413 |  | 379.3333 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-18 14:00 | 14:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-18 14:00 | 14:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.5698 | 20.4783 | 430.3174 | Average of the hour | 2020-09-18 14:00 | 14:00 | 21.5698 | 20.4783 | 430.3174 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 36.2152 | 692.8671 | Average of the hour | 2020-09-18 14:00 | 14:00 |  | 36.2152 | 692.8671 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9948 | 25.0276 |  | Average of the hour | 2020-09-18 14:00 | 14:00 | 20.9948 | 25.0276 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 14:00
2020-09-18 | 14:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 14:00 | 14:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 14:00
2020-09-18 | 15:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 18.8083 | 29.5 | 414.575 | Average of the hour | 2020-09-18 15:00 | 15:00 | 18.8083 | 29.5 | 414.575 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.0917 | 32.2083 | 531.375 | Average of the hour | 2020-09-18 15:00 | 15:00 | 20.0917 | 32.2083 | 531.375 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.1658 | 37.3667 | 491.3333 | Average of the hour | 2020-09-18 15:00 | 15:00 | 21.1658 | 37.3667 | 491.3333 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.1083 | 37.1392 | 438.0833 | Average of the hour | 2020-09-18 15:00 | 15:00 | 23.1083 | 37.1392 | 438.0833 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.3208 | 39.195 | 477.9167 | Average of the hour | 2020-09-18 15:00 | 15:00 | 22.3208 | 39.195 | 477.9167 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.0217 | 34.735 | 460.9167 | Average of the hour | 2020-09-18 15:00 | 15:00 | 22.0217 | 34.735 | 460.9167 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.1233 | 25.3888 | 423.25 | Average of the hour | 2020-09-18 15:00 | 15:00 | 23.1233 | 25.3888 | 423.25 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.0483 | 32.22 | 427.1667 | Average of the hour | 2020-09-18 15:00 | 15:00 | 22.0483 | 32.22 | 427.1667 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.6753 | 30.2193 | 523.7127 | Average of the hour | 2020-09-18 15:00 | 15:00 | 20.6753 | 30.2193 | 523.7127 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.6104 | 25.8235 | 298.7005 | Average of the hour | 2020-09-18 15:00 | 15:00 | 22.6104 | 25.8235 | 298.7005 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.5002 | 30.0614 | 364.7703 | Average of the hour | 2020-09-18 15:00 | 15:00 | 22.5002 | 30.0614 | 364.7703 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.595 | 44.5613 | 660.5 | Average of the hour | 2020-09-18 15:00 | 15:00 | 21.595 | 44.5613 | 660.5 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.1975 | 45.0525 | 435.9167 | Average of the hour | 2020-09-18 15:00 | 15:00 | 21.1975 | 45.0525 | 435.9167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.4283 | 49.5063 | 429.5833 | Average of the hour | 2020-09-18 15:00 | 15:00 | 21.4283 | 49.5063 | 429.5833 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.5083 | 26.0417 | 496.0417 | Average of the hour | 2020-09-18 15:00 | 15:00 | 21.5083 | 26.0417 | 496.0417 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.05 | 28.8092 | 437.375 | Average of the hour | 2020-09-18 15:00 | 15:00 | 22.05 | 28.8092 | 437.375 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.75 |  |  | Average of the hour | 2020-09-18 15:00 | 15:00 | 22.75 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.4 |  |  | Average of the hour | 2020-09-18 15:00 | 15:00 | 20.4 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.7334 |  | 496.8167 | Average of the hour | 2020-09-18 15:00 | 15:00 | 20.7334 |  | 496.8167 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 19.777 |  | 379.6667 | Average of the hour | 2020-09-18 15:00 | 15:00 | 19.777 |  | 379.6667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.5541 | 20.0998 | 435.4629 | Average of the hour | 2020-09-18 15:00 | 15:00 | 21.5541 | 20.0998 | 435.4629 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 35.4636 | 692.858 | Average of the hour | 2020-09-18 15:00 | 15:00 |  | 35.4636 | 692.858 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.1476 | 23.8487 |  | Average of the hour | 2020-09-18 15:00 | 15:00 | 21.1476 | 23.8487 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 15:00
2020-09-18 | 16:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 18.6417 | 28.9583 | 413.0583 | Average of the hour | 2020-09-18 16:00 | 16:00 | 18.6417 | 28.9583 | 413.0583 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.0917 | 31.7917 | 531.125 | Average of the hour | 2020-09-18 16:00 | 16:00 | 20.0917 | 31.7917 | 531.125 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.1517 | 36.3917 | 484.5833 | Average of the hour | 2020-09-18 16:00 | 16:00 | 21.1517 | 36.3917 | 484.5833 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.0017 | 35.4967 | 422.5 | Average of the hour | 2020-09-18 16:00 | 16:00 | 23.0017 | 35.4967 | 422.5 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.3742 | 37.4542 | 465.8333 | Average of the hour | 2020-09-18 16:00 | 16:00 | 22.3742 | 37.4542 | 465.8333 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.07 | 33.4225 | 457.5833 | Average of the hour | 2020-09-18 16:00 | 16:00 | 22.07 | 33.4225 | 457.5833 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.16 | 24.04 | 422.3333 | Average of the hour | 2020-09-18 16:00 | 16:00 | 23.16 | 24.04 | 422.3333 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.0567 | 30.8108 | 422 | Average of the hour | 2020-09-18 16:00 | 16:00 | 22.0567 | 30.8108 | 422 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.6753 | 28.8224 | 521.7286 | Average of the hour | 2020-09-18 16:00 | 16:00 | 20.6753 | 28.8224 | 521.7286 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.652 | 24.6822 | 295.5061 | Average of the hour | 2020-09-18 16:00 | 16:00 | 22.652 | 24.6822 | 295.5061 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.3956 | 29.7346 | 362.6255 | Average of the hour | 2020-09-18 16:00 | 16:00 | 22.3956 | 29.7346 | 362.6255 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.7083 | 44.7583 | 651.1667 | Average of the hour | 2020-09-18 16:00 | 16:00 | 21.7083 | 44.7583 | 651.1667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.3058 | 44.1417 | 427.0833 | Average of the hour | 2020-09-18 16:00 | 16:00 | 21.3058 | 44.1417 | 427.0833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.54 | 49.2817 | 422.1667 | Average of the hour | 2020-09-18 16:00 | 16:00 | 21.54 | 49.2817 | 422.1667 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.5 | 24.6667 | 468.1333 | Average of the hour | 2020-09-18 16:00 | 16:00 | 21.5 | 24.6667 | 468.1333 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.9 | 27.3458 | 432.8917 | Average of the hour | 2020-09-18 16:00 | 16:00 | 21.9 | 27.3458 | 432.8917 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.9 |  |  | Average of the hour | 2020-09-18 16:00 | 16:00 | 22.9 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.4 |  |  | Average of the hour | 2020-09-18 16:00 | 16:00 | 20.4 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 21.108 |  | 469.1667 | Average of the hour | 2020-09-18 16:00 | 16:00 | 21.108 |  | 469.1667 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 20.292 |  | 380.1667 | Average of the hour | 2020-09-18 16:00 | 16:00 | 20.292 |  | 380.1667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-18 16:00 | 16:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-18 16:00 | 16:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.5642 | 19.7545 | 425.4233 | Average of the hour | 2020-09-18 16:00 | 16:00 | 21.5642 | 19.7545 | 425.4233 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 34.9638 | 692.6763 | Average of the hour | 2020-09-18 16:00 | 16:00 |  | 34.9638 | 692.6763 |  | low | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.226 | 23.2444 |  | Average of the hour | 2020-09-18 16:00 | 16:00 | 21.226 | 23.2444 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 16:00
2020-09-18 | 16:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 16:00 | 16:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 16:00
2020-09-18 | 17:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 18.65 | 27.75 | 412.7167 | Average of the hour | 2020-09-18 17:00 | 17:00 | 18.65 | 27.75 | 412.7167 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.1417 | 30.7917 | 526.6667 | Average of the hour | 2020-09-18 17:00 | 17:00 | 20.1417 | 30.7917 | 526.6667 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.0717 | 35.3417 | 432.8333 | Average of the hour | 2020-09-18 17:00 | 17:00 | 21.0717 | 35.3417 | 432.8333 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.03 | 34.9408 | 413.75 | Average of the hour | 2020-09-18 17:00 | 17:00 | 23.03 | 34.9408 | 413.75 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.285 | 35.9608 | 451.4167 | Average of the hour | 2020-09-18 17:00 | 17:00 | 22.285 | 35.9608 | 451.4167 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.0367 | 32.86 | 457.5833 | Average of the hour | 2020-09-18 17:00 | 17:00 | 22.0367 | 32.86 | 457.5833 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.155 | 24.2183 | 418.3333 | Average of the hour | 2020-09-18 17:00 | 17:00 | 23.155 | 24.2183 | 418.3333 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.0525 | 30.0675 | 416.5 | Average of the hour | 2020-09-18 17:00 | 17:00 | 22.0525 | 30.0675 | 416.5 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.6753 | 27.97 | 515.3185 | Average of the hour | 2020-09-18 17:00 | 17:00 | 20.6753 | 27.97 | 515.3185 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.7187 | 23.9532 | 291.8739 | Average of the hour | 2020-09-18 17:00 | 17:00 | 22.7187 | 23.9532 | 291.8739 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.2952 | 30.4284 | 360.4544 | Average of the hour | 2020-09-18 17:00 | 17:00 | 22.2952 | 30.4284 | 360.4544 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.775 | 44.5479 | 623.6667 | Average of the hour | 2020-09-18 17:00 | 17:00 | 21.775 | 44.5479 | 623.6667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.38 | 44.4317 | 415.4167 | Average of the hour | 2020-09-18 17:00 | 17:00 | 21.38 | 44.4317 | 415.4167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.7208 | 49.3179 | 419.8333 | Average of the hour | 2020-09-18 17:00 | 17:00 | 21.7208 | 49.3179 | 419.8333 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.5 | 24.0833 | 451.3167 | Average of the hour | 2020-09-18 17:00 | 17:00 | 21.5 | 24.0833 | 451.3167 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.8667 | 27.3283 | 428.8667 | Average of the hour | 2020-09-18 17:00 | 17:00 | 21.8667 | 27.3283 | 428.8667 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.7083 |  |  | Average of the hour | 2020-09-18 17:00 | 17:00 | 22.7083 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.375 |  |  | Average of the hour | 2020-09-18 17:00 | 17:00 | 20.375 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.6644 |  | 452.6667 | Average of the hour | 2020-09-18 17:00 | 17:00 | 20.6644 |  | 452.6667 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 20.2006 |  | 379.75 | Average of the hour | 2020-09-18 17:00 | 17:00 | 20.2006 |  | 379.75 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-18 17:00 | 17:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-18 17:00 | 17:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.5237 | 19.4608 | 419.5073 | Average of the hour | 2020-09-18 17:00 | 17:00 | 21.5237 | 19.4608 | 419.5073 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 34.8229 | 691.6954 | Average of the hour | 2020-09-18 17:00 | 17:00 |  | 34.8229 | 691.6954 |  | low | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.1319 | 23.1867 |  | Average of the hour | 2020-09-18 17:00 | 17:00 | 21.1319 | 23.1867 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 17:00
2020-09-18 | 17:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 17:00 | 17:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 17:00
2020-09-18 | 18:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 18.3667 | 27.5833 | 412.7833 | Average of the hour | 2020-09-18 18:00 | 18:00 | 18.3667 | 27.5833 | 412.7833 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 19.9083 | 30.5 | 518.1667 | Average of the hour | 2020-09-18 18:00 | 18:00 | 19.9083 | 30.5 | 518.1667 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.0858 | 34.6408 | 400.8333 | Average of the hour | 2020-09-18 18:00 | 18:00 | 21.0858 | 34.6408 | 400.8333 |  | low | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.0508 | 34.5925 | 399.5 | Average of the hour | 2020-09-18 18:00 | 18:00 | 23.0508 | 34.5925 | 399.5 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.255 | 35.1683 | 437.3333 | Average of the hour | 2020-09-18 18:00 | 18:00 | 22.255 | 35.1683 | 437.3333 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.1517 | 32.5283 | 456.5833 | Average of the hour | 2020-09-18 18:00 | 18:00 | 22.1517 | 32.5283 | 456.5833 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.3908 | 29.6479 | 413.75 | Average of the hour | 2020-09-18 18:00 | 18:00 | 23.3908 | 29.6479 | 413.75 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.1958 | 30.5921 | 412.1667 | Average of the hour | 2020-09-18 18:00 | 18:00 | 22.1958 | 30.5921 | 412.1667 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.1019 | 28.1072 | 498.9177 | Average of the hour | 2020-09-18 18:00 | 18:00 | 21.1019 | 28.1072 | 498.9177 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.9656 | 23.1148 | 292.3821 | Average of the hour | 2020-09-18 18:00 | 18:00 | 23.9656 | 23.1148 | 292.3821 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.8247 | 23.9451 | 357.745 | Average of the hour | 2020-09-18 18:00 | 18:00 | 22.8247 | 23.9451 | 357.745 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.8192 | 44.7754 | 609.8333 | Average of the hour | 2020-09-18 18:00 | 18:00 | 21.8192 | 44.7754 | 609.8333 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.405 | 45.2954 | 406.8333 | Average of the hour | 2020-09-18 18:00 | 18:00 | 21.405 | 45.2954 | 406.8333 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.765 | 50.1792 | 415.9167 | Average of the hour | 2020-09-18 18:00 | 18:00 | 21.765 | 50.1792 | 415.9167 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.5 | 24 | 441.4417 | Average of the hour | 2020-09-18 18:00 | 18:00 | 21.5 | 24 | 441.4417 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.8 | 27.2617 | 421.55 | Average of the hour | 2020-09-18 18:00 | 18:00 | 21.8 | 27.2617 | 421.55 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22 |  |  | Average of the hour | 2020-09-18 18:00 | 18:00 | 22 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.3 |  |  | Average of the hour | 2020-09-18 18:00 | 18:00 | 20.3 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 19.642 |  | 442.2417 | Average of the hour | 2020-09-18 18:00 | 18:00 | 19.642 |  | 442.2417 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 19.5934 |  | 379.25 | Average of the hour | 2020-09-18 18:00 | 18:00 | 19.5934 |  | 379.25 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-18 18:00 | 18:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-18 18:00 | 18:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.6439 | 19.9889 | 435.2788 | Average of the hour | 2020-09-18 18:00 | 18:00 | 21.6439 | 19.9889 | 435.2788 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 34.9532 | 690.1839 | Average of the hour | 2020-09-18 18:00 | 18:00 |  | 34.9532 | 690.1839 |  | low | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.0841 | 23.2745 |  | Average of the hour | 2020-09-18 18:00 | 18:00 | 21.0841 | 23.2745 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 18:00
2020-09-18 | 18:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 18:00 | 18:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 18:00
2020-09-18 | 19:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 17.775 | 27.25 | 421.375 | Average of the hour | 2020-09-18 19:00 | 19:00 | 17.775 | 27.25 | 421.375 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 18.075 | 28.125 | 529.5 | Average of the hour | 2020-09-18 19:00 | 19:00 | 18.075 | 28.125 | 529.5 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.0758 | 34.1992 | 388.9167 | Average of the hour | 2020-09-18 19:00 | 19:00 | 21.0758 | 34.1992 | 388.9167 |  | low | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.045 | 34.3058 | 393.25 | Average of the hour | 2020-09-18 19:00 | 19:00 | 23.045 | 34.3058 | 393.25 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 19.9958 | 33.7083 | 434 | Average of the hour | 2020-09-18 19:00 | 19:00 | 19.9958 | 33.7083 | 434 |  | low | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.1892 | 31.4017 | 455.6667 | Average of the hour | 2020-09-18 19:00 | 19:00 | 22.1892 | 31.4017 | 455.6667 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.55 | 33.67 | 414.5833 | Average of the hour | 2020-09-18 19:00 | 19:00 | 23.55 | 33.67 | 414.5833 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.5075 | 31.7563 | 412 | Average of the hour | 2020-09-18 19:00 | 19:00 | 22.5075 | 31.7563 | 412 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.8028 | 28.2685 | 492.7812 | Average of the hour | 2020-09-18 19:00 | 19:00 | 21.8028 | 28.2685 | 492.7812 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.1475 | 23.1223 | 296.3633 | Average of the hour | 2020-09-18 19:00 | 19:00 | 25.1475 | 23.1223 | 296.3633 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.5552 | 21.967 | 367.8598 | Average of the hour | 2020-09-18 19:00 | 19:00 | 23.5552 | 21.967 | 367.8598 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.7925 | 45.7163 | 613.4167 | Average of the hour | 2020-09-18 19:00 | 19:00 | 21.7925 | 45.7163 | 613.4167 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.3642 | 45.6 | 406.4167 | Average of the hour | 2020-09-18 19:00 | 19:00 | 21.3642 | 45.6 | 406.4167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.7108 | 49.7025 | 410.5833 | Average of the hour | 2020-09-18 19:00 | 19:00 | 21.7108 | 49.7025 | 410.5833 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.4333 | 24.2083 | 432.975 | Average of the hour | 2020-09-18 19:00 | 19:00 | 21.4333 | 24.2083 | 432.975 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.8 | 27.4008 | 419.0583 | Average of the hour | 2020-09-18 19:00 | 19:00 | 21.8 | 27.4008 | 419.0583 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.6667 |  |  | Average of the hour | 2020-09-18 19:00 | 19:00 | 22.6667 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.2583 |  |  | Average of the hour | 2020-09-18 19:00 | 19:00 | 20.2583 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 18.9694 |  | 432.325 | Average of the hour | 2020-09-18 19:00 | 19:00 | 18.9694 |  | 432.325 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 18.7083 |  | 379.8333 | Average of the hour | 2020-09-18 19:00 | 19:00 | 18.7083 |  | 379.8333 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-18 19:00 | 19:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-18 19:00 | 19:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.7997 | 20.753 | 434.8767 | Average of the hour | 2020-09-18 19:00 | 19:00 | 21.7997 | 20.753 | 434.8767 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 35.4597 | 689.383 | Average of the hour | 2020-09-18 19:00 | 19:00 |  | 35.4597 | 689.383 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.0568 | 23.6135 |  | Average of the hour | 2020-09-18 19:00 | 19:00 | 21.0568 | 23.6135 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 19:00
2020-09-18 | 19:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 19:00 | 19:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 19:00
2020-09-18 | 20:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [8 empty] | Average of the hour | 2020-09-18 20:00 | 20:00 | [5 empty] | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [8 empty] | Average of the hour | 2020-09-18 20:00 | 20:00 | [5 empty] | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.1367 | 33.6217 | 389.5 | Average of the hour | 2020-09-18 20:00 | 20:00 | 21.1367 | 33.6217 | 389.5 |  | low | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.1742 | 30.8075 | 383.6667 | Average of the hour | 2020-09-18 20:00 | 20:00 | 22.1742 | 30.8075 | 383.6667 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 18.6908 | 35.2267 | 428.5 | Average of the hour | 2020-09-18 20:00 | 20:00 | 18.6908 | 35.2267 | 428.5 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.1483 | 30.9208 | 455 | Average of the hour | 2020-09-18 20:00 | 20:00 | 22.1483 | 30.9208 | 455 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.685 | 30.6525 | 421.6667 | Average of the hour | 2020-09-18 20:00 | 20:00 | 23.685 | 30.6525 | 421.6667 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.7283 | 32.9329 | 414 | Average of the hour | 2020-09-18 20:00 | 20:00 | 22.7283 | 32.9329 | 414 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.0474 | 28.5709 | 491.1452 | Average of the hour | 2020-09-18 20:00 | 20:00 | 22.0474 | 28.5709 | 491.1452 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.424 | 22.7854 | 297.0041 | Average of the hour | 2020-09-18 20:00 | 20:00 | 25.424 | 22.7854 | 297.0041 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.7588 | 20.2283 | 369.041 | Average of the hour | 2020-09-18 20:00 | 20:00 | 22.7588 | 20.2283 | 369.041 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.7675 | 45.6233 | 613.5833 | Average of the hour | 2020-09-18 20:00 | 20:00 | 21.7675 | 45.6233 | 613.5833 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.2725 | 45.5221 | 407.5833 | Average of the hour | 2020-09-18 20:00 | 20:00 | 21.2725 | 45.5221 | 407.5833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.6725 | 49.35 | 407.9167 | Average of the hour | 2020-09-18 20:00 | 20:00 | 21.6725 | 49.35 | 407.9167 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.2583 | 24.875 | 428.625 | Average of the hour | 2020-09-18 20:00 | 20:00 | 21.2583 | 24.875 | 428.625 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.7667 | 28.055 | 419.475 | Average of the hour | 2020-09-18 20:00 | 20:00 | 21.7667 | 28.055 | 419.475 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 17.2667 |  |  | Average of the hour | 2020-09-18 20:00 | 20:00 | 17.2667 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 15.4917 |  |  | Average of the hour | 2020-09-18 20:00 | 20:00 | 15.4917 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 15.307 |  | 428.7083 | Average of the hour | 2020-09-18 20:00 | 20:00 | 15.307 |  | 428.7083 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 15.5238 |  | 380.25 | Average of the hour | 2020-09-18 20:00 | 20:00 | 15.5238 |  | 380.25 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-18 20:00 | 20:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-18 20:00 | 20:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.8811 | 21.4529 | 433.9242 | Average of the hour | 2020-09-18 20:00 | 20:00 | 21.8811 | 21.4529 | 433.9242 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 35.9923 | 689.0723 | Average of the hour | 2020-09-18 20:00 | 20:00 |  | 35.9923 | 689.0723 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.013 | 24.2233 |  | Average of the hour | 2020-09-18 20:00 | 20:00 | 21.013 | 24.2233 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 20:00
2020-09-18 | 20:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 20:00 | 20:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 20:00
2020-09-18 | 21:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [8 empty] | Average of the hour | 2020-09-18 21:00 | 21:00 | [5 empty] | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [8 empty] | Average of the hour | 2020-09-18 21:00 | 21:00 | [5 empty] | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.2317 | 31.0342 | 390.25 | Average of the hour | 2020-09-18 21:00 | 21:00 | 21.2317 | 31.0342 | 390.25 |  | low | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 21.6992 | 27.6 | 382.25 | Average of the hour | 2020-09-18 21:00 | 21:00 | 21.6992 | 27.6 | 382.25 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 17.9792 | 36.2708 | 430.3333 | Average of the hour | 2020-09-18 21:00 | 21:00 | 17.9792 | 36.2708 | 430.3333 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.1483 | 30.7158 | 456.25 | Average of the hour | 2020-09-18 21:00 | 21:00 | 22.1483 | 30.7158 | 456.25 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.8408 | 29.1921 | 421.0833 | Average of the hour | 2020-09-18 21:00 | 21:00 | 23.8408 | 29.1921 | 421.0833 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.845 | 33.6958 | 414.75 | Average of the hour | 2020-09-18 21:00 | 21:00 | 22.845 | 33.6958 | 414.75 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.164 | 29.0418 | 491.1652 | Average of the hour | 2020-09-18 21:00 | 21:00 | 22.164 | 29.0418 | 491.1652 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.5668 | 21.7373 | 298.1346 | Average of the hour | 2020-09-18 21:00 | 21:00 | 25.5668 | 21.7373 | 298.1346 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.6672 | 20.6392 | 368.354 | Average of the hour | 2020-09-18 21:00 | 21:00 | 22.6672 | 20.6392 | 368.354 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.7208 | 45.8525 | 615.5 | Average of the hour | 2020-09-18 21:00 | 21:00 | 21.7208 | 45.8525 | 615.5 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.285 | 45.355 | 405.9167 | Average of the hour | 2020-09-18 21:00 | 21:00 | 21.285 | 45.355 | 405.9167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.6225 | 49.5012 | 411.4167 | Average of the hour | 2020-09-18 21:00 | 21:00 | 21.6225 | 49.5012 | 411.4167 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 16.9917 | 27.125 | 445.875 | Average of the hour | 2020-09-18 21:00 | 21:00 | 16.9917 | 27.125 | 445.875 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 20.3333 | 25.7242 | 416.1917 | Average of the hour | 2020-09-18 21:00 | 21:00 | 20.3333 | 25.7242 | 416.1917 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 10.1917 |  |  | Average of the hour | 2020-09-18 21:00 | 21:00 | 10.1917 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 12.375 |  |  | Average of the hour | 2020-09-18 21:00 | 21:00 | 12.375 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 11.2336 |  | 444.6 | Average of the hour | 2020-09-18 21:00 | 21:00 | 11.2336 |  | 444.6 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 11.5066 |  | 379.4167 | Average of the hour | 2020-09-18 21:00 | 21:00 | 11.5066 |  | 379.4167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-18 21:00 | 21:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-18 21:00 | 21:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.9382 | 22.1843 | 441.3022 | Average of the hour | 2020-09-18 21:00 | 21:00 | 21.9382 | 22.1843 | 441.3022 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 36.2742 | 689.0049 | Average of the hour | 2020-09-18 21:00 | 21:00 |  | 36.2742 | 689.0049 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.8714 | 24.0801 |  | Average of the hour | 2020-09-18 21:00 | 21:00 | 20.8714 | 24.0801 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 21:00
2020-09-18 | 21:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 21:00 | 21:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 21:00
2020-09-18 | 22:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [8 empty] | Average of the hour | 2020-09-18 22:00 | 22:00 | [5 empty] | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [8 empty] | Average of the hour | 2020-09-18 22:00 | 22:00 | [5 empty] | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 17.0617 | 32.5942 | 394.4167 | Average of the hour | 2020-09-18 22:00 | 22:00 | 17.0617 | 32.5942 | 394.4167 |  | low | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 20.8183 | 27.8608 | 385.0833 | Average of the hour | 2020-09-18 22:00 | 22:00 | 20.8183 | 27.8608 | 385.0833 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 16.9975 | 38.1358 | 431.75 | Average of the hour | 2020-09-18 22:00 | 22:00 | 16.9975 | 38.1358 | 431.75 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.5217 | 31.2658 | 458 | Average of the hour | 2020-09-18 22:00 | 22:00 | 22.5217 | 31.2658 | 458 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.8842 | 28.6646 | 421.1667 | Average of the hour | 2020-09-18 22:00 | 22:00 | 23.8842 | 28.6646 | 421.1667 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.8708 | 34.2742 | 415.4167 | Average of the hour | 2020-09-18 22:00 | 22:00 | 22.8708 | 34.2742 | 415.4167 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.2227 | 29.4861 | 491.5533 | Average of the hour | 2020-09-18 22:00 | 22:00 | 22.2227 | 29.4861 | 491.5533 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.574 | 20.6938 | 297.4199 | Average of the hour | 2020-09-18 22:00 | 22:00 | 25.574 | 20.6938 | 297.4199 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.2604 | 22.2076 | 369.7609 | Average of the hour | 2020-09-18 22:00 | 22:00 | 22.2604 | 22.2076 | 369.7609 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.6333 | 45.7808 | 618.4167 | Average of the hour | 2020-09-18 22:00 | 22:00 | 21.6333 | 45.7808 | 618.4167 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.1225 | 45.3154 | 412.6667 | Average of the hour | 2020-09-18 22:00 | 22:00 | 21.1225 | 45.3154 | 412.6667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.7317 | 49.5063 | 410.0833 | Average of the hour | 2020-09-18 22:00 | 22:00 | 21.7317 | 49.5063 | 410.0833 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 13.7333 | 33.0417 | 443.7417 | Average of the hour | 2020-09-18 22:00 | 22:00 | 13.7333 | 33.0417 | 443.7417 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 18.55 | 26.9542 | 417.5167 | Average of the hour | 2020-09-18 22:00 | 22:00 | 18.55 | 26.9542 | 417.5167 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 7.6167 |  |  | Average of the hour | 2020-09-18 22:00 | 22:00 | 7.6167 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 11.2417 |  |  | Average of the hour | 2020-09-18 22:00 | 22:00 | 11.2417 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 9.3823 |  | 443.5 | Average of the hour | 2020-09-18 22:00 | 22:00 | 9.3823 |  | 443.5 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 9.5027 |  | 379.5 | Average of the hour | 2020-09-18 22:00 | 22:00 | 9.5027 |  | 379.5 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-18 22:00 | 22:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-18 22:00 | 22:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.9703 | 22.8343 | 446.032 | Average of the hour | 2020-09-18 22:00 | 22:00 | 21.9703 | 22.8343 | 446.032 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 36.495 | 688.9239 | Average of the hour | 2020-09-18 22:00 | 22:00 |  | 36.495 | 688.9239 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.682 | 24.0975 |  | Average of the hour | 2020-09-18 22:00 | 22:00 | 20.682 | 24.0975 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 22:00
2020-09-18 | 22:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 22:00 | 22:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 22:00
2020-09-18 | 23:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [8 empty] | Average of the hour | 2020-09-18 23:00 | 23:00 | [5 empty] | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [8 empty] | Average of the hour | 2020-09-18 23:00 | 23:00 | [5 empty] | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 15.5967 | 35.8583 | 398.6667 | Average of the hour | 2020-09-18 23:00 | 23:00 | 15.5967 | 35.8583 | 398.6667 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 20.2825 | 29.0242 | 385 | Average of the hour | 2020-09-18 23:00 | 23:00 | 20.2825 | 29.0242 | 385 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 16.4608 | 40.01 | 433.9167 | Average of the hour | 2020-09-18 23:00 | 23:00 | 16.4608 | 40.01 | 433.9167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.8992 | 32.8183 | 457.0833 | Average of the hour | 2020-09-18 23:00 | 23:00 | 22.8992 | 32.8183 | 457.0833 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.9433 | 28.2237 | 421.25 | Average of the hour | 2020-09-18 23:00 | 23:00 | 23.9433 | 28.2237 | 421.25 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.6775 | 34.9563 | 413.75 | Average of the hour | 2020-09-18 23:00 | 23:00 | 22.6775 | 34.9563 | 413.75 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.2227 | 29.9364 | 491.7893 | Average of the hour | 2020-09-18 23:00 | 23:00 | 22.2227 | 29.9364 | 491.7893 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.403 | 20.1559 | 298.6216 | Average of the hour | 2020-09-18 23:00 | 23:00 | 25.403 | 20.1559 | 298.6216 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 21.5979 | 22.6673 | 369.0881 | Average of the hour | 2020-09-18 23:00 | 23:00 | 21.5979 | 22.6673 | 369.0881 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.5625 | 45.5921 | 620.3333 | Average of the hour | 2020-09-18 23:00 | 23:00 | 21.5625 | 45.5921 | 620.3333 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.0467 | 45.4642 | 412.5833 | Average of the hour | 2020-09-18 23:00 | 23:00 | 21.0467 | 45.4642 | 412.5833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.6 | 49.3704 | 411.5 | Average of the hour | 2020-09-18 23:00 | 23:00 | 21.6 | 49.3704 | 411.5 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 12.5333 | 36 | 437.5583 | Average of the hour | 2020-09-18 23:00 | 23:00 | 12.5333 | 36 | 437.5583 |  | caution | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 17.5583 | 28.2658 | 417.8083 | Average of the hour | 2020-09-18 23:00 | 23:00 | 17.5583 | 28.2658 | 417.8083 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 6.875 |  |  | Average of the hour | 2020-09-18 23:00 | 23:00 | 6.875 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 10.775 |  |  | Average of the hour | 2020-09-18 23:00 | 23:00 | 10.775 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 8.6143 |  | 437.7833 | Average of the hour | 2020-09-18 23:00 | 23:00 | 8.6143 |  | 437.7833 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 8.599 |  | 379.1667 | Average of the hour | 2020-09-18 23:00 | 23:00 | 8.599 |  | 379.1667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-18 23:00 | 23:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-18 23:00 | 23:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.9976 | 23.4183 | 452.6254 | Average of the hour | 2020-09-18 23:00 | 23:00 | 21.9976 | 23.4183 | 452.6254 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 36.9197 | 688.8563 | Average of the hour | 2020-09-18 23:00 | 23:00 |  | 36.9197 | 688.8563 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.56 | 24.7046 |  | Average of the hour | 2020-09-18 23:00 | 23:00 | 20.56 | 24.7046 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-18-2020 23:00
2020-09-18 | 23:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-18 23:00 | 23:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-18-2020 23:00
2020-09-19 | 0:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 11.7 | 44.875 | 438.075 | Average of the hour | 2020-09-19 | 0:00 | 11.7 | 44.875 | 438.075 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 7.425 | 33.375 | 403.375 | Average of the hour | 2020-09-19 | 0:00 | 7.425 | 33.375 | 403.375 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 15.1308 | 36.9917 | 401.3333 | Average of the hour | 2020-09-19 | 0:00 | 15.1308 | 36.9917 | 401.3333 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 19.8233 | 29.8817 | 389 | Average of the hour | 2020-09-19 | 0:00 | 19.8233 | 29.8817 | 389 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 15.965 | 41.3733 | 435.25 | Average of the hour | 2020-09-19 | 0:00 | 15.965 | 41.3733 | 435.25 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 23.1108 | 33.6692 | 457.0833 | Average of the hour | 2020-09-19 | 0:00 | 23.1108 | 33.6692 | 457.0833 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.9633 | 28.0621 | 420.3333 | Average of the hour | 2020-09-19 | 0:00 | 23.9633 | 28.0621 | 420.3333 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.5733 | 35.4342 | 414.4167 | Average of the hour | 2020-09-19 | 0:00 | 22.5733 | 35.4342 | 414.4167 |  | caution | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.2987 | 30.3572 | 491.8702 | Average of the hour | 2020-09-19 | 0:00 | 22.2987 | 30.3572 | 491.8702 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.5286 | 18.9187 | 301.5146 | Average of the hour | 2020-09-19 | 0:00 | 25.5286 | 18.9187 | 301.5146 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.2112 | 21.2092 | 373.9281 | Average of the hour | 2020-09-19 | 0:00 | 22.2112 | 21.2092 | 373.9281 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.7 | 44.9038 | 620.75 | Average of the hour | 2020-09-19 | 0:00 | 21.7 | 44.9038 | 620.75 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.0942 | 45.25 | 413.25 | Average of the hour | 2020-09-19 | 0:00 | 21.0942 | 45.25 | 413.25 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.6258 | 49.195 | 413.9167 | Average of the hour | 2020-09-19 | 0:00 | 21.6258 | 49.195 | 413.9167 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 11.7917 | 38.6667 | 436.275 | Average of the hour | 2020-09-19 | 0:00 | 11.7917 | 38.6667 | 436.275 |  | caution | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 17.1417 | 29.2158 | 414.9833 | Average of the hour | 2020-09-19 | 0:00 | 17.1417 | 29.2158 | 414.9833 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 6.3667 |  |  | Average of the hour | 2020-09-19 | 0:00 | 6.3667 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 10.425 |  |  | Average of the hour | 2020-09-19 | 0:00 | 10.425 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 8.1198 |  | 436.2167 | Average of the hour | 2020-09-19 | 0:00 | 8.1198 |  | 436.2167 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 8.1897 |  | 379.1667 | Average of the hour | 2020-09-19 | 0:00 | 8.1897 |  | 379.1667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 33.7 |  | Average of the hour | 2020-09-19 | 0:00 |  | 33.7 |  |  | low | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 31.65 |  | Average of the hour | 2020-09-19 | 0:00 |  | 31.65 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.9957 | 23.7172 | 451.8558 | Average of the hour | 2020-09-19 | 0:00 | 21.9957 | 23.7172 | 451.8558 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 37.0853 | 688.414 | Average of the hour | 2020-09-19 | 0:00 |  | 37.0853 | 688.414 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.8073 | 24.9998 |  | Average of the hour | 2020-09-19 | 0:00 | 20.8073 | 24.9998 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 00:00
2020-09-19 | 0:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 | 0:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 00:00
2020-09-19 | 1:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 11.0833 | 45.0417 | 434.475 | Average of the hour | 2020-09-19 01:00 | 1:00 | 11.0833 | 45.0417 | 434.475 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 9.1833 | 45.875 | 546.625 | Average of the hour | 2020-09-19 01:00 | 1:00 | 9.1833 | 45.875 | 546.625 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 14.7283 | 38.3683 | 402.75 | Average of the hour | 2020-09-19 01:00 | 1:00 | 14.7283 | 38.3683 | 402.75 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 19.4342 | 30.8017 | 393.8333 | Average of the hour | 2020-09-19 01:00 | 1:00 | 19.4342 | 30.8017 | 393.8333 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 15.5317 | 42.8433 | 440.6667 | Average of the hour | 2020-09-19 01:00 | 1:00 | 15.5317 | 42.8433 | 440.6667 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 23.1717 | 34.15 | 457.0833 | Average of the hour | 2020-09-19 01:00 | 1:00 | 23.1717 | 34.15 | 457.0833 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.9583 | 28.0267 | 422.0833 | Average of the hour | 2020-09-19 01:00 | 1:00 | 23.9583 | 28.0267 | 422.0833 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.56 | 35.8883 | 414.5 | Average of the hour | 2020-09-19 01:00 | 1:00 | 22.56 | 35.8883 | 414.5 |  | caution | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.324 | 30.7114 | 491.7131 | Average of the hour | 2020-09-19 01:00 | 1:00 | 22.324 | 30.7114 | 491.7131 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.6262 | 17.8635 | 303.7049 | Average of the hour | 2020-09-19 01:00 | 1:00 | 25.6262 | 17.8635 | 303.7049 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.3575 | 19.6588 | 376.8901 | Average of the hour | 2020-09-19 01:00 | 1:00 | 22.3575 | 19.6588 | 376.8901 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.7867 | 44.4271 | 618.5 | Average of the hour | 2020-09-19 01:00 | 1:00 | 21.7867 | 44.4271 | 618.5 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.1975 | 44.47 | 411.1667 | Average of the hour | 2020-09-19 01:00 | 1:00 | 21.1975 | 44.47 | 411.1667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.7367 | 49.2163 | 418.3333 | Average of the hour | 2020-09-19 01:00 | 1:00 | 21.7367 | 49.2163 | 418.3333 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 11.3167 | 40.5833 | 435.65 | Average of the hour | 2020-09-19 01:00 | 1:00 | 11.3167 | 40.5833 | 435.65 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 16.9083 | 29.8675 | 417.1 | Average of the hour | 2020-09-19 01:00 | 1:00 | 16.9083 | 29.8675 | 417.1 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 6.0833 |  |  | Average of the hour | 2020-09-19 01:00 | 1:00 | 6.0833 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 10.175 |  |  | Average of the hour | 2020-09-19 01:00 | 1:00 | 10.175 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 7.7888 |  | 435.5167 | Average of the hour | 2020-09-19 01:00 | 1:00 | 7.7888 |  | 435.5167 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 7.9426 |  | 379.1667 | Average of the hour | 2020-09-19 01:00 | 1:00 | 7.9426 |  | 379.1667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 34.1 |  | Average of the hour | 2020-09-19 01:00 | 1:00 |  | 34.1 |  |  | low | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 32.0333 |  | Average of the hour | 2020-09-19 01:00 | 1:00 |  | 32.0333 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.9839 | 23.8226 | 445.0265 | Average of the hour | 2020-09-19 01:00 | 1:00 | 21.9839 | 23.8226 | 445.0265 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 37.1135 | 688.0601 | Average of the hour | 2020-09-19 01:00 | 1:00 |  | 37.1135 | 688.0601 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9698 | 25.2887 |  | Average of the hour | 2020-09-19 01:00 | 1:00 | 20.9698 | 25.2887 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 01:00
2020-09-19 | 1:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 01:00 | 1:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 01:00
2020-09-19 | 2:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 10.6333 | 44.5 | 433.9583 | Average of the hour | 2020-09-19 02:00 | 2:00 | 10.6333 | 44.5 | 433.9583 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 9.0667 | 44.375 | 534 | Average of the hour | 2020-09-19 02:00 | 2:00 | 9.0667 | 44.375 | 534 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 14.3692 | 40.5158 | 405.6667 | Average of the hour | 2020-09-19 02:00 | 2:00 | 14.3692 | 40.5158 | 405.6667 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 19.1117 | 32.435 | 394.9167 | Average of the hour | 2020-09-19 02:00 | 2:00 | 19.1117 | 32.435 | 394.9167 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 15.1983 | 45.1517 | 440.1667 | Average of the hour | 2020-09-19 02:00 | 2:00 | 15.1983 | 45.1517 | 440.1667 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 23.1683 | 34.4442 | 457.3333 | Average of the hour | 2020-09-19 02:00 | 2:00 | 23.1683 | 34.4442 | 457.3333 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.0183 | 27.5162 | 420 | Average of the hour | 2020-09-19 02:00 | 2:00 | 24.0183 | 27.5162 | 420 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.56 | 36.15 | 414.3333 | Average of the hour | 2020-09-19 02:00 | 2:00 | 22.56 | 36.15 | 414.3333 |  | caution | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.3993 | 31.0534 | 490.7534 | Average of the hour | 2020-09-19 02:00 | 2:00 | 22.3993 | 31.0534 | 490.7534 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.2836 | 18.6074 | 303.6445 | Average of the hour | 2020-09-19 02:00 | 2:00 | 25.2836 | 18.6074 | 303.6445 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.0018 | 19.3495 | 376.2972 | Average of the hour | 2020-09-19 02:00 | 2:00 | 23.0018 | 19.3495 | 376.2972 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.8033 | 44.4275 | 625.0833 | Average of the hour | 2020-09-19 02:00 | 2:00 | 21.8033 | 44.4275 | 625.0833 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.1958 | 44.1829 | 412.1667 | Average of the hour | 2020-09-19 02:00 | 2:00 | 21.1958 | 44.1829 | 412.1667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.71 | 49.9771 | 414.5 | Average of the hour | 2020-09-19 02:00 | 2:00 | 21.71 | 49.9771 | 414.5 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 10.9083 | 42.5833 | 435.7583 | Average of the hour | 2020-09-19 02:00 | 2:00 | 10.9083 | 42.5833 | 435.7583 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 16.9 | 30.25 | 417.925 | Average of the hour | 2020-09-19 02:00 | 2:00 | 16.9 | 30.25 | 417.925 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 5.825 |  |  | Average of the hour | 2020-09-19 02:00 | 2:00 | 5.825 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 9.8417 |  |  | Average of the hour | 2020-09-19 02:00 | 2:00 | 9.8417 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 7.4638 |  | 434.4667 | Average of the hour | 2020-09-19 02:00 | 2:00 | 7.4638 |  | 434.4667 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 7.7797 |  | 380.9167 | Average of the hour | 2020-09-19 02:00 | 2:00 | 7.7797 |  | 380.9167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 34.3833 |  | Average of the hour | 2020-09-19 02:00 | 2:00 |  | 34.3833 |  |  | low | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 32.3917 |  | Average of the hour | 2020-09-19 02:00 | 2:00 |  | 32.3917 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.0143 | 24.0348 | 442.593 | Average of the hour | 2020-09-19 02:00 | 2:00 | 22.0143 | 24.0348 | 442.593 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 37.3297 | 688.0602 | Average of the hour | 2020-09-19 02:00 | 2:00 |  | 37.3297 | 688.0602 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9407 | 25.3155 |  | Average of the hour | 2020-09-19 02:00 | 2:00 | 20.9407 | 25.3155 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 02:00
2020-09-19 | 2:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 02:00 | 2:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 02:00
2020-09-19 | 3:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 10.4667 | 45.5 | 444.7667 | Average of the hour | 2020-09-19 03:00 | 3:00 | 10.4667 | 45.5 | 444.7667 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 8.3083 | 46.9167 | 551.1667 | Average of the hour | 2020-09-19 03:00 | 3:00 | 8.3083 | 46.9167 | 551.1667 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 14.0867 | 43.0783 | 402.5833 | Average of the hour | 2020-09-19 03:00 | 3:00 | 14.0867 | 43.0783 | 402.5833 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 18.835 | 34.3658 | 395.0833 | Average of the hour | 2020-09-19 03:00 | 3:00 | 18.835 | 34.3658 | 395.0833 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 15.0083 | 47.2867 | 439.75 | Average of the hour | 2020-09-19 03:00 | 3:00 | 15.0083 | 47.2867 | 439.75 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 23.1408 | 34.7308 | 458 | Average of the hour | 2020-09-19 03:00 | 3:00 | 23.1408 | 34.7308 | 458 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.0325 | 27.4854 | 423.6667 | Average of the hour | 2020-09-19 03:00 | 3:00 | 24.0325 | 27.4854 | 423.6667 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.6058 | 36.2783 | 416.1667 | Average of the hour | 2020-09-19 03:00 | 3:00 | 22.6058 | 36.2783 | 416.1667 |  | caution | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.4244 | 31.4531 | 488.7485 | Average of the hour | 2020-09-19 03:00 | 3:00 | 22.4244 | 31.4531 | 488.7485 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.1293 | 19.4832 | 307.0455 | Average of the hour | 2020-09-19 03:00 | 3:00 | 25.1293 | 19.4832 | 307.0455 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.9593 | 19.5371 | 379.8417 | Average of the hour | 2020-09-19 03:00 | 3:00 | 22.9593 | 19.5371 | 379.8417 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.775 | 44.485 | 627.6667 | Average of the hour | 2020-09-19 03:00 | 3:00 | 21.775 | 44.485 | 627.6667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.2217 | 44.3588 | 416.9167 | Average of the hour | 2020-09-19 03:00 | 3:00 | 21.2217 | 44.3588 | 416.9167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.5725 | 50.065 | 422.5 | Average of the hour | 2020-09-19 03:00 | 3:00 | 21.5725 | 50.065 | 422.5 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 10.5083 | 43.7917 | 434.8417 | Average of the hour | 2020-09-19 03:00 | 3:00 | 10.5083 | 43.7917 | 434.8417 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 16.8083 | 30.43 | 417.7833 | Average of the hour | 2020-09-19 03:00 | 3:00 | 16.8083 | 30.43 | 417.7833 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 5.2583 |  |  | Average of the hour | 2020-09-19 03:00 | 3:00 | 5.2583 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 9.6833 |  |  | Average of the hour | 2020-09-19 03:00 | 3:00 | 9.6833 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 7.2393 |  | 435.4083 | Average of the hour | 2020-09-19 03:00 | 3:00 | 7.2393 |  | 435.4083 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 7.5963 |  | 379 | Average of the hour | 2020-09-19 03:00 | 3:00 | 7.5963 |  | 379 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 34.5667 |  | Average of the hour | 2020-09-19 03:00 | 3:00 |  | 34.5667 |  |  | low | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 32.8333 |  | Average of the hour | 2020-09-19 03:00 | 3:00 |  | 32.8333 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.0217 | 24.3198 | 450.0286 | Average of the hour | 2020-09-19 03:00 | 3:00 | 22.0217 | 24.3198 | 450.0286 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 37.5033 | 688.0605 | Average of the hour | 2020-09-19 03:00 | 3:00 |  | 37.5033 | 688.0605 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.8953 | 24.998 |  | Average of the hour | 2020-09-19 03:00 | 3:00 | 20.8953 | 24.998 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 03:00
2020-09-19 | 3:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 03:00 | 3:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 03:00
2020-09-19 | 4:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 10.1417 | 45.2083 | 449.7833 | Average of the hour | 2020-09-19 04:00 | 4:00 | 10.1417 | 45.2083 | 449.7833 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 7.8417 | 46.5 | 563.4167 | Average of the hour | 2020-09-19 04:00 | 4:00 | 7.8417 | 46.5 | 563.4167 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 14.6617 | 41.5258 | 404.75 | Average of the hour | 2020-09-19 04:00 | 4:00 | 14.6617 | 41.5258 | 404.75 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 19.0533 | 34.0317 | 398.5 | Average of the hour | 2020-09-19 04:00 | 4:00 | 19.0533 | 34.0317 | 398.5 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 15.43 | 46.3275 | 444.9167 | Average of the hour | 2020-09-19 04:00 | 4:00 | 15.43 | 46.3275 | 444.9167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.4717 | 33.9117 | 459 | Average of the hour | 2020-09-19 04:00 | 4:00 | 22.4717 | 33.9117 | 459 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.0525 | 27.3608 | 426 | Average of the hour | 2020-09-19 04:00 | 4:00 | 24.0525 | 27.3608 | 426 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.7125 | 36.3671 | 416.5 | Average of the hour | 2020-09-19 04:00 | 4:00 | 22.7125 | 36.3671 | 416.5 |  | caution | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.4244 | 31.7309 | 490.4446 | Average of the hour | 2020-09-19 04:00 | 4:00 | 22.4244 | 31.7309 | 490.4446 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.029 | 19.7483 | 309.5597 | Average of the hour | 2020-09-19 04:00 | 4:00 | 25.029 | 19.7483 | 309.5597 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.6393 | 20.0775 | 381.8121 | Average of the hour | 2020-09-19 04:00 | 4:00 | 22.6393 | 20.0775 | 381.8121 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.7758 | 44.6238 | 633.25 | Average of the hour | 2020-09-19 04:00 | 4:00 | 21.7758 | 44.6238 | 633.25 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.1942 | 44.4296 | 423 | Average of the hour | 2020-09-19 04:00 | 4:00 | 21.1942 | 44.4296 | 423 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.54 | 49.695 | 423.8333 | Average of the hour | 2020-09-19 04:00 | 4:00 | 21.54 | 49.695 | 423.8333 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 19.3917 | 30.4167 | 450.075 | Average of the hour | 2020-09-19 04:00 | 4:00 | 19.3917 | 30.4167 | 450.075 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 16.375 | 31.1317 | 424.4333 | Average of the hour | 2020-09-19 04:00 | 4:00 | 16.375 | 31.1317 | 424.4333 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 4.6083 |  |  | Average of the hour | 2020-09-19 04:00 | 4:00 | 4.6083 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 9.025 |  |  | Average of the hour | 2020-09-19 04:00 | 4:00 | 9.025 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 6.7238 |  | 450.075 | Average of the hour | 2020-09-19 04:00 | 4:00 | 6.7238 |  | 450.075 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 7.0458 |  | 379.0833 | Average of the hour | 2020-09-19 04:00 | 4:00 | 7.0458 |  | 379.0833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 34.8083 |  | Average of the hour | 2020-09-19 04:00 | 4:00 |  | 34.8083 |  |  | low | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 33.1167 |  | Average of the hour | 2020-09-19 04:00 | 4:00 |  | 33.1167 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.0366 | 24.4932 | 456.7277 | Average of the hour | 2020-09-19 04:00 | 4:00 | 22.0366 | 24.4932 | 456.7277 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 37.6373 | 688.0599 | Average of the hour | 2020-09-19 04:00 | 4:00 |  | 37.6373 | 688.0599 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.8998 | 24.9363 |  | Average of the hour | 2020-09-19 04:00 | 4:00 | 20.8998 | 24.9363 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 04:00
2020-09-19 | 4:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 04:00 | 4:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 04:00
2020-09-19 | 5:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 9.5083 | 48.4583 | 482.8667 | Average of the hour | 2020-09-19 05:00 | 5:00 | 9.5083 | 48.4583 | 482.8667 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 10.7417 | 46.5417 | 581.5 | Average of the hour | 2020-09-19 05:00 | 5:00 | 10.7417 | 46.5417 | 581.5 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 14.0633 | 43.4467 | 414.6667 | Average of the hour | 2020-09-19 05:00 | 5:00 | 14.0633 | 43.4467 | 414.6667 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 19.0925 | 34.2025 | 404.1667 | Average of the hour | 2020-09-19 05:00 | 5:00 | 19.0925 | 34.2025 | 404.1667 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 14.7358 | 48.4608 | 450.9167 | Average of the hour | 2020-09-19 05:00 | 5:00 | 14.7358 | 48.4608 | 450.9167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.345 | 33.2783 | 465.75 | Average of the hour | 2020-09-19 05:00 | 5:00 | 22.345 | 33.2783 | 465.75 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.0817 | 27.0892 | 428.75 | Average of the hour | 2020-09-19 05:00 | 5:00 | 24.0817 | 27.0892 | 428.75 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.765 | 36.48 | 419.5833 | Average of the hour | 2020-09-19 05:00 | 5:00 | 22.765 | 36.48 | 419.5833 |  | caution | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.4244 | 31.9824 | 493.1897 | Average of the hour | 2020-09-19 05:00 | 5:00 | 22.4244 | 31.9824 | 493.1897 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 24.988 | 20.2495 | 312.1153 | Average of the hour | 2020-09-19 05:00 | 5:00 | 24.988 | 20.2495 | 312.1153 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 20.9495 | 22.3992 | 384.2988 | Average of the hour | 2020-09-19 05:00 | 5:00 | 20.9495 | 22.3992 | 384.2988 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.79 | 44.7983 | 637.4167 | Average of the hour | 2020-09-19 05:00 | 5:00 | 21.79 | 44.7983 | 637.4167 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.1483 | 44.4888 | 425.75 | Average of the hour | 2020-09-19 05:00 | 5:00 | 21.1483 | 44.4888 | 425.75 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.4375 | 49.5925 | 433.25 | Average of the hour | 2020-09-19 05:00 | 5:00 | 21.4375 | 49.5925 | 433.25 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 20.025 | 28.125 | 448.0167 | Average of the hour | 2020-09-19 05:00 | 5:00 | 20.025 | 28.125 | 448.0167 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 18.1917 | 33.495 | 430.8417 | Average of the hour | 2020-09-19 05:00 | 5:00 | 18.1917 | 33.495 | 430.8417 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 17.325 |  |  | Average of the hour | 2020-09-19 05:00 | 5:00 | 17.325 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 10.9167 |  |  | Average of the hour | 2020-09-19 05:00 | 5:00 | 10.9167 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 7.6475 |  | 447.125 | Average of the hour | 2020-09-19 05:00 | 5:00 | 7.6475 |  | 447.125 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 7.7733 |  | 380.5 | Average of the hour | 2020-09-19 05:00 | 5:00 | 7.7733 |  | 380.5 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 34.925 |  | Average of the hour | 2020-09-19 05:00 | 5:00 |  | 34.925 |  |  | low | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 33.375 |  | Average of the hour | 2020-09-19 05:00 | 5:00 |  | 33.375 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.0442 | 24.549 | 462.7294 | Average of the hour | 2020-09-19 05:00 | 5:00 | 22.0442 | 24.549 | 462.7294 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 38.1255 | 688.2589 | Average of the hour | 2020-09-19 05:00 | 5:00 |  | 38.1255 | 688.2589 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.8183 | 24.9353 |  | Average of the hour | 2020-09-19 05:00 | 5:00 | 20.8183 | 24.9353 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 05:00
2020-09-19 | 5:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 05:00 | 5:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 05:00
2020-09-19 | 6:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 8.6 | 50.5 | 489.7833 | Average of the hour | 2020-09-19 06:00 | 6:00 | 8.6 | 50.5 | 489.7833 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 19.85 | 36.5833 | 560.0833 | Average of the hour | 2020-09-19 06:00 | 6:00 | 19.85 | 36.5833 | 560.0833 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 12.5933 | 44.4842 | 419.25 | Average of the hour | 2020-09-19 06:00 | 6:00 | 12.5933 | 44.4842 | 419.25 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 17.5583 | 34.6583 | 402.75 | Average of the hour | 2020-09-19 06:00 | 6:00 | 17.5583 | 34.6583 | 402.75 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 13.42 | 48.7825 | 444.25 | Average of the hour | 2020-09-19 06:00 | 6:00 | 13.42 | 48.7825 | 444.25 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.2575 | 32.5125 | 467.5 | Average of the hour | 2020-09-19 06:00 | 6:00 | 22.2575 | 32.5125 | 467.5 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.15 | 26.9667 | 431.75 | Average of the hour | 2020-09-19 06:00 | 6:00 | 24.15 | 26.9667 | 431.75 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.8067 | 36.5967 | 421.8333 | Average of the hour | 2020-09-19 06:00 | 6:00 | 22.8067 | 36.5967 | 421.8333 |  | caution | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.4244 | 32.3036 | 493.7398 | Average of the hour | 2020-09-19 06:00 | 6:00 | 22.4244 | 32.3036 | 493.7398 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.0503 | 20.6083 | 316.6667 | Average of the hour | 2020-09-19 06:00 | 6:00 | 25.0503 | 20.6083 | 316.6667 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 19.6599 | 25.2556 | 385.4326 | Average of the hour | 2020-09-19 06:00 | 6:00 | 19.6599 | 25.2556 | 385.4326 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.82 | 44.7642 | 651.6667 | Average of the hour | 2020-09-19 06:00 | 6:00 | 21.82 | 44.7642 | 651.6667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.2617 | 44.5283 | 429.8333 | Average of the hour | 2020-09-19 06:00 | 6:00 | 21.2617 | 44.5283 | 429.8333 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.5 | 49.2908 | 430.8333 | Average of the hour | 2020-09-19 06:00 | 6:00 | 21.5 | 49.2908 | 430.8333 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 19.7917 | 28 | 449.075 | Average of the hour | 2020-09-19 06:00 | 6:00 | 19.7917 | 28 | 449.075 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.1417 | 29.9942 | 446.025 | Average of the hour | 2020-09-19 06:00 | 6:00 | 21.1417 | 29.9942 | 446.025 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 24.1167 |  |  | Average of the hour | 2020-09-19 06:00 | 6:00 | 24.1167 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 19.5833 |  |  | Average of the hour | 2020-09-19 06:00 | 6:00 | 19.5833 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 15.9318 |  | 449.2333 | Average of the hour | 2020-09-19 06:00 | 6:00 | 15.9318 |  | 449.2333 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 14.3204 |  | 379.9167 | Average of the hour | 2020-09-19 06:00 | 6:00 | 14.3204 |  | 379.9167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 33.1417 |  | Average of the hour | 2020-09-19 06:00 | 6:00 |  | 33.1417 |  |  | low | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 32.3 |  | Average of the hour | 2020-09-19 06:00 | 6:00 |  | 32.3 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.0391 | 24.5646 | 467.089 | Average of the hour | 2020-09-19 06:00 | 6:00 | 22.0391 | 24.5646 | 467.089 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 38.3087 | 688.7142 | Average of the hour | 2020-09-19 06:00 | 6:00 |  | 38.3087 | 688.7142 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.2821 | 25.1831 |  | Average of the hour | 2020-09-19 06:00 | 6:00 | 20.2821 | 25.1831 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 06:00
2020-09-19 | 6:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 06:00 | 6:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 06:00
2020-09-19 | 7:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 8.8917 | 50.7917 | 507.1333 | Average of the hour | 2020-09-19 07:00 | 7:00 | 8.8917 | 50.7917 | 507.1333 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 15.9083 | 35.7917 | 594.0833 | Average of the hour | 2020-09-19 07:00 | 7:00 | 15.9083 | 35.7917 | 594.0833 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 12.26 | 45.195 | 414.5 | Average of the hour | 2020-09-19 07:00 | 7:00 | 12.26 | 45.195 | 414.5 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 17.0942 | 35.5475 | 406.5 | Average of the hour | 2020-09-19 07:00 | 7:00 | 17.0942 | 35.5475 | 406.5 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 13.0975 | 49.5692 | 445.75 | Average of the hour | 2020-09-19 07:00 | 7:00 | 13.0975 | 49.5692 | 445.75 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.1925 | 31.7183 | 469.5833 | Average of the hour | 2020-09-19 07:00 | 7:00 | 22.1925 | 31.7183 | 469.5833 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.1725 | 26.8371 | 442.5 | Average of the hour | 2020-09-19 07:00 | 7:00 | 24.1725 | 26.8371 | 442.5 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.845 | 36.6183 | 426 | Average of the hour | 2020-09-19 07:00 | 7:00 | 22.845 | 36.6183 | 426 |  | caution | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.4244 | 32.5879 | 496.3451 | Average of the hour | 2020-09-19 07:00 | 7:00 | 22.4244 | 32.5879 | 496.3451 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 24.984 | 20.265 | 329.4368 | Average of the hour | 2020-09-19 07:00 | 7:00 | 24.984 | 20.265 | 329.4368 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 20.3746 | 24.1577 | 402.7902 | Average of the hour | 2020-09-19 07:00 | 7:00 | 20.3746 | 24.1577 | 402.7902 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.81 | 44.4746 | 650.5 | Average of the hour | 2020-09-19 07:00 | 7:00 | 21.81 | 44.4746 | 650.5 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.15 | 44.6408 | 440.25 | Average of the hour | 2020-09-19 07:00 | 7:00 | 21.15 | 44.6408 | 440.25 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.45 | 49.195 | 434.75 | Average of the hour | 2020-09-19 07:00 | 7:00 | 21.45 | 49.195 | 434.75 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 19.6333 | 28 | 444.7833 | Average of the hour | 2020-09-19 07:00 | 7:00 | 19.6333 | 28 | 444.7833 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.3 | 29.1833 | 442.725 | Average of the hour | 2020-09-19 07:00 | 7:00 | 21.3 | 29.1833 | 442.725 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 24.6 |  |  | Average of the hour | 2020-09-19 07:00 | 7:00 | 24.6 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 19.6 |  |  | Average of the hour | 2020-09-19 07:00 | 7:00 | 19.6 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 17.3816 |  | 445.9583 | Average of the hour | 2020-09-19 07:00 | 7:00 | 17.3816 |  | 445.9583 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 15.3641 |  | 379.3333 | Average of the hour | 2020-09-19 07:00 | 7:00 | 15.3641 |  | 379.3333 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 33.3667 |  | Average of the hour | 2020-09-19 07:00 | 7:00 |  | 33.3667 |  |  | low | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 31.4 |  | Average of the hour | 2020-09-19 07:00 | 7:00 |  | 31.4 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.0296 | 24.5814 | 466.6733 | Average of the hour | 2020-09-19 07:00 | 7:00 | 22.0296 | 24.5814 | 466.6733 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 38.0345 | 688.811 | Average of the hour | 2020-09-19 07:00 | 7:00 |  | 38.0345 | 688.811 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.2905 | 25.406 |  | Average of the hour | 2020-09-19 07:00 | 7:00 | 20.2905 | 25.406 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 07:00
2020-09-19 | 7:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 07:00 | 7:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 07:00
2020-09-19 | 8:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 11.55 | 48.9583 | 499.3583 | Average of the hour | 2020-09-19 08:00 | 8:00 | 11.55 | 48.9583 | 499.3583 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 8.0417 | 47.625 | 604.7917 | Average of the hour | 2020-09-19 08:00 | 8:00 | 8.0417 | 47.625 | 604.7917 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 12.2108 | 46.0167 | 426.1667 | Average of the hour | 2020-09-19 08:00 | 8:00 | 12.2108 | 46.0167 | 426.1667 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 16.9683 | 36.335 | 419.5833 | Average of the hour | 2020-09-19 08:00 | 8:00 | 16.9683 | 36.335 | 419.5833 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 12.9425 | 50.3158 | 458.9167 | Average of the hour | 2020-09-19 08:00 | 8:00 | 12.9425 | 50.3158 | 458.9167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.0792 | 31.8808 | 471.75 | Average of the hour | 2020-09-19 08:00 | 8:00 | 22.0792 | 31.8808 | 471.75 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.8442 | 28.3758 | 439.1667 | Average of the hour | 2020-09-19 08:00 | 8:00 | 23.8442 | 28.3758 | 439.1667 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.87 | 35.4437 | 424.5 | Average of the hour | 2020-09-19 08:00 | 8:00 | 22.87 | 35.4437 | 424.5 |  | caution | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.7442 | 33.7851 | 524.3507 | Average of the hour | 2020-09-19 08:00 | 8:00 | 21.7442 | 33.7851 | 524.3507 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.8942 | 29.005 | 323.8291 | Average of the hour | 2020-09-19 08:00 | 8:00 | 23.8942 | 29.005 | 323.8291 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 20.7813 | 23.7727 | 399.7382 | Average of the hour | 2020-09-19 08:00 | 8:00 | 20.7813 | 23.7727 | 399.7382 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.91 | 44.3525 | 653 | Average of the hour | 2020-09-19 08:00 | 8:00 | 21.91 | 44.3525 | 653 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.2292 | 44.6954 | 437.9167 | Average of the hour | 2020-09-19 08:00 | 8:00 | 21.2292 | 44.6954 | 437.9167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.4642 | 49.2329 | 436.25 | Average of the hour | 2020-09-19 08:00 | 8:00 | 21.4642 | 49.2329 | 436.25 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 19.5 | 28 | 442.8417 | Average of the hour | 2020-09-19 08:00 | 8:00 | 19.5 | 28 | 442.8417 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.3 | 28.8733 | 435.1083 | Average of the hour | 2020-09-19 08:00 | 8:00 | 21.3 | 28.8733 | 435.1083 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.7083 |  |  | Average of the hour | 2020-09-19 08:00 | 8:00 | 23.7083 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 19.6833 |  |  | Average of the hour | 2020-09-19 08:00 | 8:00 | 19.6833 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 18.0388 |  | 442.8 | Average of the hour | 2020-09-19 08:00 | 8:00 | 18.0388 |  | 442.8 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 16.0543 |  | 379.8333 | Average of the hour | 2020-09-19 08:00 | 8:00 | 16.0543 |  | 379.8333 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 33.7167 |  | Average of the hour | 2020-09-19 08:00 | 8:00 |  | 33.7167 |  |  | low | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 31.1167 |  | Average of the hour | 2020-09-19 08:00 | 8:00 |  | 31.1167 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.0179 | 24.7189 | 472.7223 | Average of the hour | 2020-09-19 08:00 | 8:00 | 22.0179 | 24.7189 | 472.7223 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 37.441 | 689.4047 | Average of the hour | 2020-09-19 08:00 | 8:00 |  | 37.441 | 689.4047 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.2756 | 25.1564 |  | Average of the hour | 2020-09-19 08:00 | 8:00 | 20.2756 | 25.1564 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 08:00
2020-09-19 | 8:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 08:00 | 8:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 08:00
2020-09-19 | 9:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 13.8917 | 46.5833 | 464.5 | Average of the hour | 2020-09-19 09:00 | 9:00 | 13.8917 | 46.5833 | 464.5 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 9.1917 | 50.2083 | 565.75 | Average of the hour | 2020-09-19 09:00 | 9:00 | 9.1917 | 50.2083 | 565.75 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 12.5433 | 45.63 | 425.25 | Average of the hour | 2020-09-19 09:00 | 9:00 | 12.5433 | 45.63 | 425.25 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 17.2308 | 36.1242 | 412.8333 | Average of the hour | 2020-09-19 09:00 | 9:00 | 17.2308 | 36.1242 | 412.8333 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 13.33 | 49.7133 | 452.5 | Average of the hour | 2020-09-19 09:00 | 9:00 | 13.33 | 49.7133 | 452.5 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.9825 | 31.8617 | 471.8333 | Average of the hour | 2020-09-19 09:00 | 9:00 | 21.9825 | 31.8617 | 471.8333 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.54 | 27.4083 | 438.25 | Average of the hour | 2020-09-19 09:00 | 9:00 | 23.54 | 27.4083 | 438.25 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.6075 | 33.8762 | 426.8333 | Average of the hour | 2020-09-19 09:00 | 9:00 | 22.6075 | 33.8762 | 426.8333 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.5445 | 31.5334 | 538.4036 | Average of the hour | 2020-09-19 09:00 | 9:00 | 21.5445 | 31.5334 | 538.4036 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.1694 | 28.5024 | 316.8739 | Average of the hour | 2020-09-19 09:00 | 9:00 | 23.1694 | 28.5024 | 316.8739 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.2647 | 23.5512 | 392.434 | Average of the hour | 2020-09-19 09:00 | 9:00 | 23.2647 | 23.5512 | 392.434 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.0858 | 44.9596 | 643.5 | Average of the hour | 2020-09-19 09:00 | 9:00 | 22.0858 | 44.9596 | 643.5 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.3375 | 45.7642 | 435.5833 | Average of the hour | 2020-09-19 09:00 | 9:00 | 21.3375 | 45.7642 | 435.5833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.6625 | 49.19 | 438.75 | Average of the hour | 2020-09-19 09:00 | 9:00 | 21.6625 | 49.19 | 438.75 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 19.5167 | 27.9167 | 440.4833 | Average of the hour | 2020-09-19 09:00 | 9:00 | 19.5167 | 27.9167 | 440.4833 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.3583 | 28.6342 | 431.8667 | Average of the hour | 2020-09-19 09:00 | 9:00 | 21.3583 | 28.6342 | 431.8667 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.9917 |  |  | Average of the hour | 2020-09-19 09:00 | 9:00 | 23.9917 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 19.825 |  |  | Average of the hour | 2020-09-19 09:00 | 9:00 | 19.825 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 19.1194 |  | 440.775 | Average of the hour | 2020-09-19 09:00 | 9:00 | 19.1194 |  | 440.775 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 16.3517 |  | 379 | Average of the hour | 2020-09-19 09:00 | 9:00 | 16.3517 |  | 379 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 33.825 |  | Average of the hour | 2020-09-19 09:00 | 9:00 |  | 33.825 |  |  | low | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 31.1417 |  | Average of the hour | 2020-09-19 09:00 | 9:00 |  | 31.1417 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.0225 | 24.9064 | 467.7138 | Average of the hour | 2020-09-19 09:00 | 9:00 | 22.0225 | 24.9064 | 467.7138 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 36.6951 | 690.0616 | Average of the hour | 2020-09-19 09:00 | 9:00 |  | 36.6951 | 690.0616 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.3084 | 24.3828 |  | Average of the hour | 2020-09-19 09:00 | 9:00 | 20.3084 | 24.3828 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 09:00
2020-09-19 | 9:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 09:00 | 9:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 09:00
2020-09-19 | 10:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 15.0917 | 38.6667 | 430.7167 | Average of the hour | 2020-09-19 10:00 | 10:00 | 15.0917 | 38.6667 | 430.7167 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 10.6167 | 38.0417 | 531.0833 | Average of the hour | 2020-09-19 10:00 | 10:00 | 10.6167 | 38.0417 | 531.0833 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 13.6225 | 41.5942 | 403.9167 | Average of the hour | 2020-09-19 10:00 | 10:00 | 13.6225 | 41.5942 | 403.9167 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 18.0817 | 33.325 | 388.3333 | Average of the hour | 2020-09-19 10:00 | 10:00 | 18.0817 | 33.325 | 388.3333 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 14.6683 | 45.1975 | 434.3333 | Average of the hour | 2020-09-19 10:00 | 10:00 | 14.6683 | 45.1975 | 434.3333 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.8583 | 31.7975 | 466.3333 | Average of the hour | 2020-09-19 10:00 | 10:00 | 21.8583 | 31.7975 | 466.3333 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.4842 | 26.9842 | 428.8333 | Average of the hour | 2020-09-19 10:00 | 10:00 | 23.4842 | 26.9842 | 428.8333 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.3675 | 32.8908 | 420.6667 | Average of the hour | 2020-09-19 10:00 | 10:00 | 22.3675 | 32.8908 | 420.6667 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.2749 | 31.387 | 530.5979 | Average of the hour | 2020-09-19 10:00 | 10:00 | 21.2749 | 31.387 | 530.5979 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.0494 | 27.6676 | 306.9377 | Average of the hour | 2020-09-19 10:00 | 10:00 | 23.0494 | 27.6676 | 306.9377 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 24.1293 | 22.8204 | 378.491 | Average of the hour | 2020-09-19 10:00 | 10:00 | 24.1293 | 22.8204 | 378.491 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.2208 | 45.0942 | 633.1667 | Average of the hour | 2020-09-19 10:00 | 10:00 | 22.2208 | 45.0942 | 633.1667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.57 | 45.8225 | 427.25 | Average of the hour | 2020-09-19 10:00 | 10:00 | 21.57 | 45.8225 | 427.25 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.9325 | 49.8908 | 433.25 | Average of the hour | 2020-09-19 10:00 | 10:00 | 21.9325 | 49.8908 | 433.25 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 19.6 | 26.7917 | 434.6667 | Average of the hour | 2020-09-19 10:00 | 10:00 | 19.6 | 26.7917 | 434.6667 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.4 | 28.2675 | 426.425 | Average of the hour | 2020-09-19 10:00 | 10:00 | 21.4 | 28.2675 | 426.425 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.8417 |  |  | Average of the hour | 2020-09-19 10:00 | 10:00 | 23.8417 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 19.9833 |  |  | Average of the hour | 2020-09-19 10:00 | 10:00 | 19.9833 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 19.6384 |  | 434.6833 | Average of the hour | 2020-09-19 10:00 | 10:00 | 19.6384 |  | 434.6833 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 17.2175 |  | 379.5833 | Average of the hour | 2020-09-19 10:00 | 10:00 | 17.2175 |  | 379.5833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 33.8167 |  | Average of the hour | 2020-09-19 10:00 | 10:00 |  | 33.8167 |  |  | low | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 30.9583 |  | Average of the hour | 2020-09-19 10:00 | 10:00 |  | 30.9583 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.027 | 25.2082 | 457.1899 | Average of the hour | 2020-09-19 10:00 | 10:00 | 22.027 | 25.2082 | 457.1899 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 35.7313 | 690.0594 | Average of the hour | 2020-09-19 10:00 | 10:00 |  | 35.7313 | 690.0594 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.469 | 23.2227 |  | Average of the hour | 2020-09-19 10:00 | 10:00 | 20.469 | 23.2227 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 10:00
2020-09-19 | 10:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 10:00 | 10:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 10:00
2020-09-19 | 11:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 15.8 | 34.5417 | 423.2333 | Average of the hour | 2020-09-19 11:00 | 11:00 | 15.8 | 34.5417 | 423.2333 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 10.9667 | 33.375 | 518.7917 | Average of the hour | 2020-09-19 11:00 | 11:00 | 10.9667 | 33.375 | 518.7917 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 14.1667 | 37.8567 | 392 | Average of the hour | 2020-09-19 11:00 | 11:00 | 14.1667 | 37.8567 | 392 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 18.4617 | 30.7517 | 377.5833 | Average of the hour | 2020-09-19 11:00 | 11:00 | 18.4617 | 30.7517 | 377.5833 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 15.325 | 41.5075 | 425.6667 | Average of the hour | 2020-09-19 11:00 | 11:00 | 15.325 | 41.5075 | 425.6667 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.7792 | 30.8342 | 457.9167 | Average of the hour | 2020-09-19 11:00 | 11:00 | 21.7792 | 30.8342 | 457.9167 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.4225 | 26.6942 | 423.25 | Average of the hour | 2020-09-19 11:00 | 11:00 | 23.4225 | 26.6942 | 423.25 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.2975 | 32.3287 | 412 | Average of the hour | 2020-09-19 11:00 | 11:00 | 22.2975 | 32.3287 | 412 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.9056 | 31.3857 | 522.6146 | Average of the hour | 2020-09-19 11:00 | 11:00 | 20.9056 | 31.3857 | 522.6146 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.792 | 28.1364 | 296.9235 | Average of the hour | 2020-09-19 11:00 | 11:00 | 22.792 | 28.1364 | 296.9235 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 24.7279 | 23.066 | 375.8429 | Average of the hour | 2020-09-19 11:00 | 11:00 | 24.7279 | 23.066 | 375.8429 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.205 | 44.7708 | 628 | Average of the hour | 2020-09-19 11:00 | 11:00 | 22.205 | 44.7708 | 628 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.5117 | 44.9587 | 416.5 | Average of the hour | 2020-09-19 11:00 | 11:00 | 21.5117 | 44.9587 | 416.5 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.1325 | 50.3217 | 422.6667 | Average of the hour | 2020-09-19 11:00 | 11:00 | 22.1325 | 50.3217 | 422.6667 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 19.6667 | 25.4167 | 428.5333 | Average of the hour | 2020-09-19 11:00 | 11:00 | 19.6667 | 25.4167 | 428.5333 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.4833 | 27.91 | 422.0833 | Average of the hour | 2020-09-19 11:00 | 11:00 | 21.4833 | 27.91 | 422.0833 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.5833 |  |  | Average of the hour | 2020-09-19 11:00 | 11:00 | 23.5833 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.15 |  |  | Average of the hour | 2020-09-19 11:00 | 11:00 | 20.15 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.4121 |  | 428.2583 | Average of the hour | 2020-09-19 11:00 | 11:00 | 20.4121 |  | 428.2583 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 17.8596 |  | 378.9167 | Average of the hour | 2020-09-19 11:00 | 11:00 | 17.8596 |  | 378.9167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 33.5 |  | Average of the hour | 2020-09-19 11:00 | 11:00 |  | 33.5 |  |  | low | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 30.4583 |  | Average of the hour | 2020-09-19 11:00 | 11:00 |  | 30.4583 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.0585 | 25.4817 | 449.0283 | Average of the hour | 2020-09-19 11:00 | 11:00 | 22.0585 | 25.4817 | 449.0283 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 34.6228 | 689.9991 | Average of the hour | 2020-09-19 11:00 | 11:00 |  | 34.6228 | 689.9991 |  | low | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.6923 | 22.0471 |  | Average of the hour | 2020-09-19 11:00 | 11:00 | 20.6923 | 22.0471 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 11:00
2020-09-19 | 11:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 11:00 | 11:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 11:00
2020-09-19 | 12:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 15.6 | 30.5 | 425.05 | Average of the hour | 2020-09-19 12:00 | 12:00 | 15.6 | 30.5 | 425.05 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 11.875 | 30 | 517.7917 | Average of the hour | 2020-09-19 12:00 | 12:00 | 11.875 | 30 | 517.7917 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 14.4892 | 32.8808 | 388.4167 | Average of the hour | 2020-09-19 12:00 | 12:00 | 14.4892 | 32.8808 | 388.4167 |  | low | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 18.7408 | 27.2225 | 375.9167 | Average of the hour | 2020-09-19 12:00 | 12:00 | 18.7408 | 27.2225 | 375.9167 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 15.6517 | 36.4017 | 424.1667 | Average of the hour | 2020-09-19 12:00 | 12:00 | 15.6517 | 36.4017 | 424.1667 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.8033 | 29.1875 | 455.3333 | Average of the hour | 2020-09-19 12:00 | 12:00 | 21.8033 | 29.1875 | 455.3333 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.3267 | 26.0708 | 417.6667 | Average of the hour | 2020-09-19 12:00 | 12:00 | 23.3267 | 26.0708 | 417.6667 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.2975 | 31.5683 | 409.5833 | Average of the hour | 2020-09-19 12:00 | 12:00 | 22.2975 | 31.5683 | 409.5833 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.7376 | 30.6082 | 517.2327 | Average of the hour | 2020-09-19 12:00 | 12:00 | 20.7376 | 30.6082 | 517.2327 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.6411 | 26.4498 | 292.7025 | Average of the hour | 2020-09-19 12:00 | 12:00 | 22.6411 | 26.4498 | 292.7025 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 24.5004 | 23.773 | 372.8942 | Average of the hour | 2020-09-19 12:00 | 12:00 | 24.5004 | 23.773 | 372.8942 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.1867 | 44.6467 | 614.4167 | Average of the hour | 2020-09-19 12:00 | 12:00 | 22.1867 | 44.6467 | 614.4167 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.5858 | 44.1467 | 412.0833 | Average of the hour | 2020-09-19 12:00 | 12:00 | 21.5858 | 44.1467 | 412.0833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.1908 | 50.205 | 414.9167 | Average of the hour | 2020-09-19 12:00 | 12:00 | 22.1908 | 50.205 | 414.9167 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 19.775 | 24.75 | 424.8167 | Average of the hour | 2020-09-19 12:00 | 12:00 | 19.775 | 24.75 | 424.8167 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.5 | 27.81 | 421.275 | Average of the hour | 2020-09-19 12:00 | 12:00 | 21.5 | 27.81 | 421.275 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.975 |  |  | Average of the hour | 2020-09-19 12:00 | 12:00 | 22.975 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.2417 |  |  | Average of the hour | 2020-09-19 12:00 | 12:00 | 20.2417 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 21.0319 |  | 424.8583 | Average of the hour | 2020-09-19 12:00 | 12:00 | 21.0319 |  | 424.8583 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 18.6042 |  | 379.5833 | Average of the hour | 2020-09-19 12:00 | 12:00 | 18.6042 |  | 379.5833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 33.425 |  | Average of the hour | 2020-09-19 12:00 | 12:00 |  | 33.425 |  |  | low | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 30.275 |  | Average of the hour | 2020-09-19 12:00 | 12:00 |  | 30.275 |  |  | low | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.1034 | 25.3828 | 445.4133 | Average of the hour | 2020-09-19 12:00 | 12:00 | 22.1034 | 25.3828 | 445.4133 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 34.2791 | 689.7303 | Average of the hour | 2020-09-19 12:00 | 12:00 |  | 34.2791 | 689.7303 |  | low | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.7913 | 22.1729 |  | Average of the hour | 2020-09-19 12:00 | 12:00 | 20.7913 | 22.1729 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 12:00
2020-09-19 | 12:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 12:00 | 12:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 12:00
2020-09-19 | 13:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 15.2333 | 27.9167 | 421.6583 | Average of the hour | 2020-09-19 13:00 | 13:00 | 15.2333 | 27.9167 | 421.6583 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 12.1833 | 27.7083 | 517.875 | Average of the hour | 2020-09-19 13:00 | 13:00 | 12.1833 | 27.7083 | 517.875 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 14.8408 | 31.7925 | 383.1667 | Average of the hour | 2020-09-19 13:00 | 13:00 | 14.8408 | 31.7925 | 383.1667 |  | low | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 18.9358 | 26.865 | 378.8333 | Average of the hour | 2020-09-19 13:00 | 13:00 | 18.9358 | 26.865 | 378.8333 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 15.9717 | 35.6358 | 427.0833 | Average of the hour | 2020-09-19 13:00 | 13:00 | 15.9717 | 35.6358 | 427.0833 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.7617 | 28.3667 | 454.5833 | Average of the hour | 2020-09-19 13:00 | 13:00 | 21.7617 | 28.3667 | 454.5833 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.2475 | 25.3175 | 416.5 | Average of the hour | 2020-09-19 13:00 | 13:00 | 23.2475 | 25.3175 | 416.5 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.26 | 30.71 | 408.5 | Average of the hour | 2020-09-19 13:00 | 13:00 | 22.26 | 30.71 | 408.5 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.6212 | 29.5249 | 513.4304 | Average of the hour | 2020-09-19 13:00 | 13:00 | 20.6212 | 29.5249 | 513.4304 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.6161 | 25.2979 | 290.9931 | Average of the hour | 2020-09-19 13:00 | 13:00 | 22.6161 | 25.2979 | 290.9931 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 24.4713 | 23.358 | 370.2762 | Average of the hour | 2020-09-19 13:00 | 13:00 | 24.4713 | 23.358 | 370.2762 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.1692 | 44.3888 | 613.25 | Average of the hour | 2020-09-19 13:00 | 13:00 | 22.1692 | 44.3888 | 613.25 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.6475 | 44.2092 | 411.25 | Average of the hour | 2020-09-19 13:00 | 13:00 | 21.6475 | 44.2092 | 411.25 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.1825 | 49.7404 | 411.5 | Average of the hour | 2020-09-19 13:00 | 13:00 | 22.1825 | 49.7404 | 411.5 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 19.9083 | 24.0417 | 424.3667 | Average of the hour | 2020-09-19 13:00 | 13:00 | 19.9083 | 24.0417 | 424.3667 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.5167 | 27.6658 | 418.6583 | Average of the hour | 2020-09-19 13:00 | 13:00 | 21.5167 | 27.6658 | 418.6583 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.7417 |  |  | Average of the hour | 2020-09-19 13:00 | 13:00 | 22.7417 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.325 |  |  | Average of the hour | 2020-09-19 13:00 | 13:00 | 20.325 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.8929 |  | 424.1667 | Average of the hour | 2020-09-19 13:00 | 13:00 | 20.8929 |  | 424.1667 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 19.4596 |  | 379.6667 | Average of the hour | 2020-09-19 13:00 | 13:00 | 19.4596 |  | 379.6667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-19 13:00 | 13:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-19 13:00 | 13:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.1701 | 25.2492 | 441.3995 | Average of the hour | 2020-09-19 13:00 | 13:00 | 22.1701 | 25.2492 | 441.3995 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 34.3006 | 689.3809 | Average of the hour | 2020-09-19 13:00 | 13:00 |  | 34.3006 | 689.3809 |  | low | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.8928 | 22.6106 |  | Average of the hour | 2020-09-19 13:00 | 13:00 | 20.8928 | 22.6106 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 13:00
2020-09-19 | 13:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 13:00 | 13:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 13:00
2020-09-19 | 14:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 15.3917 | 26.9167 | 418.3667 | Average of the hour | 2020-09-19 14:00 | 14:00 | 15.3917 | 26.9167 | 418.3667 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 13.0333 | 25.0833 | 518.6667 | Average of the hour | 2020-09-19 14:00 | 14:00 | 13.0333 | 25.0833 | 518.6667 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 14.9833 | 25.7792 | 390.0833 | Average of the hour | 2020-09-19 14:00 | 14:00 | 14.9833 | 25.7792 | 390.0833 |  | low | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 18.8508 | 21.7408 | 377.75 | Average of the hour | 2020-09-19 14:00 | 14:00 | 18.8508 | 21.7408 | 377.75 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 16.1658 | 28.2042 | 424.3333 | Average of the hour | 2020-09-19 14:00 | 14:00 | 16.1658 | 28.2042 | 424.3333 |  | low | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.8167 | 27.2942 | 455.0833 | Average of the hour | 2020-09-19 14:00 | 14:00 | 21.8167 | 27.2942 | 455.0833 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.2167 | 24.1754 | 416 | Average of the hour | 2020-09-19 14:00 | 14:00 | 23.2167 | 24.1754 | 416 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.1633 | 29.4354 | 408.9167 | Average of the hour | 2020-09-19 14:00 | 14:00 | 22.1633 | 29.4354 | 408.9167 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.5882 | 27.92 | 512.8365 | Average of the hour | 2020-09-19 14:00 | 14:00 | 20.5882 | 27.92 | 512.8365 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.6161 | 24.0633 | 289.8843 | Average of the hour | 2020-09-19 14:00 | 14:00 | 22.6161 | 24.0633 | 289.8843 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 24.1528 | 24.6001 | 367.6045 | Average of the hour | 2020-09-19 14:00 | 14:00 | 24.1528 | 24.6001 | 367.6045 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.1858 | 44.1329 | 613.3333 | Average of the hour | 2020-09-19 14:00 | 14:00 | 22.1858 | 44.1329 | 613.3333 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.6675 | 44.5246 | 408 | Average of the hour | 2020-09-19 14:00 | 14:00 | 21.6675 | 44.5246 | 408 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.3108 | 49.4321 | 405.5 | Average of the hour | 2020-09-19 14:00 | 14:00 | 22.3108 | 49.4321 | 405.5 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 20.0417 | 24.2083 | 422.9333 | Average of the hour | 2020-09-19 14:00 | 14:00 | 20.0417 | 24.2083 | 422.9333 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.6 | 27.6917 | 417.5083 | Average of the hour | 2020-09-19 14:00 | 14:00 | 21.6 | 27.6917 | 417.5083 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.2417 |  |  | Average of the hour | 2020-09-19 14:00 | 14:00 | 23.2417 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.3917 |  |  | Average of the hour | 2020-09-19 14:00 | 14:00 | 20.3917 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.7083 |  | 422.975 | Average of the hour | 2020-09-19 14:00 | 14:00 | 20.7083 |  | 422.975 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 20.353 |  | 379.75 | Average of the hour | 2020-09-19 14:00 | 14:00 | 20.353 |  | 379.75 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-19 14:00 | 14:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-19 14:00 | 14:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.2162 | 25.1185 | 439.1551 | Average of the hour | 2020-09-19 14:00 | 14:00 | 22.2162 | 25.1185 | 439.1551 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 34.6095 | 689.3581 | Average of the hour | 2020-09-19 14:00 | 14:00 |  | 34.6095 | 689.3581 |  | low | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9036 | 23.115 |  | Average of the hour | 2020-09-19 14:00 | 14:00 | 20.9036 | 23.115 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 14:00
2020-09-19 | 14:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 14:00 | 14:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 14:00
2020-09-19 | 15:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 15.8583 | 28.4583 | 418.7583 | Average of the hour | 2020-09-19 15:00 | 15:00 | 15.8583 | 28.4583 | 418.7583 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 13.5833 | 27.9167 | 518.625 | Average of the hour | 2020-09-19 15:00 | 15:00 | 13.5833 | 27.9167 | 518.625 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 15.4333 | 25.0817 | 389.4167 | Average of the hour | 2020-09-19 15:00 | 15:00 | 15.4333 | 25.0817 | 389.4167 |  | low | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 19.2475 | 21.12 | 380.5 | Average of the hour | 2020-09-19 15:00 | 15:00 | 19.2475 | 21.12 | 380.5 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 16.6633 | 27.3842 | 427.5 | Average of the hour | 2020-09-19 15:00 | 15:00 | 16.6633 | 27.3842 | 427.5 |  | low | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.865 | 25.8742 | 456.4167 | Average of the hour | 2020-09-19 15:00 | 15:00 | 21.865 | 25.8742 | 456.4167 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.5842 | 26.2404 | 422.9167 | Average of the hour | 2020-09-19 15:00 | 15:00 | 23.5842 | 26.2404 | 422.9167 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.2817 | 29.2608 | 407.75 | Average of the hour | 2020-09-19 15:00 | 15:00 | 22.2817 | 29.2608 | 407.75 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.0391 | 27.0474 | 494.5329 | Average of the hour | 2020-09-19 15:00 | 15:00 | 21.0391 | 27.0474 | 494.5329 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.7336 | 19.7559 | 290.9501 | Average of the hour | 2020-09-19 15:00 | 15:00 | 23.7336 | 19.7559 | 290.9501 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 24.261 | 24.3046 | 365.1186 | Average of the hour | 2020-09-19 15:00 | 15:00 | 24.261 | 24.3046 | 365.1186 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.205 | 44.9025 | 611.5833 | Average of the hour | 2020-09-19 15:00 | 15:00 | 22.205 | 44.9025 | 611.5833 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.8367 | 44.8625 | 406.25 | Average of the hour | 2020-09-19 15:00 | 15:00 | 21.8367 | 44.8625 | 406.25 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.3225 | 50.6937 | 404.4167 | Average of the hour | 2020-09-19 15:00 | 15:00 | 22.3225 | 50.6937 | 404.4167 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 20.3 | 24.9167 | 421.7167 | Average of the hour | 2020-09-19 15:00 | 15:00 | 20.3 | 24.9167 | 421.7167 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.6 | 27.83 | 416.1583 | Average of the hour | 2020-09-19 15:00 | 15:00 | 21.6 | 27.83 | 416.1583 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.9167 |  |  | Average of the hour | 2020-09-19 15:00 | 15:00 | 22.9167 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.4 |  |  | Average of the hour | 2020-09-19 15:00 | 15:00 | 20.4 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.6706 |  | 421.1083 | Average of the hour | 2020-09-19 15:00 | 15:00 | 20.6706 |  | 421.1083 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 20.5966 |  | 379.3333 | Average of the hour | 2020-09-19 15:00 | 15:00 | 20.5966 |  | 379.3333 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-19 15:00 | 15:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-19 15:00 | 15:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.2526 | 25.0115 | 435.5656 | Average of the hour | 2020-09-19 15:00 | 15:00 | 22.2526 | 25.0115 | 435.5656 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 35.1006 | 689.3756 | Average of the hour | 2020-09-19 15:00 | 15:00 |  | 35.1006 | 689.3756 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.8951 | 23.6675 |  | Average of the hour | 2020-09-19 15:00 | 15:00 | 20.8951 | 23.6675 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 15:00
2020-09-19 | 15:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 15:00 | 15:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 15:00
2020-09-19 | 16:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 15.8333 | 29.7917 | 419.1417 | Average of the hour | 2020-09-19 16:00 | 16:00 | 15.8333 | 29.7917 | 419.1417 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 13.8083 | 29.3333 | 516.2083 | Average of the hour | 2020-09-19 16:00 | 16:00 | 13.8083 | 29.3333 | 516.2083 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 15.5808 | 25.7717 | 391.5 | Average of the hour | 2020-09-19 16:00 | 16:00 | 15.5808 | 25.7717 | 391.5 |  | low | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 19.3017 | 21.7658 | 383.1667 | Average of the hour | 2020-09-19 16:00 | 16:00 | 19.3017 | 21.7658 | 383.1667 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 16.8067 | 28.0367 | 430.4167 | Average of the hour | 2020-09-19 16:00 | 16:00 | 16.8067 | 28.0367 | 430.4167 |  | low | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.9458 | 25.5425 | 460.9167 | Average of the hour | 2020-09-19 16:00 | 16:00 | 21.9458 | 25.5425 | 460.9167 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.9725 | 29.2379 | 432.5833 | Average of the hour | 2020-09-19 16:00 | 16:00 | 23.9725 | 29.2379 | 432.5833 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.5158 | 27.4658 | 408.4167 | Average of the hour | 2020-09-19 16:00 | 16:00 | 22.5158 | 27.4658 | 408.4167 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.8169 | 25.2836 | 486.0521 | Average of the hour | 2020-09-19 16:00 | 16:00 | 21.8169 | 25.2836 | 486.0521 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.2025 | 17.9825 | 292.5158 | Average of the hour | 2020-09-19 16:00 | 16:00 | 25.2025 | 17.9825 | 292.5158 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 24.8938 | 21.5543 | 366.1183 | Average of the hour | 2020-09-19 16:00 | 16:00 | 24.8938 | 21.5543 | 366.1183 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.2725 | 45.6346 | 612.6667 | Average of the hour | 2020-09-19 16:00 | 16:00 | 22.2725 | 45.6346 | 612.6667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.9 | 45.1288 | 401.4167 | Average of the hour | 2020-09-19 16:00 | 16:00 | 21.9 | 45.1288 | 401.4167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.2467 | 50.8454 | 404.0833 | Average of the hour | 2020-09-19 16:00 | 16:00 | 22.2467 | 50.8454 | 404.0833 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 20.5 | 25.125 | 421.3417 | Average of the hour | 2020-09-19 16:00 | 16:00 | 20.5 | 25.125 | 421.3417 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.5583 | 28.0192 | 416.675 | Average of the hour | 2020-09-19 16:00 | 16:00 | 21.5583 | 28.0192 | 416.675 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.3167 |  |  | Average of the hour | 2020-09-19 16:00 | 16:00 | 22.3167 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.325 |  |  | Average of the hour | 2020-09-19 16:00 | 16:00 | 20.325 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.6959 |  | 421.2917 | Average of the hour | 2020-09-19 16:00 | 16:00 | 20.6959 |  | 421.2917 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 20.4965 |  | 379.5833 | Average of the hour | 2020-09-19 16:00 | 16:00 | 20.4965 |  | 379.5833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-19 16:00 | 16:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-19 16:00 | 16:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.2906 | 25.0503 | 438.7726 | Average of the hour | 2020-09-19 16:00 | 16:00 | 22.2906 | 25.0503 | 438.7726 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 35.3872 | 689.1428 | Average of the hour | 2020-09-19 16:00 | 16:00 |  | 35.3872 | 689.1428 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9357 | 23.8225 |  | Average of the hour | 2020-09-19 16:00 | 16:00 | 20.9357 | 23.8225 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 16:00
2020-09-19 | 16:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 16:00 | 16:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 16:00
2020-09-19 | 17:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 15.95 | 32.2083 | 419.8667 | Average of the hour | 2020-09-19 17:00 | 17:00 | 15.95 | 32.2083 | 419.8667 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 13.725 | 32.7917 | 516.9167 | Average of the hour | 2020-09-19 17:00 | 17:00 | 13.725 | 32.7917 | 516.9167 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 15.8008 | 27.9492 | 390.8333 | Average of the hour | 2020-09-19 17:00 | 17:00 | 15.8008 | 27.9492 | 390.8333 |  | low | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 19.5792 | 23.7583 | 380.1667 | Average of the hour | 2020-09-19 17:00 | 17:00 | 19.5792 | 23.7583 | 380.1667 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 17.0567 | 30.35 | 425.1667 | Average of the hour | 2020-09-19 17:00 | 17:00 | 17.0567 | 30.35 | 425.1667 |  | low | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.0275 | 26.2217 | 459.5 | Average of the hour | 2020-09-19 17:00 | 17:00 | 22.0275 | 26.2217 | 459.5 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.1025 | 29.0446 | 430.75 | Average of the hour | 2020-09-19 17:00 | 17:00 | 24.1025 | 29.0446 | 430.75 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.555 | 29.0729 | 408.5833 | Average of the hour | 2020-09-19 17:00 | 17:00 | 22.555 | 29.0729 | 408.5833 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.1134 | 24.0534 | 486.1683 | Average of the hour | 2020-09-19 17:00 | 17:00 | 22.1134 | 24.0534 | 486.1683 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.4663 | 18.3255 | 294.3926 | Average of the hour | 2020-09-19 17:00 | 17:00 | 25.4663 | 18.3255 | 294.3926 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 24.7469 | 23.8895 | 365.9907 | Average of the hour | 2020-09-19 17:00 | 17:00 | 24.7469 | 23.8895 | 365.9907 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.3608 | 45.6546 | 611.5 | Average of the hour | 2020-09-19 17:00 | 17:00 | 22.3608 | 45.6546 | 611.5 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.8525 | 45.0979 | 409.5833 | Average of the hour | 2020-09-19 17:00 | 17:00 | 21.8525 | 45.0979 | 409.5833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.2892 | 50.9279 | 399.25 | Average of the hour | 2020-09-19 17:00 | 17:00 | 22.2892 | 50.9279 | 399.25 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 20.675 | 25.5 | 420.375 | Average of the hour | 2020-09-19 17:00 | 17:00 | 20.675 | 25.5 | 420.375 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.5 | 28.1658 | 415.2667 | Average of the hour | 2020-09-19 17:00 | 17:00 | 21.5 | 28.1658 | 415.2667 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.8333 |  |  | Average of the hour | 2020-09-19 17:00 | 17:00 | 22.8333 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.225 |  |  | Average of the hour | 2020-09-19 17:00 | 17:00 | 20.225 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.6707 |  | 420.1333 | Average of the hour | 2020-09-19 17:00 | 17:00 | 20.6707 |  | 420.1333 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 20.9482 |  | 379.8333 | Average of the hour | 2020-09-19 17:00 | 17:00 | 20.9482 |  | 379.8333 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-19 17:00 | 17:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-19 17:00 | 17:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.3345 | 25.081 | 434.1505 | Average of the hour | 2020-09-19 17:00 | 17:00 | 22.3345 | 25.081 | 434.1505 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 35.6606 | 688.6883 | Average of the hour | 2020-09-19 17:00 | 17:00 |  | 35.6606 | 688.6883 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9399 | 24.3816 |  | Average of the hour | 2020-09-19 17:00 | 17:00 | 20.9399 | 24.3816 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 17:00
2020-09-19 | 17:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 17:00 | 17:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 17:00
2020-09-19 | 18:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 15.3333 | 33.6667 | 420.9167 | Average of the hour | 2020-09-19 18:00 | 18:00 | 15.3333 | 33.6667 | 420.9167 |  | low | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 13.4417 | 34.25 | 515.6667 | Average of the hour | 2020-09-19 18:00 | 18:00 | 13.4417 | 34.25 | 515.6667 |  | low | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 15.8825 | 27.79 | 392 | Average of the hour | 2020-09-19 18:00 | 18:00 | 15.8825 | 27.79 | 392 |  | low | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 19.7175 | 23.5567 | 379.9167 | Average of the hour | 2020-09-19 18:00 | 18:00 | 19.7175 | 23.5567 | 379.9167 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 17.0842 | 30.3192 | 426.25 | Average of the hour | 2020-09-19 18:00 | 18:00 | 17.0842 | 30.3192 | 426.25 |  | low | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.13 | 26.3075 | 462.8333 | Average of the hour | 2020-09-19 18:00 | 18:00 | 22.13 | 26.3075 | 462.8333 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.2125 | 28.8275 | 428.5 | Average of the hour | 2020-09-19 18:00 | 18:00 | 24.2125 | 28.8275 | 428.5 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.7083 | 32.6667 | 409.9167 | Average of the hour | 2020-09-19 18:00 | 18:00 | 22.7083 | 32.6667 | 409.9167 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.1896 | 27.4023 | 484.177 | Average of the hour | 2020-09-19 18:00 | 18:00 | 22.1896 | 27.4023 | 484.177 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.469 | 19.1451 | 293.0044 | Average of the hour | 2020-09-19 18:00 | 18:00 | 25.469 | 19.1451 | 293.0044 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 24.9965 | 24.0676 | 368.5101 | Average of the hour | 2020-09-19 18:00 | 18:00 | 24.9965 | 24.0676 | 368.5101 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.3817 | 45.2038 | 613.5833 | Average of the hour | 2020-09-19 18:00 | 18:00 | 22.3817 | 45.2038 | 613.5833 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.92 | 45.3488 | 410.1667 | Average of the hour | 2020-09-19 18:00 | 18:00 | 21.92 | 45.3488 | 410.1667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.1892 | 50.7254 | 407.0833 | Average of the hour | 2020-09-19 18:00 | 18:00 | 22.1892 | 50.7254 | 407.0833 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 20.8 | 25.5 | 427.3 | Average of the hour | 2020-09-19 18:00 | 18:00 | 20.8 | 25.5 | 427.3 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.5 | 28.3525 | 417.4167 | Average of the hour | 2020-09-19 18:00 | 18:00 | 21.5 | 28.3525 | 417.4167 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.3 |  |  | Average of the hour | 2020-09-19 18:00 | 18:00 | 22.3 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.2 |  |  | Average of the hour | 2020-09-19 18:00 | 18:00 | 20.2 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 19.9799 |  | 425.9167 | Average of the hour | 2020-09-19 18:00 | 18:00 | 19.9799 |  | 425.9167 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 20.8254 |  | 379.5 | Average of the hour | 2020-09-19 18:00 | 18:00 | 20.8254 |  | 379.5 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-19 18:00 | 18:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-19 18:00 | 18:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.3816 | 25.1794 | 431.2606 | Average of the hour | 2020-09-19 18:00 | 18:00 | 22.3816 | 25.1794 | 431.2606 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 35.7793 | 688.5744 | Average of the hour | 2020-09-19 18:00 | 18:00 |  | 35.7793 | 688.5744 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.8702 | 24.3592 |  | Average of the hour | 2020-09-19 18:00 | 18:00 | 20.8702 | 24.3592 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 18:00
2020-09-19 | 18:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 18:00 | 18:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 18:00
2020-09-19 | 19:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 14.7667 | 35.7083 | 426.6917 | Average of the hour | 2020-09-19 19:00 | 19:00 | 14.7667 | 35.7083 | 426.6917 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 13.4917 | 35.5417 | 520.9583 | Average of the hour | 2020-09-19 19:00 | 19:00 | 13.4917 | 35.5417 | 520.9583 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 15.6267 | 28.2042 | 391.4167 | Average of the hour | 2020-09-19 19:00 | 19:00 | 15.6267 | 28.2042 | 391.4167 |  | low | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 19.5008 | 23.9833 | 383.5 | Average of the hour | 2020-09-19 19:00 | 19:00 | 19.5008 | 23.9833 | 383.5 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 16.8325 | 31.0742 | 429.3333 | Average of the hour | 2020-09-19 19:00 | 19:00 | 16.8325 | 31.0742 | 429.3333 |  | low | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.1592 | 26.08 | 462.0833 | Average of the hour | 2020-09-19 19:00 | 19:00 | 22.1592 | 26.08 | 462.0833 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.2792 | 26.8346 | 428.1667 | Average of the hour | 2020-09-19 19:00 | 19:00 | 24.2792 | 26.8346 | 428.1667 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.5083 | 31.7592 | 408.3333 | Average of the hour | 2020-09-19 19:00 | 19:00 | 22.5083 | 31.7592 | 408.3333 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.4031 | 26.7412 | 486.2334 | Average of the hour | 2020-09-19 19:00 | 19:00 | 22.4031 | 26.7412 | 486.2334 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 26.1301 | 22.0947 | 292.0491 | Average of the hour | 2020-09-19 19:00 | 19:00 | 26.1301 | 22.0947 | 292.0491 | caution | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 25.0256 | 24.3581 | 368.2069 | Average of the hour | 2020-09-19 19:00 | 19:00 | 25.0256 | 24.3581 | 368.2069 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.48 | 45.5833 | 613.25 | Average of the hour | 2020-09-19 19:00 | 19:00 | 22.48 | 45.5833 | 613.25 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.88 | 45.8183 | 403.25 | Average of the hour | 2020-09-19 19:00 | 19:00 | 21.88 | 45.8183 | 403.25 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.1567 | 50.795 | 404.5 | Average of the hour | 2020-09-19 19:00 | 19:00 | 22.1567 | 50.795 | 404.5 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 20.8 | 26.25 | 427.2417 | Average of the hour | 2020-09-19 19:00 | 19:00 | 20.8 | 26.25 | 427.2417 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.5 | 28.3258 | 418.275 | Average of the hour | 2020-09-19 19:00 | 19:00 | 21.5 | 28.3258 | 418.275 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.3 |  |  | Average of the hour | 2020-09-19 19:00 | 19:00 | 23.3 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.2 |  |  | Average of the hour | 2020-09-19 19:00 | 19:00 | 20.2 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 19.3242 |  | 426.5667 | Average of the hour | 2020-09-19 19:00 | 19:00 | 19.3242 |  | 426.5667 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 19.784 |  | 380.25 | Average of the hour | 2020-09-19 19:00 | 19:00 | 19.784 |  | 380.25 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-19 19:00 | 19:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-19 19:00 | 19:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.438 | 25.2805 | 432.8678 | Average of the hour | 2020-09-19 19:00 | 19:00 | 22.438 | 25.2805 | 432.8678 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 36.3376 | 688.5258 | Average of the hour | 2020-09-19 19:00 | 19:00 |  | 36.3376 | 688.5258 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.7676 | 24.8162 |  | Average of the hour | 2020-09-19 19:00 | 19:00 | 20.7676 | 24.8162 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 19:00
2020-09-19 | 19:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 19:00 | 19:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 19:00
2020-09-19 | 20:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 14.4417 | 39.75 | 442.45 | Average of the hour | 2020-09-19 20:00 | 20:00 | 14.4417 | 39.75 | 442.45 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 13.7333 | 38.4167 | 546.7917 | Average of the hour | 2020-09-19 20:00 | 20:00 | 13.7333 | 38.4167 | 546.7917 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 15.28 | 33.1342 | 396.8333 | Average of the hour | 2020-09-19 20:00 | 20:00 | 15.28 | 33.1342 | 396.8333 |  | low | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 19.3067 | 27.865 | 394.0833 | Average of the hour | 2020-09-19 20:00 | 20:00 | 19.3067 | 27.865 | 394.0833 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 16.47 | 36.5167 | 435.0833 | Average of the hour | 2020-09-19 20:00 | 20:00 | 16.47 | 36.5167 | 435.0833 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.2408 | 26.465 | 460.4167 | Average of the hour | 2020-09-19 20:00 | 20:00 | 22.2408 | 26.465 | 460.4167 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.3708 | 26.7875 | 425.8333 | Average of the hour | 2020-09-19 20:00 | 20:00 | 24.3708 | 26.7875 | 425.8333 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.6358 | 34.055 | 409.5833 | Average of the hour | 2020-09-19 20:00 | 20:00 | 22.6358 | 34.055 | 409.5833 |  | low | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.5399 | 28.1871 | 483.6488 | Average of the hour | 2020-09-19 20:00 | 20:00 | 22.5399 | 28.1871 | 483.6488 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 26.1899 | 22.9183 | 297.7058 | Average of the hour | 2020-09-19 20:00 | 20:00 | 26.1899 | 22.9183 | 297.7058 | caution | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 25.5572 | 23.5342 | 368.8903 | Average of the hour | 2020-09-19 20:00 | 20:00 | 25.5572 | 23.5342 | 368.8903 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.39 | 45.6383 | 619.3333 | Average of the hour | 2020-09-19 20:00 | 20:00 | 22.39 | 45.6383 | 619.3333 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.7408 | 45.9388 | 408.75 | Average of the hour | 2020-09-19 20:00 | 20:00 | 21.7408 | 45.9388 | 408.75 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.2375 | 50.6317 | 409 | Average of the hour | 2020-09-19 20:00 | 20:00 | 22.2375 | 50.6317 | 409 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 20.7583 | 26.5833 | 427.2833 | Average of the hour | 2020-09-19 20:00 | 20:00 | 20.7583 | 26.5833 | 427.2833 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.5 | 28.51 | 420.3333 | Average of the hour | 2020-09-19 20:00 | 20:00 | 21.5 | 28.51 | 420.3333 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 14.85 |  |  | Average of the hour | 2020-09-19 20:00 | 20:00 | 14.85 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 15.8833 |  |  | Average of the hour | 2020-09-19 20:00 | 20:00 | 15.8833 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 15.4078 |  | 427.5083 | Average of the hour | 2020-09-19 20:00 | 20:00 | 15.4078 |  | 427.5083 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 17.2955 |  | 379.8333 | Average of the hour | 2020-09-19 20:00 | 20:00 | 17.2955 |  | 379.8333 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-19 20:00 | 20:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-19 20:00 | 20:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.4886 | 25.4392 | 434.8813 | Average of the hour | 2020-09-19 20:00 | 20:00 | 22.4886 | 25.4392 | 434.8813 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 36.8948 | 688.3673 | Average of the hour | 2020-09-19 20:00 | 20:00 |  | 36.8948 | 688.3673 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.8901 | 25.2722 |  | Average of the hour | 2020-09-19 20:00 | 20:00 | 20.8901 | 25.2722 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 20:00
2020-09-19 | 20:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 20:00 | 20:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 20:00
2020-09-19 | 21:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 13.775 | 43.75 | 441.7833 | Average of the hour | 2020-09-19 21:00 | 21:00 | 13.775 | 43.75 | 441.7833 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 13.1333 | 40.5833 | 540.125 | Average of the hour | 2020-09-19 21:00 | 21:00 | 13.1333 | 40.5833 | 540.125 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 15.7325 | 40.7692 | 410.5 | Average of the hour | 2020-09-19 21:00 | 21:00 | 15.7325 | 40.7692 | 410.5 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 19.9183 | 33.6958 | 401.9167 | Average of the hour | 2020-09-19 21:00 | 21:00 | 19.9183 | 33.6958 | 401.9167 |  | low | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 16.4333 | 45.2317 | 445.4167 | Average of the hour | 2020-09-19 21:00 | 21:00 | 16.4333 | 45.2317 | 445.4167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.1108 | 29.5133 | 463.75 | Average of the hour | 2020-09-19 21:00 | 21:00 | 22.1108 | 29.5133 | 463.75 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.4508 | 26.7842 | 424.3333 | Average of the hour | 2020-09-19 21:00 | 21:00 | 24.4508 | 26.7842 | 424.3333 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.75 | 36.2475 | 412 | Average of the hour | 2020-09-19 21:00 | 21:00 | 22.75 | 36.2475 | 412 |  | caution | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.5739 | 28.8729 | 484.8227 | Average of the hour | 2020-09-19 21:00 | 21:00 | 22.5739 | 28.8729 | 484.8227 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.8108 | 24.3933 | 299.8301 | Average of the hour | 2020-09-19 21:00 | 21:00 | 25.8108 | 24.3933 | 299.8301 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 25.6345 | 23.8808 | 373.1015 | Average of the hour | 2020-09-19 21:00 | 21:00 | 25.6345 | 23.8808 | 373.1015 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.34 | 45.4454 | 618.25 | Average of the hour | 2020-09-19 21:00 | 21:00 | 22.34 | 45.4454 | 618.25 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.7242 | 45.8608 | 412.5 | Average of the hour | 2020-09-19 21:00 | 21:00 | 21.7242 | 45.8608 | 412.5 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.1292 | 50.83 | 418.5833 | Average of the hour | 2020-09-19 21:00 | 21:00 | 22.1292 | 50.83 | 418.5833 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 17.8333 | 29.375 | 452.1583 | Average of the hour | 2020-09-19 21:00 | 21:00 | 17.8333 | 29.375 | 452.1583 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 20.3333 | 28.1442 | 424.3667 | Average of the hour | 2020-09-19 21:00 | 21:00 | 20.3333 | 28.1442 | 424.3667 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 11.7333 |  |  | Average of the hour | 2020-09-19 21:00 | 21:00 | 11.7333 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 13.6667 |  |  | Average of the hour | 2020-09-19 21:00 | 21:00 | 13.6667 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 13.1357 |  | 452.4917 | Average of the hour | 2020-09-19 21:00 | 21:00 | 13.1357 |  | 452.4917 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 14.4771 |  | 379.5833 | Average of the hour | 2020-09-19 21:00 | 21:00 | 14.4771 |  | 379.5833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-19 21:00 | 21:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-19 21:00 | 21:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.5119 | 25.8659 | 445.1545 | Average of the hour | 2020-09-19 21:00 | 21:00 | 22.5119 | 25.8659 | 445.1545 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 37.2834 | 688.2437 | Average of the hour | 2020-09-19 21:00 | 21:00 |  | 37.2834 | 688.2437 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.8313 | 25.5116 |  | Average of the hour | 2020-09-19 21:00 | 21:00 | 20.8313 | 25.5116 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 21:00
2020-09-19 | 21:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 21:00 | 21:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 21:00
2020-09-19 | 22:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 13.5333 | 45.9583 | 451.65 | Average of the hour | 2020-09-19 22:00 | 22:00 | 13.5333 | 45.9583 | 451.65 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 12.05 | 44.625 | 548.25 | Average of the hour | 2020-09-19 22:00 | 22:00 | 12.05 | 44.625 | 548.25 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 15.2475 | 45.4917 | 411.8333 | Average of the hour | 2020-09-19 22:00 | 22:00 | 15.2475 | 45.4917 | 411.8333 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 19.7475 | 36.7925 | 402.6667 | Average of the hour | 2020-09-19 22:00 | 22:00 | 19.7475 | 36.7925 | 402.6667 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 16.1742 | 48.8033 | 443.9167 | Average of the hour | 2020-09-19 22:00 | 22:00 | 16.1742 | 48.8033 | 443.9167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.505 | 31.19 | 462.75 | Average of the hour | 2020-09-19 22:00 | 22:00 | 22.505 | 31.19 | 462.75 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.4758 | 28.2837 | 425.0833 | Average of the hour | 2020-09-19 22:00 | 22:00 | 24.4758 | 28.2837 | 425.0833 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.7592 | 36.8108 | 412.8333 | Average of the hour | 2020-09-19 22:00 | 22:00 | 22.7592 | 36.8108 | 412.8333 |  | caution | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.6502 | 29.1599 | 484.2398 | Average of the hour | 2020-09-19 22:00 | 22:00 | 22.6502 | 29.1599 | 484.2398 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.8426 | 23.8441 | 299.7452 | Average of the hour | 2020-09-19 22:00 | 22:00 | 25.8426 | 23.8441 | 299.7452 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 24.5299 | 24.2771 | 370.918 | Average of the hour | 2020-09-19 22:00 | 22:00 | 24.5299 | 24.2771 | 370.918 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.3225 | 45.5012 | 623.1667 | Average of the hour | 2020-09-19 22:00 | 22:00 | 22.3225 | 45.5012 | 623.1667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.5767 | 45.3392 | 410.5833 | Average of the hour | 2020-09-19 22:00 | 22:00 | 21.5767 | 45.3392 | 410.5833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.0975 | 50.0329 | 418 | Average of the hour | 2020-09-19 22:00 | 22:00 | 22.0975 | 50.0329 | 418 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 15.7083 | 33.6667 | 458.0583 | Average of the hour | 2020-09-19 22:00 | 22:00 | 15.7083 | 33.6667 | 458.0583 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 18.9583 | 29.6642 | 426.35 | Average of the hour | 2020-09-19 22:00 | 22:00 | 18.9583 | 29.6642 | 426.35 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 11.0667 |  |  | Average of the hour | 2020-09-19 22:00 | 22:00 | 11.0667 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 13.25 |  |  | Average of the hour | 2020-09-19 22:00 | 22:00 | 13.25 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 12.4376 |  | 458.5667 | Average of the hour | 2020-09-19 22:00 | 22:00 | 12.4376 |  | 458.5667 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 13.0557 |  | 380.4167 | Average of the hour | 2020-09-19 22:00 | 22:00 | 13.0557 |  | 380.4167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-19 22:00 | 22:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-19 22:00 | 22:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.5453 | 26.4272 | 454.9783 | Average of the hour | 2020-09-19 22:00 | 22:00 | 22.5453 | 26.4272 | 454.9783 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 37.3003 | 687.603 | Average of the hour | 2020-09-19 22:00 | 22:00 |  | 37.3003 | 687.603 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9612 | 25.4776 |  | Average of the hour | 2020-09-19 22:00 | 22:00 | 20.9612 | 25.4776 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 22:00
2020-09-19 | 22:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 22:00 | 22:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 22:00
2020-09-19 | 23:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 13.3167 | 47.375 | 458.4833 | Average of the hour | 2020-09-19 23:00 | 23:00 | 13.3167 | 47.375 | 458.4833 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 11.6333 | 47.5 | 558.5833 | Average of the hour | 2020-09-19 23:00 | 23:00 | 11.6333 | 47.5 | 558.5833 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 14.9058 | 44.695 | 412.5833 | Average of the hour | 2020-09-19 23:00 | 23:00 | 14.9058 | 44.695 | 412.5833 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 19.58 | 35.8425 | 401.4167 | Average of the hour | 2020-09-19 23:00 | 23:00 | 19.58 | 35.8425 | 401.4167 |  | caution | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 15.96 | 47.8183 | 443.8333 | Average of the hour | 2020-09-19 23:00 | 23:00 | 15.96 | 47.8183 | 443.8333 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.9333 | 31.5633 | 461 | Average of the hour | 2020-09-19 23:00 | 23:00 | 22.9333 | 31.5633 | 461 |  | low | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.455 | 28.9992 | 426.5 | Average of the hour | 2020-09-19 23:00 | 23:00 | 24.455 | 28.9992 | 426.5 |  | low | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.6917 | 36.8879 | 415.3333 | Average of the hour | 2020-09-19 23:00 | 23:00 | 22.6917 | 36.8879 | 415.3333 |  | caution | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.6502 | 29.6527 | 484.1677 | Average of the hour | 2020-09-19 23:00 | 23:00 | 22.6502 | 29.6527 | 484.1677 |  | low | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.6202 | 24.5987 | 300.857 | Average of the hour | 2020-09-19 23:00 | 23:00 | 25.6202 | 24.5987 | 300.857 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.7856 | 25.15 | 374.0033 | Average of the hour | 2020-09-19 23:00 | 23:00 | 23.7856 | 25.15 | 374.0033 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.2 | 45.8108 | 634.3333 | Average of the hour | 2020-09-19 23:00 | 23:00 | 22.2 | 45.8108 | 634.3333 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.5133 | 45.5129 | 418.3333 | Average of the hour | 2020-09-19 23:00 | 23:00 | 21.5133 | 45.5129 | 418.3333 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.9567 | 49.7875 | 424.1667 | Average of the hour | 2020-09-19 23:00 | 23:00 | 21.9567 | 49.7875 | 424.1667 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 14.8083 | 38.5417 | 462.6333 | Average of the hour | 2020-09-19 23:00 | 23:00 | 14.8083 | 38.5417 | 462.6333 |  | caution | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 18.3333 | 32.2483 | 430.65 | Average of the hour | 2020-09-19 23:00 | 23:00 | 18.3333 | 32.2483 | 430.65 |  | low | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 10.5917 |  |  | Average of the hour | 2020-09-19 23:00 | 23:00 | 10.5917 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 12.975 |  |  | Average of the hour | 2020-09-19 23:00 | 23:00 | 12.975 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 12.0966 |  | 462.975 | Average of the hour | 2020-09-19 23:00 | 23:00 | 12.0966 |  | 462.975 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 12.4214 |  | 379.25 | Average of the hour | 2020-09-19 23:00 | 23:00 | 12.4214 |  | 379.25 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-19 23:00 | 23:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-19 23:00 | 23:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.5685 | 26.8285 | 461.9013 | Average of the hour | 2020-09-19 23:00 | 23:00 | 22.5685 | 26.8285 | 461.9013 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 37.1756 | 687.6025 | Average of the hour | 2020-09-19 23:00 | 23:00 |  | 37.1756 | 687.6025 |  | caution | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 20.9542 | 25.6406 |  | Average of the hour | 2020-09-19 23:00 | 23:00 | 20.9542 | 25.6406 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-19-2020 23:00
2020-09-19 | 23:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-19 23:00 | 23:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-19-2020 23:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Library | [5 empty] | 21.1111 | 42 | 482 |  | 2020-09-17 09:00 | 9:00 | 21.1111 | 42 | 482 |  |  | 2020-09-14 | B10246¦Library¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 20 | 38 | 455 | Justice Wilcox Chambers | 2020-09-17 09:00 | 9:00 | 20 | 38 | 455 |  | caution | 2020-09-14 | B10246¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | 2nd fl lobby | [5 empty] | 21.6667 | 36 | 453 | Middle of hallway | 2020-09-17 09:00 | 9:00 | 21.6667 | 36 | 453 |  | caution | 2020-09-14 | B10246¦2nd fl lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 2 | [5 empty] | 20.5556 | 38 | 458 |  | 2020-09-17 09:00 | 9:00 | 20.5556 | 38 | 458 |  | caution | 2020-09-14 | B10246¦Courtroom 2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Trial Co-ordinators Office | [5 empty] | 21.1111 | 35 | 507 |  | 2020-09-17 09:00 | 9:00 | 21.1111 | 35 | 507 |  | caution | 2020-09-14 | B10246¦Trial Co-ordinators Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Main Floor Entrance Lobby | [5 empty] | 20.5556 | 34 | 460 | Middle of hallway | 2020-09-17 09:00 | 9:00 | 20.5556 | 34 | 460 |  | low | 2020-09-14 | B10246¦Main Floor Entrance Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 20.5556 | 37 | 464 | Office to the left of office 10 | 2020-09-17 09:00 | 9:00 | 20.5556 | 37 | 464 |  | caution | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 20 | 38 | 456 | Office to the right of office 10 | 2020-09-17 09:00 | 9:00 | 20 | 38 | 456 |  | caution | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Lobby | [5 empty] | 20 | 45 | 559 |  | 2020-09-17 09:00 | 9:00 | 20 | 45 | 559 |  |  | 2020-09-14 | B10002¦Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Outdoors |  |  | 7 | 61 | 368 |  |  |  | North entrance - partly cloudy, light breeze | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B13049¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 2nd fl lobby | [5 empty] | 18 | 41 | 431 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 18 | 41 | 431 |  |  | 2020-09-14 | B13049¦2nd fl lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 250 | [5 empty] | 20 | 35 | 389 | No windows, no plants | 2020-09-17 09:00 | 9:00 | 20 | 35 | 389 |  | caution | 2020-09-14 | B13049¦Courtroom 250¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Skeggs | [5 empty] | 21 | 43 | 564 | Door Open | 2020-09-17 09:00 | 9:00 | 21 | 43 | 564 |  |  | 2020-09-14 | B10002¦Office Skeggs¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Administration office | [5 empty] | 21 | 33 | 423 | Windows closed, 4 plants total at various locations | 2020-09-17 09:00 | 9:00 | 21 | 33 | 423 |  | low | 2020-09-14 | B13049¦Administration office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Cubicle Office | [5 empty] | 22 | 42 | 602 | Door Open | 2020-09-17 09:00 | 9:00 | 22 | 42 | 602 |  |  | 2020-09-14 | B10002¦Cubicle Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 1 (Center) | [5 empty] | 20 | 33 | 439 |  | 2020-09-17 09:00 | 9:00 | 20 | 33 | 439 |  | low | 2020-09-14 | B10246¦Courtroom 1 (Center)¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 1st Floor Lobby next to courtroom 122 | [5 empty] | 22 | 31 | 410 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 22 | 31 | 410 |  | low | 2020-09-14 | B13049¦1st Floor Lobby next to courtroom 122¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown attorney admin area | [5 empty] | 20.5556 | 38 | 540 |  | 2020-09-17 09:00 | 9:00 | 20.5556 | 38 | 540 |  | caution | 2020-09-14 | B10246¦Crown attorney admin area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | File Room | [5 empty] | 22 | 40 | 570 |  | 2020-09-17 09:00 | 9:00 | 22 | 40 | 570 |  | caution | 2020-09-14 | B10002¦File Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Administration office | [5 empty] | 20.5556 | 35 | 506 |  | 2020-09-17 09:00 | 9:00 | 20.5556 | 35 | 506 |  | caution | 2020-09-14 | B10246¦Administration office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 122 | [5 empty] | 21 | 31 | 426 | No windows, no plants | 2020-09-17 09:00 | 9:00 | 21 | 31 | 426 |  | low | 2020-09-14 | B13049¦Courtroom 122¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 21.1111 | 35 | 467 | Basement lobby - bottom of the stairs | 2020-09-17 09:00 | 9:00 | 21.1111 | 35 | 467 |  | caution | 2020-09-14 | B10246¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 20.5556 | 37 | 462 | Basement cells - hallway | 2020-09-17 09:00 | 9:00 | 20.5556 | 37 | 462 |  | caution | 2020-09-14 | B10246¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Didiodato | [5 empty] | 22 | 41 | 607 | Door Open | 2020-09-17 09:00 | 9:00 | 22 | 41 | 607 |  |  | 2020-09-14 | B10002¦Office Didiodato¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Outdoors |  |  | 11.1111 | 31 | 407 |  |  |  | Directly outside main entrance: clear and sunny | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10246¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Outdoors |  |  | 16 | 33 | 405 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10002¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Court Security office #142 | [5 empty] | 23 | 30 | 450 | No windows, no plants | 2020-09-17 09:00 | 9:00 | 23 | 30 | 450 |  | low | 2020-09-14 | B13049¦Court Security office #142¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Lobby Administration | [5 empty] | 16 | 56 | 446 |  | 2020-09-17 09:00 | 9:00 | 16 | 56 | 446 |  |  | 2020-09-14 | B10003¦Lobby Administration¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 140 | [5 empty] | 22 | 30 | 424 | No windows, no plants | 2020-09-17 09:00 | 9:00 | 22 | 30 | 424 |  | low | 2020-09-14 | B13049¦Courtroom 140¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Library | [5 empty] | 17 | 54 | 463 | Wall mount AC unit running | 2020-09-17 09:00 | 9:00 | 17 | 54 | 463 |  |  | 2020-09-14 | B10003¦Library¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 20 | 59 | 497 | north section | 2020-09-17 09:00 | 9:00 | 20 | 59 | 497 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 20 | 59 | 488 | south section | 2020-09-17 09:00 | 9:00 | 20 | 59 | 488 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 1st floor cell holding area Hallway | [5 empty] | 21 | 30 | 443 | Across from door #3 - no windows, no plants | 2020-09-17 09:00 | 9:00 | 21 | 30 | 443 |  | low | 2020-09-14 | B13049¦1st floor cell holding area Hallway¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 1E | [5 empty] | 20 | 58 | 486 | ground floor | 2020-09-17 09:00 | 9:00 | 20 | 58 | 486 |  |  | 2020-09-14 | B14164¦Hallway by courtroom 1E¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 20 | 60 | 479 | north section | 2020-09-17 09:00 | 9:00 | 20 | 60 | 479 |  | caution | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Basement Library | [5 empty] | 17 | 53 | 420 |  | 2020-09-17 09:00 | 9:00 | 17 | 53 | 420 |  |  | 2020-09-14 | B10003¦Basement Library¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 20 | 60 | 460 | south section | 2020-09-17 09:00 | 9:00 | 20 | 60 | 460 |  | caution | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by Courtoom 6 | [5 empty] | 20 | 60 | 473 | second floor | 2020-09-17 09:00 | 9:00 | 20 | 60 | 473 |  | caution | 2020-09-14 | B14164¦Hallway by Courtoom 6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtoom 10 | [5 empty] | 20 | 60 | 482 | North section | 2020-09-17 09:00 | 9:00 | 20 | 60 | 482 |  | caution | 2020-09-14 | B14164¦Courtoom 10¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 21 | 59 | 478 | south section | 2020-09-17 09:00 | 9:00 | 21 | 59 | 478 |  |  | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Outdoors |  |  | 15 | 70 | 451 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10639¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 10 | [5 empty] | 21 | 57 | 447 | basement | 2020-09-17 09:00 | 9:00 | 21 | 57 | 447 |  |  | 2020-09-14 | B14164¦Hallway by courtroom 10¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown Attorney Office | [5 empty] | 23 | 31 | 617 | Office #1 - east side - window closed, no plants | 2020-09-17 09:00 | 9:00 | 23 | 31 | 617 |  | low | 2020-09-14 | B13049¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Outdoors |  |  | 16 | 33 | 398 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10003¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, basement | [5 empty] | 21 | 59 | 520 |  | 2020-09-17 09:00 | 9:00 | 21 | 59 | 520 |  |  | 2020-09-14 | B14164¦Common area by elevator, basement¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, ground floor | [5 empty] | 21 | 56 | 493 |  | 2020-09-17 09:00 | 9:00 | 21 | 56 | 493 |  |  | 2020-09-14 | B14164¦Common area by elevator, ground floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Family office, Ground floor | [5 empty] | 21 | 57 | 563 |  | 2020-09-17 09:00 | 9:00 | 21 | 57 | 563 |  |  | 2020-09-14 | B14164¦Family office, Ground floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 6 North side | [5 empty] | 21 | 53 | 470 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 470 |  |  | 2020-09-14 | B10639¦courtroom 6 North side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Family office, ground floor | [5 empty] | 21 | 58 | 557 |  | 2020-09-17 09:00 | 9:00 | 21 | 58 | 557 |  |  | 2020-09-14 | B14164¦Family office, ground floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown Attorney Office | [5 empty] | 22 | 30 | 521 | Office #2 - north side - windows closed, no plants | 2020-09-17 09:00 | 9:00 | 22 | 30 | 521 |  | low | 2020-09-14 | B13049¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 60 | 483 | east | 2020-09-17 09:00 | 9:00 | 22 | 60 | 483 |  | caution | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 6 south | [5 empty] | 21 | 53 | 470 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 470 |  |  | 2020-09-14 | B10639¦courtroom 6 south¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 60 | 473 | west | 2020-09-17 09:00 | 9:00 | 22 | 60 | 473 |  | caution | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, second floor | [5 empty] | 21 | 56 | 511 |  | 2020-09-17 09:00 | 9:00 | 21 | 56 | 511 |  |  | 2020-09-14 | B14164¦Common area by elevator, second floor¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown attorney admin area | [5 empty] | 23 | 29 | 512 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 23 | 29 | 512 |  | low | 2020-09-14 | B13049¦Crown attorney admin area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 21 | 60 | 481 | east | 2020-09-17 09:00 | 9:00 | 21 | 60 | 481 |  | caution | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Outdoors |  |  | 19 | 57 | 423 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B14164¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 21 | 60 | 479 | west | 2020-09-17 09:00 | 9:00 | 21 | 60 | 479 |  | caution | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 21 | 60 | 496 | east | 2020-09-17 09:00 | 9:00 | 21 | 60 | 496 |  | caution | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 6 | [5 empty] | 21 | 53 | 468 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 468 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 21 | 60 | 485 | west | 2020-09-17 09:00 | 9:00 | 21 | 60 | 485 |  | caution | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 5 North side | [5 empty] | 21 | 56 | 506 |  | 2020-09-17 09:00 | 9:00 | 21 | 56 | 506 |  |  | 2020-09-14 | B10639¦courtroom 5 North side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 5 South side | [5 empty] | 21 | 55 | 490 |  | 2020-09-17 09:00 | 9:00 | 21 | 55 | 490 |  |  | 2020-09-14 | B10639¦courtroom 5 South side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 5 | [5 empty] | 21 | 54 | 515 |  | 2020-09-17 09:00 | 9:00 | 21 | 54 | 515 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 5¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 3 south east side | [5 empty] | 20 | 62 | 510 |  | 2020-09-17 09:00 | 9:00 | 20 | 62 | 510 |  | caution | 2020-09-14 | B10639¦courtroom 3 south east side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 3 northeast side | [5 empty] | 20 | 59 | 484 |  | 2020-09-17 09:00 | 9:00 | 20 | 59 | 484 |  |  | 2020-09-14 | B10639¦courtroom 3 northeast side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 21 | 60 | 511 | east | 2020-09-17 09:00 | 9:00 | 21 | 60 | 511 |  | caution | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | hallway by courtroom 3 | [5 empty] | 20 | 57 | 485 |  | 2020-09-17 09:00 | 9:00 | 20 | 57 | 485 |  |  | 2020-09-14 | B10639¦hallway by courtroom 3¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 22 | 60 | 480 | west | 2020-09-17 09:00 | 9:00 | 22 | 60 | 480 |  | caution | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Outdoors |  |  | 12 | 37 | 411 |  |  |  | Window closed, no plants | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B13095¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 58 | 470 | east | 2020-09-17 09:00 | 9:00 | 22 | 58 | 470 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | lobby by statue | [5 empty] | 21 | 53 | 459 |  | 2020-09-17 09:00 | 9:00 | 21 | 53 | 459 |  |  | 2020-09-14 | B10639¦lobby by statue¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Hallway | [5 empty] | 21 | 34 | 446 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 21 | 34 | 446 |  | low | 2020-09-14 | B13095¦Hallway¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby East Side | [5 empty] | 21 | 52 | 510 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 510 |  |  | 2020-09-14 | B10639¦Entrance Lobby East Side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 58 | 476 | west | 2020-09-17 09:00 | 9:00 | 22 | 58 | 476 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 58 | 480 | east | 2020-09-17 09:00 | 9:00 | 22 | 58 | 480 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby West Side | [5 empty] | 21 | 52 | 510 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 510 |  |  | 2020-09-14 | B10639¦Entrance Lobby West Side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 58 | 487 | west | 2020-09-17 09:00 | 9:00 | 22 | 58 | 487 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by COA intake office | [5 empty] | 21 | 52 | 548 |  | 2020-09-17 09:00 | 9:00 | 21 | 52 | 548 |  |  | 2020-09-14 | B10639¦Hallway by COA intake office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by Law Society of Ontario | [5 empty] | 21 | 51 | 480 |  | 2020-09-17 09:00 | 9:00 | 21 | 51 | 480 |  |  | 2020-09-14 | B10639¦Hallway by Law Society of Ontario¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Outdoors |  |  | 17 | 66 | 448 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20265¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 59 | 484 | east | 2020-09-17 09:00 | 9:00 | 21 | 59 | 484 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | office - B04A | [5 empty] | 21 | 34 | 566 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 21 | 34 | 566 |  | low | 2020-09-14 | B13095¦office - B04A¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 59 | 484 | west | 2020-09-17 09:00 | 9:00 | 21 | 59 | 484 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 north side | [5 empty] | 22 | 51 | 475 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 475 |  |  | 2020-09-14 | B20265¦courtroom M1 north side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 south side | [5 empty] | 22 | 51 | 465 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 465 |  |  | 2020-09-14 | B20265¦courtroom M1 south side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 21 | 59 | 482 | east | 2020-09-17 09:00 | 9:00 | 21 | 59 | 482 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by Courtroom M1 | [5 empty] | 22 | 53 | 482 |  | 2020-09-17 09:00 | 9:00 | 22 | 53 | 482 |  |  | 2020-09-14 | B20265¦hallway by Courtroom M1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 21 | 58 | 494 | east | 2020-09-17 09:00 | 9:00 | 21 | 58 | 494 |  |  | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 21 | 59 | 482 |  | 2020-09-17 09:00 | 9:00 | 21 | 59 | 482 |  |  | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom J south side | [5 empty] | 22 | 50 | 477 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 477 |  |  | 2020-09-14 | B20265¦courtroom J south side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Main Lobby | [5 empty] | 22 | 35 | 579 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 22 | 35 | 579 |  | caution | 2020-09-14 | B13095¦Main Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom J north side | [5 empty] | 22 | 50 | 473 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 473 |  |  | 2020-09-14 | B20265¦courtroom J north side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 21 | 59 | 501 | east | 2020-09-17 09:00 | 9:00 | 21 | 59 | 501 |  |  | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 21 | 60 | 512 | west | 2020-09-17 09:00 | 9:00 | 21 | 60 | 512 |  | caution | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom J | [5 empty] | 22 | 50 | 496 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 496 |  |  | 2020-09-14 | B20265¦hallway by courtroom J¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G south side | [5 empty] | 23 | 59 | 493 |  | 2020-09-17 09:00 | 9:00 | 23 | 59 | 493 |  |  | 2020-09-14 | B20265¦courtroom G south side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 21 | 54 | 500 | east | 2020-09-17 09:00 | 9:00 | 21 | 54 | 500 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 21 | 54 | 505 | west | 2020-09-17 09:00 | 9:00 | 21 | 54 | 505 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G north side | [5 empty] | 22 | 50 | 499 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 499 |  |  | 2020-09-14 | B20265¦courtroom G north side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 59 | 495 | east | 2020-09-17 09:00 | 9:00 | 21 | 59 | 495 |  |  | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 121 west side | [5 empty] | 22 | 47 | 460 |  | 2020-09-17 09:00 | 9:00 | 22 | 47 | 460 |  |  | 2020-09-14 | B20265¦courtroom 121 west side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 59 | 480 | west | 2020-09-17 09:00 | 9:00 | 21 | 59 | 480 |  |  | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 121 East side | [5 empty] | 22 | 47 | 463 |  | 2020-09-17 09:00 | 9:00 | 22 | 47 | 463 |  |  | 2020-09-14 | B20265¦courtroom 121 East side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Outdoors |  |  | 19 | 61 | 489 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B91122¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 123 east side | [5 empty] | 22 | 50 | 470 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 470 |  |  | 2020-09-14 | B20265¦courtroom 123 east side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 123 west side | [5 empty] | 22 | 49 | 461 |  | 2020-09-17 09:00 | 9:00 | 22 | 49 | 461 |  |  | 2020-09-14 | B20265¦courtroom 123 west side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 east side | [5 empty] | 22 | 51 | 485 |  | 2020-09-17 09:00 | 9:00 | 22 | 51 | 485 |  |  | 2020-09-14 | B20265¦courtroom 124 east side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 west side | [5 empty] | 22 | 50 | 485 |  | 2020-09-17 09:00 | 9:00 | 22 | 50 | 485 |  |  | 2020-09-14 | B20265¦courtroom 124 west side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Outdoors |  |  | 7 | 55 | 417 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B12955¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 125 south side | [5 empty] | 22 | 47 | 465 |  | 2020-09-17 09:00 | 9:00 | 22 | 47 | 465 |  |  | 2020-09-14 | B20265¦courtroom 125 south side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Main Floor Entrance Lobby | [5 empty] | 9 | 60 | 456 | front lobby | 2020-09-17 09:00 | 9:00 | 9 | 60 | 456 |  | caution | 2020-09-14 | B12955¦Main Floor Entrance Lobby¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 125 north side | [5 empty] | 21 | 49 | 457 |  | 2020-09-17 09:00 | 9:00 | 21 | 49 | 457 |  |  | 2020-09-14 | B20265¦courtroom 125 north side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | OTHER | [5 empty] | 11 | 69 | 494 | waiting room | 2020-09-17 09:00 | 9:00 | 11 | 69 | 494 |  | high | 2020-09-14 | B12955¦OTHER¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 126 south side | [5 empty] | 22 | 47 | 473 |  | 2020-09-17 09:00 | 9:00 | 22 | 47 | 473 |  |  | 2020-09-14 | B20265¦courtroom 126 south side¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Administration office | [5 empty] | 15 | 64 | 505 |  | 2020-09-17 09:00 | 9:00 | 15 | 64 | 505 |  | caution | 2020-09-14 | B12955¦Administration office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 203 | [5 empty] | 18 | 53 | 452 |  | 2020-09-17 09:00 | 9:00 | 18 | 53 | 452 |  |  | 2020-09-14 | B12955¦Courtroom 203¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom 126 | [5 empty] | 23 | 49 | 483 |  | 2020-09-17 09:00 | 9:00 | 23 | 49 | 483 |  |  | 2020-09-14 | B20265¦hallway by courtroom 126¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 103 | [5 empty] | 17 | 56 | 418 |  | 2020-09-17 09:00 | 9:00 | 17 | 56 | 418 |  |  | 2020-09-14 | B12955¦Courtroom 103¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by receiving | [5 empty] | 20 | 61 | 555 |  | 2020-09-17 09:00 | 9:00 | 20 | 61 | 555 |  | caution | 2020-09-14 | B20265¦hallway by receiving¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Outdoors |  |  | 20 | 50 | 440 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10639¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 6 north side | [5 empty] | 21 | 50 | 443 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 443 |  |  | 2020-09-14 | B10639¦courtroom 6 north side¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Lunch Room | [5 empty] | 23 | 54 | 489 |  | 2020-09-17 09:00 | 9:00 | 23 | 54 | 489 |  |  | 2020-09-14 | B70451¦Lunch Room¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 23 | 54 | 504 | east | 2020-09-17 09:00 | 9:00 | 23 | 54 | 504 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 6 south side | [5 empty] | 21 | 48 | 443 |  | 2020-09-17 12:00 | 12:00 | 21 | 48 | 443 |  |  | 2020-09-14 | B10639¦courtroom 6 south side¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 23 | 54 | 497 | west | 2020-09-17 09:00 | 9:00 | 23 | 54 | 497 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 6 | [5 empty] | 21 | 49 | 458 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 458 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 6¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 602 | [5 empty] | 23 | 55 | 511 |  | 2020-09-17 09:00 | 9:00 | 23 | 55 | 511 |  |  | 2020-09-14 | B70451¦hallway by courtroom 602¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 5 North side | [5 empty] | 21 | 49 | 445 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 445 |  |  | 2020-09-14 | B10639¦courtroom 5 North side¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 603 | [5 empty] | 23 | 55 | 509 |  | 2020-09-17 09:00 | 9:00 | 23 | 55 | 509 |  |  | 2020-09-14 | B70451¦hallway by courtroom 603¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | conference room 4 | [5 empty] | 23 | 54 | 488 |  | 2020-09-17 09:00 | 9:00 | 23 | 54 | 488 |  |  | 2020-09-14 | B70451¦conference room 4¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Lobby | [5 empty] | 23 | 32 | 583 |  | 2020-09-17 12:00 | 12:00 | 23 | 32 | 583 |  | low | 2020-09-14 | B10002¦Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 5 south side | [5 empty] | 21 | 48 | 440 |  | 2020-09-17 12:00 | 12:00 | 21 | 48 | 440 |  |  | 2020-09-14 | B10639¦courtroom 5 south side¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 56 | 496 | east | 2020-09-17 09:00 | 9:00 | 23 | 56 | 496 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 56 | 475 | west | 2020-09-17 09:00 | 9:00 | 23 | 56 | 475 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 5 | [5 empty] | 21 | 48 | 443 |  | 2020-09-17 12:00 | 12:00 | 21 | 48 | 443 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 5¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 607 | [5 empty] | 23 | 56 | 484 |  | 2020-09-17 09:00 | 9:00 | 23 | 56 | 484 |  |  | 2020-09-14 | B70451¦hallway by courtroom 607¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 3 southeast side | [5 empty] | 22 | 49 | 457 |  | 2020-09-17 12:00 | 12:00 | 22 | 49 | 457 |  |  | 2020-09-14 | B10639¦courtroom 3 southeast side¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | enforcement/finance office | [5 empty] | 23 | 55 | 509 |  | 2020-09-17 09:00 | 9:00 | 23 | 55 | 509 |  |  | 2020-09-14 | B70451¦enforcement/finance office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Skeggs | [5 empty] | 22 | 34 | 615 | Door Open | 2020-09-17 12:00 | 12:00 | 22 | 34 | 615 |  | low | 2020-09-14 | B10002¦Office Skeggs¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 22 | 57 | 487 | east | 2020-09-17 09:00 | 9:00 | 22 | 57 | 487 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 3 northeast side | [5 empty] | 22 | 49 | 453 |  | 2020-09-17 12:00 | 12:00 | 22 | 49 | 453 |  |  | 2020-09-14 | B10639¦courtroom 3 northeast side¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 22 | 57 | 475 | west | 2020-09-17 09:00 | 9:00 | 22 | 57 | 475 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 605 | [5 empty] | 22 | 57 | 485 |  | 2020-09-17 09:00 | 9:00 | 22 | 57 | 485 |  |  | 2020-09-14 | B70451¦hallway by courtroom 605¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | hallway by courtroom 3 | [5 empty] | 22 | 49 | 478 |  | 2020-09-17 12:00 | 12:00 | 22 | 49 | 478 |  |  | 2020-09-14 | B10639¦hallway by courtroom 3¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters administration office | [5 empty] | 23 | 54 | 492 |  | 2020-09-17 09:00 | 9:00 | 23 | 54 | 492 |  |  | 2020-09-14 | B70451¦masters administration office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | lobby by statue | [5 empty] | 21 | 53 | 463 |  | 2020-09-17 12:00 | 12:00 | 21 | 53 | 463 |  |  | 2020-09-14 | B10639¦lobby by statue¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-10 | [5 empty] | 23 | 54 | 483 |  | 2020-09-17 09:00 | 9:00 | 23 | 54 | 483 |  |  | 2020-09-14 | B70451¦room 6-10¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-9 | [5 empty] | 22 | 55 | 495 |  | 2020-09-17 09:00 | 9:00 | 22 | 55 | 495 |  |  | 2020-09-14 | B70451¦room 6-9¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby East Side | [5 empty] | 21 | 52 | 473 |  | 2020-09-17 12:00 | 12:00 | 21 | 52 | 473 |  |  | 2020-09-14 | B10639¦Entrance Lobby East Side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Cubicle Office | [5 empty] | 23 | 31 | 599 | Door Open | 2020-09-17 12:00 | 12:00 | 23 | 31 | 599 |  | low | 2020-09-14 | B10002¦Cubicle Office¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters library | [5 empty] | 22 | 55 | 485 |  | 2020-09-17 09:00 | 9:00 | 22 | 55 | 485 |  |  | 2020-09-14 | B70451¦masters library¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby West Side | [5 empty] | 21 | 52 | 510 |  | 2020-09-17 12:00 | 12:00 | 21 | 52 | 510 |  |  | 2020-09-14 | B10639¦Entrance Lobby West Side¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-4 | [5 empty] | 23 | 52 | 490 |  | 2020-09-17 09:00 | 9:00 | 23 | 52 | 490 |  |  | 2020-09-14 | B70451¦room 6-4¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | reception area-masters | [5 empty] | 23 | 55 | 493 |  | 2020-09-17 09:00 | 9:00 | 23 | 55 | 493 |  |  | 2020-09-14 | B70451¦reception area-masters¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by COA intake office | [5 empty] | 21 | 51 | 480 |  | 2020-09-17 12:00 | 12:00 | 21 | 51 | 480 |  |  | 2020-09-14 | B10639¦Hallway by COA intake office¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Outdoors |  |  | 19 | 61 | 489 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70451¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by Law Society of Ontario | [5 empty] | 21 | 50 | 470 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 470 |  |  | 2020-09-14 | B10639¦Hallway by Law Society of Ontario¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Library | [5 empty] | 21.1111 | 37 | 507 |  | 2020-09-17 12:00 | 12:00 | 21.1111 | 37 | 507 |  | caution | 2020-09-14 | B10246¦Library¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Outdoors |  |  | 18 | 60 | 438 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20265¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | File Room | [5 empty] | 23 | 34 | 605 |  | 2020-09-17 12:00 | 12:00 | 23 | 34 | 605 |  | low | 2020-09-14 | B10002¦File Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Lunch Room | [5 empty] | 23 | 53 | 528 |  | 2020-09-17 12:00 | 12:00 | 23 | 53 | 528 |  |  | 2020-09-14 | B70451¦Lunch Room¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 north side | [5 empty] | 22 | 51 | 526 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 526 |  |  | 2020-09-14 | B20265¦courtroom M1 north side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 23 | 53 | 507 | east | 2020-09-17 12:00 | 12:00 | 23 | 53 | 507 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | OTHER | [5 empty] | 21.1111 | 33 | 480 | Justice Wilcox Chambers | 2020-09-17 12:00 | 12:00 | 21.1111 | 33 | 480 |  | low | 2020-09-14 | B10246¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 22 | 53 | 500 | west | 2020-09-17 12:00 | 12:00 | 22 | 53 | 500 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 602 | [5 empty] | 23 | 53 | 513 |  | 2020-09-17 12:00 | 12:00 | 23 | 53 | 513 |  |  | 2020-09-14 | B70451¦hallway by courtroom 602¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 south side | [5 empty] | 22 | 50 | 533 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 533 |  |  | 2020-09-14 | B20265¦courtroom M1 south side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 603 | [5 empty] | 23 | 52 | 514 |  | 2020-09-17 12:00 | 12:00 | 23 | 52 | 514 |  |  | 2020-09-14 | B70451¦hallway by courtroom 603¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by Courtroom M1 | [5 empty] | 22 | 52 | 520 |  | 2020-09-17 12:00 | 12:00 | 22 | 52 | 520 |  |  | 2020-09-14 | B20265¦hallway by Courtroom M1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Didiodato | [5 empty] | 22 | 36 | 651 | Door Open | 2020-09-17 12:00 | 12:00 | 22 | 36 | 651 |  | caution | 2020-09-14 | B10002¦Office Didiodato¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | 2nd fl lobby | [5 empty] | 21.1111 | 32 | 474 | Middle of hallway | 2020-09-17 12:00 | 12:00 | 21.1111 | 32 | 474 |  | low | 2020-09-14 | B10246¦2nd fl lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom J south side | [5 empty] | 22 | 50 | 520 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 520 |  |  | 2020-09-14 | B20265¦courtroom J south side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | conference room 4 | [5 empty] | 23 | 51 | 482 |  | 2020-09-17 12:00 | 12:00 | 23 | 51 | 482 |  |  | 2020-09-14 | B70451¦conference room 4¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Outdoors |  |  | 11 | 28 | 377 |  |  |  | North entrance - partly cloudy, light breeze | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B21030¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 52 | 501 | east | 2020-09-17 12:00 | 12:00 | 23 | 52 | 501 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom J north side | [5 empty] | 22 | 50 | 522 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 522 |  |  | 2020-09-14 | B20265¦courtroom J north side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 52 | 484 | west | 2020-09-17 12:00 | 12:00 | 23 | 52 | 484 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 2 | [5 empty] | 21.6111 | 34 | 557 |  | 2020-09-17 12:00 | 12:00 | 21.6111 | 34 | 557 |  | low | 2020-09-14 | B10246¦Courtroom 2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom J | [5 empty] | 22 | 50 | 526 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 526 |  |  | 2020-09-14 | B20265¦hallway by courtroom J¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 607 | [5 empty] | 24 | 51 | 519 |  | 2020-09-17 12:00 | 12:00 | 24 | 51 | 519 |  |  | 2020-09-14 | B70451¦hallway by courtroom 607¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Trial Co-ordinators Office | [5 empty] | 21.6667 | 30 | 555 |  | 2020-09-17 12:00 | 12:00 | 21.6667 | 30 | 555 |  | low | 2020-09-14 | B10246¦Trial Co-ordinators Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G south side | [5 empty] | 22 | 50 | 564 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 564 |  |  | 2020-09-14 | B20265¦courtroom G south side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | enforcement/finance office | [5 empty] | 23 | 50 | 506 |  | 2020-09-17 12:00 | 12:00 | 23 | 50 | 506 |  |  | 2020-09-14 | B70451¦enforcement/finance office¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Boardroom used as a courtroom | [5 empty] | 22 | 30 | 487 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 22 | 30 | 487 |  | low | 2020-09-14 | B21030¦Boardroom used as a courtroom¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Main Floor Entrance Lobby | [5 empty] | 21.1111 | 31 | 484 | Middle of hallway | 2020-09-17 12:00 | 12:00 | 21.1111 | 31 | 484 |  | low | 2020-09-14 | B10246¦Main Floor Entrance Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 23 | 51 | 504 | east | 2020-09-17 12:00 | 12:00 | 23 | 51 | 504 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G north side | [5 empty] | 22 | 50 | 590 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 590 |  |  | 2020-09-14 | B20265¦courtroom G north side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Outdoors |  |  | 15 | 31 | 402 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10002¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 21.1111 | 33 | 490 | Office to the left of office 10 | 2020-09-17 12:00 | 12:00 | 21.1111 | 33 | 490 |  | low | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 23 | 51 | 501 | west | 2020-09-17 12:00 | 12:00 | 23 | 51 | 501 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 605 | [5 empty] | 23 | 52 | 549 |  | 2020-09-17 12:00 | 12:00 | 23 | 52 | 549 |  |  | 2020-09-14 | B70451¦hallway by courtroom 605¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 121 west side | [5 empty] | 22 | 48 | 544 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 544 |  |  | 2020-09-14 | B20265¦courtroom 121 west side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters administration office | [5 empty] | 23 | 52 | 494 |  | 2020-09-17 12:00 | 12:00 | 23 | 52 | 494 |  |  | 2020-09-14 | B70451¦masters administration office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 121 east side | [5 empty] | 21 | 49 | 533 |  | 2020-09-17 12:00 | 12:00 | 21 | 49 | 533 |  |  | 2020-09-14 | B20265¦courtroom 121 east side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-10 | [5 empty] | 23 | 51 | 480 |  | 2020-09-17 12:00 | 12:00 | 23 | 51 | 480 |  |  | 2020-09-14 | B70451¦room 6-10¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | 2nd Floor Holding Cell (hallway) | [5 empty] | 23 | 28 | 462 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 23 | 28 | 462 |  | low | 2020-09-14 | B21030¦2nd Floor Holding Cell (hallway)¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-9 | [5 empty] | 22 | 53 | 484 |  | 2020-09-17 12:00 | 12:00 | 22 | 53 | 484 |  |  | 2020-09-14 | B70451¦room 6-9¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 123 east side | [5 empty] | 22 | 52 | 558 |  | 2020-09-17 12:00 | 12:00 | 22 | 52 | 558 |  |  | 2020-09-14 | B20265¦courtroom 123 east side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters library | [5 empty] | 22 | 53 | 485 |  | 2020-09-17 12:00 | 12:00 | 22 | 53 | 485 |  |  | 2020-09-14 | B70451¦masters library¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-4 | [5 empty] | 22 | 53 | 486 |  | 2020-09-17 12:00 | 12:00 | 22 | 53 | 486 |  |  | 2020-09-14 | B70451¦room 6-4¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Lobby Administration | [5 empty] | 18 | 53 | 543 |  | 2020-09-17 12:00 | 12:00 | 18 | 53 | 543 |  |  | 2020-09-14 | B10003¦Lobby Administration¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 123 west side | [5 empty] | 22 | 51 | 548 |  | 2020-09-17 12:00 | 12:00 | 22 | 51 | 548 |  |  | 2020-09-14 | B20265¦courtroom 123 west side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 21.1111 | 33 | 487 | Office to the right of office 10 | 2020-09-17 12:00 | 12:00 | 21.1111 | 33 | 487 |  | low | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | reception area-masters | [5 empty] | 22 | 53 | 484 |  | 2020-09-17 12:00 | 12:00 | 22 | 53 | 484 |  |  | 2020-09-14 | B70451¦reception area-masters¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 1 (Center) | [5 empty] | 20.5556 | 28 | 443 |  | 2020-09-17 12:00 | 12:00 | 20.5556 | 28 | 443 |  | low | 2020-09-14 | B10246¦Courtroom 1 (Center)¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Outdoors |  |  | 19 | 55 | 500 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70451¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Courtroom 113 | [5 empty] | 24 | 28 | 621 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 24 | 28 | 621 |  | low | 2020-09-14 | B21030¦Courtroom 113¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 east side | [5 empty] | 22 | 50 | 605 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 605 |  |  | 2020-09-14 | B20265¦courtroom 124 east side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 west side | [5 empty] | 22 | 50 | 607 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 607 |  |  | 2020-09-14 | B20265¦courtroom 124 west side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 125 south side | [5 empty] | 21 | 48 | 542 |  | 2020-09-17 12:00 | 12:00 | 21 | 48 | 542 |  |  | 2020-09-14 | B20265¦courtroom 125 south side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown attorney admin area | [5 empty] | 21.6667 | 33 | 489 |  | 2020-09-17 12:00 | 12:00 | 21.6667 | 33 | 489 |  | low | 2020-09-14 | B10246¦Crown attorney admin area¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 125 north side | [5 empty] | 21 | 50 | 549 |  | 2020-09-17 12:00 | 12:00 | 21 | 50 | 549 |  |  | 2020-09-14 | B20265¦courtroom 125 north side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Library | [5 empty] | 18 | 52 | 553 | Wall mount AC unit running | 2020-09-17 12:00 | 12:00 | 18 | 52 | 553 |  |  | 2020-09-14 | B10003¦Library¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 126 south side | [5 empty] | 22 | 48 | 508 |  | 2020-09-17 12:00 | 12:00 | 22 | 48 | 508 |  |  | 2020-09-14 | B20265¦courtroom 126 south side¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom 126 | [5 empty] | 22 | 50 | 538 |  | 2020-09-17 12:00 | 12:00 | 22 | 50 | 538 |  |  | 2020-09-14 | B20265¦hallway by courtroom 126¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Administration office | [5 empty] | 22.2222 | 29 | 498 |  | 2020-09-17 12:00 | 12:00 | 22.2222 | 29 | 498 |  | low | 2020-09-14 | B10246¦Administration office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by recieving | [5 empty] | 20 | 55 | 525 |  | 2020-09-17 12:00 | 12:00 | 20 | 55 | 525 |  |  | 2020-09-14 | B20265¦hallway by recieving¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Basement cells - hallway | [5 empty] | 21.6667 | 31 | 478 |  | 2020-09-17 12:00 | 12:00 | 21.6667 | 31 | 478 |  | low | 2020-09-14 | B10246¦Basement cells - hallway¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Administration office | [5 empty] | 24 | 28 | 596 | Windows closed - 4 plants total along south window | 2020-09-17 09:00 | 9:00 | 24 | 28 | 596 |  | low | 2020-09-14 | B21030¦Administration office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Basement lobby - bottom of stairs | [5 empty] | 20.5556 | 33 | 471 |  | 2020-09-17 12:00 | 12:00 | 20.5556 | 33 | 471 |  | low | 2020-09-14 | B10246¦Basement lobby - bottom of stairs¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 21 | 59 | 727 | north section | 2020-09-17 12:00 | 12:00 | 21 | 59 | 727 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Basement Library | [5 empty] | 17 | 52 | 437 |  | 2020-09-17 12:00 | 12:00 | 17 | 52 | 437 |  |  | 2020-09-14 | B10003¦Basement Library¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 21 | 59 | 758 | south section | 2020-09-17 12:00 | 12:00 | 21 | 59 | 758 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by Courtrooom 1E | [5 empty] | 21 | 57 | 514 | ground floor | 2020-09-17 12:00 | 12:00 | 21 | 57 | 514 |  |  | 2020-09-14 | B14164¦Hallway by Courtrooom 1E¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Outdoors |  |  | 15 | 33 | 410 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10003¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 20 | 60 | 624 | north section | 2020-09-17 12:00 | 12:00 | 20 | 60 | 624 |  | caution | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown attorney lobby | [5 empty] | 24 | 29 | 674 | No windows, no plants | 2020-09-17 09:00 | 9:00 | 24 | 29 | 674 |  | low | 2020-09-14 | B21030¦Crown attorney lobby¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 20 | 60 | 563 | south section | 2020-09-17 12:00 | 12:00 | 20 | 60 | 563 |  | caution | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Outdoors |  |  | 12.6111 | 24 | 429 |  |  |  | Directly outside main entrance: clear/sunny | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10246¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown attorney admin area | [5 empty] | 24 | 28 | 524 | Windows closed, no plants | 2020-09-17 09:00 | 9:00 | 24 | 28 | 524 |  | low | 2020-09-14 | B21030¦Crown attorney admin area¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 24 | 27 | 476 | Office #1 - SW corner - windows closed, no plants | 2020-09-17 09:00 | 9:00 | 24 | 27 | 476 |  | low | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 24 | 29 | 574 | Office #2 - NE corner - no windows, no plants | 2020-09-17 09:00 | 9:00 | 24 | 29 | 574 |  | low | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-17-2020 09:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 6 | [5 empty] | 20 | 60 | 552 | second floor | 2020-09-17 12:00 | 12:00 | 20 | 60 | 552 |  | caution | 2020-09-14 | B14164¦Hallway by courtroom 6¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 21 | 64 | 860 | north section | 2020-09-17 12:00 | 12:00 | 21 | 64 | 860 |  | caution | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 22 | 62 | 841 | south section | 2020-09-17 12:00 | 12:00 | 22 | 62 | 841 |  | caution | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by Courtroom 10 | [5 empty] | 22 | 56 | 567 | basement | 2020-09-17 12:00 | 12:00 | 22 | 56 | 567 |  |  | 2020-09-14 | B14164¦Hallway by Courtroom 10¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, basement | [5 empty] | 21 | 57 | 598 |  | 2020-09-17 12:00 | 12:00 | 21 | 57 | 598 |  |  | 2020-09-14 | B14164¦Common area by elevator, basement¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, ground floor | [5 empty] | 21 | 57 | 523 |  | 2020-09-17 12:00 | 12:00 | 21 | 57 | 523 |  |  | 2020-09-14 | B14164¦Common area by elevator, ground floor¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Youth office, ground floor | [5 empty] | 21 | 58 | 627 |  | 2020-09-17 12:00 | 12:00 | 21 | 58 | 627 |  |  | 2020-09-14 | B14164¦Youth office, ground floor¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Family office, ground floor | [5 empty] | 21 | 58 | 578 |  | 2020-09-17 12:00 | 12:00 | 21 | 58 | 578 |  |  | 2020-09-14 | B14164¦Family office, ground floor¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | common area by elevator, second floor | [5 empty] | 21 | 57 | 534 |  | 2020-09-17 12:00 | 12:00 | 21 | 57 | 534 |  |  | 2020-09-14 | B14164¦common area by elevator, second floor¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Outdoors |  |  | 20 | 55 | 431 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B14164¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Outdoors |  |  | 11 | 32 | 415 |  |  |  | North entrance - partly cloudy, light breeze | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B21030¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Boardroom used as a courtroom | [5 empty] | 23 | 28 | 497 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 23 | 28 | 497 |  | low | 2020-09-14 | B21030¦Boardroom used as a courtroom¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | 2nd Floor Holding Cell (hallway) | [5 empty] | 23 | 27 | 474 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 23 | 27 | 474 |  | low | 2020-09-14 | B21030¦2nd Floor Holding Cell (hallway)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Courtroom 113 | [5 empty] | 24 | 26 | 500 | Windows closed, no windows | 2020-09-17 15:00 | 15:00 | 24 | 26 | 500 |  | low | 2020-09-14 | B21030¦Courtroom 113¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Administration office | [5 empty] | 25 | 26 | 474 | Windows closed, 4 plants total along south window | 2020-09-17 15:00 | 15:00 | 25 | 26 | 474 |  | low | 2020-09-14 | B21030¦Administration office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown attorney lobby | [5 empty] | 24 | 29 | 566 | No windows, no plants | 2020-09-17 15:00 | 15:00 | 24 | 29 | 566 |  | low | 2020-09-14 | B21030¦Crown attorney lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown attorney admin area | [5 empty] | 24 | 27 | 521 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 24 | 27 | 521 |  | low | 2020-09-14 | B21030¦Crown attorney admin area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Coourtroom 1E | [5 empty] | 22 | 51 | 595 | north section | 2020-09-17 15:00 | 15:00 | 22 | 51 | 595 |  |  | 2020-09-14 | B14164¦Coourtroom 1E¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 22 | 51 | 586 | south section | 2020-09-17 15:00 | 15:00 | 22 | 51 | 586 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by Courtroom 1E | [5 empty] | 23 | 49 | 525 | ground floor | 2020-09-17 15:00 | 15:00 | 23 | 49 | 525 |  |  | 2020-09-14 | B14164¦Hallway by Courtroom 1E¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 21 | 57 | 579 | north section | 2020-09-17 15:00 | 15:00 | 21 | 57 | 579 |  |  | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 21 | 57 | 596 | south section | 2020-09-17 15:00 | 15:00 | 21 | 57 | 596 |  |  | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 24 | 26 | 477 | Office #1 - SW corner - windows closed, no plants | 2020-09-17 15:00 | 15:00 | 24 | 26 | 477 |  | low | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 6 | [5 empty] | 20 | 56 | 537 | second floor | 2020-09-17 15:00 | 15:00 | 20 | 56 | 537 |  |  | 2020-09-14 | B14164¦Hallway by courtroom 6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 21 | 58 | 701 | north section | 2020-09-17 15:00 | 15:00 | 21 | 58 | 701 |  |  | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 22 | 57 | 721 | south section | 2020-09-17 15:00 | 15:00 | 22 | 57 | 721 |  |  | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 10 | [5 empty] | 22 | 54 | 563 | basement | 2020-09-17 15:00 | 15:00 | 22 | 54 | 563 |  |  | 2020-09-14 | B14164¦Hallway by courtroom 10¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, basement | [5 empty] | 21 | 54 | 583 |  | 2020-09-17 15:00 | 15:00 | 21 | 54 | 583 |  |  | 2020-09-14 | B14164¦Common area by elevator, basement¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, ground floor | [5 empty] | 22 | 52 | 532 |  | 2020-09-17 15:00 | 15:00 | 22 | 52 | 532 |  |  | 2020-09-14 | B14164¦Common area by elevator, ground floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 24 | 29 | 687 | Office #2 - NE corner - no windows, no plants | 2020-09-17 15:00 | 15:00 | 24 | 29 | 687 |  | low | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Youth office, ground floor | [5 empty] | 21 | 57 | 677 |  | 2020-09-17 15:00 | 15:00 | 21 | 57 | 677 |  |  | 2020-09-14 | B14164¦Youth office, ground floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Family office, ground floor | [5 empty] | 21 | 55 | 569 |  | 2020-09-17 15:00 | 15:00 | 21 | 55 | 569 |  |  | 2020-09-14 | B14164¦Family office, ground floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Commmon area by elevator, second floor | [5 empty] | 21 | 55 | 533 |  | 2020-09-17 15:00 | 15:00 | 21 | 55 | 533 |  |  | 2020-09-14 | B14164¦Commmon area by elevator, second floor¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Outdoors |  |  | 20 | 50 | 426 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B14164¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Outdoors |  |  | 12 | 29 | 391 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B11589¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Security Desk | [5 empty] | 18 | 47 | 659 |  | 2020-09-17 12:00 | 12:00 | 18 | 47 | 659 |  |  | 2020-09-14 | B11589¦Security Desk¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom A | [5 empty] | 20 | 44 | 470 |  | 2020-09-17 12:00 | 12:00 | 20 | 44 | 470 |  |  | 2020-09-14 | B11589¦Courtroom A¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom B | [5 empty] | 21 | 26 | 422 |  | 2020-09-17 12:00 | 12:00 | 21 | 26 | 422 |  | low | 2020-09-14 | B11589¦Courtroom B¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom D | [5 empty] | 20 | 32 | 562 |  | 2020-09-17 12:00 | 12:00 | 20 | 32 | 562 |  | low | 2020-09-14 | B11589¦Courtroom D¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom E | [5 empty] | 21 | 26 | 444 |  | 2020-09-17 12:00 | 12:00 | 21 | 26 | 444 |  | low | 2020-09-14 | B11589¦Courtroom E¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Walker | [5 empty] | 21 | 37 | 502 |  | 2020-09-17 12:00 | 12:00 | 21 | 37 | 502 |  | caution | 2020-09-14 | B11589¦Office Walker¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Martin | [5 empty] | 21 | 39 | 509 |  | 2020-09-17 12:00 | 12:00 | 21 | 39 | 509 |  | caution | 2020-09-14 | B11589¦Office Martin¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Baker | [5 empty] | 21 | 30 | 455 |  | 2020-09-17 12:00 | 12:00 | 21 | 30 | 455 |  | low | 2020-09-14 | B11589¦Office Baker¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Attorney General Administration Office | [5 empty] | 22 | 28 | 544 |  | 2020-09-17 12:00 | 12:00 | 22 | 28 | 544 |  | low | 2020-09-14 | B11589¦Attorney General Administration Office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Hallway | [5 empty] | 22 | 29 | 508 |  | 2020-09-17 12:00 | 12:00 | 22 | 29 | 508 |  | low | 2020-09-14 | B11589¦Hallway¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom H | [5 empty] | 22 | 29 | 432 |  | 2020-09-17 12:00 | 12:00 | 22 | 29 | 432 |  | low | 2020-09-14 | B11589¦Courtroom H¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Outdoors |  |  | 13 | 27 | 405 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B12955¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom J | [5 empty] | 21 | 20 | 400 | Window Open | 2020-09-17 12:00 | 12:00 | 21 | 20 | 400 |  | low | 2020-09-14 | B11589¦Courtroom J¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Main Floor Entrance Lobby | [5 empty] | 14 | 35 | 417 | Front lobby | 2020-09-17 12:00 | 12:00 | 14 | 35 | 417 |  | caution | 2020-09-14 | B12955¦Main Floor Entrance Lobby¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | OTHER | [5 empty] | 15 | 43 | 441 | waiting area | 2020-09-17 12:00 | 12:00 | 15 | 43 | 441 |  |  | 2020-09-14 | B12955¦OTHER¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Administration office | [5 empty] | 18 | 48 | 477 |  | 2020-09-17 12:00 | 12:00 | 18 | 48 | 477 |  |  | 2020-09-14 | B12955¦Administration office¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 103 | [5 empty] | 20 | 34 | 442 |  | 2020-09-17 12:00 | 12:00 | 20 | 34 | 442 |  | low | 2020-09-14 | B12955¦Courtroom 103¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 203 | [5 empty] | 20 | 28 | 436 |  | 2020-09-17 12:00 | 12:00 | 20 | 28 | 436 |  | low | 2020-09-14 | B12955¦Courtroom 203¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Lobby | [5 empty] | 25 | 26 | 591 |  | 2020-09-17 15:00 | 15:00 | 25 | 26 | 591 |  | low | 2020-09-14 | B10002¦Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Skeggs | [5 empty] | 24 | 28 | 545 | Door Open | 2020-09-17 15:00 | 15:00 | 24 | 28 | 545 |  | low | 2020-09-14 | B10002¦Office Skeggs¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Cubicle Office | [5 empty] | 24 | 29 | 548 | Door Open | 2020-09-17 15:00 | 15:00 | 24 | 29 | 548 |  | low | 2020-09-14 | B10002¦Cubicle Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | File Room | [5 empty] | 23 | 31 | 551 |  | 2020-09-17 15:00 | 15:00 | 23 | 31 | 551 |  | low | 2020-09-14 | B10002¦File Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Didiodato | [5 empty] | 22 | 32 | 554 | Door Open | 2020-09-17 15:00 | 15:00 | 22 | 32 | 554 |  | low | 2020-09-14 | B10002¦Office Didiodato¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Outdoors |  |  | 14 | 27 | 397 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10002¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Library | [5 empty] | 21.1111 | 32 | 462 |  | 2020-09-17 15:00 | 15:00 | 21.1111 | 32 | 462 |  | low | 2020-09-14 | B10246¦Library¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Justice Wilcox Chambers | [5 empty] | 20.5556 | 25 | 428 |  | 2020-09-17 15:00 | 15:00 | 20.5556 | 25 | 428 |  | low | 2020-09-14 | B10246¦Justice Wilcox Chambers¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Lobby Administration | [5 empty] | 18 | 53 | 556 |  | 2020-09-17 15:00 | 15:00 | 18 | 53 | 556 |  |  | 2020-09-14 | B10003¦Lobby Administration¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Library | [5 empty] | 19 | 51 | 576 | Wall mount AC unit running | 2020-09-17 15:00 | 15:00 | 19 | 51 | 576 |  |  | 2020-09-14 | B10003¦Library¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | 2nd fl lobby | [5 empty] | 21.1111 | 30 | 456 | Middle of hallway | 2020-09-17 15:00 | 15:00 | 21.1111 | 30 | 456 |  | low | 2020-09-14 | B10246¦2nd fl lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 2 | [5 empty] | 21.6667 | 29 | 556 |  | 2020-09-17 15:00 | 15:00 | 21.6667 | 29 | 556 |  | low | 2020-09-14 | B10246¦Courtroom 2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Basement Library | [5 empty] | 18 | 52 | 441 |  | 2020-09-17 15:00 | 15:00 | 18 | 52 | 441 |  |  | 2020-09-14 | B10003¦Basement Library¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Trial Co-ordinators Office | [5 empty] | 21.6667 | 29 | 532 |  | 2020-09-17 15:00 | 15:00 | 21.6667 | 29 | 532 |  | low | 2020-09-14 | B10246¦Trial Co-ordinators Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Main Floor Entrance Lobby | [5 empty] | 21.6667 | 28 | 459 | Middle of hallway | 2020-09-17 15:00 | 15:00 | 21.6667 | 28 | 459 |  | low | 2020-09-14 | B10246¦Main Floor Entrance Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 21.1111 | 27 | 455 | Office to the left of office 10 | 2020-09-17 15:00 | 15:00 | 21.1111 | 27 | 455 |  | low | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Outdoors |  |  | 14 | 28 | 409 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10003¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Outdoors |  |  | 20 | 50 | 431 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10639¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 21.1111 | 29 | 452 | Office to the right of office 10 | 2020-09-17 15:00 | 15:00 | 21.1111 | 29 | 452 |  | low | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 6 north side | [5 empty] | 21 | 47 | 440 |  | 2020-09-17 15:00 | 15:00 | 21 | 47 | 440 |  |  | 2020-09-14 | B10639¦courtroom 6 north side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown attorney admin area | [5 empty] | 21.6667 | 33 | 521 |  | 2020-09-17 15:00 | 15:00 | 21.6667 | 33 | 521 |  | low | 2020-09-14 | B10246¦Crown attorney admin area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Administration office | [5 empty] | 21.6667 | 27 | 509 |  | 2020-09-17 15:00 | 15:00 | 21.6667 | 27 | 509 |  | low | 2020-09-14 | B10246¦Administration office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 6 south side | [5 empty] | 21 | 47 | 441 |  | 2020-09-17 15:00 | 15:00 | 21 | 47 | 441 |  |  | 2020-09-14 | B10639¦courtroom 6 south side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 1 (Center) | [5 empty] | 21.1111 | 24 | 420 |  | 2020-09-17 15:00 | 15:00 | 21.1111 | 24 | 420 |  | low | 2020-09-14 | B10246¦Courtroom 1 (Center)¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 6 | [5 empty] | 21 | 48 | 452 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 452 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Outdoors |  |  | 16 | 28 | 420 |  |  |  | East entrance - partly cloudy, light Breeze | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B13095¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 5 north side | [5 empty] | 21 | 49 | 452 |  | 2020-09-17 15:00 | 15:00 | 21 | 49 | 452 |  |  | 2020-09-14 | B10639¦courtroom 5 north side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 5 south side | [5 empty] | 21 | 49 | 460 |  | 2020-09-17 15:00 | 15:00 | 21 | 49 | 460 |  |  | 2020-09-14 | B10639¦courtroom 5 south side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 5 | [5 empty] | 21 | 48 | 467 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 467 |  |  | 2020-09-14 | B10639¦Hallway by courtroom 5¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Basement cells - hallway | [5 empty] | 20.5556 | 33 | 460 |  | 2020-09-17 15:00 | 15:00 | 20.5556 | 33 | 460 |  | low | 2020-09-14 | B10246¦Basement cells - hallway¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 3 southeast side | [5 empty] | 21 | 48 | 459 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 459 |  |  | 2020-09-14 | B10639¦courtroom 3 southeast side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 3 northeast side | [5 empty] | 21 | 49 | 485 |  | 2020-09-17 15:00 | 15:00 | 21 | 49 | 485 |  |  | 2020-09-14 | B10639¦courtroom 3 northeast side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Basement lobby - bottom of stairs | [5 empty] | 20.5556 | 31 | 452 |  | 2020-09-17 15:00 | 15:00 | 20.5556 | 31 | 452 |  | low | 2020-09-14 | B10246¦Basement lobby - bottom of stairs¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | hallway by courtroom 3 | [5 empty] | 22 | 48 | 487 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 487 |  |  | 2020-09-14 | B10639¦hallway by courtroom 3¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Outdoors |  |  | 13 | 27 | 13405 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B12955¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | lobby by statue | [5 empty] | 21 | 51 | 468 |  | 2020-09-17 15:00 | 15:00 | 21 | 51 | 468 |  |  | 2020-09-14 | B10639¦lobby by statue¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Outdoors |  |  | 16.1111 | 22 | 407 |  |  |  | Directly outside main entrance: clear/sunny | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10246¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby East Side | [5 empty] | 21 | 48 | 467 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 467 |  |  | 2020-09-14 | B10639¦Entrance Lobby East Side¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Outdoors |  |  | 12 | 44 | 436 |  |  |  |  | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B11589¦Outdoors¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Security Desk | [5 empty] | 19 | 52 | 520 |  | 2020-09-17 09:00 | 9:00 | 19 | 52 | 520 |  |  | 2020-09-14 | B11589¦Security Desk¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby West Side | [5 empty] | 21 | 48 | 470 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 470 |  |  | 2020-09-14 | B10639¦Entrance Lobby West Side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Hallway | [5 empty] | 21 | 32 | 518 | Window closed, no plants | 2020-09-17 15:00 | 15:00 | 21 | 32 | 518 |  | low | 2020-09-14 | B13095¦Hallway¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom A | [5 empty] | 21 | 45 | 430 |  | 2020-09-17 09:00 | 9:00 | 21 | 45 | 430 |  |  | 2020-09-14 | B11589¦Courtroom A¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by COA intake office | [5 empty] | 21 | 48 | 468 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 468 |  |  | 2020-09-14 | B10639¦Hallway by COA intake office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Main Floor Entrance Lobby | [5 empty] | 14 | 35 | 417 | front lobby | 2020-09-17 15:00 | 15:00 | 14 | 35 | 417 |  | caution | 2020-09-14 | B12955¦Main Floor Entrance Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom B | [5 empty] | 21 | 35 | 420 |  | 2020-09-17 09:00 | 9:00 | 21 | 35 | 420 |  | caution | 2020-09-14 | B11589¦Courtroom B¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | office - B04A | [5 empty] | 21 | 30 | 476 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 21 | 30 | 476 |  | low | 2020-09-14 | B13095¦office - B04A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | OTHER | [5 empty] | 15 | 43 | 441 | Waiting area | 2020-09-17 15:00 | 15:00 | 15 | 43 | 441 |  |  | 2020-09-14 | B12955¦OTHER¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom C | [5 empty] | 21 | 35 | 435 |  | 2020-09-17 09:00 | 9:00 | 21 | 35 | 435 |  | caution | 2020-09-14 | B11589¦Courtroom C¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by Law Society of Ontario | [5 empty] | 21 | 48 | 467 |  | 2020-09-17 15:00 | 15:00 | 21 | 48 | 467 |  |  | 2020-09-14 | B10639¦Hallway by Law Society of Ontario¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Administration office | [5 empty] | 18 | 48 | 477 |  | 2020-09-17 15:00 | 15:00 | 18 | 48 | 477 |  |  | 2020-09-14 | B12955¦Administration office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Main Lobby | [5 empty] | 21 | 29 | 491 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 21 | 29 | 491 |  | low | 2020-09-14 | B13095¦Main Lobby¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom D | [5 empty] | 21 | 37 | 520 |  | 2020-09-17 09:00 | 9:00 | 21 | 37 | 520 |  | caution | 2020-09-14 | B11589¦Courtroom D¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 203 | [5 empty] | 20 | 34 | 484 |  | 2020-09-17 15:00 | 15:00 | 20 | 34 | 484 |  | low | 2020-09-14 | B12955¦Courtroom 203¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom E | [5 empty] | 21 | 33 | 477 |  | 2020-09-17 09:00 | 9:00 | 21 | 33 | 477 |  | low | 2020-09-14 | B11589¦Courtroom E¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Outdoors |  |  | 19 | 54 | 439 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B20265¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 103 | [5 empty] | 19 | 31 | 445 |  | 2020-09-17 15:00 | 15:00 | 19 | 31 | 445 |  | low | 2020-09-14 | B12955¦Courtroom 103¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Walker | [5 empty] | 21 | 39 | 431 | Door Open | 2020-09-17 09:00 | 9:00 | 21 | 39 | 431 |  | caution | 2020-09-14 | B11589¦Office Walker¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Martin | [5 empty] | 21 | 40 | 438 |  | 2020-09-17 09:00 | 9:00 | 21 | 40 | 438 |  | caution | 2020-09-14 | B11589¦Office Martin¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 north side | [5 empty] | 22 | 49 | 556 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 556 |  |  | 2020-09-14 | B20265¦courtroom M1 north side¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Baker | [5 empty] | 21 | 38 | 420 |  | 2020-09-17 09:00 | 9:00 | 21 | 38 | 420 |  | caution | 2020-09-14 | B11589¦Office Baker¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Outdoors |  |  | 12 | 35 | 412 |  |  |  | North entrance - partly cloudy, light breeze | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B13049¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom M1 south side | [5 empty] | 22 | 49 | 556 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 556 |  |  | 2020-09-14 | B10639¦courtroom M1 south side¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Attorney General Administration Office | [5 empty] | 22 | 38 | 506 |  | 2020-09-17 09:00 | 9:00 | 22 | 38 | 506 |  | caution | 2020-09-14 | B11589¦Attorney General Administration Office¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Hallway | [5 empty] | 22 | 37 | 497 |  | 2020-09-17 09:00 | 9:00 | 22 | 37 | 497 |  | caution | 2020-09-14 | B11589¦Hallway¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by Courtroom M1 | [5 empty] | 22 | 50 | 565 |  | 2020-09-17 15:00 | 15:00 | 22 | 50 | 565 |  |  | 2020-09-14 | B20265¦hallway by Courtroom M1¦¦Sep-17-2020 15:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom H | [5 empty] | 22 | 36 | 430 |  | 2020-09-17 09:00 | 9:00 | 22 | 36 | 430 |  | caution | 2020-09-14 | B11589¦Courtroom H¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom J | [5 empty] | 22 | 41 | 418 |  | 2020-09-17 09:00 | 9:00 | 22 | 41 | 418 |  |  | 2020-09-14 | B11589¦Courtroom J¦¦Sep-17-2020 09:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom J south side | [5 empty] | 22 | 47 | 506 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 506 |  |  | 2020-09-14 | B20265¦courtroom J south side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Outdoors |  |  | 14 | 28 | 373 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B11589¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Security Desk | [5 empty] | 17 | 47 | 569 |  | 2020-09-17 15:00 | 15:00 | 17 | 47 | 569 |  |  | 2020-09-14 | B11589¦Security Desk¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom J north side | [5 empty] | 22 | 48 | 532 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 532 |  |  | 2020-09-14 | B20265¦courtroom J north side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom A | [5 empty] | 20 | 44 | 473 |  | 2020-09-17 15:00 | 15:00 | 20 | 44 | 473 |  |  | 2020-09-14 | B11589¦Courtroom A¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom B | [5 empty] | 21 | 27 | 425 |  | 2020-09-17 15:00 | 15:00 | 21 | 27 | 425 |  | low | 2020-09-14 | B11589¦Courtroom B¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 57 | 692 | east | 2020-09-17 12:00 | 12:00 | 22 | 57 | 692 |  |  | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 2nd fl lobby | [5 empty] | 19 | 32 | 477 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 19 | 32 | 477 |  | low | 2020-09-14 | B13049¦2nd fl lobby¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom J | [5 empty] | 22 | 48 | 532 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 532 |  |  | 2020-09-14 | B20265¦hallway by courtroom J¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom C | [5 empty] | 21 | 26 | 473 |  | 2020-09-17 15:00 | 15:00 | 21 | 26 | 473 |  | low | 2020-09-14 | B11589¦Courtroom C¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 23 | 56 | 695 | west | 2020-09-17 12:00 | 12:00 | 23 | 56 | 695 |  |  | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom D | [5 empty] | 21 | 30 | 444 |  | 2020-09-17 15:00 | 15:00 | 21 | 30 | 444 |  | low | 2020-09-14 | B11589¦Courtroom D¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G south side | [5 empty] | 22 | 49 | 615 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 615 |  |  | 2020-09-14 | B20265¦courtroom G south side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom E | [5 empty] | 21 | 25 | 453 |  | 2020-09-17 15:00 | 15:00 | 21 | 25 | 453 |  | low | 2020-09-14 | B11589¦Courtroom E¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 22 | 56 | 493 | east | 2020-09-17 12:00 | 12:00 | 22 | 56 | 493 |  |  | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Walker | [5 empty] | 22 | 36 | 503 |  | 2020-09-17 15:00 | 15:00 | 22 | 36 | 503 |  | caution | 2020-09-14 | B11589¦Office Walker¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 22 | 56 | 501 | west | 2020-09-17 12:00 | 12:00 | 22 | 56 | 501 |  |  | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G north side | [5 empty] | 22 | 49 | 598 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 598 |  |  | 2020-09-14 | B20265¦courtroom G north side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Martin | [5 empty] | 21 | 38 | 503 |  | 2020-09-17 15:00 | 15:00 | 21 | 38 | 503 |  | caution | 2020-09-14 | B11589¦Office Martin¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office Baker | [5 empty] | 21 | 31 | 460 |  | 2020-09-17 15:00 | 15:00 | 21 | 31 | 460 |  | low | 2020-09-14 | B11589¦Office Baker¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 21 | 58 | 491 | east | 2020-09-17 12:00 | 12:00 | 21 | 58 | 491 |  |  | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 121 west side | [5 empty] | 22 | 47 | 545 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 545 |  |  | 2020-09-14 | B20265¦courtroom 121 west side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 250 | [5 empty] | 20 | 26 | 400 | No windows, no plants | 2020-09-17 15:00 | 15:00 | 20 | 26 | 400 |  | low | 2020-09-14 | B13049¦Courtroom 250¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 22 | 57 | 490 | west | 2020-09-17 12:00 | 12:00 | 22 | 57 | 490 |  |  | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Attorney General Administration Office | [5 empty] | 22 | 30 | 490 |  | 2020-09-17 15:00 | 15:00 | 22 | 30 | 490 |  | low | 2020-09-14 | B11589¦Attorney General Administration Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Hallway | [5 empty] | 22 | 30 | 498 |  | 2020-09-17 15:00 | 15:00 | 22 | 30 | 498 |  | low | 2020-09-14 | B11589¦Hallway¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 22 | 57 | 485 | east | 2020-09-17 12:00 | 12:00 | 22 | 57 | 485 |  |  | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 121 east side | [5 empty] | 22 | 47 | 548 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 548 |  |  | 2020-09-14 | B20265¦courtroom 121 east side¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 22 | 57 | 485 | west | 2020-09-17 12:00 | 12:00 | 22 | 57 | 485 |  |  | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom H | [5 empty] | 22 | 28 | 425 |  | 2020-09-17 15:00 | 15:00 | 22 | 28 | 425 |  | low | 2020-09-14 | B11589¦Courtroom H¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 123 east side | [5 empty] | 22 | 48 | 580 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 580 |  |  | 2020-09-14 | B20265¦courtroom 123 east side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom J | [5 empty] | 22 | 21 | 388 | Open Window | 2020-09-17 15:00 | 15:00 | 22 | 21 | 388 |  | low | 2020-09-14 | B11589¦Courtroom J¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 57 | 521 | east | 2020-09-17 12:00 | 12:00 | 22 | 57 | 521 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 57 | 521 | west | 2020-09-17 12:00 | 12:00 | 22 | 57 | 521 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 123 west side | [5 empty] | 22 | 47 | 593 |  | 2020-09-17 15:00 | 15:00 | 22 | 47 | 593 |  |  | 2020-09-14 | B20265¦courtroom 123 west side¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Administration office | [5 empty] | 22 | 26 | 532 | Windows closed, 4 plants total at various locations | 2020-09-17 15:00 | 15:00 | 22 | 26 | 532 |  | low | 2020-09-14 | B13049¦Administration office¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 57 | 532 | east | 2020-09-17 12:00 | 12:00 | 22 | 57 | 532 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 east side | [5 empty] | 22 | 49 | 550 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 550 |  |  | 2020-09-14 | B20265¦courtroom 124 east side¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 57 | 522 | west | 2020-09-17 12:00 | 12:00 | 22 | 57 | 522 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 58 | 531 | east | 2020-09-17 12:00 | 12:00 | 21 | 58 | 531 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 west side | [5 empty] | 22 | 49 | 545 |  | 2020-09-17 15:00 | 15:00 | 22 | 49 | 545 |  |  | 2020-09-14 | B20265¦courtroom 124 west side¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 58 | 534 | west | 2020-09-17 12:00 | 12:00 | 21 | 58 | 534 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 57 | 543 | east | 2020-09-17 12:00 | 12:00 | 22 | 57 | 543 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courroom 125 south side | [5 empty] | 21 | 46 | 522 |  | 2020-09-17 15:00 | 15:00 | 21 | 46 | 522 |  |  | 2020-09-14 | B20265¦courroom 125 south side¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 57 | 546 | west | 2020-09-17 12:00 | 12:00 | 22 | 57 | 546 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 21 | 54 | 488 | east | 2020-09-17 12:00 | 12:00 | 21 | 54 | 488 |  |  | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 125 north side | [5 empty] | 21 | 47 | 533 |  | 2020-09-17 15:00 | 15:00 | 21 | 47 | 533 |  |  | 2020-09-14 | B20265¦courtroom 125 north side¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 21 | 55 | 476 | west | 2020-09-17 12:00 | 12:00 | 21 | 55 | 476 |  |  | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown Attorney Office | [5 empty] | 22 | 25 | 446 | Office #2 - north side - windows closed, no plants | 2020-09-17 15:00 | 15:00 | 22 | 25 | 446 |  | low | 2020-09-14 | B13049¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 21 | 55 | 537 | east | 2020-09-17 12:00 | 12:00 | 21 | 55 | 537 |  |  | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 126 south side | [5 empty] | 22 | 46 | 506 |  | 2020-09-17 15:00 | 15:00 | 22 | 46 | 506 |  |  | 2020-09-14 | B20265¦courtroom 126 south side¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 21 | 55 | 503 | west | 2020-09-17 12:00 | 12:00 | 21 | 55 | 503 |  |  | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 22 | 53 | 572 | east | 2020-09-17 12:00 | 12:00 | 22 | 53 | 572 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom 126 | [5 empty] | 22 | 48 | 586 |  | 2020-09-17 15:00 | 15:00 | 22 | 48 | 586 |  |  | 2020-09-14 | B20265¦hallway by courtroom 126¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 22 | 51 | 544 | west | 2020-09-17 12:00 | 12:00 | 22 | 51 | 544 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 54 | 532 | east | 2020-09-17 12:00 | 12:00 | 21 | 54 | 532 |  |  | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by receiving | [5 empty] | 20 | 55 | 586 |  | 2020-09-17 15:00 | 15:00 | 20 | 55 | 586 |  |  | 2020-09-14 | B20265¦hallway by receiving¦¦Sep-17-2020 15:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 54 | 526 | west | 2020-09-17 12:00 | 12:00 | 21 | 54 | 526 |  |  | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Outdoors |  |  | 19 | 55 | 500 |  |  |  |  | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B91122¦Outdoors¦¦Sep-17-2020 12:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown attorney admin area | [5 empty] | 22 | 25 | 522 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 22 | 25 | 522 |  | low | 2020-09-14 | B13049¦Crown attorney admin area¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 56 | 614 | east | 2020-09-17 15:00 | 15:00 | 22 | 56 | 614 |  |  | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 56 | 615 | west | 2020-09-17 15:00 | 15:00 | 22 | 56 | 615 |  |  | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 22 | 57 | 561 | east | 2020-09-17 15:00 | 15:00 | 22 | 57 | 561 |  |  | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 22 | 57 | 554 | west | 2020-09-17 15:00 | 15:00 | 22 | 57 | 554 |  |  | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 22 | 57 | 499 | east | 2020-09-17 15:00 | 15:00 | 22 | 57 | 499 |  |  | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown Attorney Office | [5 empty] | 22 | 24 | 491 | Office #1 - east side - windows closed, no plants | 2020-09-17 15:00 | 15:00 | 22 | 24 | 491 |  | low | 2020-09-14 | B13049¦Crown Attorney Office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 22 | 57 | 502 | west | 2020-09-17 15:00 | 15:00 | 22 | 57 | 502 |  |  | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 22 | 57 | 489 | east | 2020-09-17 15:00 | 15:00 | 22 | 57 | 489 |  |  | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 22 | 57 | 486 | west | 2020-09-17 15:00 | 15:00 | 22 | 57 | 486 |  |  | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 57 | 530 | est | 2020-09-17 15:00 | 15:00 | 22 | 57 | 530 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 57 | 529 | west | 2020-09-17 15:00 | 15:00 | 22 | 57 | 529 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 58 | 526 | east | 2020-09-17 15:00 | 15:00 | 22 | 58 | 526 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 57 | 530 | west | 2020-09-17 15:00 | 15:00 | 22 | 57 | 530 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 58 | 539 | east | 2020-09-17 15:00 | 15:00 | 21 | 58 | 539 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 58 | 533 | west | 2020-09-17 15:00 | 15:00 | 21 | 58 | 533 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 57 | 530 | east | 2020-09-17 15:00 | 15:00 | 22 | 57 | 530 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 58 | 534 | west | 2020-09-17 15:00 | 15:00 | 22 | 58 | 534 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 21 | 53 | 491 | east | 2020-09-17 15:00 | 15:00 | 21 | 53 | 491 |  |  | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 1st Floor Lobby next to courtroom 122 | [5 empty] | 22 | 24 | 420 | Windows closed, no plants | 2020-09-17 15:00 | 15:00 | 22 | 24 | 420 |  | low | 2020-09-14 | B13049¦1st Floor Lobby next to courtroom 122¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 21 | 53 | 477 | west | 2020-09-17 15:00 | 15:00 | 21 | 53 | 477 |  |  | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 21 | 55 | 509 | east | 2020-09-17 15:00 | 15:00 | 21 | 55 | 509 |  |  | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 21 | 54 | 511 | west | 2020-09-17 15:00 | 15:00 | 21 | 54 | 511 |  |  | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 22 | 52 | 588 | east | 2020-09-17 15:00 | 15:00 | 22 | 52 | 588 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 22 | 51 | 558 | west | 2020-09-17 15:00 | 15:00 | 22 | 51 | 558 |  |  | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 55 | 533 | east | 2020-09-17 15:00 | 15:00 | 21 | 55 | 533 |  |  | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 55 | 481 | west | 2020-09-17 15:00 | 15:00 | 21 | 55 | 481 |  |  | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 122 | [5 empty] | 20 | 24 | 456 | No windows, no plants | 2020-09-17 15:00 | 15:00 | 20 | 24 | 456 |  | low | 2020-09-14 | B13049¦Courtroom 122¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Outdoors |  |  | 21 | 50 | 481 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B91122¦Outdoors¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Lunch Room | [5 empty] | 23 | 52 | 531 |  | 2020-09-17 15:00 | 15:00 | 23 | 52 | 531 |  |  | 2020-09-14 | B70451¦Lunch Room¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Court Security office #142 | [5 empty] | 22 | 26 | 420 | No windows, no plants | 2020-09-17 15:00 | 15:00 | 22 | 26 | 420 |  | low | 2020-09-14 | B13049¦Court Security office #142¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 23 | 51 | 527 | east | 2020-09-17 15:00 | 15:00 | 23 | 51 | 527 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 22 | 52 | 522 | west | 2020-09-17 15:00 | 15:00 | 22 | 52 | 522 |  |  | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 602 | [5 empty] | 23 | 53 | 560 |  | 2020-09-17 15:00 | 15:00 | 23 | 53 | 560 |  |  | 2020-09-14 | B70451¦hallway by courtroom 602¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 603 | [5 empty] | 22 | 53 | 537 |  | 2020-09-17 15:00 | 15:00 | 22 | 53 | 537 |  |  | 2020-09-14 | B70451¦hallway by courtroom 603¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | conference room 4 | [5 empty] | 23 | 52 | 512 |  | 2020-09-17 15:00 | 15:00 | 23 | 52 | 512 |  |  | 2020-09-14 | B70451¦conference room 4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 22 | 54 | 509 | east | 2020-09-17 15:00 | 15:00 | 22 | 54 | 509 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 22 | 54 | 501 | west | 2020-09-17 15:00 | 15:00 | 22 | 54 | 501 |  |  | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 607 | [5 empty] | 23 | 52 | 511 |  | 2020-09-17 15:00 | 15:00 | 23 | 52 | 511 |  |  | 2020-09-14 | B70451¦hallway by courtroom 607¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | enforcementoffice | [5 empty] | 23 | 51 | 523 |  | 2020-09-17 15:00 | 15:00 | 23 | 51 | 523 |  |  | 2020-09-14 | B70451¦enforcementoffice¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 23 | 52 | 517 | east | 2020-09-17 15:00 | 15:00 | 23 | 52 | 517 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 140 | [5 empty] | 22 | 24 | 421 | No windows, no plants | 2020-09-17 15:00 | 15:00 | 22 | 24 | 421 |  | low | 2020-09-14 | B13049¦Courtroom 140¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 22 | 52 | 505 | west | 2020-09-17 15:00 | 15:00 | 22 | 52 | 505 |  |  | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 605 | [5 empty] | 22 | 53 | 514 |  | 2020-09-17 15:00 | 15:00 | 22 | 53 | 514 |  |  | 2020-09-14 | B70451¦hallway by courtroom 605¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters administration office | [5 empty] | 23 | 52 | 540 |  | 2020-09-17 15:00 | 15:00 | 23 | 52 | 540 |  |  | 2020-09-14 | B70451¦masters administration office¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-10 | [5 empty] | 22 | 52 | 505 |  | 2020-09-17 15:00 | 15:00 | 22 | 52 | 505 |  |  | 2020-09-14 | B70451¦room 6-10¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-9 | [5 empty] | 21 | 53 | 507 |  | 2020-09-17 15:00 | 15:00 | 21 | 53 | 507 |  |  | 2020-09-14 | B70451¦room 6-9¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters library | [5 empty] | 22 | 54 | 507 |  | 2020-09-17 15:00 | 15:00 | 22 | 54 | 507 |  |  | 2020-09-14 | B70451¦masters library¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-4 | [5 empty] | 22 | 53 | 504 |  | 2020-09-17 15:00 | 15:00 | 22 | 53 | 504 |  |  | 2020-09-14 | B70451¦room 6-4¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | reception area-masters | [5 empty] | 22 | 54 | 505 |  | 2020-09-17 15:00 | 15:00 | 22 | 54 | 505 |  |  | 2020-09-14 | B70451¦reception area-masters¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 1st floor cell holding area Hallway | [5 empty] | 22 | 24 | 440 | Across from door #3 - no windows, no plants | 2020-09-17 15:00 | 15:00 | 22 | 24 | 440 |  | low | 2020-09-14 | B13049¦1st floor cell holding area Hallway¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Outdoors |  |  | 21 | 50 | 481 |  |  |  |  | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70451¦Outdoors¦¦Sep-17-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Library | [5 empty] | 19.4444 | 39 | 473 |  | 2020-09-18 09:00 | 9:00 | 19.4444 | 39 | 473 |  | caution | 2020-09-14 | B10246¦Library¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Justice Wilcox Chambers | [5 empty] | 19.4444 | 34 | 490 |  | 2020-09-18 09:00 | 9:00 | 19.4444 | 34 | 490 |  | low | 2020-09-14 | B10246¦Justice Wilcox Chambers¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | 2nd fl lobby | [5 empty] | 20.5556 | 32 | 470 | Middle of hallway | 2020-09-18 09:00 | 9:00 | 20.5556 | 32 | 470 |  | low | 2020-09-14 | B10246¦2nd fl lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 2 | [5 empty] | 20 | 34 | 475 |  | 2020-09-18 09:00 | 9:00 | 20 | 34 | 475 |  | low | 2020-09-14 | B10246¦Courtroom 2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Outdoors |  |  | 4 | 62 | 421 |  |  |  | North entrance - sunny, light breeze | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B13049¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Trial Co-ordinators Office | [5 empty] | 21.1111 | 31 | 574 |  | 2020-09-18 09:00 | 9:00 | 21.1111 | 31 | 574 |  | low | 2020-09-14 | B10246¦Trial Co-ordinators Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 2nd fl lobby | [5 empty] | 15 | 47 | 454 | Windows closed, no plants | 2020-09-18 09:00 | 9:00 | 15 | 47 | 454 |  |  | 2020-09-14 | B13049¦2nd fl lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Main Floor Entrance Lobby | [5 empty] | 21.1111 | 29 | 474 | Middle of hallway | 2020-09-18 09:00 | 9:00 | 21.1111 | 29 | 474 |  | low | 2020-09-14 | B10246¦Main Floor Entrance Lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 20.5556 | 31 | 483 | Office to the left of office 10 | 2020-09-18 09:00 | 9:00 | 20.5556 | 31 | 483 |  | low | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 250 | [5 empty] | 20 | 36 | 438 | No windows, no plants | 2020-09-18 09:00 | 9:00 | 20 | 36 | 438 |  | caution | 2020-09-14 | B13049¦Courtroom 250¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Administration office | [5 empty] | 21 | 33 | 454 | Windows closed, total of 2 plants at various desks | 2020-09-18 09:00 | 9:00 | 21 | 33 | 454 |  | low | 2020-09-14 | B13049¦Administration office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Lobby | [5 empty] | 21 | 33 | 554 |  | 2020-09-18 09:00 | 9:00 | 21 | 33 | 554 |  | low | 2020-09-14 | B10002¦Lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 20.5556 | 32 | 515 | Office to the right of office 10 | 2020-09-18 09:00 | 9:00 | 20.5556 | 32 | 515 |  | low | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 1st Floor Lobby next to courtroom 122 | [5 empty] | 22 | 32 | 453 | Windows closed, no plants | 2020-09-18 09:00 | 9:00 | 22 | 32 | 453 |  | low | 2020-09-14 | B13049¦1st Floor Lobby next to courtroom 122¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Skeggs | [5 empty] | 21 | 33 | 578 | Door Open | 2020-09-18 09:00 | 9:00 | 21 | 33 | 578 |  | low | 2020-09-14 | B10002¦Office Skeggs¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 1 (Center) | [5 empty] | 20.5556 | 27 | 461 |  | 2020-09-18 09:00 | 9:00 | 20.5556 | 27 | 461 |  | low | 2020-09-14 | B10246¦Courtroom 1 (Center)¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown attorney admin area | [5 empty] | 21.6667 | 32 | 577 |  | 2020-09-18 09:00 | 9:00 | 21.6667 | 32 | 577 |  | low | 2020-09-14 | B10246¦Crown attorney admin area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 122 | [5 empty] | 21 | 31 | 485 | No windows, no plants | 2020-09-18 09:00 | 9:00 | 21 | 31 | 485 |  | low | 2020-09-14 | B13049¦Courtroom 122¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Cubicle Office | [5 empty] | 22 | 33 | 601 | Door Open | 2020-09-18 09:00 | 9:00 | 22 | 33 | 601 |  | low | 2020-09-14 | B10002¦Cubicle Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Administration office | [5 empty] | 21.1111 | 29 | 566 |  | 2020-09-18 09:00 | 9:00 | 21.1111 | 29 | 566 |  | low | 2020-09-14 | B10246¦Administration office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Basement lobby - bottom of stairs | [5 empty] | 21.1111 | 31 | 491 |  | 2020-09-18 09:00 | 9:00 | 21.1111 | 31 | 491 |  | low | 2020-09-14 | B10246¦Basement lobby - bottom of stairs¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Basement cells - hallway | [5 empty] | 20.5556 | 32 | 460 |  | 2020-09-18 09:00 | 9:00 | 20.5556 | 32 | 460 |  | low | 2020-09-14 | B10246¦Basement cells - hallway¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | File Room | [5 empty] | 22 | 32 | 621 |  | 2020-09-18 09:00 | 9:00 | 22 | 32 | 621 |  | low | 2020-09-14 | B10002¦File Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 20 | 41 | 510 | north section | 2020-09-18 09:00 | 9:00 | 20 | 41 | 510 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Court Security office #142 | [5 empty] | 22 | 31 | 466 | No windows, no plants | 2020-09-18 09:00 | 9:00 | 22 | 31 | 466 |  | low | 2020-09-14 | B13049¦Court Security office #142¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 20 | 41 | 451 | south section | 2020-09-18 09:00 | 9:00 | 20 | 41 | 451 |  |  | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 1E | [5 empty] | 20 | 38 | 462 |  | 2020-09-18 09:00 | 9:00 | 20 | 38 | 462 |  | caution | 2020-09-14 | B14164¦Hallway by courtroom 1E¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 19 | 43 | 473 | north | 2020-09-18 09:00 | 9:00 | 19 | 43 | 473 |  |  | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Didiodato | [5 empty] | 22 | 33 | 657 | Door Open | 2020-09-18 09:00 | 9:00 | 22 | 33 | 657 |  | low | 2020-09-14 | B10002¦Office Didiodato¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Outdoors |  |  | 7.7778 | 49 | 420 |  |  |  | Directly outside main entrance | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10246¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 19 | 43 | 473 | south | 2020-09-18 09:00 | 9:00 | 19 | 43 | 473 |  |  | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 140 | [5 empty] | 22 | 31 | 482 | No windows, no plants | 2020-09-18 09:00 | 9:00 | 22 | 31 | 482 |  | low | 2020-09-14 | B13049¦Courtroom 140¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 6 | [5 empty] | 19 | 41 | 458 |  | 2020-09-18 09:00 | 9:00 | 19 | 41 | 458 |  |  | 2020-09-14 | B14164¦Hallway by courtroom 6¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 20 | 40 | 491 | north | 2020-09-18 09:00 | 9:00 | 20 | 40 | 491 |  | caution | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Outdoors |  |  | 12 | 29 | 408 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10002¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 20 | 40 | 449 | South | 2020-09-18 09:00 | 9:00 | 20 | 40 | 449 |  | caution | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 10 | [5 empty] | 20 | 39 | 462 |  | 2020-09-18 09:00 | 9:00 | 20 | 39 | 462 |  | caution | 2020-09-14 | B14164¦Hallway by courtroom 10¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 1st floor cell holding area Hallway | [5 empty] | 21 | 29 | 513 | Across from door #3 - no windows, no plants | 2020-09-18 09:00 | 9:00 | 21 | 29 | 513 |  | low | 2020-09-14 | B13049¦1st floor cell holding area Hallway¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common areaa by elevator, basement | [5 empty] | 20 | 38 | 457 |  | 2020-09-18 09:00 | 9:00 | 20 | 38 | 457 |  | caution | 2020-09-14 | B14164¦Common areaa by elevator, basement¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, ground floor | [5 empty] | 20 | 37 | 456 |  | 2020-09-18 09:00 | 9:00 | 20 | 37 | 456 |  | caution | 2020-09-14 | B14164¦Common area by elevator, ground floor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Outdoors |  |  | 11 | 41 | 444 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10639¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Youth office, ground floor | [5 empty] | 20 | 37 | 494 |  | 2020-09-18 09:00 | 9:00 | 20 | 37 | 494 |  | caution | 2020-09-14 | B14164¦Youth office, ground floor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Family office, ground floor | [5 empty] | 21 | 38 | 504 |  | 2020-09-18 09:00 | 9:00 | 21 | 38 | 504 |  | caution | 2020-09-14 | B14164¦Family office, ground floor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Lobby Administration | [5 empty] | 18 | 50 | 625 |  | 2020-09-18 09:00 | 9:00 | 18 | 50 | 625 |  |  | 2020-09-14 | B10003¦Lobby Administration¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, second floor | [5 empty] | 20 | 37 | 461 |  | 2020-09-18 09:00 | 9:00 | 20 | 37 | 461 |  | caution | 2020-09-14 | B14164¦Common area by elevator, second floor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom M1 north side | [5 empty] | 21 | 34 | 494 |  | 2020-09-18 09:00 | 9:00 | 21 | 34 | 494 |  | low | 2020-09-14 | B10639¦courtroom M1 north side¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Outdoors |  |  | 13 | 35 | 430 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B14164¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Library | [5 empty] | 19 | 47 | 544 | Wall mount AC unit running | 2020-09-18 09:00 | 9:00 | 19 | 47 | 544 |  |  | 2020-09-14 | B10003¦Library¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown Attorney Office | [5 empty] | 23 | 29 | 501 | Office #1 - east side - windows closed, no plants | 2020-09-18 09:00 | 9:00 | 23 | 29 | 501 |  | low | 2020-09-14 | B13049¦Crown Attorney Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom M1 south side | [5 empty] | 21 | 33 | 479 |  | 2020-09-18 09:00 | 9:00 | 21 | 33 | 479 |  | low | 2020-09-14 | B10639¦courtroom M1 south side¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Reception area | [5 empty] | 19 | 44 | 499 |  | 2020-09-18 09:00 | 9:00 | 19 | 44 | 499 |  |  | 2020-09-14 | B70003¦Reception area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Front main hallway | [5 empty] | 20 | 41 | 478 |  | 2020-09-18 09:00 | 9:00 | 20 | 41 | 478 |  |  | 2020-09-14 | B70003¦Front main hallway¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | hallway by Courtroom M1 | [5 empty] | 21 | 32 | 530 |  | 2020-09-18 09:00 | 9:00 | 21 | 32 | 530 |  | low | 2020-09-14 | B10639¦hallway by Courtroom M1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 20 | 40 | 467 | outside of 503 | 2020-09-18 09:00 | 9:00 | 20 | 40 | 467 |  | caution | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown Attorney Office | [5 empty] | 22 | 31 | 562 | Office #2 - north side - windows closed, no plants | 2020-09-18 09:00 | 9:00 | 22 | 31 | 562 |  | low | 2020-09-14 | B13049¦Crown Attorney Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Basement Library | [5 empty] | 22 | 45 | 486 | Heat turned On | 2020-09-18 09:00 | 9:00 | 22 | 45 | 486 |  |  | 2020-09-14 | B10003¦Basement Library¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502, Public area | [5 empty] | 20 | 40 | 489 |  | 2020-09-18 09:00 | 9:00 | 20 | 40 | 489 |  | caution | 2020-09-14 | B70003¦Courtroom 502, Public area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 20 | 39 | 485 | judge area | 2020-09-18 09:00 | 9:00 | 20 | 39 | 485 |  | caution | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 39 | 478 | outside of 503 | 2020-09-18 09:00 | 9:00 | 20 | 39 | 478 |  | caution | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom J | [5 empty] | 22 | 28 | 472 | South | 2020-09-18 09:00 | 9:00 | 22 | 28 | 472 |  | low | 2020-09-14 | B10639¦Courtroom J¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown attorney admin area | [5 empty] | 23 | 30 | 580 | Windows closed, no plants | 2020-09-18 09:00 | 9:00 | 23 | 30 | 580 |  | low | 2020-09-14 | B13049¦Crown attorney admin area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Outdoors |  |  | 12 | 30 | 398 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10003¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 38 | 512 | public area | 2020-09-18 09:00 | 9:00 | 20 | 38 | 512 |  | caution | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom J | [5 empty] | 21 | 27 | 483 | North | 2020-09-18 09:00 | 9:00 | 21 | 27 | 483 |  | low | 2020-09-14 | B10639¦Courtroom J¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 20 | 38 | 493 | judge area | 2020-09-18 09:00 | 9:00 | 20 | 38 | 493 |  | caution | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | hallway by courtroom J | [5 empty] | 22 | 31 | 476 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 476 |  | low | 2020-09-14 | B10639¦hallway by courtroom J¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 38 | 475 | outside 506 | 2020-09-18 09:00 | 9:00 | 20 | 38 | 475 |  | caution | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 21 | 43 | 472 | east | 2020-09-18 09:00 | 9:00 | 21 | 43 | 472 |  |  | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | courtoom 506 | [5 empty] | 20 | 37 | 472 | public area | 2020-09-18 09:00 | 9:00 | 20 | 37 | 472 |  | caution | 2020-09-14 | B70003¦courtoom 506¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 21 | 43 | 478 | west | 2020-09-18 09:00 | 9:00 | 21 | 43 | 478 |  |  | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 20 | 38 | 474 | Judge area | 2020-09-18 09:00 | 9:00 | 20 | 38 | 474 |  | caution | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom G south side | [5 empty] | 22 | 33 | 490 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 490 |  | low | 2020-09-14 | B10639¦courtroom G south side¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 21 | 40 | 471 | east | 2020-09-18 09:00 | 9:00 | 21 | 40 | 471 |  | caution | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 38 | 472 | outside 506 | 2020-09-18 09:00 | 9:00 | 20 | 38 | 472 |  | caution | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Outdoors |  |  | 15 | 36 | 474 |  |  |  | East entrance - sunny, light breeze | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B13095¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 21 | 40 | 483 | west | 2020-09-18 09:00 | 9:00 | 21 | 40 | 483 |  | caution | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 38 | 518 | public | 2020-09-18 09:00 | 9:00 | 20 | 38 | 518 |  | caution | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Hallway | [5 empty] | 20 | 33 | 581 | Window closed, no plants | 2020-09-18 09:00 | 9:00 | 20 | 33 | 581 |  | low | 2020-09-14 | B13095¦Hallway¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 21 | 41 | 496 | east | 2020-09-18 09:00 | 9:00 | 21 | 41 | 496 |  |  | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 20 | 38 | 474 | judge area | 2020-09-18 09:00 | 9:00 | 20 | 38 | 474 |  | caution | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 21 | 40 | 487 | west | 2020-09-18 09:00 | 9:00 | 21 | 40 | 487 |  | caution | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 20 | 38 | 502 | outside 510 | 2020-09-18 09:00 | 9:00 | 20 | 38 | 502 |  | caution | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom G south side | [5 empty] | 22 | 33 | 468 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 468 |  | low | 2020-09-14 | B10639¦courtroom G south side¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 21 | 41 | 486 | east | 2020-09-18 09:00 | 9:00 | 21 | 41 | 486 |  |  | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 21 | 41 | 493 | west | 2020-09-18 09:00 | 9:00 | 21 | 41 | 493 |  |  | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | office - B04A | [5 empty] | 19 | 33 | 480 | Windows closed, no plants | 2020-09-18 09:00 | 9:00 | 19 | 33 | 480 |  | low | 2020-09-14 | B13095¦office - B04A¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Outdoors |  |  | 8 | 45 | 400 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B11589¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 121 | [5 empty] | 22 | 36 | 520 | West | 2020-09-18 09:00 | 9:00 | 22 | 36 | 520 |  | caution | 2020-09-14 | B10639¦Courtroom 121¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 121 | [5 empty] | 21 | 36 | 497 | Easr | 2020-09-18 09:00 | 9:00 | 21 | 36 | 497 |  | caution | 2020-09-14 | B10639¦Courtroom 121¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Main Lobby | [5 empty] | 21 | 34 | 541 | 1 window open, no plants | 2020-09-18 09:00 | 9:00 | 21 | 34 | 541 |  | low | 2020-09-14 | B13095¦Main Lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 123 | [5 empty] | 21 | 29 | 465 | East | 2020-09-18 09:00 | 9:00 | 21 | 29 | 465 |  | low | 2020-09-14 | B10639¦Courtroom 123¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Security Desk | [5 empty] | 17 | 43 | 463 |  | 2020-09-18 09:00 | 9:00 | 17 | 43 | 463 |  |  | 2020-09-14 | B11589¦Security Desk¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 123 | [5 empty] | 21 | 29 | 470 | West | 2020-09-18 09:00 | 9:00 | 21 | 29 | 470 |  | low | 2020-09-14 | B10639¦Courtroom 123¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 50 | 474 | east | 2020-09-18 09:00 | 9:00 | 22 | 50 | 474 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 124 east side | [5 empty] | 22 | 36 | 508 |  | 2020-09-18 09:00 | 9:00 | 22 | 36 | 508 |  | caution | 2020-09-14 | B10639¦courtroom 124 east side¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 50 | 474 | west | 2020-09-18 09:00 | 9:00 | 22 | 50 | 474 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom A | [5 empty] | 20 | 38 | 430 |  | 2020-09-18 09:00 | 9:00 | 20 | 38 | 430 |  | caution | 2020-09-14 | B11589¦Courtroom A¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 124 west side | [5 empty] | 22 | 37 | 470 |  | 2020-09-18 09:00 | 9:00 | 22 | 37 | 470 |  | caution | 2020-09-14 | B10639¦courtroom 124 west side¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom D | [5 empty] | 21 | 30 | 495 |  | 2020-09-18 09:00 | 9:00 | 21 | 30 | 495 |  | low | 2020-09-14 | B11589¦Courtroom D¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 51 | 479 | east | 2020-09-18 09:00 | 9:00 | 22 | 51 | 479 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 125 | [5 empty] | 21 | 33 | 450 | South | 2020-09-18 09:00 | 9:00 | 21 | 33 | 450 |  | low | 2020-09-14 | B10639¦Courtroom 125¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 51 | 481 | west | 2020-09-18 09:00 | 9:00 | 22 | 51 | 481 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 125 | [5 empty] | 21 | 32 | 454 | North | 2020-09-18 09:00 | 9:00 | 21 | 32 | 454 |  | low | 2020-09-14 | B10639¦Courtroom 125¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | courtoom 510 | [5 empty] | 20 | 38 | 502 | public area ` | 2020-09-18 09:00 | 9:00 | 20 | 38 | 502 |  | caution | 2020-09-14 | B70003¦courtoom 510¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 50 | 480 | east | 2020-09-18 09:00 | 9:00 | 21 | 50 | 480 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtoom 510 | [5 empty] | 20 | 37 | 486 | judge area | 2020-09-18 09:00 | 9:00 | 20 | 37 | 486 |  | caution | 2020-09-14 | B70003¦Courtoom 510¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 21 | 50 | 479 | west | 2020-09-18 09:00 | 9:00 | 21 | 50 | 479 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | courtroom 126 south side | [5 empty] | 21 | 31 | 513 |  | 2020-09-18 09:00 | 9:00 | 21 | 31 | 513 |  | low | 2020-09-14 | B10639¦courtroom 126 south side¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | courtroom c | [5 empty] | 21 | 29 | 439 |  | 2020-09-18 09:00 | 9:00 | 21 | 29 | 439 |  | low | 2020-09-14 | B11589¦courtroom c¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Back main hallway | [5 empty] | 21 | 38 | 481 |  | 2020-09-18 09:00 | 9:00 | 21 | 38 | 481 |  | caution | 2020-09-14 | B70003¦Back main hallway¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 50 | 490 | east | 2020-09-18 09:00 | 9:00 | 22 | 50 | 490 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | hallway by courtroom 126 | [5 empty] | 21 | 29 | 525 |  | 2020-09-18 09:00 | 9:00 | 21 | 29 | 525 |  | low | 2020-09-14 | B10639¦hallway by courtroom 126¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Elevator area, second floor | [5 empty] | 21 | 37 | 496 |  | 2020-09-18 09:00 | 9:00 | 21 | 37 | 496 |  | caution | 2020-09-14 | B70003¦Elevator area, second floor¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 50 | 479 | west | 2020-09-18 09:00 | 9:00 | 22 | 50 | 479 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom B | [5 empty] | 21 | 29 | 417 |  | 2020-09-18 09:00 | 9:00 | 21 | 29 | 417 |  | low | 2020-09-14 | B11589¦Courtroom B¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 22 | 32 | 491 | east | 2020-09-18 09:00 | 9:00 | 22 | 32 | 491 |  | low | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Outdoors |  |  | 13 | 35 | 430 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70003¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 22 | 32 | 481 | west | 2020-09-18 09:00 | 9:00 | 22 | 32 | 481 |  | low | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway | [5 empty] | 21 | 28 | 488 | By receiving | 2020-09-18 09:00 | 9:00 | 21 | 28 | 488 |  | low | 2020-09-14 | B10639¦Hallway¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 22 | 33 | 523 | east | 2020-09-18 09:00 | 9:00 | 22 | 33 | 523 |  | low | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom E | [5 empty] | 20 | 27 | 441 |  | 2020-09-18 09:00 | 9:00 | 20 | 27 | 441 |  | low | 2020-09-14 | B11589¦Courtroom E¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 22 | 33 | 515 | west | 2020-09-18 09:00 | 9:00 | 22 | 33 | 515 |  | low | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office, Walker | [5 empty] | 21 | 32 | 447 |  | 2020-09-18 09:00 | 9:00 | 21 | 32 | 447 |  | low | 2020-09-14 | B11589¦Office, Walker¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Outdoors |  |  | 11 | 40 | 432 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B10639¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | lunch room on B2 level | [5 empty] | 20 | 33 | 504 |  | 2020-09-18 09:00 | 9:00 | 20 | 33 | 504 |  | low | 2020-09-14 | B91122¦lunch room on B2 level¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | hallway by Room B2-10 | [5 empty] | 20 | 35 | 536 |  | 2020-09-18 09:00 | 9:00 | 20 | 35 | 536 |  | caution | 2020-09-14 | B91122¦hallway by Room B2-10¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office, Martin | [5 empty] | 21 | 32 | 419 |  | 2020-09-18 09:00 | 9:00 | 21 | 32 | 419 |  | low | 2020-09-14 | B11589¦Office, Martin¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 6 | [5 empty] | 20 | 28 | 473 | North | 2020-09-18 09:00 | 9:00 | 20 | 28 | 473 |  | low | 2020-09-14 | B10639¦Courtroom 6¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | file room A, B2 level | [5 empty] | 20 | 43 | 595 |  | 2020-09-18 09:00 | 9:00 | 20 | 43 | 595 |  |  | 2020-09-14 | B91122¦file room A, B2 level¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | 2nd Floor Holding Cell (hallway) Courtroom 6 | [5 empty] | 20 | 29 | 452 | South | 2020-09-18 09:00 | 9:00 | 20 | 29 | 452 |  | low | 2020-09-14 | B10639¦2nd Floor Holding Cell (hallway) Courtroom 6¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | file room B, B2 level | [5 empty] | 21 | 45 | 547 |  | 2020-09-18 09:00 | 9:00 | 21 | 45 | 547 |  |  | 2020-09-14 | B91122¦file room B, B2 level¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office, Baker | [5 empty] | 21 | 30 | 409 |  | 2020-09-18 09:00 | 9:00 | 21 | 30 | 409 |  | low | 2020-09-14 | B11589¦Office, Baker¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | office area, B2 level | [5 empty] | 21 | 42 | 627 |  | 2020-09-18 09:00 | 9:00 | 21 | 42 | 627 |  |  | 2020-09-14 | B91122¦office area, B2 level¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 22 | 39 | 504 | east | 2020-09-18 09:00 | 9:00 | 22 | 39 | 504 |  | caution | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 22 | 39 | 508 | west | 2020-09-18 09:00 | 9:00 | 22 | 39 | 508 |  | caution | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | attorney general admin office | [5 empty] | 22 | 30 | 485 |  | 2020-09-18 09:00 | 9:00 | 22 | 30 | 485 |  | low | 2020-09-14 | B11589¦attorney general admin office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 6 | [5 empty] | 20 | 29 | 458 |  | 2020-09-18 09:00 | 9:00 | 20 | 29 | 458 |  | low | 2020-09-14 | B10639¦Hallway by courtroom 6¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 22 | 40 | 517 | east | 2020-09-18 09:00 | 9:00 | 22 | 40 | 517 |  | caution | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Hallway | [5 empty] | 22 | 30 | 472 |  | 2020-09-18 09:00 | 9:00 | 22 | 30 | 472 |  | low | 2020-09-14 | B11589¦Hallway¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 23 | 40 | 502 | west | 2020-09-18 09:00 | 9:00 | 23 | 40 | 502 |  | caution | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Outdoors |  |  | 13 | 34 | 484 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B91122¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 5 | [5 empty] | 20 | 36 | 435 | North | 2020-09-18 09:00 | 9:00 | 20 | 36 | 435 |  | caution | 2020-09-14 | B10639¦Courtroom 5¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom H | [5 empty] | 22 | 29 | 426 |  | 2020-09-18 09:00 | 9:00 | 22 | 29 | 426 |  | low | 2020-09-14 | B11589¦Courtroom H¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 5 | [5 empty] | 21 | 35 | 505 | South | 2020-09-18 09:00 | 9:00 | 21 | 35 | 505 |  | caution | 2020-09-14 | B10639¦Courtroom 5¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom J | [5 empty] | 22 | 26 | 405 |  | 2020-09-18 09:00 | 9:00 | 22 | 26 | 405 |  | low | 2020-09-14 | B11589¦Courtroom J¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 5 | [5 empty] | 20 | 28 | 465 |  | 2020-09-18 09:00 | 9:00 | 20 | 28 | 465 |  | low | 2020-09-14 | B10639¦Hallway by courtroom 5¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Lunch Room | [5 empty] | 23 | 30 | 511 |  | 2020-09-18 09:00 | 9:00 | 23 | 30 | 511 |  | low | 2020-09-14 | B70451¦Lunch Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | hallway by courtroom 3 | [5 empty] | 20 | 30 | 460 |  | 2020-09-18 09:00 | 9:00 | 20 | 30 | 460 |  | low | 2020-09-14 | B10639¦hallway by courtroom 3¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 21 | 34 | 505 | east | 2020-09-18 09:00 | 9:00 | 21 | 34 | 505 |  | low | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 21 | 35 | 502 | west | 2020-09-18 09:00 | 9:00 | 21 | 35 | 502 |  | caution | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Outdoors |  |  | 9 | 42 | 426 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B12955¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 3 | [5 empty] | 21 | 30 | 527 | Southeast | 2020-09-18 09:00 | 9:00 | 21 | 30 | 527 |  | low | 2020-09-14 | B10639¦Courtroom 3¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 602 | [5 empty] | 22 | 35 | 530 |  | 2020-09-18 09:00 | 9:00 | 22 | 35 | 530 |  | caution | 2020-09-14 | B70451¦hallway by courtroom 602¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Main Floor Entrance Lobby | [5 empty] | 11 | 47 | 470 | front lobby | 2020-09-18 09:00 | 9:00 | 11 | 47 | 470 |  |  | 2020-09-14 | B12955¦Main Floor Entrance Lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 603 | [5 empty] | 22 | 35 | 515 |  | 2020-09-18 09:00 | 9:00 | 22 | 35 | 515 |  | caution | 2020-09-14 | B70451¦hallway by courtroom 603¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 3 | [5 empty] | 21 | 30 | 470 | Northwest | 2020-09-18 09:00 | 9:00 | 21 | 30 | 470 |  | low | 2020-09-14 | B10639¦Courtroom 3¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Waiting Room | [5 empty] | 13 | 50 | 488 | waiting area | 2020-09-18 09:00 | 9:00 | 13 | 50 | 488 |  |  | 2020-09-14 | B12955¦Waiting Room¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Administration office | [5 empty] | 16 | 48 | 515 |  | 2020-09-18 09:00 | 9:00 | 16 | 48 | 515 |  |  | 2020-09-14 | B12955¦Administration office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | conference room 4 | [5 empty] | 22 | 31 | 485 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 485 |  | low | 2020-09-14 | B70451¦conference room 4¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 203 | [5 empty] | 19 | 42 | 506 |  | 2020-09-18 09:00 | 9:00 | 19 | 42 | 506 |  |  | 2020-09-14 | B12955¦Courtroom 203¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | lobby by statue | [5 empty] | 20 | 31 | 451 |  | 2020-09-18 09:00 | 9:00 | 20 | 31 | 451 |  | low | 2020-09-14 | B10639¦lobby by statue¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 22 | 35 | 517 | east | 2020-09-18 09:00 | 9:00 | 22 | 35 | 517 |  | caution | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 103 | [5 empty] | 19 | 38 | 436 |  | 2020-09-18 09:00 | 9:00 | 19 | 38 | 436 |  | caution | 2020-09-14 | B12955¦Courtroom 103¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 35 | 487 | west | 2020-09-18 09:00 | 9:00 | 23 | 35 | 487 |  | caution | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby East Side | [5 empty] | 20 | 32 | 472 |  | 2020-09-18 09:00 | 9:00 | 20 | 32 | 472 |  | low | 2020-09-14 | B10639¦Entrance Lobby East Side¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby West Side | [5 empty] | 20 | 32 | 476 |  | 2020-09-18 09:00 | 9:00 | 20 | 32 | 476 |  | low | 2020-09-14 | B10639¦Entrance Lobby West Side¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by COA intake office | [5 empty] | 20 | 31 | 470 |  | 2020-09-18 09:00 | 9:00 | 20 | 31 | 470 |  | low | 2020-09-14 | B10639¦Hallway by COA intake office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 607 | [5 empty] | 23 | 34 | 490 |  | 2020-09-18 09:00 | 9:00 | 23 | 34 | 490 |  | low | 2020-09-14 | B70451¦hallway by courtroom 607¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by Law Society of Ontario | [5 empty] | 20 | 32 | 465 |  | 2020-09-18 09:00 | 9:00 | 20 | 32 | 465 |  | low | 2020-09-14 | B10639¦Hallway by Law Society of Ontario¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | enforcement office | [5 empty] | 23 | 30 | 523 |  | 2020-09-18 09:00 | 9:00 | 23 | 30 | 523 |  | low | 2020-09-14 | B70451¦enforcement office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 22 | 31 | 482 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 482 |  | low | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 22 | 31 | 480 | west | 2020-09-18 09:00 | 9:00 | 22 | 31 | 480 |  | low | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 605 | [5 empty] | 22 | 32 | 508 |  | 2020-09-18 09:00 | 9:00 | 22 | 32 | 508 |  | low | 2020-09-14 | B70451¦hallway by courtroom 605¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters admin office | [5 empty] | 23 | 30 | 541 |  | 2020-09-18 09:00 | 9:00 | 23 | 30 | 541 |  | low | 2020-09-14 | B70451¦masters admin office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-10 | [5 empty] | 23 | 27 | 495 |  | 2020-09-18 09:00 | 9:00 | 23 | 27 | 495 |  | low | 2020-09-14 | B70451¦room 6-10¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-9 | [5 empty] | 22 | 28 | 491 |  | 2020-09-18 09:00 | 9:00 | 22 | 28 | 491 |  | low | 2020-09-14 | B70451¦room 6-9¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters library | [5 empty] | 22 | 31 | 484 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 484 |  | low | 2020-09-14 | B70451¦masters library¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | reception area-masters | [5 empty] | 22 | 30 | 500 |  | 2020-09-18 09:00 | 9:00 | 22 | 30 | 500 |  | low | 2020-09-14 | B70451¦reception area-masters¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Outdoors |  |  | 13 | 34 | 484 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B70451¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Library | [5 empty] | 21.1111 | 33 | 531 |  | 2020-09-18 12:00 | 12:00 | 21.1111 | 33 | 531 |  | low | 2020-09-14 | B10246¦Library¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Justice Wilcox Chambers | [5 empty] | 21.1111 | 31 | 484 |  | 2020-09-18 12:00 | 12:00 | 21.1111 | 31 | 484 |  | low | 2020-09-14 | B10246¦Justice Wilcox Chambers¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Outdoors |  |  | 16 | 25 | 426 |  |  |  | North entrance - sunny, light breeze | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B21030¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | 2nd fl lobby | [5 empty] | 21.1111 | 30 | 469 | Middle of hallway | 2020-09-18 12:00 | 12:00 | 21.1111 | 30 | 469 |  | low | 2020-09-14 | B10246¦2nd fl lobby¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 2 | [5 empty] | 21.1111 | 32 | 485 |  | 2020-09-18 12:00 | 12:00 | 21.1111 | 32 | 485 |  | low | 2020-09-14 | B10246¦Courtroom 2¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Lunch Room | [5 empty] | 23 | 28 | 539 |  | 2020-09-18 12:00 | 12:00 | 23 | 28 | 539 |  | low | 2020-09-14 | B70451¦Lunch Room¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 22 | 29 | 501 | east | 2020-09-18 12:00 | 12:00 | 22 | 29 | 501 |  | low | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Skeggs | [5 empty] | 21 | 31 | 623 | Door Open | 2020-09-18 12:00 | 12:00 | 21 | 31 | 623 |  | low | 2020-09-14 | B10002¦Office Skeggs¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 22 | 29 | 503 | west | 2020-09-18 12:00 | 12:00 | 22 | 29 | 503 |  | low | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Boardroom used as a courtroom | [5 empty] | 21 | 28 | 485 | Windows closed, no plants | 2020-09-18 09:00 | 9:00 | 21 | 28 | 485 |  | low | 2020-09-14 | B21030¦Boardroom used as a courtroom¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 602 | [5 empty] | 23 | 30 | 505 |  | 2020-09-18 12:00 | 12:00 | 23 | 30 | 505 |  | low | 2020-09-14 | B70451¦hallway by courtroom 602¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 603 | [5 empty] | 23 | 29 | 498 |  | 2020-09-18 12:00 | 12:00 | 23 | 29 | 498 |  | low | 2020-09-14 | B70451¦hallway by courtroom 603¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | conference room 4 | [5 empty] | 23 | 26 | 475 |  | 2020-09-18 12:00 | 12:00 | 23 | 26 | 475 |  | low | 2020-09-14 | B70451¦conference room 4¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Trial Co-ordinators Office | [5 empty] | 21.1111 | 29 | 495 |  | 2020-09-18 12:00 | 12:00 | 21.1111 | 29 | 495 |  | low | 2020-09-14 | B10246¦Trial Co-ordinators Office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Main Floor Entrance Lobby | [5 empty] | 21.1111 | 30 | 489 | Middle of hallway | 2020-09-18 12:00 | 12:00 | 21.1111 | 30 | 489 |  | low | 2020-09-14 | B10246¦Main Floor Entrance Lobby¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Cubicle Office | [5 empty] | 22 | 29 | 621 | Door Open | 2020-09-18 12:00 | 12:00 | 22 | 29 | 621 |  | low | 2020-09-14 | B10002¦Cubicle Office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 31 | 489 | east | 2020-09-18 12:00 | 12:00 | 23 | 31 | 489 |  | low | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Administration office | [5 empty] | 23 | 26 | 586 | Windows closed - 4 plants total along South window | 2020-09-18 09:00 | 9:00 | 23 | 26 | 586 |  | low | 2020-09-14 | B21030¦Administration office¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 31 | 476 | west | 2020-09-18 12:00 | 12:00 | 23 | 31 | 476 |  | low | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 607 | [5 empty] | 23 | 29 | 486 |  | 2020-09-18 12:00 | 12:00 | 23 | 29 | 486 |  | low | 2020-09-14 | B70451¦hallway by courtroom 607¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 20.5556 | 31 | 495 | Office to the left of Office 10 | 2020-09-18 12:00 | 12:00 | 20.5556 | 31 | 495 |  | low | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | enforcement office | [5 empty] | 23 | 26 | 497 |  | 2020-09-18 12:00 | 12:00 | 23 | 26 | 497 |  | low | 2020-09-14 | B70451¦enforcement office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 23 | 28 | 491 | east | 2020-09-18 12:00 | 12:00 | 23 | 28 | 491 |  | low | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | File Room | [5 empty] | 23 | 30 | 692 |  | 2020-09-18 12:00 | 12:00 | 23 | 30 | 692 |  | low | 2020-09-14 | B10002¦File Room¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 22 | 28 | 476 | west | 2020-09-18 12:00 | 12:00 | 22 | 28 | 476 |  | low | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 20.5556 | 31 | 477 | Office to the right of office 10 | 2020-09-18 12:00 | 12:00 | 20.5556 | 31 | 477 |  | low | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 605 | [5 empty] | 22 | 28 | 487 |  | 2020-09-18 12:00 | 12:00 | 22 | 28 | 487 |  | low | 2020-09-14 | B70451¦hallway by courtroom 605¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Courtroom 113 | [5 empty] | 23 | 24 | 522 | Windows closed, no plants | 2020-09-18 09:00 | 9:00 | 23 | 24 | 522 |  | low | 2020-09-14 | B21030¦Courtroom 113¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters admin office | [5 empty] | 23 | 26 | 524 |  | 2020-09-18 12:00 | 12:00 | 23 | 26 | 524 |  | low | 2020-09-14 | B70451¦masters admin office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-10 | [5 empty] | 23 | 25 | 475 |  | 2020-09-18 12:00 | 12:00 | 23 | 25 | 475 |  | low | 2020-09-14 | B70451¦room 6-10¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Reception area | [5 empty] | 21 | 32 | 530 |  | 2020-09-18 12:00 | 12:00 | 21 | 32 | 530 |  | low | 2020-09-14 | B70003¦Reception area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-9 | [5 empty] | 22 | 25 | 481 |  | 2020-09-18 12:00 | 12:00 | 22 | 25 | 481 |  | low | 2020-09-14 | B70451¦room 6-9¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Front main hallway | [5 empty] | 21 | 31 | 515 |  | 2020-09-18 12:00 | 12:00 | 21 | 31 | 515 |  | low | 2020-09-14 | B70003¦Front main hallway¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters library | [5 empty] | 22 | 27 | 483 |  | 2020-09-18 12:00 | 12:00 | 22 | 27 | 483 |  | low | 2020-09-14 | B70451¦masters library¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 31 | 513 | outside of 502 | 2020-09-18 12:00 | 12:00 | 21 | 31 | 513 |  | low | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-4 | [5 empty] | 22 | 27 | 493 |  | 2020-09-18 12:00 | 12:00 | 22 | 27 | 493 |  | low | 2020-09-14 | B70451¦room 6-4¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Didiodato | [5 empty] | 22 | 31 | 680 | Door Open | 2020-09-18 12:00 | 12:00 | 22 | 31 | 680 |  | low | 2020-09-14 | B10002¦Office Didiodato¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 30 | 516 | public | 2020-09-18 12:00 | 12:00 | 21 | 30 | 516 |  | low | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | reception area-masters | [5 empty] | 22 | 27 | 488 |  | 2020-09-18 12:00 | 12:00 | 22 | 27 | 488 |  | low | 2020-09-14 | B70451¦reception area-masters¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Outdoors |  |  | 17 | 28 | 514 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70451¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 32 | 502 | judge area | 2020-09-18 12:00 | 12:00 | 21 | 32 | 502 |  | low | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 31 | 514 | outside of 503 | 2020-09-18 12:00 | 12:00 | 21 | 31 | 514 |  | low | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 33 | 555 | public area | 2020-09-18 12:00 | 12:00 | 21 | 33 | 555 |  | low | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | 2nd Floor Holding Cell (hallway) | [5 empty] | 23 | 25 | 491 | Windows closed, no plants | 2020-09-18 09:00 | 9:00 | 23 | 25 | 491 |  | low | 2020-09-14 | B21030¦2nd Floor Holding Cell (hallway)¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 32 | 558 | judge area | 2020-09-18 12:00 | 12:00 | 21 | 32 | 558 |  | low | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Outdoors |  |  | 11 | 41 | 444 |  |  |  |  | 2020-09-18 09:00 | 9:00 | [5 empty] | 2020-09-14 | B20265¦Outdoors¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 21 | 31 | 511 | outside 506 | 2020-09-18 12:00 | 12:00 | 21 | 31 | 511 |  | low | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Lobby | [5 empty] | 23 | 25 | 561 |  | 2020-09-18 12:00 | 12:00 | 23 | 25 | 561 |  | low | 2020-09-14 | B10002¦Lobby¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 1 (Center) | [5 empty] | 20.5556 | 26.2 | 457 |  | 2020-09-18 12:00 | 12:00 | 20.5556 | 26.2 | 457 |  | low | 2020-09-14 | B10246¦Courtroom 1 (Center)¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 21 | 30 | 483 | public area | 2020-09-18 12:00 | 12:00 | 21 | 30 | 483 |  | low | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown attorney admin area | [5 empty] | 21.6667 | 32 | 497 |  | 2020-09-18 12:00 | 12:00 | 21.6667 | 32 | 497 |  | low | 2020-09-14 | B10246¦Crown attorney admin area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 21 | 31 | 482 | judge area | 2020-09-18 12:00 | 12:00 | 21 | 31 | 482 |  | low | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 21 | 32 | 517 | outside 509 | 2020-09-18 12:00 | 12:00 | 21 | 32 | 517 |  | low | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 north side | [5 empty] | 21 | 34 | 494 |  | 2020-09-18 09:00 | 9:00 | 21 | 34 | 494 |  | low | 2020-09-14 | B20265¦courtroom M1 north side¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 21 | 32 | 537 | public | 2020-09-18 12:00 | 12:00 | 21 | 32 | 537 |  | low | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Administration office | [5 empty] | 21.1111 | 29 | 516 |  | 2020-09-18 12:00 | 12:00 | 21.1111 | 29 | 516 |  | low | 2020-09-14 | B10246¦Administration office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 21 | 31 | 551 | judge area | 2020-09-18 12:00 | 12:00 | 21 | 31 | 551 |  | low | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Basement lobby - bottom of stairs | [5 empty] | 21.1111 | 30 | 481 |  | 2020-09-18 12:00 | 12:00 | 21.1111 | 30 | 481 |  | low | 2020-09-14 | B10246¦Basement lobby - bottom of stairs¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 south side | [5 empty] | 21 | 33 | 479 |  | 2020-09-18 09:00 | 9:00 | 21 | 33 | 479 |  | low | 2020-09-14 | B20265¦courtroom M1 south side¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Outdoors |  |  | 15 | 22 | 397 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10002¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 21 | 32 | 519 | outside 510 | 2020-09-18 12:00 | 12:00 | 21 | 32 | 519 |  | low | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by Courtroom M1 | [5 empty] | 21 | 32 | 530 |  | 2020-09-18 09:00 | 9:00 | 21 | 32 | 530 |  | low | 2020-09-14 | B20265¦hallway by Courtroom M1¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown attorney lobby | [5 empty] | 23 | 26 | 636 | No windows, no plants | 2020-09-18 09:00 | 9:00 | 23 | 26 | 636 |  | low | 2020-09-14 | B21030¦Crown attorney lobby¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 21 | 31 | 504 | public area | 2020-09-18 12:00 | 12:00 | 21 | 31 | 504 |  | low | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 10 | [5 empty] | 21 | 32 | 517 | judge area | 2020-09-18 12:00 | 12:00 | 21 | 32 | 517 |  | low | 2020-09-14 | B70003¦Courtroom 10¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Basement cells - hallway | [5 empty] | 20.5556 | 33 | 479 |  | 2020-09-18 12:00 | 12:00 | 20.5556 | 33 | 479 |  | low | 2020-09-14 | B10246¦Basement cells - hallway¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | back main hallway | [5 empty] | 21 | 32 | 533 |  | 2020-09-18 12:00 | 12:00 | 21 | 32 | 533 |  | low | 2020-09-14 | B70003¦back main hallway¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom J | [5 empty] | 22 | 28 | 472 | South | 2020-09-18 09:00 | 9:00 | 22 | 28 | 472 |  | low | 2020-09-14 | B20265¦Courtroom J¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Elevator area, second floor | [5 empty] | 21 | 31 | 532 |  | 2020-09-18 12:00 | 12:00 | 21 | 31 | 532 |  | low | 2020-09-14 | B70003¦Elevator area, second floor¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Outdoors |  |  | 7.7778 | 44 | 411 |  |  |  | Directly outside main entrance: overcast | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10246¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Outdoors |  |  | 19 | 22 | 407 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B70003¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Lobby Administration | [5 empty] | 18 | 46 | 486 |  | 2020-09-18 12:00 | 12:00 | 18 | 46 | 486 |  |  | 2020-09-14 | B10003¦Lobby Administration¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom J | [5 empty] | 21 | 27 | 483 | North | 2020-09-18 09:00 | 9:00 | 21 | 27 | 483 |  | low | 2020-09-14 | B20265¦Courtroom J¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown attorney admin area | [5 empty] | 23 | 25 | 527 | Windows closed, no plants | 2020-09-18 09:00 | 9:00 | 23 | 25 | 527 |  | low | 2020-09-14 | B21030¦Crown attorney admin area¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 20 | 39 | 634 | north section | 2020-09-18 12:00 | 12:00 | 20 | 39 | 634 |  | caution | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 20 | 38 | 705 | south section | 2020-09-18 12:00 | 12:00 | 20 | 38 | 705 |  | caution | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by Courtroom 1E | [5 empty] | 20 | 35 | 563 |  | 2020-09-18 12:00 | 12:00 | 20 | 35 | 563 |  | caution | 2020-09-14 | B14164¦Hallway by Courtroom 1E¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 19 | 40 | 649 | north section | 2020-09-18 12:00 | 12:00 | 19 | 40 | 649 |  | caution | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [5 empty] | 20 | 41 | 709 | south section | 2020-09-18 12:00 | 12:00 | 20 | 41 | 709 |  |  | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Library | [5 empty] | 19 | 46 | 440 | Wall mount AC unit running | 2020-09-18 12:00 | 12:00 | 19 | 46 | 440 |  |  | 2020-09-14 | B10003¦Library¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 6 | [5 empty] | 19 | 37 | 588 |  | 2020-09-18 12:00 | 12:00 | 19 | 37 | 588 |  | caution | 2020-09-14 | B14164¦Hallway by courtroom 6¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 20 | 40 | 778 | north | 2020-09-18 12:00 | 12:00 | 20 | 40 | 778 |  | caution | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 23 | 24 | 477 | Office #1 - SW corner - windows closed, no plants | 2020-09-18 09:00 | 9:00 | 23 | 24 | 477 |  | low | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 21 | 40 | 755 | south section | 2020-09-18 12:00 | 12:00 | 21 | 40 | 755 |  | caution | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 10 | [5 empty] | 21 | 34 | 588 |  | 2020-09-18 12:00 | 12:00 | 21 | 34 | 588 |  | low | 2020-09-14 | B14164¦Hallway by courtroom 10¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Basement Library | [5 empty] | 21 | 47 | 528 |  | 2020-09-18 12:00 | 12:00 | 21 | 47 | 528 |  |  | 2020-09-14 | B10003¦Basement Library¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, ground floor | [5 empty] | 21 | 34 | 504 |  | 2020-09-18 12:00 | 12:00 | 21 | 34 | 504 |  | low | 2020-09-14 | B14164¦Common area by elevator, ground floor¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 22 | 25 | 506 | Office #2 - NE corner - no windows, no plants | 2020-09-18 09:00 | 9:00 | 22 | 25 | 506 |  | low | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, basement | [5 empty] | 21 | 34 | 498 |  | 2020-09-18 12:00 | 12:00 | 21 | 34 | 498 |  | low | 2020-09-14 | B14164¦Common area by elevator, basement¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Youth office, ground floor | [5 empty] | 21 | 36 | 571 |  | 2020-09-18 12:00 | 12:00 | 21 | 36 | 571 |  | caution | 2020-09-14 | B14164¦Youth office, ground floor¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Family office, ground floor | [5 empty] | 21 | 35 | 517 |  | 2020-09-18 12:00 | 12:00 | 21 | 35 | 517 |  | caution | 2020-09-14 | B14164¦Family office, ground floor¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, second floor | [5 empty] | 21 | 34 | 519 |  | 2020-09-18 12:00 | 12:00 | 21 | 34 | 519 |  | low | 2020-09-14 | B14164¦Common area by elevator, second floor¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Outdoors |  |  | 15 | 23 | 403 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10003¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Outdoors |  |  | 19 | 22 | 407 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B14164¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Outdoors |  |  | 12 | 30 | 357 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B11589¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Security Desk | [5 empty] | 19 | 32 | 494 |  | 2020-09-18 12:00 | 12:00 | 19 | 32 | 494 |  | low | 2020-09-14 | B11589¦Security Desk¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom J | [5 empty] | 22 | 31 | 476 |  | 2020-09-18 09:00 | 9:00 | 22 | 31 | 476 |  | low | 2020-09-14 | B20265¦hallway by courtroom J¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G north side | [5 empty] | 22 | 33 | 490 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 490 |  | low | 2020-09-14 | B20265¦courtroom G north side¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G north side | [5 empty] | 22 | 33 | 468 |  | 2020-09-18 09:00 | 9:00 | 22 | 33 | 468 |  | low | 2020-09-14 | B20265¦courtroom G north side¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom A | [5 empty] | 20 | 26 | 417 |  | 2020-09-18 12:00 | 12:00 | 20 | 26 | 417 |  | low | 2020-09-14 | B11589¦Courtroom A¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 121 | [5 empty] | 22 | 36 | 520 | West | 2020-09-18 09:00 | 9:00 | 22 | 36 | 520 |  | caution | 2020-09-14 | B20265¦Courtroom 121¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 121 | [5 empty] | 21 | 36 | 497 | East | 2020-09-18 09:00 | 9:00 | 21 | 36 | 497 |  | caution | 2020-09-14 | B20265¦Courtroom 121¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom B | [5 empty] | 21 | 24 | 401 |  | 2020-09-18 12:00 | 12:00 | 21 | 24 | 401 |  | low | 2020-09-14 | B11589¦Courtroom B¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 123 | [5 empty] | 21 | 29 | 465 | East | 2020-09-18 09:00 | 9:00 | 21 | 29 | 465 |  | low | 2020-09-14 | B20265¦Courtroom 123¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom C | [5 empty] | 21 | 23 | 454 |  | 2020-09-18 12:00 | 12:00 | 21 | 23 | 454 |  | low | 2020-09-14 | B11589¦Courtroom C¦¦Sep-18-2020 12:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 123 | [5 empty] | 21 | 29 | 470 | West | 2020-09-18 09:00 | 9:00 | 21 | 29 | 470 |  | low | 2020-09-14 | B20265¦Courtroom 123¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 east side | [5 empty] | 22 | 36 | 508 |  | 2020-09-18 09:00 | 9:00 | 22 | 36 | 508 |  | caution | 2020-09-14 | B20265¦courtroom 124 east side¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 west side | [5 empty] | 22 | 37 | 470 |  | 2020-09-18 09:00 | 9:00 | 22 | 37 | 470 |  | caution | 2020-09-14 | B20265¦courtroom 124 west side¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 125 | [5 empty] | 21 | 33 | 450 | South | 2020-09-18 09:00 | 9:00 | 21 | 33 | 450 |  | low | 2020-09-14 | B20265¦Courtroom 125¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 125 | [5 empty] | 21 | 21 | 454 | North | 2020-09-18 09:00 | 9:00 | 21 | 21 | 454 |  | low | 2020-09-14 | B20265¦Courtroom 125¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 126 south side | [5 empty] | 21 | 31 | 513 |  | 2020-09-18 09:00 | 9:00 | 21 | 31 | 513 |  | low | 2020-09-14 | B20265¦courtroom 126 south side¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom 126 | [5 empty] | 21 | 29 | 525 |  | 2020-09-18 09:00 | 9:00 | 21 | 29 | 525 |  | low | 2020-09-14 | B20265¦hallway by courtroom 126¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Hallway | [5 empty] | 21 | 28 | 488 | By receiving | 2020-09-18 09:00 | 9:00 | 21 | 28 | 488 |  | low | 2020-09-14 | B20265¦Hallway¦¦Sep-18-2020 09:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Outdoors |  |  | 16 | 22 | 445 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B20265¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom D | [5 empty] | 21 | 28 | 530 |  | 2020-09-18 12:00 | 12:00 | 21 | 28 | 530 |  | low | 2020-09-14 | B11589¦Courtroom D¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 north side | [5 empty] | 22 | 29 | 566 |  | 2020-09-18 12:00 | 12:00 | 22 | 29 | 566 |  | low | 2020-09-14 | B20265¦courtroom M1 north side¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom M1 south side | [5 empty] | 22 | 28 | 557 |  | 2020-09-18 12:00 | 12:00 | 22 | 28 | 557 |  | low | 2020-09-14 | B20265¦courtroom M1 south side¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom E | [5 empty] | 21 | 24.3 | 427 |  | 2020-09-18 12:00 | 12:00 | 21 | 24.3 | 427 |  | low | 2020-09-14 | B11589¦Courtroom E¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by Courtroom M1 | [5 empty] | 22 | 29 | 519 |  | 2020-09-18 12:00 | 12:00 | 22 | 29 | 519 |  | low | 2020-09-14 | B20265¦hallway by Courtroom M1¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office, Walker | [5 empty] | 21 | 27 | 417 |  | 2020-09-18 12:00 | 12:00 | 21 | 27 | 417 |  | low | 2020-09-14 | B11589¦Office, Walker¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office, Martin | [5 empty] | 21 | 33 | 462 |  | 2020-09-18 12:00 | 12:00 | 21 | 33 | 462 |  | low | 2020-09-14 | B11589¦Office, Martin¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom J | [5 empty] | 22 | 25 | 514 | South | 2020-09-18 12:00 | 12:00 | 22 | 25 | 514 |  | low | 2020-09-14 | B20265¦Courtroom J¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office, baker | [5 empty] | 21 | 27 | 412 |  | 2020-09-18 12:00 | 12:00 | 21 | 27 | 412 |  | low | 2020-09-14 | B11589¦Office, baker¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom J | [5 empty] | 22 | 25 | 514 | South | 2020-09-18 12:00 | 12:00 | 22 | 25 | 514 |  | low | 2020-09-14 | B20265¦Courtroom J¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom J | [5 empty] | 22 | 24 | 510 | North | 2020-09-18 12:00 | 12:00 | 22 | 24 | 510 |  | low | 2020-09-14 | B20265¦Courtroom J¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Attorney General Admin office | [5 empty] | 21 | 25 | 431 |  | 2020-09-18 12:00 | 12:00 | 21 | 25 | 431 |  | low | 2020-09-14 | B11589¦Attorney General Admin office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | hallway by courtroom J | [5 empty] | 22 | 28 | 507 |  | 2020-09-18 12:00 | 12:00 | 22 | 28 | 507 |  | low | 2020-09-14 | B20265¦hallway by courtroom J¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Hallway | [5 empty] | 22 | 25 | 450 |  | 2020-09-18 12:00 | 12:00 | 22 | 25 | 450 |  | low | 2020-09-14 | B11589¦Hallway¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G south side | [5 empty] | 22 | 30 | 540 |  | 2020-09-18 12:00 | 12:00 | 22 | 30 | 540 |  | low | 2020-09-14 | B20265¦courtroom G south side¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom G north side | [5 empty] | 22 | 31 | 538 |  | 2020-09-18 12:00 | 12:00 | 22 | 31 | 538 |  | low | 2020-09-14 | B20265¦courtroom G north side¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 121 | [5 empty] | 22 | 31 | 552 | West | 2020-09-18 12:00 | 12:00 | 22 | 31 | 552 |  | low | 2020-09-14 | B20265¦Courtroom 121¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courthouse h | [5 empty] | 22 | 26 | 405 |  | 2020-09-18 12:00 | 12:00 | 22 | 26 | 405 |  | low | 2020-09-14 | B11589¦Courthouse h¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Outdoors |  |  | 15 | 26 | 426 |  |  |  | North entrance - partly cloudy, light breeze | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B21030¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 121 | [5 empty] | 22 | 31 | 547 | Easr | 2020-09-18 12:00 | 12:00 | 22 | 31 | 547 |  | low | 2020-09-14 | B20265¦Courtroom 121¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 123 | [5 empty] | 22 | 26 | 500 | Easr | 2020-09-18 12:00 | 12:00 | 22 | 26 | 500 |  | low | 2020-09-14 | B20265¦Courtroom 123¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 123 | [5 empty] | 21 | 26 | 464 |  | 2020-09-18 12:00 | 12:00 | 21 | 26 | 464 |  | low | 2020-09-14 | B20265¦Courtroom 123¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 123 | [5 empty] | 21 | 26 | 464 | West | 2020-09-18 12:00 | 12:00 | 21 | 26 | 464 |  | low | 2020-09-14 | B20265¦Courtroom 123¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom J | [5 empty] | 21 | 23 | 390 |  | 2020-09-18 12:00 | 12:00 | 21 | 23 | 390 |  | low | 2020-09-14 | B11589¦Courtroom J¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Boardroom used as a courtroom | [5 empty] | 22 | 23 | 443 | Windows closed, no plants | 2020-09-18 15:00 | 15:00 | 22 | 23 | 443 |  | low | 2020-09-14 | B21030¦Boardroom used as a courtroom¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 east side | [5 empty] | 22 | 37 | 516 |  | 2020-09-18 12:00 | 12:00 | 22 | 37 | 516 |  | caution | 2020-09-14 | B20265¦courtroom 124 east side¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 124 west side | [5 empty] | 22 | 39 | 524 |  | 2020-09-18 12:00 | 12:00 | 22 | 39 | 524 |  | caution | 2020-09-14 | B20265¦courtroom 124 west side¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 125 | [5 empty] | 22 | 29 | 500 | South | 2020-09-18 12:00 | 12:00 | 22 | 29 | 500 |  | low | 2020-09-14 | B20265¦Courtroom 125¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Administration office | [5 empty] | 23 | 22 | 494 | Windows closed, 4 plants total along South window | 2020-09-18 15:00 | 15:00 | 23 | 22 | 494 |  | low | 2020-09-14 | B21030¦Administration office¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Courtroom 125 | [5 empty] | 21 | 30 | 481 | North | 2020-09-18 12:00 | 12:00 | 21 | 30 | 481 |  | low | 2020-09-14 | B20265¦Courtroom 125¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | courtroom 126 south side | [5 empty] | 22 | 26 | 622 |  | 2020-09-18 12:00 | 12:00 | 22 | 26 | 622 |  | low | 2020-09-14 | B20265¦courtroom 126 south side¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B20265 | B20265 - 60 Queen St W - Toronto | Hallway | [5 empty] | 22 | 24 | 509 | By receiving | 2020-09-18 12:00 | 12:00 | 22 | 24 | 509 |  | low | 2020-09-14 | B20265¦Hallway¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Outdoors |  |  | 19 | 21 | 436 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B10639¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Courtroom 113 | [5 empty] | 22 | 22 | 449 | Windows closed, no plants | 2020-09-18 15:00 | 15:00 | 22 | 22 | 449 |  | low | 2020-09-14 | B21030¦Courtroom 113¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 6 | [5 empty] | 21 | 21 | 445 | North | 2020-09-18 12:00 | 12:00 | 21 | 21 | 445 |  | low | 2020-09-14 | B10639¦Courtroom 6¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 6 | [5 empty] | 21 | 21 | 459 | South | 2020-09-18 12:00 | 12:00 | 21 | 21 | 459 |  | low | 2020-09-14 | B10639¦Courtroom 6¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | 2nd Floor Holding Cell (hallway) | [5 empty] | 23 | 22 | 435 | Windows closed, no plants | 2020-09-18 15:00 | 15:00 | 23 | 22 | 435 |  | low | 2020-09-14 | B21030¦2nd Floor Holding Cell (hallway)¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 6 | [5 empty] | 21 | 24 | 452 |  | 2020-09-18 12:00 | 12:00 | 21 | 24 | 452 |  | low | 2020-09-14 | B10639¦Hallway by courtroom 6¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 5 | [5 empty] | 21 | 27 | 470 | North | 2020-09-18 12:00 | 12:00 | 21 | 27 | 470 |  | low | 2020-09-14 | B10639¦Courtroom 5¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 5 | [5 empty] | 21 | 28 | 440 | South | 2020-09-18 12:00 | 12:00 | 21 | 28 | 440 |  | low | 2020-09-14 | B10639¦Courtroom 5¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by courtroom 5 | [5 empty] | 21 | 24 | 449 |  | 2020-09-18 12:00 | 12:00 | 21 | 24 | 449 |  | low | 2020-09-14 | B10639¦Hallway by courtroom 5¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown attorney admin area | [5 empty] | 22 | 23 | 445 | Windows closed, no plants | 2020-09-18 15:00 | 15:00 | 22 | 23 | 445 |  | low | 2020-09-14 | B21030¦Crown attorney admin area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 22 | 21 | 420 | Office #1 - SW corner - windows closed, no plants | 2020-09-18 15:00 | 15:00 | 22 | 21 | 420 |  | low | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Crown Attorney Office | [5 empty] | 22 | 24 | 456 | Office #2 - NE corner - no windows, no plants | 2020-09-18 15:00 | 15:00 | 22 | 24 | 456 |  | low | 2020-09-14 | B21030¦Crown Attorney Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 1E | [5 empty] | 21 | 36 | 604 | north section | 2020-09-18 15:00 | 15:00 | 21 | 36 | 604 |  | caution | 2020-09-14 | B14164¦Courtroom 1E¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B21030 | B21030 - 479 Government St - Dryden | Main Lobby | [5 empty] | 22 | 23 | 490 | No windows, no plants | 2020-09-18 15:00 | 15:00 | 22 | 23 | 490 |  | low | 2020-09-14 | B21030¦Main Lobby¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Coutrtoom 1E | [8 empty] | Not allowed by the Court Clerk to go to the south section of the courtroom | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B14164¦Coutrtoom 1E¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by Courtroom 1E | [5 empty] | 20 | 32 | 478 | ground floor | 2020-09-18 15:00 | 15:00 | 20 | 32 | 478 |  | low | 2020-09-14 | B14164¦Hallway by Courtroom 1E¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 6 | [8 empty] | Door locked- Ongoing trail | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B14164¦Courtroom 6¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Hallway by courtroom 6 | [5 empty] | 20 | 35 | 525 |  | 2020-09-18 15:00 | 15:00 | 20 | 35 | 525 |  | caution | 2020-09-14 | B14164¦Hallway by courtroom 6¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 21 | 36 | 557 | north section | 2020-09-18 15:00 | 15:00 | 21 | 36 | 557 |  | caution | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Courtroom 10 | [5 empty] | 21 | 35 | 532 | SOUTH SECTION | 2020-09-18 15:00 | 15:00 | 21 | 35 | 532 |  | caution | 2020-09-14 | B14164¦Courtroom 10¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | hALLWAY BY COURTROOM 10 | [5 empty] | 21 | 33 | 490 |  | 2020-09-18 15:00 | 15:00 | 21 | 33 | 490 |  | low | 2020-09-14 | B14164¦hALLWAY BY COURTROOM 10¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, basement | [5 empty] | 21 | 33 | 491 |  | 2020-09-18 15:00 | 15:00 | 21 | 33 | 491 |  | low | 2020-09-14 | B14164¦Common area by elevator, basement¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, ground floor | [5 empty] | 21 | 33 | 538 |  | 2020-09-18 15:00 | 15:00 | 21 | 33 | 538 |  | low | 2020-09-14 | B14164¦Common area by elevator, ground floor¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Youth office, ground floor | [5 empty] | 21 | 36 | 556 |  | 2020-09-18 15:00 | 15:00 | 21 | 36 | 556 |  | caution | 2020-09-14 | B14164¦Youth office, ground floor¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Family office, ground floor | [5 empty] | 21 | 34 | 541 |  | 2020-09-18 15:00 | 15:00 | 21 | 34 | 541 |  | low | 2020-09-14 | B14164¦Family office, ground floor¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Common area by elevator, second floor | [5 empty] | 21 | 33 | 508 |  | 2020-09-18 15:00 | 15:00 | 21 | 33 | 508 |  | low | 2020-09-14 | B14164¦Common area by elevator, second floor¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14164 | B14164 - 311 Jarvis St - Toronto | Outdoors |  |  | 18 | 26 | 403 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B14164¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Outdoors |  |  | 18 | 26 | 403 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70003¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Lobby | [5 empty] | 22 | 23 | 563 |  | 2020-09-18 15:00 | 15:00 | 22 | 23 | 563 |  | low | 2020-09-14 | B10002¦Lobby¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 209 | [5 empty] | 21 | 44 | 428 | south | 2020-09-18 15:00 | 15:00 | 21 | 44 | 428 |  |  | 2020-09-14 | B18359¦courtroom 209¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 21 | 44 | 433 | north | 2020-09-18 15:00 | 15:00 | 21 | 44 | 433 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | Courtroom 210 | [5 empty] | 21 | 44 | 421 | south | 2020-09-18 15:00 | 15:00 | 21 | 44 | 421 |  |  | 2020-09-14 | B18359¦Courtroom 210¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 21 | 44 | 426 | north | 2020-09-18 15:00 | 15:00 | 21 | 44 | 426 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Skeggs | [5 empty] | 22 | 24 | 618 | Door Open | 2020-09-18 15:00 | 15:00 | 22 | 24 | 618 |  | low | 2020-09-14 | B10002¦Office Skeggs¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 211 | [5 empty] | 21 | 44 | 422 | south | 2020-09-18 15:00 | 15:00 | 21 | 44 | 422 |  |  | 2020-09-14 | B18359¦courtroom 211¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 21 | 43 | 420 | north | 2020-09-18 15:00 | 15:00 | 21 | 43 | 420 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 212 | [5 empty] | 21 | 43 | 419 | south | 2020-09-18 15:00 | 15:00 | 21 | 43 | 419 |  |  | 2020-09-14 | B18359¦courtroom 212¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 21 | 44 | 424 | north | 2020-09-18 15:00 | 15:00 | 21 | 44 | 424 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 213 | [5 empty] | 21 | 44 | 418 | south | 2020-09-18 15:00 | 15:00 | 21 | 44 | 418 |  |  | 2020-09-14 | B18359¦courtroom 213¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 21 | 44 | 431 | north | 2020-09-18 15:00 | 15:00 | 21 | 44 | 431 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 3 | [5 empty] | 22 | 21 | 497 | Southeast | 2020-09-18 12:00 | 12:00 | 22 | 21 | 497 |  | low | 2020-09-14 | B10639¦Courtroom 3¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Cubicle Office | [5 empty] | 23 | 24 | 582 |  | 2020-09-18 15:00 | 15:00 | 23 | 24 | 582 |  | low | 2020-09-14 | B10002¦Cubicle Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 214 | [5 empty] | 22 | 43 | 415 | south | 2020-09-18 15:00 | 15:00 | 22 | 43 | 415 |  |  | 2020-09-14 | B18359¦courtroom 214¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Outdoors |  |  | 17 | 19 | 396 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B12955¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 22 | 44 | 440 | north | 2020-09-18 15:00 | 15:00 | 22 | 44 | 440 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Courtroom 3 | [5 empty] | 22 | 22 | 452 | Northwest | 2020-09-18 12:00 | 12:00 | 22 | 22 | 452 |  | low | 2020-09-14 | B10639¦Courtroom 3¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Main Floor Entrance Lobby | [5 empty] | 17 | 31 | 432 | front lobby | 2020-09-18 12:00 | 12:00 | 17 | 31 | 432 |  | low | 2020-09-14 | B12955¦Main Floor Entrance Lobby¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | courtroom 215 | [5 empty] | 22 | 44 | 434 | south | 2020-09-18 15:00 | 15:00 | 22 | 44 | 434 |  |  | 2020-09-14 | B18359¦courtroom 215¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | northeast corridor | [5 empty] | 21 | 43 | 423 |  | 2020-09-18 15:00 | 15:00 | 21 | 43 | 423 |  |  | 2020-09-14 | B18359¦northeast corridor¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | OTHER | [5 empty] | 18 | 35 | 457 | waiting area | 2020-09-18 12:00 | 12:00 | 18 | 35 | 457 |  | caution | 2020-09-14 | B12955¦OTHER¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Administration office | [5 empty] | 21 | 36 | 465 |  | 2020-09-18 12:00 | 12:00 | 21 | 36 | 465 |  | caution | 2020-09-14 | B12955¦Administration office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | hallway by courtroom 3 | [5 empty] | 21 | 22 | 456 |  | 2020-09-18 12:00 | 12:00 | 21 | 22 | 456 |  | low | 2020-09-14 | B10639¦hallway by courtroom 3¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 203 | [5 empty] | 21 | 27 | 435 |  | 2020-09-18 12:00 | 12:00 | 21 | 27 | 435 |  | low | 2020-09-14 | B12955¦Courtroom 203¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | File Room | [5 empty] | 23 | 25 | 591 |  | 2020-09-18 15:00 | 15:00 | 23 | 25 | 591 |  | low | 2020-09-14 | B10002¦File Room¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 103 | [5 empty] | 20 | 29 | 454 |  | 2020-09-18 12:00 | 12:00 | 20 | 29 | 454 |  | low | 2020-09-14 | B12955¦Courtroom 103¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | lobby by statue | [5 empty] | 21 | 24 | 450 |  | 2020-09-18 12:00 | 12:00 | 21 | 24 | 450 |  | low | 2020-09-14 | B10639¦lobby by statue¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby East Side | [5 empty] | 22 | 21 | 465 |  | 2020-09-18 12:00 | 12:00 | 22 | 21 | 465 |  | low | 2020-09-14 | B10639¦Entrance Lobby East Side¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Office Didiodato | [5 empty] | 22 | 26 | 602 | Door Open | 2020-09-18 15:00 | 15:00 | 22 | 26 | 602 |  | low | 2020-09-14 | B10002¦Office Didiodato¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Entrance Lobby West Side | [5 empty] | 21 | 24 | 455 |  | 2020-09-18 12:00 | 12:00 | 21 | 24 | 455 |  | low | 2020-09-14 | B10639¦Entrance Lobby West Side¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by COA intake office | [5 empty] | 21 | 25 | 456 |  | 2020-09-18 12:00 | 12:00 | 21 | 25 | 456 |  | low | 2020-09-14 | B10639¦Hallway by COA intake office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B10639 | B10639 - 130 Queen St W - Toronto | Hallway by Law Society of Ontario | [5 empty] | 21 | 26 | 461 |  | 2020-09-18 12:00 | 12:00 | 21 | 26 | 461 |  | low | 2020-09-14 | B10639¦Hallway by Law Society of Ontario¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Reception area | [5 empty] | 21 | 31 | 562 |  | 2020-09-18 15:00 | 15:00 | 21 | 31 | 562 |  | low | 2020-09-14 | B70003¦Reception area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B18359 | B18359 - 25 Grosvenor St - Toronto | outside | [5 empty] | 19 | 52 | 417 |  | 2020-09-18 15:00 | 15:00 | 19 | 52 | 417 |  |  | 2020-09-14 | B18359¦outside¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Front main hallway | [5 empty] | 21 | 29 | 507 |  | 2020-09-18 15:00 | 15:00 | 21 | 29 | 507 |  | low | 2020-09-14 | B70003¦Front main hallway¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10002 | B10002 - 445 Albert St E - Sault Ste. Marie | Outdoors |  |  | 15 | 22 | 411 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10002¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 29 | 494 | outside of 502 | 2020-09-18 15:00 | 15:00 | 21 | 29 | 494 |  | low | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 29 | 491 | public area | 2020-09-18 15:00 | 15:00 | 21 | 29 | 491 |  | low | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 502 | [5 empty] | 21 | 30 | 498 | Judge area | 2020-09-18 15:00 | 15:00 | 21 | 30 | 498 |  | low | 2020-09-14 | B70003¦Courtroom 502¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 30 | 504 | outside of 503 | 2020-09-18 15:00 | 15:00 | 21 | 30 | 504 |  | low | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Lobby Administration | [5 empty] | 19 | 48 | 450 |  | 2020-09-18 15:00 | 15:00 | 19 | 48 | 450 |  |  | 2020-09-14 | B10003¦Lobby Administration¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 30 | 559 | public area | 2020-09-18 15:00 | 15:00 | 21 | 30 | 559 |  | low | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 503 | [5 empty] | 21 | 30 | 547 | judge area | 2020-09-18 15:00 | 15:00 | 21 | 30 | 547 |  | low | 2020-09-14 | B70003¦Courtroom 503¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 21 | 30 | 508 | outside 506 | 2020-09-18 15:00 | 15:00 | 21 | 30 | 508 |  | low | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 21 | 29 | 477 | public area | 2020-09-18 15:00 | 15:00 | 21 | 29 | 477 |  | low | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 506 | [5 empty] | 21 | 29 | 511 | judge area | 2020-09-18 15:00 | 15:00 | 21 | 29 | 511 |  | low | 2020-09-14 | B70003¦Courtroom 506¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 21 | 30 | 508 | outside of 509 | 2020-09-18 15:00 | 15:00 | 21 | 30 | 508 |  | low | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Library | [5 empty] | 19 | 45 | 488 | Wall mount AC unit running | 2020-09-18 15:00 | 15:00 | 19 | 45 | 488 |  |  | 2020-09-14 | B10003¦Library¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 21 | 33 | 536 | public area | 2020-09-18 15:00 | 15:00 | 21 | 33 | 536 |  | low | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 509 | [5 empty] | 21 | 31 | 545 | judge area | 2020-09-18 15:00 | 15:00 | 21 | 31 | 545 |  | low | 2020-09-14 | B70003¦Courtroom 509¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 21 | 30 | 520 | outside of 510 | 2020-09-18 15:00 | 15:00 | 21 | 30 | 520 |  | low | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 21 | 30 | 506 | public area | 2020-09-18 15:00 | 15:00 | 21 | 30 | 506 |  | low | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Courtroom 510 | [5 empty] | 21 | 31 | 510 | judge area | 2020-09-18 15:00 | 15:00 | 21 | 31 | 510 |  | low | 2020-09-14 | B70003¦Courtroom 510¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Back main hallway | [5 empty] | 21 | 30 | 514 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 514 |  | low | 2020-09-14 | B70003¦Back main hallway¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Basement Library | [5 empty] | 21 | 47 | 437 |  | 2020-09-18 15:00 | 15:00 | 21 | 47 | 437 |  |  | 2020-09-14 | B10003¦Basement Library¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70003 | B70003 - 444 Yonge St - Toronto | Elevator area, second floor | [5 empty] | 21 | 30 | 516 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 516 |  | low | 2020-09-14 | B70003¦Elevator area, second floor¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10003 | B10003 - 444 Queen St E - Sault Ste. Marie | Outdoors |  |  | 15 | 23 | 389 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10003¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Crown Attorney Office | [5 empty] | 21 | 30 | 464 |  | 2020-09-18 09:00 | 9:00 | 21 | 30 | 464 |  | low | 2020-09-14 | B20016¦Crown Attorney Office¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Legal Aid Ontario | [5 empty] | 21 | 30 | 465 |  | 2020-09-18 09:00 | 9:00 | 21 | 30 | 465 |  | low | 2020-09-14 | B20016¦Legal Aid Ontario¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel Waiting Area | [5 empty] | 21 | 30 | 462 |  | 2020-09-18 09:00 | 9:00 | 21 | 30 | 462 |  | low | 2020-09-14 | B20016¦Duty Counsel Waiting Area¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lobby Courtroom 1 - 2 | [5 empty] | 21 | 30 | 478 |  | 2020-09-18 09:00 | 9:00 | 21 | 30 | 478 |  | low | 2020-09-14 | B20016¦Lobby Courtroom 1 - 2¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Main Lobby | [5 empty] | 21 | 29 | 527 |  | 2020-09-18 09:00 | 9:00 | 21 | 29 | 527 |  | low | 2020-09-14 | B20016¦Main Lobby¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lower Hallway | [5 empty] | 21 | 29 | 527 |  | 2020-09-18 09:00 | 9:00 | 21 | 29 | 527 |  | low | 2020-09-14 | B20016¦Lower Hallway¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | OTHER | [5 empty] | 21 | 29 | 500 | Courtroom 1-2-3 | 2020-09-18 09:00 | 9:00 | 21 | 29 | 500 |  | low | 2020-09-14 | B20016¦OTHER¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation | [5 empty] | 21 | 31 | 514 |  | 2020-09-18 09:00 | 9:00 | 21 | 31 | 514 |  | low | 2020-09-14 | B20016¦Family Mediation¦¦Sep-18-2020 09:00
2020-09-18 | 9:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation Across Stairs | [5 empty] | 20 | 29 | 527 |  | 2020-09-18 09:00 | 9:00 | 20 | 29 | 527 |  | low | 2020-09-14 | B20016¦Family Mediation Across Stairs¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Outdoors |  |  | 13 | 34 | 424 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B12948¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 9:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 1 | [5 empty] | 20 | 26 | 406 |  | 2020-09-18 09:00 | 9:00 | 20 | 26 | 406 |  | low | 2020-09-14 | B12948¦Courtroom 1¦¦Sep-18-2020 09:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 | [5 empty] | 21 | 26 | 438 |  | 2020-09-18 15:00 | 15:00 | 21 | 26 | 438 |  | low | 2020-09-14 | B12948¦Courtroom 2¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 | [5 empty] | 21 | 25 | 416 |  | 2020-09-18 15:00 | 15:00 | 21 | 25 | 416 |  | low | 2020-09-14 | B12948¦Courtroom 3¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 | [5 empty] | 21 | 25 | 407 |  | 2020-09-18 15:00 | 15:00 | 21 | 25 | 407 |  | low | 2020-09-14 | B12948¦Courtroom 4¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Outdoors |  |  | 13 | 28 | 384 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B11589¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Security Desk | [5 empty] | 18 | 37 | 525 |  | 2020-09-18 15:00 | 15:00 | 18 | 37 | 525 |  | caution | 2020-09-14 | B11589¦Security Desk¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom A | [5 empty] | 20 | 32 | 434 |  | 2020-09-18 15:00 | 15:00 | 20 | 32 | 434 |  | low | 2020-09-14 | B11589¦Courtroom A¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom B | [5 empty] | 21 | 22 | 395 |  | 2020-09-18 15:00 | 15:00 | 21 | 22 | 395 |  | low | 2020-09-14 | B11589¦Courtroom B¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | courtroom c | [5 empty] | 21 | 22 | 393 |  | 2020-09-18 15:00 | 15:00 | 21 | 22 | 393 |  | low | 2020-09-14 | B11589¦courtroom c¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 | [5 empty] | 21 | 25 | 406 |  | 2020-09-18 15:00 | 15:00 | 21 | 25 | 406 |  | low | 2020-09-14 | B12948¦Courtroom 5¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 6 | [5 empty] | 21 | 25 | 408 |  | 2020-09-18 15:00 | 15:00 | 21 | 25 | 408 |  | low | 2020-09-14 | B12948¦Courtroom 6¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom D | [5 empty] | 21 | 27 | 570 |  | 2020-09-18 15:00 | 15:00 | 21 | 27 | 570 |  | low | 2020-09-14 | B11589¦Courtroom D¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Cell Basement | [5 empty] | 22 | 26 | 417 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 417 |  | low | 2020-09-14 | B12948¦Cell Basement¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | outdoor |  |  | 18 | 23 | 390 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B11586¦outdoor¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration Office Waiting Area | [5 empty] | 22 | 26 | 420 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 420 |  | low | 2020-09-14 | B12948¦Administration Office Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Administration office | [5 empty] | 22 | 28 | 430 |  | 2020-09-18 15:00 | 15:00 | 22 | 28 | 430 |  | low | 2020-09-14 | B12948¦Administration office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Front lobby | [5 empty] | 20.5 | 40.4 | 494 |  | 2020-09-18 15:00 | 15:00 | 20.5 | 40.4 | 494 |  |  | 2020-09-14 | B11586¦Front lobby¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom E | [5 empty] | 21 | 23 | 428 |  | 2020-09-18 15:00 | 15:00 | 21 | 23 | 428 |  | low | 2020-09-14 | B11589¦Courtroom E¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Administration office | [5 empty] | 21 | 41 | 527 |  | 2020-09-18 15:00 | 15:00 | 21 | 41 | 527 |  |  | 2020-09-14 | B11586¦Administration office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Crown attorney admin area | [5 empty] | 22 | 28 | 436 |  | 2020-09-18 15:00 | 15:00 | 22 | 28 | 436 |  | low | 2020-09-14 | B12948¦Crown attorney admin area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 2 | [5 empty] | 21 | 41 | 570 |  | 2020-09-18 15:00 | 15:00 | 21 | 41 | 570 |  |  | 2020-09-14 | B11586¦Courtroom 2¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office, Walker | [5 empty] | 21 | 29 | 463 |  | 2020-09-18 15:00 | 15:00 | 21 | 29 | 463 |  | low | 2020-09-14 | B11589¦Office, Walker¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main entrance | [5 empty] | 22 | 25 | 433 |  | 2020-09-18 15:00 | 15:00 | 22 | 25 | 433 |  | low | 2020-09-14 | B12948¦Main entrance¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown attorney office Beaton | [5 empty] | 21 | 37 | 530 |  | 2020-09-18 15:00 | 15:00 | 21 | 37 | 530 |  | caution | 2020-09-14 | B11586¦Crown attorney office Beaton¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Main Entrance Waiting Area | [5 empty] | 22 | 26 | 435 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 435 |  | low | 2020-09-14 | B12948¦Main Entrance Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office, Martin | [5 empty] | 21 | 30 | 465 |  | 2020-09-18 15:00 | 15:00 | 21 | 30 | 465 |  | low | 2020-09-14 | B11589¦Office, Martin¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Court Room 1 Waiting Area | [5 empty] | 22 | 25 | 440 |  | 2020-09-18 15:00 | 15:00 | 22 | 25 | 440 |  | low | 2020-09-14 | B12948¦Court Room 1 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown attorney office Hundeault | [5 empty] | 21 | 37 | 572 |  | 2020-09-18 15:00 | 15:00 | 21 | 37 | 572 |  | caution | 2020-09-14 | B11586¦Crown attorney office Hundeault¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 2 Waiting Area | [5 empty] | 22 | 25 | 438 |  | 2020-09-18 15:00 | 15:00 | 22 | 25 | 438 |  | low | 2020-09-14 | B12948¦Courtroom 2 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Crown attorney admin area | [5 empty] | 21 | 42 | 523 |  | 2020-09-18 15:00 | 15:00 | 21 | 42 | 523 |  |  | 2020-09-14 | B11586¦Crown attorney admin area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 3 Waiting Area | [5 empty] | 22 | 26 | 428 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 428 |  | low | 2020-09-14 | B12948¦Courtroom 3 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Office, Baker | [5 empty] | 21 | 27 | 444 |  | 2020-09-18 15:00 | 15:00 | 21 | 27 | 444 |  | low | 2020-09-14 | B11589¦Office, Baker¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 5 Waiting Area | [5 empty] | 22 | 26 | 433 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 433 |  | low | 2020-09-14 | B12948¦Courtroom 5 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Court Room 1 Waiting Area | [5 empty] | 21 | 47 | 518 |  | 2020-09-18 15:00 | 15:00 | 21 | 47 | 518 |  |  | 2020-09-14 | B11586¦Court Room 1 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12948 | B12948 - 297 Pembroke St E - Pembroke | Courtroom 4 and 6 Waiting Area | [5 empty] | 22 | 25 | 430 |  | 2020-09-18 15:00 | 15:00 | 22 | 25 | 430 |  | low | 2020-09-14 | B12948¦Courtroom 4 and 6 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Courtroom 1 | [5 empty] | 21 | 47 | 474 |  | 2020-09-18 15:00 | 15:00 | 21 | 47 | 474 |  |  | 2020-09-14 | B11586¦Courtroom 1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | 2nd Floor Holding Cell | [5 empty] | 21 | 43 | 423 |  | 2020-09-18 15:00 | 15:00 | 21 | 43 | 423 |  |  | 2020-09-14 | B11586¦2nd Floor Holding Cell¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Attorney General Admin Office | [5 empty] | 22 | 26 | 443 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 443 |  | low | 2020-09-14 | B11589¦Attorney General Admin Office¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Main Lobby | [5 empty] | 19 | 26 | 449 |  | 2020-09-18 12:00 | 12:00 | 19 | 26 | 449 |  | low | 2020-09-14 | B19523¦Main Lobby¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B11586 | B11586 - 27 Phipps St - Gore Bay | Judge office | [5 empty] | 21 | 43 | 434 |  | 2020-09-18 15:00 | 15:00 | 21 | 43 | 434 |  |  | 2020-09-14 | B11586¦Judge office¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Holding Cell | [5 empty] | 21 | 22 | 515 |  | 2020-09-18 12:00 | 12:00 | 21 | 22 | 515 |  | low | 2020-09-14 | B19523¦Holding Cell¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Library | [5 empty] | 21.1111 | 31 | 491 |  | 2020-09-18 15:00 | 15:00 | 21.1111 | 31 | 491 |  | low | 2020-09-14 | B10246¦Library¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 1 | [5 empty] | 21 | 23 | 437 |  | 2020-09-18 12:00 | 12:00 | 21 | 23 | 437 |  | low | 2020-09-14 | B19523¦Courtroom 1¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Hallway | [5 empty] | 22 | 26 | 460 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 460 |  | low | 2020-09-14 | B11589¦Hallway¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Justice Wilcox Chambers | [5 empty] | 21.1111 | 29 | 445 |  | 2020-09-18 15:00 | 15:00 | 21.1111 | 29 | 445 |  | low | 2020-09-14 | B10246¦Justice Wilcox Chambers¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Court Services | [5 empty] | 21 | 21 | 439 |  | 2020-09-18 12:00 | 12:00 | 21 | 21 | 439 |  | low | 2020-09-14 | B19523¦Court Services¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | JP Office | [5 empty] | 21 | 22 | 431 |  | 2020-09-18 12:00 | 12:00 | 21 | 22 | 431 |  | low | 2020-09-14 | B19523¦JP Office¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | 2nd fl lobby | [5 empty] | 21.1111 | 30 | 456 |  | 2020-09-18 15:00 | 15:00 | 21.1111 | 30 | 456 |  | low | 2020-09-14 | B10246¦2nd fl lobby¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | OPP Office | [5 empty] | 20 | 22 | 446 |  | 2020-09-18 12:00 | 12:00 | 20 | 22 | 446 |  | low | 2020-09-14 | B19523¦OPP Office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Crown Attorney Office | [5 empty] | 21 | 20 | 436 |  | 2020-09-18 12:00 | 12:00 | 21 | 20 | 436 |  | low | 2020-09-14 | B19523¦Crown Attorney Office¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 2 | [5 empty] | 21.1111 | 33 | 460 |  | 2020-09-18 15:00 | 15:00 | 21.1111 | 33 | 460 |  | low | 2020-09-14 | B10246¦Courtroom 2¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 20 | 459 |  | 2020-09-18 12:00 | 12:00 | 22 | 20 | 459 |  | low | 2020-09-14 | B19523¦VWAP Office¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Trial Co-ordinators Office | [5 empty] | 21.1111 | 29 | 488 |  | 2020-09-18 15:00 | 15:00 | 21.1111 | 29 | 488 |  | low | 2020-09-14 | B10246¦Trial Co-ordinators Office¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 20 | 457 |  | 2020-09-18 12:00 | 12:00 | 22 | 20 | 457 |  | low | 2020-09-14 | B19523¦VWAP Office¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 5 | [5 empty] | 21 | 23 | 447 |  | 2020-09-18 12:00 | 12:00 | 21 | 23 | 447 |  | low | 2020-09-14 | B19523¦Courtroom 5¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Main Floor Entrance Lobby | [5 empty] | 21.1111 | 30 | 477 | Middle of hallway | 2020-09-18 15:00 | 15:00 | 21.1111 | 30 | 477 |  | low | 2020-09-14 | B10246¦Main Floor Entrance Lobby¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Remote Testimony Room | [5 empty] | 21 | 22 | 440 |  | 2020-09-18 12:00 | 12:00 | 21 | 22 | 440 |  | low | 2020-09-14 | B19523¦Remote Testimony Room¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom H | [5 empty] | 23 | 23 | 402 |  | 2020-09-18 15:00 | 15:00 | 23 | 23 | 402 |  | low | 2020-09-14 | B11589¦Courtroom H¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Outdoors |  |  | 22 | 22 | 403 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B12955¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Conference Room 2 | [5 empty] | 21 | 26 | 437 |  | 2020-09-18 12:00 | 12:00 | 21 | 26 | 437 |  | low | 2020-09-14 | B19523¦Conference Room 2¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 20.5556 | 30 | 487 | Office to the left of office 10 | 2020-09-18 15:00 | 15:00 | 20.5556 | 30 | 487 |  | low | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Main Floor Entrance Lobby | [5 empty] | 17 | 28 | 433 | front lobby | 2020-09-18 15:00 | 15:00 | 17 | 28 | 433 |  | low | 2020-09-14 | B12955¦Main Floor Entrance Lobby¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 | [5 empty] | 21 | 24 | 471 |  | 2020-09-18 12:00 | 12:00 | 21 | 24 | 471 |  | low | 2020-09-14 | B19523¦Courtroom 3¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown Attorney Office | [5 empty] | 20.5556 | 32 | 509 | Office to the right of office 10 | 2020-09-18 15:00 | 15:00 | 20.5556 | 32 | 509 |  | low | 2020-09-14 | B10246¦Crown Attorney Office¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 Waiting Area | [5 empty] | 21 | 22 | 451 |  | 2020-09-18 12:00 | 12:00 | 21 | 22 | 451 |  | low | 2020-09-14 | B19523¦Courtroom 3 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B11589 | B11589 - 155 Elm St - Sudbury | Courtroom J | [5 empty] | 22 | 18 | 393 |  | 2020-09-18 15:00 | 15:00 | 22 | 18 | 393 |  | low | 2020-09-14 | B11589¦Courtroom J¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | OTHER | [5 empty] | 19 | 32 | 447 | waiting area | 2020-09-18 15:00 | 15:00 | 19 | 32 | 447 |  | low | 2020-09-14 | B12955¦OTHER¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Courtroom 1 (Center) | [5 empty] | 21.1111 | 28 | 468 |  | 2020-09-18 15:00 | 15:00 | 21.1111 | 28 | 468 |  | low | 2020-09-14 | B10246¦Courtroom 1 (Center)¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 23 | 484 |  | 2020-09-18 12:00 | 12:00 | 20 | 23 | 484 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Crown attorney admin area | [5 empty] | 21.6667 | 32 | 541 |  | 2020-09-18 15:00 | 15:00 | 21.6667 | 32 | 541 |  | low | 2020-09-14 | B10246¦Crown attorney admin area¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 37 | 700 | east | 2020-09-18 12:00 | 12:00 | 22 | 37 | 700 |  | caution | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Administration office | [5 empty] | 20 | 34 | 472 |  | 2020-09-18 15:00 | 15:00 | 20 | 34 | 472 |  | low | 2020-09-14 | B12955¦Administration office¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 22 | 465 |  | 2020-09-18 12:00 | 12:00 | 20 | 22 | 465 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Administration office | [5 empty] | 21.1111 | 28 | 555 |  | 2020-09-18 15:00 | 15:00 | 21.1111 | 28 | 555 |  | low | 2020-09-14 | B10246¦Administration office¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 23 | 472 |  | 2020-09-18 12:00 | 12:00 | 20 | 23 | 472 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 22 | 37 | 693 | west | 2020-09-18 12:00 | 12:00 | 22 | 37 | 693 |  | caution | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 103 | [5 empty] | 20 | 29 | 464 |  | 2020-09-18 15:00 | 15:00 | 20 | 29 | 464 |  | low | 2020-09-14 | B12955¦Courtroom 103¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Basement lobby - bottom of stairs | [5 empty] | 21.1111 | 30 | 487 |  | 2020-09-18 15:00 | 15:00 | 21.1111 | 30 | 487 |  | low | 2020-09-14 | B10246¦Basement lobby - bottom of stairs¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 2 | [5 empty] | 20 | 23 | 447 |  | 2020-09-18 12:00 | 12:00 | 20 | 23 | 447 |  | low | 2020-09-14 | B19523¦Courtroom 2¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B12955 | B12955 - 333 Church St - Fort Frances | Courtroom 203 | [5 empty] | 19 | 38 | 432 |  | 2020-09-18 15:00 | 15:00 | 19 | 38 | 432 |  | caution | 2020-09-14 | B12955¦Courtroom 203¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Police Court Bureau | [5 empty] | 20 | 23 | 460 |  | 2020-09-18 12:00 | 12:00 | 20 | 23 | 460 |  | low | 2020-09-14 | B19523¦Police Court Bureau¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 22 | 35 | 501 | east | 2020-09-18 12:00 | 12:00 | 22 | 35 | 501 |  | caution | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 Waiting Area | [5 empty] | 21 | 24 | 472 |  | 2020-09-18 12:00 | 12:00 | 21 | 24 | 472 |  | low | 2020-09-14 | B19523¦Courtroom 4 Waiting Area¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 | [5 empty] | 21 | 23 | 433 |  | 2020-09-18 12:00 | 12:00 | 21 | 23 | 433 |  | low | 2020-09-14 | B19523¦Courtroom 4¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 22 | 35 | 504 | west | 2020-09-18 12:00 | 12:00 | 22 | 35 | 504 |  | caution | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 24 | 476 |  | 2020-09-18 12:00 | 12:00 | 20 | 24 | 476 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 23 | 477 |  | 2020-09-18 12:00 | 12:00 | 19 | 23 | 477 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Basement cells - hallway | [5 empty] | 20.5556 | 33 | 480 |  | 2020-09-18 15:00 | 15:00 | 20.5556 | 33 | 480 |  | low | 2020-09-14 | B10246¦Basement cells - hallway¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 21 | 40 | 503 | east | 2020-09-18 12:00 | 12:00 | 21 | 40 | 503 |  | caution | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 24 | 473 |  | 2020-09-18 12:00 | 12:00 | 19 | 24 | 473 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Jury Room | [5 empty] | 20 | 25 | 440 |  | 2020-09-18 12:00 | 12:00 | 20 | 25 | 440 |  | low | 2020-09-14 | B19523¦Jury Room¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 21 | 40 | 485 | west | 2020-09-18 12:00 | 12:00 | 21 | 40 | 485 |  | caution | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B10246 | B10246 - 393 Main St - Haileybury | Outdoors |  |  | 7.7778 | 38.7 | 417 |  |  |  | Directly outside main entrance: overcast | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B10246¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Ontario Court | [5 empty] | 21 | 21 | 454 |  | 2020-09-18 12:00 | 12:00 | 21 | 21 | 454 |  | low | 2020-09-14 | B19523¦Ontario Court¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Judicial Library | [5 empty] | 22 | 23 | 429 |  | 2020-09-18 12:00 | 12:00 | 22 | 23 | 429 |  | low | 2020-09-14 | B19523¦Judicial Library¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 22 | 34 | 485 | east | 2020-09-18 12:00 | 12:00 | 22 | 34 | 485 |  | low | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 22 | 34 | 480 | west | 2020-09-18 12:00 | 12:00 | 22 | 34 | 480 |  | low | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 315 | [5 empty] | 21 | 21 | 432 |  | 2020-09-18 12:00 | 12:00 | 21 | 21 | 432 |  | low | 2020-09-14 | B19523¦Office Room 315¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 316 | [5 empty] | 21 | 20 | 434 |  | 2020-09-18 12:00 | 12:00 | 21 | 20 | 434 |  | low | 2020-09-14 | B19523¦Office Room 316¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 317 | [5 empty] | 22 | 20 | 433 |  | 2020-09-18 12:00 | 12:00 | 22 | 20 | 433 |  | low | 2020-09-14 | B19523¦Office Room 317¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 23 | 51 | 750 | east | 2020-09-18 12:00 | 12:00 | 23 | 51 | 750 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Superior Court | [5 empty] | 22 | 22 | 484 |  | 2020-09-18 12:00 | 12:00 | 22 | 22 | 484 |  | low | 2020-09-14 | B19523¦Superior Court¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 23 | 51 | 788 | west | 2020-09-18 12:00 | 12:00 | 23 | 51 | 788 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 48 | 619 | east | 2020-09-18 12:00 | 12:00 | 22 | 48 | 619 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 313 | [5 empty] | 22 | 22 | 475 |  | 2020-09-18 12:00 | 12:00 | 22 | 22 | 475 |  | low | 2020-09-14 | B19523¦Office Room 313¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 312 | [5 empty] | 22 | 22 | 439 |  | 2020-09-18 12:00 | 12:00 | 22 | 22 | 439 |  | low | 2020-09-14 | B19523¦Office Room 312¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 48 | 619 | east | 2020-09-18 12:00 | 12:00 | 22 | 48 | 619 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 310 | [5 empty] | 22 | 20 | 431 |  | 2020-09-18 12:00 | 12:00 | 22 | 20 | 431 |  | low | 2020-09-14 | B19523¦Office Room 310¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Law Association | [5 empty] | 21 | 21 | 440 |  | 2020-09-18 12:00 | 12:00 | 21 | 21 | 440 |  | low | 2020-09-14 | B19523¦Law Association¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 48 | 634 | west | 2020-09-18 12:00 | 12:00 | 22 | 48 | 634 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Main Lobby | [5 empty] | 20 | 24 | 454 |  | 2020-09-18 15:00 | 15:00 | 20 | 24 | 454 |  | low | 2020-09-14 | B19523¦Main Lobby¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 22 | 47 | 525 | east | 2020-09-18 12:00 | 12:00 | 22 | 47 | 525 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Holding Cell | [5 empty] | 20 | 21 | 455 |  | 2020-09-18 15:00 | 15:00 | 20 | 21 | 455 |  | low | 2020-09-14 | B19523¦Holding Cell¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Main Floor Waiting Area | [5 empty] | 23 | 37 | 565 |  | 2020-09-18 15:00 | 15:00 | 23 | 37 | 565 |  | caution | 2020-09-14 | B14895¦Main Floor Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 22 | 47 | 525 | west | 2020-09-18 12:00 | 12:00 | 22 | 47 | 525 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 1 | [5 empty] | 21 | 24 | 467 |  | 2020-09-18 15:00 | 15:00 | 21 | 24 | 467 |  | low | 2020-09-14 | B19523¦Courtroom 1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom A | [5 empty] | 23 | 34 | 456 |  | 2020-09-18 15:00 | 15:00 | 23 | 34 | 456 |  | low | 2020-09-14 | B14895¦Courtroom A¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 47 | 539 | east | 2020-09-18 12:00 | 12:00 | 22 | 47 | 539 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Court Services | [5 empty] | 21 | 22 | 469 |  | 2020-09-18 15:00 | 15:00 | 21 | 22 | 469 |  | low | 2020-09-14 | B19523¦Court Services¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Courtroom B | [5 empty] | 23 | 36 | 481 |  | 2020-09-18 15:00 | 15:00 | 23 | 36 | 481 |  | caution | 2020-09-14 | B14895¦Courtroom B¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | JP Office | [5 empty] | 20 | 21 | 438 |  | 2020-09-18 15:00 | 15:00 | 20 | 21 | 438 |  | low | 2020-09-14 | B19523¦JP Office¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 23 | 47 | 536 | west | 2020-09-18 12:00 | 12:00 | 23 | 47 | 536 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | OPP Office | [5 empty] | 20 | 21 | 447 |  | 2020-09-18 15:00 | 15:00 | 20 | 21 | 447 |  | low | 2020-09-14 | B19523¦OPP Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | 2nd Floor Waiting Area | [5 empty] | 23 | 32 | 665 |  | 2020-09-18 15:00 | 15:00 | 23 | 32 | 665 |  | low | 2020-09-14 | B14895¦2nd Floor Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Crown Attorney Office | [5 empty] | 21 | 24 | 504 |  | 2020-09-18 15:00 | 15:00 | 21 | 24 | 504 |  | low | 2020-09-14 | B19523¦Crown Attorney Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Crown Attorney Office | [5 empty] | 23 | 34 | 572 |  | 2020-09-18 15:00 | 15:00 | 23 | 34 | 572 |  | low | 2020-09-14 | B14895¦Crown Attorney Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 24 | 494 |  | 2020-09-18 15:00 | 15:00 | 22 | 24 | 494 |  | low | 2020-09-14 | B19523¦VWAP Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Waiting Area | [5 empty] | 23 | 31 | 632 |  | 2020-09-18 15:00 | 15:00 | 23 | 31 | 632 |  | low | 2020-09-14 | B14895¦Basement Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 22 | 28 | 482 | east | 2020-09-18 12:00 | 12:00 | 22 | 28 | 482 |  | low | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | VWAP Office | [5 empty] | 22 | 23 | 528 |  | 2020-09-18 15:00 | 15:00 | 22 | 23 | 528 |  | low | 2020-09-14 | B19523¦VWAP Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Basement Boardroom | [5 empty] | 24 | 32 | 524 |  | 2020-09-18 15:00 | 15:00 | 24 | 32 | 524 |  | low | 2020-09-14 | B14895¦Basement Boardroom¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 5 | [5 empty] | 21 | 22 | 452 |  | 2020-09-18 15:00 | 15:00 | 21 | 22 | 452 |  | low | 2020-09-14 | B19523¦Courtroom 5¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 22 | 27 | 475 | west | 2020-09-18 12:00 | 12:00 | 22 | 27 | 475 |  | low | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Male Holding Cell | [5 empty] | 24 | 28 | 448 |  | 2020-09-18 15:00 | 15:00 | 24 | 28 | 448 |  | low | 2020-09-14 | B14895¦Male Holding Cell¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Remote Testimony Room | [5 empty] | 21 | 21 | 451 |  | 2020-09-18 15:00 | 15:00 | 21 | 21 | 451 |  | low | 2020-09-14 | B19523¦Remote Testimony Room¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 22 | 28 | 511 | east | 2020-09-18 12:00 | 12:00 | 22 | 28 | 511 |  | low | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Female Holding Cell | [5 empty] | 24 | 27 | 503 |  | 2020-09-18 15:00 | 15:00 | 24 | 27 | 503 |  | low | 2020-09-14 | B14895¦Female Holding Cell¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Conference Room 2 | [5 empty] | 21 | 25 | 439 |  | 2020-09-18 15:00 | 15:00 | 21 | 25 | 439 |  | low | 2020-09-14 | B19523¦Conference Room 2¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-2 | [5 empty] | 22 | 28 | 502 | west | 2020-09-18 12:00 | 12:00 | 22 | 28 | 502 |  | low | 2020-09-14 | B91122¦courtroom 8-2¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B14895 | B14895 - 149 Fourth Ave - Cochrane | Outdoors |  |  | 15 | 27 | 408 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B14895¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 | [5 empty] | 21 | 23 | 494 |  | 2020-09-18 15:00 | 15:00 | 21 | 23 | 494 |  | low | 2020-09-14 | B19523¦Courtroom 3¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 22 | 35 | 521 | east | 2020-09-18 12:00 | 12:00 | 22 | 35 | 521 |  | caution | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 22 | 35 | 520 | west | 2020-09-18 12:00 | 12:00 | 22 | 35 | 520 |  | caution | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 22 | 33 | 489 | east | 2020-09-18 12:00 | 12:00 | 22 | 33 | 489 |  | low | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 3 Waiting Area | [5 empty] | 21 | 22 | 453 |  | 2020-09-18 15:00 | 15:00 | 21 | 22 | 453 |  | low | 2020-09-14 | B19523¦Courtroom 3 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 21 | 22 | 473 |  | 2020-09-18 15:00 | 15:00 | 21 | 22 | 473 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 22 | 33 | 478 | west | 2020-09-18 12:00 | 12:00 | 22 | 33 | 478 |  | low | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 22 | 474 |  | 2020-09-18 15:00 | 15:00 | 20 | 22 | 474 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Outdoors |  |  | 17 | 28 | 514 |  |  |  |  | 2020-09-18 12:00 | 12:00 | [5 empty] | 2020-09-14 | B91122¦Outdoors¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 22 | 476 |  | 2020-09-18 15:00 | 15:00 | 20 | 22 | 476 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | lunchroom, B2 level | [5 empty] | 20 | 31 | 512 |  | 2020-09-18 12:00 | 12:00 | 20 | 31 | 512 |  | low | 2020-09-14 | B91122¦lunchroom, B2 level¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 2 | [5 empty] | 20 | 22 | 480 |  | 2020-09-18 15:00 | 15:00 | 20 | 22 | 480 |  | low | 2020-09-14 | B19523¦Courtroom 2¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | hallway by room B2-01 | [5 empty] | 20 | 31 | 518 |  | 2020-09-18 12:00 | 12:00 | 20 | 31 | 518 |  | low | 2020-09-14 | B91122¦hallway by room B2-01¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Police Court Bureau | [5 empty] | 21 | 23 | 484 |  | 2020-09-18 15:00 | 15:00 | 21 | 23 | 484 |  | low | 2020-09-14 | B19523¦Police Court Bureau¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | file room A, B2 level | [5 empty] | 20 | 39 | 503 |  | 2020-09-18 12:00 | 12:00 | 20 | 39 | 503 |  | caution | 2020-09-14 | B91122¦file room A, B2 level¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 Waiting Area | [5 empty] | 21 | 23 | 472 |  | 2020-09-18 15:00 | 15:00 | 21 | 23 | 472 |  | low | 2020-09-14 | B19523¦Courtroom 4 Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | file room B, B2 level | [5 empty] | 21 | 39 | 538 |  | 2020-09-18 12:00 | 12:00 | 21 | 39 | 538 |  | caution | 2020-09-14 | B91122¦file room B, B2 level¦¦Sep-18-2020 12:00
2020-09-18 | 12:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | office area, B2 level | [5 empty] | 21 | 38 | 608 |  | 2020-09-18 12:00 | 12:00 | 21 | 38 | 608 |  | caution | 2020-09-14 | B91122¦office area, B2 level¦¦Sep-18-2020 12:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Courtroom 4 | [5 empty] | 21 | 24 | 450 |  | 2020-09-18 15:00 | 15:00 | 21 | 24 | 450 |  | low | 2020-09-14 | B19523¦Courtroom 4¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 21 | 38 | 620 | east | 2020-09-18 15:00 | 15:00 | 21 | 38 | 620 |  | caution | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 20 | 23 | 467 |  | 2020-09-18 15:00 | 15:00 | 20 | 23 | 467 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-1 | [5 empty] | 21 | 37 | 630 | west | 2020-09-18 15:00 | 15:00 | 21 | 37 | 630 |  | caution | 2020-09-14 | B91122¦Courtroom 5-1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 22 | 466 |  | 2020-09-18 15:00 | 15:00 | 19 | 22 | 466 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Interview Room | [5 empty] | 19 | 23 | 469 |  | 2020-09-18 15:00 | 15:00 | 19 | 23 | 469 |  | low | 2020-09-14 | B19523¦Interview Room¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 21 | 36 | 520 | east | 2020-09-18 15:00 | 15:00 | 21 | 36 | 520 |  | caution | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Jury Room | [5 empty] | 20 | 22 | 434 |  | 2020-09-18 15:00 | 15:00 | 20 | 22 | 434 |  | low | 2020-09-14 | B19523¦Jury Room¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 5-5 | [5 empty] | 21 | 36 | 507 | west | 2020-09-18 15:00 | 15:00 | 21 | 36 | 507 |  | caution | 2020-09-14 | B91122¦Courtroom 5-5¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Ontario Court | [5 empty] | 21 | 25 | 453 |  | 2020-09-18 15:00 | 15:00 | 21 | 25 | 453 |  | low | 2020-09-14 | B19523¦Ontario Court¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Judicial Library | [5 empty] | 21 | 23 | 446 |  | 2020-09-18 15:00 | 15:00 | 21 | 23 | 446 |  | low | 2020-09-14 | B19523¦Judicial Library¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 21 | 40 | 504 | east | 2020-09-18 15:00 | 15:00 | 21 | 40 | 504 |  | caution | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 315 | [5 empty] | 21 | 21 | 444 |  | 2020-09-18 15:00 | 15:00 | 21 | 21 | 444 |  | low | 2020-09-14 | B19523¦Office Room 315¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-6 | [5 empty] | 21 | 40 | 504 | west | 2020-09-18 15:00 | 15:00 | 21 | 40 | 504 |  | caution | 2020-09-14 | B91122¦courtroom 5-6¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 316 | [5 empty] | 21 | 21 | 433 |  | 2020-09-18 15:00 | 15:00 | 21 | 21 | 433 |  | low | 2020-09-14 | B19523¦Office Room 316¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 317 | [5 empty] | 21 | 19 | 428 |  | 2020-09-18 15:00 | 15:00 | 21 | 19 | 428 |  | low | 2020-09-14 | B19523¦Office Room 317¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 21 | 35 | 489 | east | 2020-09-18 15:00 | 15:00 | 21 | 35 | 489 |  | caution | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Superior Court | [5 empty] | 22 | 22 | 475 |  | 2020-09-18 15:00 | 15:00 | 22 | 22 | 475 |  | low | 2020-09-14 | B19523¦Superior Court¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 5-7 | [5 empty] | 21 | 35 | 483 | west | 2020-09-18 15:00 | 15:00 | 21 | 35 | 483 |  | caution | 2020-09-14 | B91122¦courtroom 5-7¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 313 | [5 empty] | 22 | 23 | 451 |  | 2020-09-18 15:00 | 15:00 | 22 | 23 | 451 |  | low | 2020-09-14 | B19523¦Office Room 313¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 312 | [5 empty] | 22 | 23 | 442 |  | 2020-09-18 15:00 | 15:00 | 22 | 23 | 442 |  | low | 2020-09-14 | B19523¦Office Room 312¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 22 | 51 | 868 | east | 2020-09-18 15:00 | 15:00 | 22 | 51 | 868 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Office Room 310 | [5 empty] | 22 | 23 | 448 |  | 2020-09-18 15:00 | 15:00 | 22 | 23 | 448 |  | low | 2020-09-14 | B19523¦Office Room 310¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-1 | [5 empty] | 23 | 50 | 881 | west | 2020-09-18 15:00 | 15:00 | 23 | 50 | 881 |  |  | 2020-09-14 | B91122¦Courtroom 7-1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Law Association | [5 empty] | 21 | 18 | 428 |  | 2020-09-18 15:00 | 15:00 | 21 | 18 | 428 |  | low | 2020-09-14 | B19523¦Law Association¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 47 | 612 | east | 2020-09-18 15:00 | 15:00 | 22 | 47 | 612 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Courtroom 7-2 | [5 empty] | 22 | 47 | 620 | west | 2020-09-18 15:00 | 15:00 | 22 | 47 | 620 |  |  | 2020-09-14 | B91122¦Courtroom 7-2¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Crown Attorney Office | [5 empty] | 21 | 20 | 454 |  | 2020-09-18 15:00 | 15:00 | 21 | 20 | 454 |  | low | 2020-09-14 | B20016¦Crown Attorney Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-8 | [5 empty] | 22 | 47 | 527 | east and west, same | 2020-09-18 15:00 | 15:00 | 22 | 47 | 527 |  |  | 2020-09-14 | B91122¦courtroom 7-8¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Legal Aid Ontario | [5 empty] | 21 | 20 | 480 |  | 2020-09-18 15:00 | 15:00 | 21 | 20 | 480 |  | low | 2020-09-14 | B20016¦Legal Aid Ontario¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 47 | 528 | east | 2020-09-18 15:00 | 15:00 | 22 | 47 | 528 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 7-9 | [5 empty] | 22 | 47 | 527 | west | 2020-09-18 15:00 | 15:00 | 22 | 47 | 527 |  |  | 2020-09-14 | B91122¦courtroom 7-9¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel Waiting Area | [5 empty] | 22 | 19 | 481 |  | 2020-09-18 15:00 | 15:00 | 22 | 19 | 481 |  | low | 2020-09-14 | B20016¦Duty Counsel Waiting Area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 22 | 29 | 496 | east | 2020-09-18 15:00 | 15:00 | 22 | 29 | 496 |  | low | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B19523 | B19523 - 41 Court House Sq - Brockville | Duty Counsel | [5 empty] | 22 | 19 | 481 |  | 2020-09-18 15:00 | 15:00 | 22 | 19 | 481 |  | low | 2020-09-14 | B19523¦Duty Counsel¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-1 | [5 empty] | 22 | 29 | 475 | west | 2020-09-18 15:00 | 15:00 | 22 | 29 | 475 |  | low | 2020-09-14 | B91122¦courtroom 8-1¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Duty Counsel | [5 empty] | 22 | 22 | 467 |  | 2020-09-18 15:00 | 15:00 | 22 | 22 | 467 |  | low | 2020-09-14 | B20016¦Duty Counsel¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtoom 8-2 | [5 empty] | 22 | 31 | 544 | east | 2020-09-18 15:00 | 15:00 | 22 | 31 | 544 |  | low | 2020-09-14 | B91122¦courtoom 8-2¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lobby Courtroom 1 - 2 | [5 empty] | 22 | 19 | 456 |  | 2020-09-18 15:00 | 15:00 | 22 | 19 | 456 |  | low | 2020-09-14 | B20016¦Lobby Courtroom 1 - 2¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtrooom 8-2 | [5 empty] | 22 | 32 | 539 | west | 2020-09-18 15:00 | 15:00 | 22 | 32 | 539 |  | low | 2020-09-14 | B91122¦courtrooom 8-2¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-4 | [5 empty] | 21 | 37 | 541 | east | 2020-09-18 15:00 | 15:00 | 21 | 37 | 541 |  | caution | 2020-09-14 | B91122¦courtroom 8-4¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 35 | 492 | east | 2020-09-18 15:00 | 15:00 | 21 | 35 | 492 |  | caution | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Main Lobby | [5 empty] | 22 | 20 | 450 |  | 2020-09-18 15:00 | 15:00 | 22 | 20 | 450 |  | low | 2020-09-14 | B20016¦Main Lobby¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Lower Hallway | [5 empty] | 21 | 19 | 439 |  | 2020-09-18 15:00 | 15:00 | 21 | 19 | 439 |  | low | 2020-09-14 | B20016¦Lower Hallway¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | courtroom 8-6 | [5 empty] | 21 | 34 | 491 | west | 2020-09-18 15:00 | 15:00 | 21 | 34 | 491 |  | low | 2020-09-14 | B91122¦courtroom 8-6¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | Outdoors |  |  | 17 | 33 | 497 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B91122¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | OTHER | [5 empty] | 21 | 19 | 460 | Courtroom 1-2-3 | 2020-09-18 15:00 | 15:00 | 21 | 19 | 460 |  | low | 2020-09-14 | B20016¦OTHER¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | lunchroom, B2 level | [5 empty] | 20 | 33 | 486 |  | 2020-09-18 15:00 | 15:00 | 20 | 33 | 486 |  | low | 2020-09-14 | B91122¦lunchroom, B2 level¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation | [5 empty] | 21 | 21 | 452 |  | 2020-09-18 15:00 | 15:00 | 21 | 21 | 452 |  | low | 2020-09-14 | B20016¦Family Mediation¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | hallway by room B2-01 | [5 empty] | 20 | 34 | 481 |  | 2020-09-18 15:00 | 15:00 | 20 | 34 | 481 |  | low | 2020-09-14 | B91122¦hallway by room B2-01¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Family Mediation Across Stairs | [5 empty] | 20 | 21 | 470 |  | 2020-09-18 15:00 | 15:00 | 20 | 21 | 470 |  | low | 2020-09-14 | B20016¦Family Mediation Across Stairs¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | file room A, B2 level | [5 empty] | 20 | 40 | 523 |  | 2020-09-18 15:00 | 15:00 | 20 | 40 | 523 |  | caution | 2020-09-14 | B91122¦file room A, B2 level¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Justice of the Peace Office | [5 empty] | 20 | 22 | 522 |  | 2020-09-18 15:00 | 15:00 | 20 | 22 | 522 |  | low | 2020-09-14 | B20016¦Justice of the Peace Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B20016 | B20016 - 43 Drummond St E - Perth | Holding Cell | [5 empty] | 21 | 20 | 437 |  | 2020-09-18 15:00 | 15:00 | 21 | 20 | 437 |  | low | 2020-09-14 | B20016¦Holding Cell¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | file room B, B2 level | [5 empty] | 20 | 41 | 518 |  | 2020-09-18 15:00 | 15:00 | 20 | 41 | 518 |  |  | 2020-09-14 | B91122¦file room B, B2 level¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B91122 | B91122 - 330 University Ave - Toronto | office area, B2 level | [5 empty] | 21 | 39 | 600 |  | 2020-09-18 15:00 | 15:00 | 21 | 39 | 600 |  | caution | 2020-09-14 | B91122¦office area, B2 level¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Lunch Room | [5 empty] | 22 | 29 | 514 |  | 2020-09-18 15:00 | 15:00 | 22 | 29 | 514 |  | low | 2020-09-14 | B70451¦Lunch Room¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 602 | [5 empty] | 21 | 29 | 488 | west | 2020-09-18 15:00 | 15:00 | 21 | 29 | 488 |  | low | 2020-09-14 | B70451¦Courtroom 602¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 602 | [5 empty] | 23 | 28 | 506 |  | 2020-09-18 15:00 | 15:00 | 23 | 28 | 506 |  | low | 2020-09-14 | B70451¦hallway by courtroom 602¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 603 | [5 empty] | 23 | 28 | 499 |  | 2020-09-18 15:00 | 15:00 | 23 | 28 | 499 |  | low | 2020-09-14 | B70451¦hallway by courtroom 603¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | conference room 4 | [5 empty] | 23 | 26 | 473 |  | 2020-09-18 15:00 | 15:00 | 23 | 26 | 473 |  | low | 2020-09-14 | B70451¦conference room 4¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 30 | 490 | east | 2020-09-18 15:00 | 15:00 | 23 | 30 | 490 |  | low | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Outdoors |  |  | 14 | 45 | 408 |  |  |  | East entrance - raining, light breeze | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B13095¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 607 | [5 empty] | 23 | 30 | 474 | west | 2020-09-18 15:00 | 15:00 | 23 | 30 | 474 |  | low | 2020-09-14 | B70451¦Courtroom 607¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 607 | [5 empty] | 22 | 28 | 480 |  | 2020-09-18 15:00 | 15:00 | 22 | 28 | 480 |  | low | 2020-09-14 | B70451¦hallway by courtroom 607¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | enforcement office | [5 empty] | 23 | 27 | 485 |  | 2020-09-18 15:00 | 15:00 | 23 | 27 | 485 |  | low | 2020-09-14 | B70451¦enforcement office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Hallway | [5 empty] | 19 | 43 | 615 | Window closed, no plants | 2020-09-18 15:00 | 15:00 | 19 | 43 | 615 |  |  | 2020-09-14 | B13095¦Hallway¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Courtroom 605 | [5 empty] | 22 | 26 | 479 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 479 |  | low | 2020-09-14 | B70451¦Courtroom 605¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | hallway by courtroom 605 | [5 empty] | 23 | 28 | 509 |  | 2020-09-18 15:00 | 15:00 | 23 | 28 | 509 |  | low | 2020-09-14 | B70451¦hallway by courtroom 605¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters admin office | [5 empty] | 23 | 26 | 496 |  | 2020-09-18 15:00 | 15:00 | 23 | 26 | 496 |  | low | 2020-09-14 | B70451¦masters admin office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-10 | [5 empty] | 22 | 26 | 473 |  | 2020-09-18 15:00 | 15:00 | 22 | 26 | 473 |  | low | 2020-09-14 | B70451¦room 6-10¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-9 | [5 empty] | 22 | 27 | 473 |  | 2020-09-18 15:00 | 15:00 | 22 | 27 | 473 |  | low | 2020-09-14 | B70451¦room 6-9¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | masters library | [5 empty] | 22 | 28 | 479 |  | 2020-09-18 15:00 | 15:00 | 22 | 28 | 479 |  | low | 2020-09-14 | B70451¦masters library¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | room 6-4 | [5 empty] | 22 | 28 | 485 |  | 2020-09-18 15:00 | 15:00 | 22 | 28 | 485 |  | low | 2020-09-14 | B70451¦room 6-4¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | reception area-masters | [5 empty] | 22 | 28 | 475 |  | 2020-09-18 15:00 | 15:00 | 22 | 28 | 475 |  | low | 2020-09-14 | B70451¦reception area-masters¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B70451 | B70451 - 393 University Ave - Toronto | Outdoors |  |  | 17 | 33 | 497 |  |  |  |  | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B70451¦Outdoors¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | office - B04A | [5 empty] | 20 | 37 | 531 | Windows closed, no plants | 2020-09-18 15:00 | 15:00 | 20 | 37 | 531 |  | caution | 2020-09-14 | B13095¦office - B04A¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B13095 | B13095 - 220 Main St S - Kenora | Main Lobby | [5 empty] | 21 | 37 | 635 | Windows closed, no plants | 2020-09-18 15:00 | 15:00 | 21 | 37 | 635 |  | caution | 2020-09-14 | B13095¦Main Lobby¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown Attorney Office | [5 empty] | 21 | 34 | 398 | Office #1 - east side - window closed, no plants | 2020-09-18 15:00 | 15:00 | 21 | 34 | 398 |  | low | 2020-09-14 | B13049¦Crown Attorney Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown Attorney Office | [5 empty] | 21 | 34 | 436 | Office #2 - north side - windows closed, no plants | 2020-09-18 15:00 | 15:00 | 21 | 34 | 436 |  | low | 2020-09-14 | B13049¦Crown Attorney Office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Crown attorney admin area | [5 empty] | 22 | 34 | 510 | Windows closed, no plants | 2020-09-18 15:00 | 15:00 | 22 | 34 | 510 |  | low | 2020-09-14 | B13049¦Crown attorney admin area¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Administration office | [5 empty] | 23 | 32 | 500 | Windows closed, 2 plants total at various desks | 2020-09-18 15:00 | 15:00 | 23 | 32 | 500 |  | low | 2020-09-14 | B13049¦Administration office¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 1st floor cell holding area Hallway | [5 empty] | 20 | 36 | 460 | Across from door #3 - no windows, no plants | 2020-09-18 15:00 | 15:00 | 20 | 36 | 460 |  | caution | 2020-09-14 | B13049¦1st floor cell holding area Hallway¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Court Security office #142 | [5 empty] | 22 | 33 | 420 | No windows, no plants | 2020-09-18 15:00 | 15:00 | 22 | 33 | 420 |  | low | 2020-09-14 | B13049¦Court Security office #142¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 122 | [5 empty] | 20 | 35 | 484 | No windows, no plants | 2020-09-18 15:00 | 15:00 | 20 | 35 | 484 |  | caution | 2020-09-14 | B13049¦Courtroom 122¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 1st Floor Lobby next to courtroom 122 | [5 empty] | 21 | 34 | 417 | No windows, no plants | 2020-09-18 15:00 | 15:00 | 21 | 34 | 417 |  | low | 2020-09-14 | B13049¦1st Floor Lobby next to courtroom 122¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Courtroom 250 | [5 empty] | 21 | 33 | 400 | No windows, no plants | 2020-09-18 15:00 | 15:00 | 21 | 33 | 400 |  | low | 2020-09-14 | B13049¦Courtroom 250¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | 2nd fl lobby | [5 empty] | 22 | 33 | 466 | Windows closed, no plants | 2020-09-18 15:00 | 15:00 | 22 | 33 | 466 |  | low | 2020-09-14 | B13049¦2nd fl lobby¦¦Sep-18-2020 15:00
2020-09-18 | 15:00 | CBRE - BAS | B13049 | B13049 - 216 Water St - Kenora | Outdoors |  |  | 13 | 56 | 407 |  |  |  | North entrance - cloudy, windy | 2020-09-18 15:00 | 15:00 | [5 empty] | 2020-09-14 | B13049¦Outdoors¦¦Sep-18-2020 15:00
2020-09-17 | 0:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.8 | 61 | 551.9167 | Average of the hour | 2020-09-17 | 0:00 | 19.8 | 61 | 551.9167 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 16.875 | 81.5833 | 543.6667 | Average of the hour | 2020-09-17 | 0:00 | 16.875 | 81.5833 | 543.6667 |  | high | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.1417 | 63.08 | 402 | Average of the hour | 2020-09-17 | 0:00 | 20.1417 | 63.08 | 402 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.2117 | 56.1367 | 390.1667 | Average of the hour | 2020-09-17 | 0:00 | 23.2117 | 56.1367 | 390.1667 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.3125 | 66.0958 | 439.1667 | Average of the hour | 2020-09-17 | 0:00 | 21.3125 | 66.0958 | 439.1667 |  | high | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.3692 | 58.1 | 465.1667 | Average of the hour | 2020-09-17 | 0:00 | 22.3692 | 58.1 | 465.1667 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.4667 | 45.6596 | 425.9167 | Average of the hour | 2020-09-17 | 0:00 | 24.4667 | 45.6596 | 425.9167 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.6508 | 53.695 | 418.1667 | Average of the hour | 2020-09-17 | 0:00 | 22.6508 | 53.695 | 418.1667 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.7252 | 55.1418 | 517.7523 | Average of the hour | 2020-09-17 | 0:00 | 21.7252 | 55.1418 | 517.7523 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 24.1794 | 49.9729 | 307.7719 | Average of the hour | 2020-09-17 | 0:00 | 24.1794 | 49.9729 | 307.7719 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.2387 | 52.1392 | 373.8966 | Average of the hour | 2020-09-17 | 0:00 | 23.2387 | 52.1392 | 373.8966 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.8608 | 58.52 | 623 | Average of the hour | 2020-09-17 | 0:00 | 22.8608 | 58.52 | 623 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 22.2017 | 54.2987 | 422.25 | Average of the hour | 2020-09-17 | 0:00 | 22.2017 | 54.2987 | 422.25 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.1783 | 60.8454 | 421.9167 | Average of the hour | 2020-09-17 | 0:00 | 22.1783 | 60.8454 | 421.9167 |  | caution | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22.3 | 52.7917 | 447.975 | Average of the hour | 2020-09-17 | 0:00 | 22.3 | 52.7917 | 447.975 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.9 | 53.2067 | 420.575 | Average of the hour | 2020-09-17 | 0:00 | 21.9 | 53.2067 | 420.575 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 18.3333 |  |  | Average of the hour | 2020-09-17 | 0:00 | 18.3333 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 18.725 |  |  | Average of the hour | 2020-09-17 | 0:00 | 18.725 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 18.7672 |  | 448.2 | Average of the hour | 2020-09-17 | 0:00 | 18.7672 |  | 448.2 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 18.4985 |  | 379.1667 | Average of the hour | 2020-09-17 | 0:00 | 18.4985 |  | 379.1667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 53.6583 |  | Average of the hour | 2020-09-17 | 0:00 |  | 53.6583 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 52.525 |  | Average of the hour | 2020-09-17 | 0:00 |  | 52.525 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.4445 | 45.0678 | 447.1737 | Average of the hour | 2020-09-17 | 0:00 | 22.4445 | 45.0678 | 447.1737 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 56.9423 | 687.5526 | Average of the hour | 2020-09-17 | 0:00 |  | 56.9423 | 687.5526 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.0264 | 48.6403 |  | Average of the hour | 2020-09-17 | 0:00 | 21.0264 | 48.6403 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 00:00
2020-09-17 | 0:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 | 0:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 00:00
2020-09-17 | 1:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.65 | 63.3333 | 514.4 | Average of the hour | 2020-09-17 01:00 | 1:00 | 19.65 | 63.3333 | 514.4 |  | caution | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 16.4833 | 83.4167 | 546.1667 | Average of the hour | 2020-09-17 01:00 | 1:00 | 16.4833 | 83.4167 | 546.1667 |  | high | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.7642 | 57.7442 | 410.8333 | Average of the hour | 2020-09-17 01:00 | 1:00 | 20.7642 | 57.7442 | 410.8333 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.6558 | 52.085 | 396.8333 | Average of the hour | 2020-09-17 01:00 | 1:00 | 23.6558 | 52.085 | 396.8333 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.965 | 60.4758 | 443.0833 | Average of the hour | 2020-09-17 01:00 | 1:00 | 21.965 | 60.4758 | 443.0833 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.3333 | 54.2492 | 464 | Average of the hour | 2020-09-17 01:00 | 1:00 | 22.3333 | 54.2492 | 464 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.2392 | 43.7333 | 420.25 | Average of the hour | 2020-09-17 01:00 | 1:00 | 24.2392 | 43.7333 | 420.25 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.35 | 51.9696 | 415.25 | Average of the hour | 2020-09-17 01:00 | 1:00 | 22.35 | 51.9696 | 415.25 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.7252 | 53.707 | 507.7667 | Average of the hour | 2020-09-17 01:00 | 1:00 | 21.7252 | 53.707 | 507.7667 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 24.1794 | 46.8099 | 305.3931 | Average of the hour | 2020-09-17 01:00 | 1:00 | 24.1794 | 46.8099 | 305.3931 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.2387 | 51.0415 | 373.6667 | Average of the hour | 2020-09-17 01:00 | 1:00 | 23.2387 | 51.0415 | 373.6667 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.79 | 54.7704 | 613.25 | Average of the hour | 2020-09-17 01:00 | 1:00 | 22.79 | 54.7704 | 613.25 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 22.1333 | 51.4037 | 407.9167 | Average of the hour | 2020-09-17 01:00 | 1:00 | 22.1333 | 51.4037 | 407.9167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.2025 | 57.9229 | 416.3333 | Average of the hour | 2020-09-17 01:00 | 1:00 | 22.2025 | 57.9229 | 416.3333 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22.3 | 50.25 | 446.975 | Average of the hour | 2020-09-17 01:00 | 1:00 | 22.3 | 50.25 | 446.975 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.8417 | 52.9392 | 420.0167 | Average of the hour | 2020-09-17 01:00 | 1:00 | 21.8417 | 52.9392 | 420.0167 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 17.5333 |  |  | Average of the hour | 2020-09-17 01:00 | 1:00 | 17.5333 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 18.2583 |  |  | Average of the hour | 2020-09-17 01:00 | 1:00 | 18.2583 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 18.3422 |  | 447.7667 | Average of the hour | 2020-09-17 01:00 | 1:00 | 18.3422 |  | 447.7667 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 18.1189 |  | 379.5833 | Average of the hour | 2020-09-17 01:00 | 1:00 | 18.1189 |  | 379.5833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 53.0167 |  | Average of the hour | 2020-09-17 01:00 | 1:00 |  | 53.0167 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 51.8833 |  | Average of the hour | 2020-09-17 01:00 | 1:00 |  | 51.8833 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.5316 | 44.3345 | 447.0221 | Average of the hour | 2020-09-17 01:00 | 1:00 | 22.5316 | 44.3345 | 447.0221 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 55.8902 | 686.9664 | Average of the hour | 2020-09-17 01:00 | 1:00 |  | 55.8902 | 686.9664 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.3089 | 46.1998 |  | Average of the hour | 2020-09-17 01:00 | 1:00 | 21.3089 | 46.1998 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 01:00
2020-09-17 | 1:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 01:00 | 1:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 01:00
2020-09-17 | 2:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.1167 | 65.9583 | 473.35 | Average of the hour | 2020-09-17 02:00 | 2:00 | 19.1167 | 65.9583 | 473.35 |  | high | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 16.1417 | 84 | 551.875 | Average of the hour | 2020-09-17 02:00 | 2:00 | 16.1417 | 84 | 551.875 |  | high | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 19.8783 | 60.9867 | 402.9167 | Average of the hour | 2020-09-17 02:00 | 2:00 | 19.8783 | 60.9867 | 402.9167 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.1717 | 53.4025 | 386.9167 | Average of the hour | 2020-09-17 02:00 | 2:00 | 23.1717 | 53.4025 | 386.9167 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.06 | 63.9967 | 443.6667 | Average of the hour | 2020-09-17 02:00 | 2:00 | 21.06 | 63.9967 | 443.6667 |  | caution | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.22 | 54.6275 | 470.1667 | Average of the hour | 2020-09-17 02:00 | 2:00 | 22.22 | 54.6275 | 470.1667 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.16 | 43.4692 | 417.5833 | Average of the hour | 2020-09-17 02:00 | 2:00 | 24.16 | 43.4692 | 417.5833 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.2967 | 51.9817 | 413.5833 | Average of the hour | 2020-09-17 02:00 | 2:00 | 22.2967 | 51.9817 | 413.5833 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.7252 | 52.5935 | 505.8513 | Average of the hour | 2020-09-17 02:00 | 2:00 | 21.7252 | 52.5935 | 505.8513 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 24.1794 | 45.6254 | 303.0639 | Average of the hour | 2020-09-17 02:00 | 2:00 | 24.1794 | 45.6254 | 303.0639 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.2387 | 50.0675 | 370.6162 | Average of the hour | 2020-09-17 02:00 | 2:00 | 23.2387 | 50.0675 | 370.6162 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.7767 | 52.9092 | 610.75 | Average of the hour | 2020-09-17 02:00 | 2:00 | 22.7767 | 52.9092 | 610.75 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 22.1617 | 50.0442 | 407.4167 | Average of the hour | 2020-09-17 02:00 | 2:00 | 22.1617 | 50.0442 | 407.4167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.2733 | 55.9754 | 408.75 | Average of the hour | 2020-09-17 02:00 | 2:00 | 22.2733 | 55.9754 | 408.75 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22.3 | 49.5417 | 450.8333 | Average of the hour | 2020-09-17 02:00 | 2:00 | 22.3 | 49.5417 | 450.8333 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.8333 | 52.4642 | 423.2417 | Average of the hour | 2020-09-17 02:00 | 2:00 | 21.8333 | 52.4642 | 423.2417 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 16.6167 |  |  | Average of the hour | 2020-09-17 02:00 | 2:00 | 16.6167 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 17.6333 |  |  | Average of the hour | 2020-09-17 02:00 | 2:00 | 17.6333 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 17.6764 |  | 451.5833 | Average of the hour | 2020-09-17 02:00 | 2:00 | 17.6764 |  | 451.5833 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 17.5714 |  | 379.3333 | Average of the hour | 2020-09-17 02:00 | 2:00 | 17.5714 |  | 379.3333 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 52.7667 |  | Average of the hour | 2020-09-17 02:00 | 2:00 |  | 52.7667 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 51.6333 |  | Average of the hour | 2020-09-17 02:00 | 2:00 |  | 51.6333 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.588 | 43.309 | 442.3639 | Average of the hour | 2020-09-17 02:00 | 2:00 | 22.588 | 43.309 | 442.3639 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 55.5296 | 686.9584 | Average of the hour | 2020-09-17 02:00 | 2:00 |  | 55.5296 | 686.9584 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.1901 | 46.9501 |  | Average of the hour | 2020-09-17 02:00 | 2:00 | 21.1901 | 46.9501 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 02:00
2020-09-17 | 2:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 02:00 | 2:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 02:00
2020-09-17 | 3:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 18.2333 | 68.0417 | 453.7083 | Average of the hour | 2020-09-17 03:00 | 3:00 | 18.2333 | 68.0417 | 453.7083 |  | high | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 15.75 | 82.625 | 555.3333 | Average of the hour | 2020-09-17 03:00 | 3:00 | 15.75 | 82.625 | 555.3333 |  | high | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 19.2167 | 62.5483 | 397.25 | Average of the hour | 2020-09-17 03:00 | 3:00 | 19.2167 | 62.5483 | 397.25 |  | caution | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.4583 | 54.8508 | 387 | Average of the hour | 2020-09-17 03:00 | 3:00 | 22.4583 | 54.8508 | 387 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 20.5258 | 65.08 | 432.6667 | Average of the hour | 2020-09-17 03:00 | 3:00 | 20.5258 | 65.08 | 432.6667 |  | high | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.3167 | 54.8433 | 469.25 | Average of the hour | 2020-09-17 03:00 | 3:00 | 22.3167 | 54.8433 | 469.25 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.04 | 44.0371 | 415 | Average of the hour | 2020-09-17 03:00 | 3:00 | 24.04 | 44.0371 | 415 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.16 | 52.6383 | 413.25 | Average of the hour | 2020-09-17 03:00 | 3:00 | 22.16 | 52.6383 | 413.25 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.7252 | 51.8952 | 507.227 | Average of the hour | 2020-09-17 03:00 | 3:00 | 21.7252 | 51.8952 | 507.227 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 24.1794 | 45.2276 | 302.5637 | Average of the hour | 2020-09-17 03:00 | 3:00 | 24.1794 | 45.2276 | 302.5637 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.2387 | 49.2973 | 369.6323 | Average of the hour | 2020-09-17 03:00 | 3:00 | 23.2387 | 49.2973 | 369.6323 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.79 | 52.0075 | 610.3333 | Average of the hour | 2020-09-17 03:00 | 3:00 | 22.79 | 52.0075 | 610.3333 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 22.0942 | 49.5913 | 417.5833 | Average of the hour | 2020-09-17 03:00 | 3:00 | 22.0942 | 49.5913 | 417.5833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.3892 | 54.8475 | 409.0833 | Average of the hour | 2020-09-17 03:00 | 3:00 | 22.3892 | 54.8475 | 409.0833 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22.2667 | 49.5 | 452.0167 | Average of the hour | 2020-09-17 03:00 | 3:00 | 22.2667 | 49.5 | 452.0167 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.8333 | 52.2108 | 425.1417 | Average of the hour | 2020-09-17 03:00 | 3:00 | 21.8333 | 52.2108 | 425.1417 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 15.775 |  |  | Average of the hour | 2020-09-17 03:00 | 3:00 | 15.775 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 16.9083 |  |  | Average of the hour | 2020-09-17 03:00 | 3:00 | 16.9083 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 16.897 |  | 452.825 | Average of the hour | 2020-09-17 03:00 | 3:00 | 16.897 |  | 452.825 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 16.8502 |  | 379.3333 | Average of the hour | 2020-09-17 03:00 | 3:00 | 16.8502 |  | 379.3333 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 52.6083 |  | Average of the hour | 2020-09-17 03:00 | 3:00 |  | 52.6083 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 51.3083 |  | Average of the hour | 2020-09-17 03:00 | 3:00 |  | 51.3083 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.6284 | 42.2208 | 442.0804 | Average of the hour | 2020-09-17 03:00 | 3:00 | 22.6284 | 42.2208 | 442.0804 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 55.2599 | 686.9692 | Average of the hour | 2020-09-17 03:00 | 3:00 |  | 55.2599 | 686.9692 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.4639 | 46.8887 |  | Average of the hour | 2020-09-17 03:00 | 3:00 | 21.4639 | 46.8887 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 03:00
2020-09-17 | 3:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 03:00 | 3:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 03:00
2020-09-17 | 4:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 18.1583 | 66.9583 | 477.325 | Average of the hour | 2020-09-17 04:00 | 4:00 | 18.1583 | 66.9583 | 477.325 |  | high | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 16.8167 | 74.25 | 560.625 | Average of the hour | 2020-09-17 04:00 | 4:00 | 16.8167 | 74.25 | 560.625 |  | high | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.2817 | 58.5358 | 401.5 | Average of the hour | 2020-09-17 04:00 | 4:00 | 20.2817 | 58.5358 | 401.5 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.4467 | 52.6583 | 391.0833 | Average of the hour | 2020-09-17 04:00 | 4:00 | 23.4467 | 52.6583 | 391.0833 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.3742 | 57.7042 | 436.4167 | Average of the hour | 2020-09-17 04:00 | 4:00 | 22.3742 | 57.7042 | 436.4167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.8225 | 54.2458 | 463.4167 | Average of the hour | 2020-09-17 04:00 | 4:00 | 21.8225 | 54.2458 | 463.4167 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.9642 | 44.1829 | 416.3333 | Average of the hour | 2020-09-17 04:00 | 4:00 | 23.9642 | 44.1829 | 416.3333 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.0075 | 53.08 | 414.8333 | Average of the hour | 2020-09-17 04:00 | 4:00 | 22.0075 | 53.08 | 414.8333 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.7252 | 51.3785 | 505.0157 | Average of the hour | 2020-09-17 04:00 | 4:00 | 21.7252 | 51.3785 | 505.0157 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.9488 | 45.1075 | 304.1208 | Average of the hour | 2020-09-17 04:00 | 4:00 | 23.9488 | 45.1075 | 304.1208 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.2387 | 48.5724 | 371.0329 | Average of the hour | 2020-09-17 04:00 | 4:00 | 23.2387 | 48.5724 | 371.0329 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.7767 | 51.5504 | 613.6667 | Average of the hour | 2020-09-17 04:00 | 4:00 | 22.7767 | 51.5504 | 613.6667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 22.0792 | 49.3254 | 416.5833 | Average of the hour | 2020-09-17 04:00 | 4:00 | 22.0792 | 49.3254 | 416.5833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 22.175 | 54.245 | 408.5833 | Average of the hour | 2020-09-17 04:00 | 4:00 | 22.175 | 54.245 | 408.5833 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22.2 | 49.5 | 451.35 | Average of the hour | 2020-09-17 04:00 | 4:00 | 22.2 | 49.5 | 451.35 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.8333 | 52.0642 | 425.675 | Average of the hour | 2020-09-17 04:00 | 4:00 | 21.8333 | 52.0642 | 425.675 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 15.1 |  |  | Average of the hour | 2020-09-17 04:00 | 4:00 | 15.1 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 16.4167 |  |  | Average of the hour | 2020-09-17 04:00 | 4:00 | 16.4167 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 16.2831 |  | 450.925 | Average of the hour | 2020-09-17 04:00 | 4:00 | 16.2831 |  | 450.925 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 16.1694 |  | 380.3333 | Average of the hour | 2020-09-17 04:00 | 4:00 | 16.1694 |  | 380.3333 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 52.5 |  | Average of the hour | 2020-09-17 04:00 | 4:00 |  | 52.5 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 51.2083 |  | Average of the hour | 2020-09-17 04:00 | 4:00 |  | 51.2083 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.6709 | 41.2738 | 440.7429 | Average of the hour | 2020-09-17 04:00 | 4:00 | 22.6709 | 41.2738 | 440.7429 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 55.0388 | 686.9707 | Average of the hour | 2020-09-17 04:00 | 4:00 |  | 55.0388 | 686.9707 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.508 | 46.4526 |  | Average of the hour | 2020-09-17 04:00 | 4:00 | 21.508 | 46.4526 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 04:00
2020-09-17 | 4:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 04:00 | 4:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 04:00
2020-09-17 | 5:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.0417 | 58.9583 | 468.2417 | Average of the hour | 2020-09-17 05:00 | 5:00 | 20.0417 | 58.9583 | 468.2417 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.875 | 61.4583 | 562.1667 | Average of the hour | 2020-09-17 05:00 | 5:00 | 20.875 | 61.4583 | 562.1667 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.9317 | 57.45 | 401.9167 | Average of the hour | 2020-09-17 05:00 | 5:00 | 20.9317 | 57.45 | 401.9167 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.9033 | 53.5425 | 396.4167 | Average of the hour | 2020-09-17 05:00 | 5:00 | 22.9033 | 53.5425 | 396.4167 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.0858 | 58.2875 | 435.0833 | Average of the hour | 2020-09-17 05:00 | 5:00 | 22.0858 | 58.2875 | 435.0833 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.39 | 53.8058 | 463.9167 | Average of the hour | 2020-09-17 05:00 | 5:00 | 21.39 | 53.8058 | 463.9167 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.7858 | 43.7333 | 417 | Average of the hour | 2020-09-17 05:00 | 5:00 | 23.7858 | 43.7333 | 417 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.0025 | 52.4196 | 416 | Average of the hour | 2020-09-17 05:00 | 5:00 | 22.0025 | 52.4196 | 416 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.6101 | 49.9149 | 507.4539 | Average of the hour | 2020-09-17 05:00 | 5:00 | 21.6101 | 49.9149 | 507.4539 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.5307 | 44.8765 | 303.7623 | Average of the hour | 2020-09-17 05:00 | 5:00 | 23.5307 | 44.8765 | 303.7623 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.2387 | 47.3108 | 372.0386 | Average of the hour | 2020-09-17 05:00 | 5:00 | 23.2387 | 47.3108 | 372.0386 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.6067 | 50.8996 | 613.75 | Average of the hour | 2020-09-17 05:00 | 5:00 | 22.6067 | 50.8996 | 613.75 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 21.8508 | 48.9954 | 405.1667 | Average of the hour | 2020-09-17 05:00 | 5:00 | 21.8508 | 48.9954 | 405.1667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.8667 | 54.3121 | 412.75 | Average of the hour | 2020-09-17 05:00 | 5:00 | 21.8667 | 54.3121 | 412.75 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22.1583 | 49.5 | 452.6 | Average of the hour | 2020-09-17 05:00 | 5:00 | 22.1583 | 49.5 | 452.6 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.8 | 51.9192 | 424.575 | Average of the hour | 2020-09-17 05:00 | 5:00 | 21.8 | 51.9192 | 424.575 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 14.2583 |  |  | Average of the hour | 2020-09-17 05:00 | 5:00 | 14.2583 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 15.75 |  |  | Average of the hour | 2020-09-17 05:00 | 5:00 | 15.75 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 15.6147 |  | 453.475 | Average of the hour | 2020-09-17 05:00 | 5:00 | 15.6147 |  | 453.475 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 15.4066 |  | 379.3333 | Average of the hour | 2020-09-17 05:00 | 5:00 | 15.4066 |  | 379.3333 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 52.35 |  | Average of the hour | 2020-09-17 05:00 | 5:00 |  | 52.35 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 51.0333 |  | Average of the hour | 2020-09-17 05:00 | 5:00 |  | 51.0333 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.8209 | 41.1402 | 440.5428 | Average of the hour | 2020-09-17 05:00 | 5:00 | 22.8209 | 41.1402 | 440.5428 |  |  | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 55.1812 | 687.2666 | Average of the hour | 2020-09-17 05:00 | 5:00 |  | 55.1812 | 687.2666 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.4795 | 46.3352 |  | Average of the hour | 2020-09-17 05:00 | 5:00 | 21.4795 | 46.3352 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 05:00
2020-09-17 | 5:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 05:00 | 5:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 05:00
2020-09-17 | 6:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.0167 | 58.625 | 452.6917 | Average of the hour | 2020-09-17 06:00 | 6:00 | 20.0167 | 58.625 | 452.6917 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.3667 | 61.75 | 556.625 | Average of the hour | 2020-09-17 06:00 | 6:00 | 20.3667 | 61.75 | 556.625 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.9258 | 56.0458 | 399.5 | Average of the hour | 2020-09-17 06:00 | 6:00 | 20.9258 | 56.0458 | 399.5 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.6817 | 53.785 | 404.8333 | Average of the hour | 2020-09-17 06:00 | 6:00 | 22.6817 | 53.785 | 404.8333 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.0067 | 57.1892 | 436.6667 | Average of the hour | 2020-09-17 06:00 | 6:00 | 22.0067 | 57.1892 | 436.6667 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.5308 | 52.9292 | 462.4167 | Average of the hour | 2020-09-17 06:00 | 6:00 | 21.5308 | 52.9292 | 462.4167 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.6067 | 44.0079 | 417.0833 | Average of the hour | 2020-09-17 06:00 | 6:00 | 23.6067 | 44.0079 | 417.0833 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.6875 | 52.6171 | 415.3333 | Average of the hour | 2020-09-17 06:00 | 6:00 | 21.6875 | 52.6171 | 415.3333 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.0032 | 49.6899 | 509.7815 | Average of the hour | 2020-09-17 06:00 | 6:00 | 21.0032 | 49.6899 | 509.7815 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.1524 | 45.2149 | 302.2688 | Average of the hour | 2020-09-17 06:00 | 6:00 | 23.1524 | 45.2149 | 302.2688 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.2387 | 45.0447 | 373.2961 | Average of the hour | 2020-09-17 06:00 | 6:00 | 23.2387 | 45.0447 | 373.2961 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 22.1092 | 51.0492 | 614 | Average of the hour | 2020-09-17 06:00 | 6:00 | 22.1092 | 51.0492 | 614 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.8967 | 49.6042 | 410.1667 | Average of the hour | 2020-09-17 06:00 | 6:00 | 20.8967 | 49.6042 | 410.1667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.86 | 56.9988 | 414.3333 | Average of the hour | 2020-09-17 06:00 | 6:00 | 20.86 | 56.9988 | 414.3333 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22.075 | 49.2083 | 451.75 | Average of the hour | 2020-09-17 06:00 | 6:00 | 22.075 | 49.2083 | 451.75 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.9667 | 51.3292 | 430.2 | Average of the hour | 2020-09-17 06:00 | 6:00 | 21.9667 | 51.3292 | 430.2 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.9667 |  |  | Average of the hour | 2020-09-17 06:00 | 6:00 | 22.9667 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.2917 |  |  | Average of the hour | 2020-09-17 06:00 | 6:00 | 20.2917 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 18.3257 |  | 451.425 | Average of the hour | 2020-09-17 06:00 | 6:00 | 18.3257 |  | 451.425 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 17.5371 |  | 379.9167 | Average of the hour | 2020-09-17 06:00 | 6:00 | 17.5371 |  | 379.9167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 51.675 |  | Average of the hour | 2020-09-17 06:00 | 6:00 |  | 51.675 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 50.4583 |  | Average of the hour | 2020-09-17 06:00 | 6:00 |  | 50.4583 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.3994 | 39.2388 | 461.8086 | Average of the hour | 2020-09-17 06:00 | 6:00 | 22.3994 | 39.2388 | 461.8086 |  | caution | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 55.1749 | 687.6887 | Average of the hour | 2020-09-17 06:00 | 6:00 |  | 55.1749 | 687.6887 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.1833 | 46.5052 |  | Average of the hour | 2020-09-17 06:00 | 6:00 | 21.1833 | 46.5052 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 06:00
2020-09-17 | 6:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 06:00 | 6:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 06:00
2020-09-17 | 7:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20 | 58.0833 | 449.425 | Average of the hour | 2020-09-17 07:00 | 7:00 | 20 | 58.0833 | 449.425 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.175 | 61.6667 | 555 | Average of the hour | 2020-09-17 07:00 | 7:00 | 20.175 | 61.6667 | 555 |  | caution | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.3567 | 53.585 | 408.1667 | Average of the hour | 2020-09-17 07:00 | 7:00 | 21.3567 | 53.585 | 408.1667 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.8792 | 52.5342 | 407 | Average of the hour | 2020-09-17 07:00 | 7:00 | 22.8792 | 52.5342 | 407 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.2633 | 55.3675 | 441.5833 | Average of the hour | 2020-09-17 07:00 | 7:00 | 22.2633 | 55.3675 | 441.5833 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.9217 | 51.6442 | 469.6667 | Average of the hour | 2020-09-17 07:00 | 7:00 | 21.9217 | 51.6442 | 469.6667 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.675 | 43.8429 | 420.0833 | Average of the hour | 2020-09-17 07:00 | 7:00 | 23.675 | 43.8429 | 420.0833 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.7817 | 52.2079 | 419.25 | Average of the hour | 2020-09-17 07:00 | 7:00 | 21.7817 | 52.2079 | 419.25 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.9863 | 49.9107 | 515.8638 | Average of the hour | 2020-09-17 07:00 | 7:00 | 20.9863 | 49.9107 | 515.8638 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.0607 | 44.9469 | 306.0242 | Average of the hour | 2020-09-17 07:00 | 7:00 | 23.0607 | 44.9469 | 306.0242 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.2304 | 44.2212 | 376.2819 | Average of the hour | 2020-09-17 07:00 | 7:00 | 23.2304 | 44.2212 | 376.2819 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.94 | 51.4 | 620.75 | Average of the hour | 2020-09-17 07:00 | 7:00 | 21.94 | 51.4 | 620.75 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.6933 | 50.4117 | 419.5833 | Average of the hour | 2020-09-17 07:00 | 7:00 | 20.6933 | 50.4117 | 419.5833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.8333 | 57.2629 | 413.25 | Average of the hour | 2020-09-17 07:00 | 7:00 | 20.8333 | 57.2629 | 413.25 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22 | 48.5 | 457 | Average of the hour | 2020-09-17 07:00 | 7:00 | 22 | 48.5 | 457 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22 | 50.6892 | 433.55 | Average of the hour | 2020-09-17 07:00 | 7:00 | 22 | 50.6892 | 433.55 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.2333 |  |  | Average of the hour | 2020-09-17 07:00 | 7:00 | 23.2333 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.75 |  |  | Average of the hour | 2020-09-17 07:00 | 7:00 | 20.75 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 18.5151 |  | 456.4333 | Average of the hour | 2020-09-17 07:00 | 7:00 | 18.5151 |  | 456.4333 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 18.0139 |  | 380.75 | Average of the hour | 2020-09-17 07:00 | 7:00 | 18.0139 |  | 380.75 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 50.675 |  | Average of the hour | 2020-09-17 07:00 | 7:00 |  | 50.675 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 49.3917 |  | Average of the hour | 2020-09-17 07:00 | 7:00 |  | 49.3917 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.9047 | 35.1045 | 453.6142 | Average of the hour | 2020-09-17 07:00 | 7:00 | 21.9047 | 35.1045 | 453.6142 |  | caution | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 54.7749 | 687.7265 | Average of the hour | 2020-09-17 07:00 | 7:00 |  | 54.7749 | 687.7265 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.1201 | 46.0606 |  | Average of the hour | 2020-09-17 07:00 | 7:00 | 21.1201 | 46.0606 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 07:00
2020-09-17 | 7:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 07:00 | 7:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 07:00
2020-09-17 | 8:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.0833 | 56.375 | 446.5333 | Average of the hour | 2020-09-17 08:00 | 8:00 | 20.0833 | 56.375 | 446.5333 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.1417 | 59.7083 | 557.75 | Average of the hour | 2020-09-17 08:00 | 8:00 | 20.1417 | 59.7083 | 557.75 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.3425 | 52.2192 | 428.25 | Average of the hour | 2020-09-17 08:00 | 8:00 | 21.3425 | 52.2192 | 428.25 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.8375 | 51.3142 | 414.1667 | Average of the hour | 2020-09-17 08:00 | 8:00 | 22.8375 | 51.3142 | 414.1667 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.2492 | 54.2425 | 446.6667 | Average of the hour | 2020-09-17 08:00 | 8:00 | 22.2492 | 54.2425 | 446.6667 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.8717 | 50.3825 | 471.6667 | Average of the hour | 2020-09-17 08:00 | 8:00 | 21.8717 | 50.3825 | 471.6667 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.65 | 43.5842 | 425.8333 | Average of the hour | 2020-09-17 08:00 | 8:00 | 23.65 | 43.5842 | 425.8333 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.7417 | 52.1412 | 423.5833 | Average of the hour | 2020-09-17 08:00 | 8:00 | 21.7417 | 52.1412 | 423.5833 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.9863 | 49.4493 | 525.4745 | Average of the hour | 2020-09-17 08:00 | 8:00 | 20.9863 | 49.4493 | 525.4745 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.0607 | 44.6409 | 311.7879 | Average of the hour | 2020-09-17 08:00 | 8:00 | 23.0607 | 44.6409 | 311.7879 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.0793 | 43.9741 | 378.1299 | Average of the hour | 2020-09-17 08:00 | 8:00 | 23.0793 | 43.9741 | 378.1299 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.7933 | 51.6204 | 637.1667 | Average of the hour | 2020-09-17 08:00 | 8:00 | 21.7933 | 51.6204 | 637.1667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.57 | 50.76 | 428.5833 | Average of the hour | 2020-09-17 08:00 | 8:00 | 20.57 | 50.76 | 428.5833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.6917 | 57.38 | 416.3333 | Average of the hour | 2020-09-17 08:00 | 8:00 | 20.6917 | 57.38 | 416.3333 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.95 | 48.125 | 459.4 | Average of the hour | 2020-09-17 08:00 | 8:00 | 21.95 | 48.125 | 459.4 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.0667 | 50.0725 | 441.325 | Average of the hour | 2020-09-17 08:00 | 8:00 | 22.0667 | 50.0725 | 441.325 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.6583 |  |  | Average of the hour | 2020-09-17 08:00 | 8:00 | 23.6583 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.8167 |  |  | Average of the hour | 2020-09-17 08:00 | 8:00 | 20.8167 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 19.0017 |  | 459.175 | Average of the hour | 2020-09-17 08:00 | 8:00 | 19.0017 |  | 459.175 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 18.0661 |  | 379.4167 | Average of the hour | 2020-09-17 08:00 | 8:00 | 18.0661 |  | 379.4167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 50.0917 |  | Average of the hour | 2020-09-17 08:00 | 8:00 |  | 50.0917 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 48.8 |  | Average of the hour | 2020-09-17 08:00 | 8:00 |  | 48.8 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.7743 | 32.8943 | 454.6113 | Average of the hour | 2020-09-17 08:00 | 8:00 | 21.7743 | 32.8943 | 454.6113 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 54.5384 | 687.7216 | Average of the hour | 2020-09-17 08:00 | 8:00 |  | 54.5384 | 687.7216 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.1877 | 46.7094 |  | Average of the hour | 2020-09-17 08:00 | 8:00 | 21.1877 | 46.7094 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 08:00
2020-09-17 | 8:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 08:00 | 8:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 08:00
2020-09-17 | 9:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.1 | 54.9167 | 445.2333 | Average of the hour | 2020-09-17 09:00 | 9:00 | 20.1 | 54.9167 | 445.2333 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.275 | 57.8333 | 571.125 | Average of the hour | 2020-09-17 09:00 | 9:00 | 20.275 | 57.8333 | 571.125 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.3617 | 51.3133 | 471.4167 | Average of the hour | 2020-09-17 09:00 | 9:00 | 21.3617 | 51.3133 | 471.4167 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.96 | 50.2392 | 440.5833 | Average of the hour | 2020-09-17 09:00 | 9:00 | 22.96 | 50.2392 | 440.5833 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.2817 | 53.3033 | 461.25 | Average of the hour | 2020-09-17 09:00 | 9:00 | 22.2817 | 53.3033 | 461.25 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.8567 | 49.3875 | 472.8333 | Average of the hour | 2020-09-17 09:00 | 9:00 | 21.8567 | 49.3875 | 472.8333 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.6367 | 43.795 | 436.4167 | Average of the hour | 2020-09-17 09:00 | 9:00 | 23.6367 | 43.795 | 436.4167 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.6983 | 52.415 | 434.5 | Average of the hour | 2020-09-17 09:00 | 9:00 | 21.6983 | 52.415 | 434.5 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.9863 | 49.401 | 541.118 | Average of the hour | 2020-09-17 09:00 | 9:00 | 20.9863 | 49.401 | 541.118 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.027 | 45.0674 | 315.4005 | Average of the hour | 2020-09-17 09:00 | 9:00 | 23.027 | 45.0674 | 315.4005 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.8253 | 44.0624 | 381.9067 | Average of the hour | 2020-09-17 09:00 | 9:00 | 22.8253 | 44.0624 | 381.9067 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.7125 | 52.1325 | 657.1667 | Average of the hour | 2020-09-17 09:00 | 9:00 | 21.7125 | 52.1325 | 657.1667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.4742 | 51.1588 | 439.25 | Average of the hour | 2020-09-17 09:00 | 9:00 | 20.4742 | 51.1588 | 439.25 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.4633 | 57.6367 | 429.6667 | Average of the hour | 2020-09-17 09:00 | 9:00 | 20.4633 | 57.6367 | 429.6667 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.8 | 48.8333 | 480.8833 | Average of the hour | 2020-09-17 09:00 | 9:00 | 21.8 | 48.8333 | 480.8833 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.3 | 49.2867 | 449.2667 | Average of the hour | 2020-09-17 09:00 | 9:00 | 22.3 | 49.2867 | 449.2667 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.9167 |  |  | Average of the hour | 2020-09-17 09:00 | 9:00 | 22.9167 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 21.275 |  |  | Average of the hour | 2020-09-17 09:00 | 9:00 | 21.275 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.2918 |  | 480.0583 | Average of the hour | 2020-09-17 09:00 | 9:00 | 20.2918 |  | 480.0583 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 18.4091 |  | 379.6667 | Average of the hour | 2020-09-17 09:00 | 9:00 | 18.4091 |  | 379.6667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 50.2167 |  | Average of the hour | 2020-09-17 09:00 | 9:00 |  | 50.2167 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 48.9583 |  | Average of the hour | 2020-09-17 09:00 | 9:00 |  | 48.9583 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.7703 | 31.8551 | 458.5411 | Average of the hour | 2020-09-17 09:00 | 9:00 | 21.7703 | 31.8551 | 458.5411 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 54.3875 | 690.5583 | Average of the hour | 2020-09-17 09:00 | 9:00 |  | 54.3875 | 690.5583 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.2698 | 47.2181 |  | Average of the hour | 2020-09-17 09:00 | 9:00 | 21.2698 | 47.2181 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 09:00
2020-09-17 | 9:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 09:00 | 9:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 09:00
2020-09-17 | 10:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.1167 | 53.7917 | 442.7417 | Average of the hour | 2020-09-17 10:00 | 10:00 | 20.1167 | 53.7917 | 442.7417 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.35 | 56.5417 | 570.0833 | Average of the hour | 2020-09-17 10:00 | 10:00 | 20.35 | 56.5417 | 570.0833 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.4158 | 50.2475 | 479.6667 | Average of the hour | 2020-09-17 10:00 | 10:00 | 21.4158 | 50.2475 | 479.6667 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.0517 | 49.1933 | 450.8333 | Average of the hour | 2020-09-17 10:00 | 10:00 | 23.0517 | 49.1933 | 450.8333 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.3025 | 52.375 | 474.5 | Average of the hour | 2020-09-17 10:00 | 10:00 | 22.3025 | 52.375 | 474.5 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.72 | 48.6525 | 473.8333 | Average of the hour | 2020-09-17 10:00 | 10:00 | 21.72 | 48.6525 | 473.8333 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.56 | 43.3962 | 436.75 | Average of the hour | 2020-09-17 10:00 | 10:00 | 23.56 | 43.3962 | 436.75 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.6 | 52.175 | 437.1667 | Average of the hour | 2020-09-17 10:00 | 10:00 | 21.6 | 52.175 | 437.1667 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.9863 | 48.8758 | 541.9971 | Average of the hour | 2020-09-17 10:00 | 10:00 | 20.9863 | 48.8758 | 541.9971 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.9182 | 44.6121 | 316.296 | Average of the hour | 2020-09-17 10:00 | 10:00 | 22.9182 | 44.6121 | 316.296 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.7313 | 44.1196 | 408.9797 | Average of the hour | 2020-09-17 10:00 | 10:00 | 22.7313 | 44.1196 | 408.9797 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.675 | 52.155 | 663 | Average of the hour | 2020-09-17 10:00 | 10:00 | 21.675 | 52.155 | 663 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.4417 | 51.3679 | 443.25 | Average of the hour | 2020-09-17 10:00 | 10:00 | 20.4417 | 51.3679 | 443.25 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.4208 | 57.9213 | 432.0833 | Average of the hour | 2020-09-17 10:00 | 10:00 | 20.4208 | 57.9213 | 432.0833 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.9167 | 48.1667 | 511.3333 | Average of the hour | 2020-09-17 10:00 | 10:00 | 21.9167 | 48.1667 | 511.3333 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.4333 | 48.7775 | 443.85 | Average of the hour | 2020-09-17 10:00 | 10:00 | 22.4333 | 48.7775 | 443.85 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.9333 |  |  | Average of the hour | 2020-09-17 10:00 | 10:00 | 22.9333 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 21.5583 |  |  | Average of the hour | 2020-09-17 10:00 | 10:00 | 21.5583 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.4565 |  | 512.6667 | Average of the hour | 2020-09-17 10:00 | 10:00 | 20.4565 |  | 512.6667 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 18.94 |  | 379.4167 | Average of the hour | 2020-09-17 10:00 | 10:00 | 18.94 |  | 379.4167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 49.8833 |  | Average of the hour | 2020-09-17 10:00 | 10:00 |  | 49.8833 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 48.5583 |  | Average of the hour | 2020-09-17 10:00 | 10:00 |  | 48.5583 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.7485 | 29.2182 | 459.9967 | Average of the hour | 2020-09-17 10:00 | 10:00 | 21.7485 | 29.2182 | 459.9967 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 53.8615 | 694.0858 | Average of the hour | 2020-09-17 10:00 | 10:00 |  | 53.8615 | 694.0858 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.324 | 46.5161 |  | Average of the hour | 2020-09-17 10:00 | 10:00 | 21.324 | 46.5161 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 10:00
2020-09-17 | 10:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 10:00 | 10:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 10:00
2020-09-17 | 11:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.2583 | 53.0833 | 452.9083 | Average of the hour | 2020-09-17 11:00 | 11:00 | 20.2583 | 53.0833 | 452.9083 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.375 | 55.3333 | 560.5 | Average of the hour | 2020-09-17 11:00 | 11:00 | 20.375 | 55.3333 | 560.5 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.4867 | 49.0117 | 484 | Average of the hour | 2020-09-17 11:00 | 11:00 | 21.4867 | 49.0117 | 484 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.0883 | 48.21 | 456.8333 | Average of the hour | 2020-09-17 11:00 | 11:00 | 23.0883 | 48.21 | 456.8333 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.3167 | 51.4583 | 478.4167 | Average of the hour | 2020-09-17 11:00 | 11:00 | 22.3167 | 51.4583 | 478.4167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.8183 | 47.5292 | 472.1667 | Average of the hour | 2020-09-17 11:00 | 11:00 | 21.8183 | 47.5292 | 472.1667 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.4592 | 41.6442 | 430.75 | Average of the hour | 2020-09-17 11:00 | 11:00 | 23.4592 | 41.6442 | 430.75 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.625 | 49.9138 | 430.25 | Average of the hour | 2020-09-17 11:00 | 11:00 | 21.625 | 49.9138 | 430.25 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.9863 | 47.2221 | 534.6913 | Average of the hour | 2020-09-17 11:00 | 11:00 | 20.9863 | 47.2221 | 534.6913 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.8272 | 43.1468 | 315.7455 | Average of the hour | 2020-09-17 11:00 | 11:00 | 22.8272 | 43.1468 | 315.7455 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.7313 | 43.1796 | 420.8272 | Average of the hour | 2020-09-17 11:00 | 11:00 | 22.7313 | 43.1796 | 420.8272 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.5833 | 51.1046 | 660 | Average of the hour | 2020-09-17 11:00 | 11:00 | 21.5833 | 51.1046 | 660 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.315 | 51.1438 | 430.1667 | Average of the hour | 2020-09-17 11:00 | 11:00 | 20.315 | 51.1438 | 430.1667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.3617 | 57.48 | 432.5833 | Average of the hour | 2020-09-17 11:00 | 11:00 | 20.3617 | 57.48 | 432.5833 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22.0167 | 47.5833 | 520.25 | Average of the hour | 2020-09-17 11:00 | 11:00 | 22.0167 | 47.5833 | 520.25 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.5417 | 48.4108 | 448.6 | Average of the hour | 2020-09-17 11:00 | 11:00 | 22.5417 | 48.4108 | 448.6 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.3083 |  |  | Average of the hour | 2020-09-17 11:00 | 11:00 | 22.3083 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 21.7417 |  |  | Average of the hour | 2020-09-17 11:00 | 11:00 | 21.7417 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 21.1616 |  | 519.2417 | Average of the hour | 2020-09-17 11:00 | 11:00 | 21.1616 |  | 519.2417 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 19.2546 |  | 379.5 | Average of the hour | 2020-09-17 11:00 | 11:00 | 19.2546 |  | 379.5 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 49.4917 |  | Average of the hour | 2020-09-17 11:00 | 11:00 |  | 49.4917 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 48.1 |  | Average of the hour | 2020-09-17 11:00 | 11:00 |  | 48.1 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.8449 | 29.1662 | 455.4444 | Average of the hour | 2020-09-17 11:00 | 11:00 | 21.8449 | 29.1662 | 455.4444 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 52.7731 | 694.2498 | Average of the hour | 2020-09-17 11:00 | 11:00 |  | 52.7731 | 694.2498 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.4644 | 45.5009 |  | Average of the hour | 2020-09-17 11:00 | 11:00 | 21.4644 | 45.5009 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 11:00
2020-09-17 | 11:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 11:00 | 11:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 11:00
2020-09-17 | 12:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.0083 | 52.7917 | 438.2667 | Average of the hour | 2020-09-17 12:00 | 12:00 | 20.0083 | 52.7917 | 438.2667 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.3333 | 53.7917 | 549.4167 | Average of the hour | 2020-09-17 12:00 | 12:00 | 20.3333 | 53.7917 | 549.4167 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.3217 | 48.0758 | 482.9167 | Average of the hour | 2020-09-17 12:00 | 12:00 | 21.3217 | 48.0758 | 482.9167 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 23.0567 | 47.1792 | 459.25 | Average of the hour | 2020-09-17 12:00 | 12:00 | 23.0567 | 47.1792 | 459.25 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.9683 | 51.0058 | 477.0833 | Average of the hour | 2020-09-17 12:00 | 12:00 | 21.9683 | 51.0058 | 477.0833 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.7533 | 46.9733 | 474.8333 | Average of the hour | 2020-09-17 12:00 | 12:00 | 21.7533 | 46.9733 | 474.8333 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.35 | 40.47 | 427.1667 | Average of the hour | 2020-09-17 12:00 | 12:00 | 23.35 | 40.47 | 427.1667 |  |  | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.6 | 48.4196 | 429.6667 | Average of the hour | 2020-09-17 12:00 | 12:00 | 21.6 | 48.4196 | 429.6667 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.9863 | 45.7802 | 527.3655 | Average of the hour | 2020-09-17 12:00 | 12:00 | 20.9863 | 45.7802 | 527.3655 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.7611 | 42.0657 | 314.2779 | Average of the hour | 2020-09-17 12:00 | 12:00 | 22.7611 | 42.0657 | 314.2779 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.7313 | 42.1394 | 420.0268 | Average of the hour | 2020-09-17 12:00 | 12:00 | 22.7313 | 42.1394 | 420.0268 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.5325 | 50.0325 | 655.1667 | Average of the hour | 2020-09-17 12:00 | 12:00 | 21.5325 | 50.0325 | 655.1667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.2167 | 50.6475 | 423.4167 | Average of the hour | 2020-09-17 12:00 | 12:00 | 20.2167 | 50.6475 | 423.4167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.3283 | 56.8088 | 435.3333 | Average of the hour | 2020-09-17 12:00 | 12:00 | 20.3283 | 56.8088 | 435.3333 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22.1167 | 46.8333 | 524.825 | Average of the hour | 2020-09-17 12:00 | 12:00 | 22.1167 | 46.8333 | 524.825 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.575 | 48.0633 | 451.6333 | Average of the hour | 2020-09-17 12:00 | 12:00 | 22.575 | 48.0633 | 451.6333 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.4833 |  |  | Average of the hour | 2020-09-17 12:00 | 12:00 | 22.4833 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 21.3167 |  |  | Average of the hour | 2020-09-17 12:00 | 12:00 | 21.3167 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 21.2927 |  | 524.2583 | Average of the hour | 2020-09-17 12:00 | 12:00 | 21.2927 |  | 524.2583 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 19.6691 |  | 379.5 | Average of the hour | 2020-09-17 12:00 | 12:00 | 19.6691 |  | 379.5 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [6 empty] | 49.125 |  | Average of the hour | 2020-09-17 12:00 | 12:00 |  | 49.125 |  |  |  | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [6 empty] | 47.65 |  | Average of the hour | 2020-09-17 12:00 | 12:00 |  | 47.65 |  |  |  | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.9382 | 29.8795 | 447.2444 | Average of the hour | 2020-09-17 12:00 | 12:00 | 21.9382 | 29.8795 | 447.2444 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 51.6651 | 693.7638 | Average of the hour | 2020-09-17 12:00 | 12:00 |  | 51.6651 | 693.7638 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.3075 | 44.2173 |  | Average of the hour | 2020-09-17 12:00 | 12:00 | 21.3075 | 44.2173 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 12:00
2020-09-17 | 12:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 12:00 | 12:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 12:00
2020-09-17 | 13:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.05 | 51.4167 | 428.2917 | Average of the hour | 2020-09-17 13:00 | 13:00 | 20.05 | 51.4167 | 428.2917 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.3333 | 52.1667 | 547.4583 | Average of the hour | 2020-09-17 13:00 | 13:00 | 20.3333 | 52.1667 | 547.4583 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.9858 | 47.3825 | 484.5 | Average of the hour | 2020-09-17 13:00 | 13:00 | 20.9858 | 47.3825 | 484.5 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.7792 | 46.4492 | 458.6667 | Average of the hour | 2020-09-17 13:00 | 13:00 | 22.7792 | 46.4492 | 458.6667 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.5508 | 50.4942 | 475 | Average of the hour | 2020-09-17 13:00 | 13:00 | 21.5508 | 50.4942 | 475 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.6575 | 46.3433 | 473.6667 | Average of the hour | 2020-09-17 13:00 | 13:00 | 21.6575 | 46.3433 | 473.6667 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.3075 | 39.2004 | 425 | Average of the hour | 2020-09-17 13:00 | 13:00 | 23.3075 | 39.2004 | 425 |  | caution | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.5867 | 47.0217 | 425.6667 | Average of the hour | 2020-09-17 13:00 | 13:00 | 21.5867 | 47.0217 | 425.6667 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.9863 | 44.4747 | 519.1373 | Average of the hour | 2020-09-17 13:00 | 13:00 | 20.9863 | 44.4747 | 519.1373 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.6606 | 40.952 | 311.579 | Average of the hour | 2020-09-17 13:00 | 13:00 | 22.6606 | 40.952 | 311.579 |  |  | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.7227 | 40.9616 | 393.1956 | Average of the hour | 2020-09-17 13:00 | 13:00 | 22.7227 | 40.9616 | 393.1956 |  |  | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.4758 | 49.045 | 653.5 | Average of the hour | 2020-09-17 13:00 | 13:00 | 21.4758 | 49.045 | 653.5 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.1367 | 49.9117 | 421.9167 | Average of the hour | 2020-09-17 13:00 | 13:00 | 20.1367 | 49.9117 | 421.9167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.1958 | 56.0037 | 433.9167 | Average of the hour | 2020-09-17 13:00 | 13:00 | 20.1958 | 56.0037 | 433.9167 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22.2417 | 45.6667 | 523.95 | Average of the hour | 2020-09-17 13:00 | 13:00 | 22.2417 | 45.6667 | 523.95 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.6 | 47.3358 | 455.95 | Average of the hour | 2020-09-17 13:00 | 13:00 | 22.6 | 47.3358 | 455.95 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.0833 |  |  | Average of the hour | 2020-09-17 13:00 | 13:00 | 23.0833 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 21.125 |  |  | Average of the hour | 2020-09-17 13:00 | 13:00 | 21.125 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 21.6411 |  | 525.025 | Average of the hour | 2020-09-17 13:00 | 13:00 | 21.6411 |  | 525.025 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 20.2843 |  | 379.25 | Average of the hour | 2020-09-17 13:00 | 13:00 | 20.2843 |  | 379.25 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-17 13:00 | 13:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-17 13:00 | 13:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.0453 | 28.7739 | 456.1753 | Average of the hour | 2020-09-17 13:00 | 13:00 | 22.0453 | 28.7739 | 456.1753 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 50.6836 | 692.8412 | Average of the hour | 2020-09-17 13:00 | 13:00 |  | 50.6836 | 692.8412 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.413 | 43.3118 |  | Average of the hour | 2020-09-17 13:00 | 13:00 | 21.413 | 43.3118 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 13:00
2020-09-17 | 13:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 13:00 | 13:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 13:00
2020-09-17 | 14:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.125 | 49.5 | 424 | Average of the hour | 2020-09-17 14:00 | 14:00 | 20.125 | 49.5 | 424 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.3333 | 53.2917 | 566.7917 | Average of the hour | 2020-09-17 14:00 | 14:00 | 20.3333 | 53.2917 | 566.7917 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.845 | 46.4767 | 493.3333 | Average of the hour | 2020-09-17 14:00 | 14:00 | 20.845 | 46.4767 | 493.3333 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.7408 | 45.4892 | 467.3333 | Average of the hour | 2020-09-17 14:00 | 14:00 | 22.7408 | 45.4892 | 467.3333 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.595 | 49.3183 | 478.25 | Average of the hour | 2020-09-17 14:00 | 14:00 | 21.595 | 49.3183 | 478.25 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.59 | 45.4658 | 474.8333 | Average of the hour | 2020-09-17 14:00 | 14:00 | 21.59 | 45.4658 | 474.8333 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.2133 | 37.7638 | 425.1667 | Average of the hour | 2020-09-17 14:00 | 14:00 | 23.2133 | 37.7638 | 425.1667 |  | caution | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.54 | 45.4221 | 425.5 | Average of the hour | 2020-09-17 14:00 | 14:00 | 21.54 | 45.4221 | 425.5 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 20.9863 | 42.5947 | 514.1642 | Average of the hour | 2020-09-17 14:00 | 14:00 | 20.9863 | 42.5947 | 514.1642 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.5587 | 39.6291 | 311.3376 | Average of the hour | 2020-09-17 14:00 | 14:00 | 22.5587 | 39.6291 | 311.3376 |  | caution | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.6284 | 39.735 | 397.1646 | Average of the hour | 2020-09-17 14:00 | 14:00 | 22.6284 | 39.735 | 397.1646 |  | caution | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.4 | 47.8071 | 655.5 | Average of the hour | 2020-09-17 14:00 | 14:00 | 21.4 | 47.8071 | 655.5 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 19.9975 | 48.9438 | 427.0833 | Average of the hour | 2020-09-17 14:00 | 14:00 | 19.9975 | 48.9438 | 427.0833 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.1142 | 54.9225 | 440.4167 | Average of the hour | 2020-09-17 14:00 | 14:00 | 20.1142 | 54.9225 | 440.4167 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22.4667 | 44.0833 | 519.8833 | Average of the hour | 2020-09-17 14:00 | 14:00 | 22.4667 | 44.0833 | 519.8833 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.65 | 46.1233 | 449.125 | Average of the hour | 2020-09-17 14:00 | 14:00 | 22.65 | 46.1233 | 449.125 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.2167 |  |  | Average of the hour | 2020-09-17 14:00 | 14:00 | 23.2167 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 21.2583 |  |  | Average of the hour | 2020-09-17 14:00 | 14:00 | 21.2583 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 21.739 |  | 519.55 | Average of the hour | 2020-09-17 14:00 | 14:00 | 21.739 |  | 519.55 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 21.2961 |  | 379.5 | Average of the hour | 2020-09-17 14:00 | 14:00 | 21.2961 |  | 379.5 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-17 14:00 | 14:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-17 14:00 | 14:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.9023 | 24.9885 | 443.9916 | Average of the hour | 2020-09-17 14:00 | 14:00 | 21.9023 | 24.9885 | 443.9916 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 49.5624 | 692.4105 | Average of the hour | 2020-09-17 14:00 | 14:00 |  | 49.5624 | 692.4105 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.5314 | 41.9554 |  | Average of the hour | 2020-09-17 14:00 | 14:00 | 21.5314 | 41.9554 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 14:00
2020-09-17 | 14:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 14:00 | 14:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 14:00
2020-09-17 | 15:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.0083 | 46.3333 | 420.5333 | Average of the hour | 2020-09-17 15:00 | 15:00 | 20.0083 | 46.3333 | 420.5333 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.375 | 53.2917 | 569.875 | Average of the hour | 2020-09-17 15:00 | 15:00 | 20.375 | 53.2917 | 569.875 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.7058 | 45.7067 | 505.75 | Average of the hour | 2020-09-17 15:00 | 15:00 | 20.7058 | 45.7067 | 505.75 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.7725 | 44.585 | 469.6667 | Average of the hour | 2020-09-17 15:00 | 15:00 | 22.7725 | 44.585 | 469.6667 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.8683 | 48.2933 | 485.9167 | Average of the hour | 2020-09-17 15:00 | 15:00 | 21.8683 | 48.2933 | 485.9167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.4958 | 45.1167 | 473 | Average of the hour | 2020-09-17 15:00 | 15:00 | 21.4958 | 45.1167 | 473 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.1733 | 36.75 | 426.3333 | Average of the hour | 2020-09-17 15:00 | 15:00 | 23.1733 | 36.75 | 426.3333 |  | caution | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.5192 | 44.2892 | 422 | Average of the hour | 2020-09-17 15:00 | 15:00 | 21.5192 | 44.2892 | 422 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.0807 | 41.1688 | 514.9324 | Average of the hour | 2020-09-17 15:00 | 15:00 | 21.0807 | 41.1688 | 514.9324 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.5587 | 38.7043 | 311.4306 | Average of the hour | 2020-09-17 15:00 | 15:00 | 22.5587 | 38.7043 | 311.4306 |  | caution | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.6284 | 38.6943 | 410.3981 | Average of the hour | 2020-09-17 15:00 | 15:00 | 22.6284 | 38.6943 | 410.3981 |  | caution | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.3233 | 46.6942 | 658.5833 | Average of the hour | 2020-09-17 15:00 | 15:00 | 21.3233 | 46.6942 | 658.5833 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 19.8692 | 48.0329 | 442.75 | Average of the hour | 2020-09-17 15:00 | 15:00 | 19.8692 | 48.0329 | 442.75 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 19.9342 | 54.0708 | 438.5 | Average of the hour | 2020-09-17 15:00 | 15:00 | 19.9342 | 54.0708 | 438.5 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22.575 | 41.4167 | 487.7583 | Average of the hour | 2020-09-17 15:00 | 15:00 | 22.575 | 41.4167 | 487.7583 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.675 | 43.49 | 451.925 | Average of the hour | 2020-09-17 15:00 | 15:00 | 22.675 | 43.49 | 451.925 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.175 |  |  | Average of the hour | 2020-09-17 15:00 | 15:00 | 23.175 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 21.1083 |  |  | Average of the hour | 2020-09-17 15:00 | 15:00 | 21.1083 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 21.5528 |  | 488.2 | Average of the hour | 2020-09-17 15:00 | 15:00 | 21.5528 |  | 488.2 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 21.4973 |  | 379.9167 | Average of the hour | 2020-09-17 15:00 | 15:00 | 21.4973 |  | 379.9167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.725 | 22.8187 | 436.53 | Average of the hour | 2020-09-17 15:00 | 15:00 | 21.725 | 22.8187 | 436.53 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 48.1813 | 692.3541 | Average of the hour | 2020-09-17 15:00 | 15:00 |  | 48.1813 | 692.3541 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.6269 | 40.2068 |  | Average of the hour | 2020-09-17 15:00 | 15:00 | 21.6269 | 40.2068 |  |  |  | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 15:00
2020-09-17 | 15:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 15:00 | 15:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 15:00
2020-09-17 | 16:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.9667 | 43.375 | 415.7667 | Average of the hour | 2020-09-17 16:00 | 16:00 | 19.9667 | 43.375 | 415.7667 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.3333 | 52.75 | 568.2083 | Average of the hour | 2020-09-17 16:00 | 16:00 | 20.3333 | 52.75 | 568.2083 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.6542 | 45.125 | 492.4167 | Average of the hour | 2020-09-17 16:00 | 16:00 | 20.6542 | 45.125 | 492.4167 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.6667 | 43.8758 | 460.4167 | Average of the hour | 2020-09-17 16:00 | 16:00 | 22.6667 | 43.8758 | 460.4167 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.9708 | 47.4825 | 483.4167 | Average of the hour | 2020-09-17 16:00 | 16:00 | 21.9708 | 47.4825 | 483.4167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.5558 | 44.3883 | 468.75 | Average of the hour | 2020-09-17 16:00 | 16:00 | 21.5558 | 44.3883 | 468.75 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.115 | 36.1333 | 423.8333 | Average of the hour | 2020-09-17 16:00 | 16:00 | 23.115 | 36.1333 | 423.8333 |  | caution | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.505 | 43.6183 | 420 | Average of the hour | 2020-09-17 16:00 | 16:00 | 21.505 | 43.6183 | 420 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.1734 | 40.1162 | 514.5855 | Average of the hour | 2020-09-17 16:00 | 16:00 | 21.1734 | 40.1162 | 514.5855 |  |  | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.5065 | 37.9592 | 304.812 | Average of the hour | 2020-09-17 16:00 | 16:00 | 22.5065 | 37.9592 | 304.812 |  | caution | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.6284 | 37.7504 | 388.0996 | Average of the hour | 2020-09-17 16:00 | 16:00 | 22.6284 | 37.7504 | 388.0996 |  | caution | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.2767 | 45.875 | 649.6667 | Average of the hour | 2020-09-17 16:00 | 16:00 | 21.2767 | 45.875 | 649.6667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 19.9192 | 47.1821 | 429.5 | Average of the hour | 2020-09-17 16:00 | 16:00 | 19.9192 | 47.1821 | 429.5 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 19.9167 | 53.37 | 439 | Average of the hour | 2020-09-17 16:00 | 16:00 | 19.9167 | 53.37 | 439 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22.7083 | 40.7083 | 484.25 | Average of the hour | 2020-09-17 16:00 | 16:00 | 22.7083 | 40.7083 | 484.25 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.7 | 41.7483 | 433.3667 | Average of the hour | 2020-09-17 16:00 | 16:00 | 22.7 | 41.7483 | 433.3667 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.3 |  |  | Average of the hour | 2020-09-17 16:00 | 16:00 | 23.3 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 21.2583 |  |  | Average of the hour | 2020-09-17 16:00 | 16:00 | 21.2583 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 22.3453 |  | 485.6083 | Average of the hour | 2020-09-17 16:00 | 16:00 | 22.3453 |  | 485.6083 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 22.1803 |  | 378.5833 | Average of the hour | 2020-09-17 16:00 | 16:00 | 22.1803 |  | 378.5833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-17 16:00 | 16:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-17 16:00 | 16:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.6243 | 21.83 | 426.4766 | Average of the hour | 2020-09-17 16:00 | 16:00 | 21.6243 | 21.83 | 426.4766 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 47.3248 | 692.0501 | Average of the hour | 2020-09-17 16:00 | 16:00 |  | 47.3248 | 692.0501 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.3253 | 39.316 |  | Average of the hour | 2020-09-17 16:00 | 16:00 | 21.3253 | 39.316 |  |  | caution | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 16:00
2020-09-17 | 16:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 16:00 | 16:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 16:00
2020-09-17 | 17:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 20.0167 | 41.1667 | 426.9833 | Average of the hour | 2020-09-17 17:00 | 17:00 | 20.0167 | 41.1667 | 426.9833 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.325 | 51.6667 | 562.5417 | Average of the hour | 2020-09-17 17:00 | 17:00 | 20.325 | 51.6667 | 562.5417 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.5167 | 45.0375 | 445.5 | Average of the hour | 2020-09-17 17:00 | 17:00 | 20.5167 | 45.0375 | 445.5 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.5142 | 43.9092 | 444.6667 | Average of the hour | 2020-09-17 17:00 | 17:00 | 22.5142 | 43.9092 | 444.6667 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.0283 | 46.9617 | 475.6667 | Average of the hour | 2020-09-17 17:00 | 17:00 | 22.0283 | 46.9617 | 475.6667 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.5917 | 44.5408 | 469.4167 | Average of the hour | 2020-09-17 17:00 | 17:00 | 21.5917 | 44.5408 | 469.4167 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.005 | 35.2367 | 417.5 | Average of the hour | 2020-09-17 17:00 | 17:00 | 23.005 | 35.2367 | 417.5 |  | caution | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.4675 | 42.8925 | 415.0833 | Average of the hour | 2020-09-17 17:00 | 17:00 | 21.4675 | 42.8925 | 415.0833 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.1736 | 39.1718 | 511.006 | Average of the hour | 2020-09-17 17:00 | 17:00 | 21.1736 | 39.1718 | 511.006 |  | caution | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 22.4543 | 36.9343 | 302.8777 | Average of the hour | 2020-09-17 17:00 | 17:00 | 22.4543 | 36.9343 | 302.8777 |  | caution | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.6729 | 36.9194 | 374.2107 | Average of the hour | 2020-09-17 17:00 | 17:00 | 22.6729 | 36.9194 | 374.2107 |  | caution | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.2208 | 44.9792 | 629.1667 | Average of the hour | 2020-09-17 17:00 | 17:00 | 21.2208 | 44.9792 | 629.1667 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 19.7417 | 46.3579 | 413.6667 | Average of the hour | 2020-09-17 17:00 | 17:00 | 19.7417 | 46.3579 | 413.6667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 19.7133 | 52.2575 | 438.8333 | Average of the hour | 2020-09-17 17:00 | 17:00 | 19.7133 | 52.2575 | 438.8333 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.8833 | 41.8333 | 477.0667 | Average of the hour | 2020-09-17 17:00 | 17:00 | 21.8833 | 41.8333 | 477.0667 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 22.1167 | 42.21 | 423.525 | Average of the hour | 2020-09-17 17:00 | 17:00 | 22.1167 | 42.21 | 423.525 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 23.2167 |  |  | Average of the hour | 2020-09-17 17:00 | 17:00 | 23.2167 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.7917 |  |  | Average of the hour | 2020-09-17 17:00 | 17:00 | 20.7917 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 22.5376 |  | 474.8 | Average of the hour | 2020-09-17 17:00 | 17:00 | 22.5376 |  | 474.8 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 22.3353 |  | 379.0833 | Average of the hour | 2020-09-17 17:00 | 17:00 | 22.3353 |  | 379.0833 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-17 17:00 | 17:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-17 17:00 | 17:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.554 | 21.3191 | 419.9717 | Average of the hour | 2020-09-17 17:00 | 17:00 | 21.554 | 21.3191 | 419.9717 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 46.3108 | 690.5128 | Average of the hour | 2020-09-17 17:00 | 17:00 |  | 46.3108 | 690.5128 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.4298 | 38.2793 |  | Average of the hour | 2020-09-17 17:00 | 17:00 | 21.4298 | 38.2793 |  |  | caution | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 17:00
2020-09-17 | 17:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 17:00 | 17:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 17:00
2020-09-17 | 18:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.6167 | 40.5833 | 427.575 | Average of the hour | 2020-09-17 18:00 | 18:00 | 19.6167 | 40.5833 | 427.575 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 20.1833 | 50.9583 | 543.5 | Average of the hour | 2020-09-17 18:00 | 18:00 | 20.1833 | 50.9583 | 543.5 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.4642 | 46.795 | 420.5 | Average of the hour | 2020-09-17 18:00 | 18:00 | 20.4642 | 46.795 | 420.5 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.4967 | 44.965 | 420.0833 | Average of the hour | 2020-09-17 18:00 | 18:00 | 22.4967 | 44.965 | 420.0833 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 22.0367 | 47.4875 | 459.4167 | Average of the hour | 2020-09-17 18:00 | 18:00 | 22.0367 | 47.4875 | 459.4167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.6067 | 46.0983 | 468.0833 | Average of the hour | 2020-09-17 18:00 | 18:00 | 21.6067 | 46.0983 | 468.0833 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.1192 | 35.4254 | 414.5 | Average of the hour | 2020-09-17 18:00 | 18:00 | 23.1192 | 35.4254 | 414.5 |  | caution | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 21.6925 | 44.3237 | 411 | Average of the hour | 2020-09-17 18:00 | 18:00 | 21.6925 | 44.3237 | 411 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.3597 | 39.1618 | 496.5536 | Average of the hour | 2020-09-17 18:00 | 18:00 | 21.3597 | 39.1618 | 496.5536 |  | caution | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 23.9787 | 34.5416 | 302.0458 | Average of the hour | 2020-09-17 18:00 | 18:00 | 23.9787 | 34.5416 | 302.0458 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 22.9801 | 37.6495 | 366.5362 | Average of the hour | 2020-09-17 18:00 | 18:00 | 22.9801 | 37.6495 | 366.5362 |  | caution | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.2967 | 45.3858 | 613 | Average of the hour | 2020-09-17 18:00 | 18:00 | 21.2967 | 45.3858 | 613 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.2142 | 45.49 | 409.6667 | Average of the hour | 2020-09-17 18:00 | 18:00 | 20.2142 | 45.49 | 409.6667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.025 | 50.6383 | 425.5833 | Average of the hour | 2020-09-17 18:00 | 18:00 | 20.025 | 50.6383 | 425.5833 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.8417 | 41.75 | 460.4 | Average of the hour | 2020-09-17 18:00 | 18:00 | 21.8417 | 41.75 | 460.4 |  |  | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.7333 | 42.7158 | 420.4167 | Average of the hour | 2020-09-17 18:00 | 18:00 | 21.7333 | 42.7158 | 420.4167 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.8083 |  |  | Average of the hour | 2020-09-17 18:00 | 18:00 | 22.8083 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.6833 |  |  | Average of the hour | 2020-09-17 18:00 | 18:00 | 20.6833 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 21.2796 |  | 461.1833 | Average of the hour | 2020-09-17 18:00 | 18:00 | 21.2796 |  | 461.1833 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 21.2652 |  | 379.9167 | Average of the hour | 2020-09-17 18:00 | 18:00 | 21.2652 |  | 379.9167 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-17 18:00 | 18:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-17 18:00 | 18:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.6774 | 22.0086 | 435.686 | Average of the hour | 2020-09-17 18:00 | 18:00 | 21.6774 | 22.0086 | 435.686 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 45.8523 | 688.7643 | Average of the hour | 2020-09-17 18:00 | 18:00 |  | 45.8523 | 688.7643 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.3878 | 37.3145 |  | Average of the hour | 2020-09-17 18:00 | 18:00 | 21.3878 | 37.3145 |  |  | caution | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 18:00
2020-09-17 | 18:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 18:00 | 18:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 18:00
2020-09-17 | 19:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 19.0583 | 40.5417 | 427.75 | Average of the hour | 2020-09-17 19:00 | 19:00 | 19.0583 | 40.5417 | 427.75 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 16.425 | 49.625 | 528.625 | Average of the hour | 2020-09-17 19:00 | 19:00 | 16.425 | 49.625 | 528.625 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.5467 | 48.1683 | 403 | Average of the hour | 2020-09-17 19:00 | 19:00 | 20.5467 | 48.1683 | 403 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.5108 | 46.0517 | 407.4167 | Average of the hour | 2020-09-17 19:00 | 19:00 | 22.5108 | 46.0517 | 407.4167 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.9458 | 50.0892 | 445.25 | Average of the hour | 2020-09-17 19:00 | 19:00 | 21.9458 | 50.0892 | 445.25 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.535 | 47.5367 | 464.4167 | Average of the hour | 2020-09-17 19:00 | 19:00 | 21.535 | 47.5367 | 464.4167 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 23.7517 | 36.5896 | 433.75 | Average of the hour | 2020-09-17 19:00 | 19:00 | 23.7517 | 36.5896 | 433.75 |  | caution | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.1867 | 45.1779 | 411.4167 | Average of the hour | 2020-09-17 19:00 | 19:00 | 22.1867 | 45.1779 | 411.4167 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 21.9163 | 39.3303 | 485.8975 | Average of the hour | 2020-09-17 19:00 | 19:00 | 21.9163 | 39.3303 | 485.8975 |  | caution | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.3362 | 33.8874 | 309.947 | Average of the hour | 2020-09-17 19:00 | 19:00 | 25.3362 | 33.8874 | 309.947 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.3894 | 37.6358 | 372.2895 | Average of the hour | 2020-09-17 19:00 | 19:00 | 23.3894 | 37.6358 | 372.2895 |  | caution | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.5233 | 46.5275 | 612.3333 | Average of the hour | 2020-09-17 19:00 | 19:00 | 21.5233 | 46.5275 | 612.3333 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.67 | 45.3146 | 404.5 | Average of the hour | 2020-09-17 19:00 | 19:00 | 20.67 | 45.3146 | 404.5 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.5683 | 50.0367 | 417.4167 | Average of the hour | 2020-09-17 19:00 | 19:00 | 20.5683 | 50.0367 | 417.4167 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 22 | 39.5 | 447.1 | Average of the hour | 2020-09-17 19:00 | 19:00 | 22 | 39.5 | 447.1 |  | caution | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.975 | 41.2067 | 421.5917 | Average of the hour | 2020-09-17 19:00 | 19:00 | 21.975 | 41.2067 | 421.5917 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.525 |  |  | Average of the hour | 2020-09-17 19:00 | 19:00 | 22.525 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 20.6917 |  |  | Average of the hour | 2020-09-17 19:00 | 19:00 | 20.6917 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 20.1151 |  | 446.8583 | Average of the hour | 2020-09-17 19:00 | 19:00 | 20.1151 |  | 446.8583 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 19.9128 |  | 380 | Average of the hour | 2020-09-17 19:00 | 19:00 | 19.9128 |  | 380 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-17 19:00 | 19:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-17 19:00 | 19:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 21.9185 | 22.8836 | 434.9231 | Average of the hour | 2020-09-17 19:00 | 19:00 | 21.9185 | 22.8836 | 434.9231 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 45.2528 | 688.334 | Average of the hour | 2020-09-17 19:00 | 19:00 |  | 45.2528 | 688.334 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.215 | 35.8901 |  | Average of the hour | 2020-09-17 19:00 | 19:00 | 21.215 | 35.8901 |  |  | caution | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 19:00
2020-09-17 | 19:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 19:00 | 19:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 19:00
2020-09-17 | 20:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 17.35 | 44 | 428.2667 | Average of the hour | 2020-09-17 20:00 | 20:00 | 17.35 | 44 | 428.2667 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 13.0083 | 57.5 | 525.6667 | Average of the hour | 2020-09-17 20:00 | 20:00 | 13.0083 | 57.5 | 525.6667 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 20.7108 | 48.5367 | 405 | Average of the hour | 2020-09-17 20:00 | 20:00 | 20.7108 | 48.5367 | 405 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.4892 | 45.7717 | 398 | Average of the hour | 2020-09-17 20:00 | 20:00 | 22.4892 | 45.7717 | 398 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 21.015 | 52.5583 | 434.25 | Average of the hour | 2020-09-17 20:00 | 20:00 | 21.015 | 52.5583 | 434.25 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 21.6425 | 48.1633 | 465.6667 | Average of the hour | 2020-09-17 20:00 | 20:00 | 21.6425 | 48.1633 | 465.6667 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.015 | 37.4571 | 436.25 | Average of the hour | 2020-09-17 20:00 | 20:00 | 24.015 | 37.4571 | 436.25 |  | caution | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.4942 | 44.9433 | 415.5 | Average of the hour | 2020-09-17 20:00 | 20:00 | 22.4942 | 44.9433 | 415.5 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.2643 | 39.1772 | 483.4912 | Average of the hour | 2020-09-17 20:00 | 20:00 | 22.2643 | 39.1772 | 483.4912 |  | caution | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 25.6931 | 33.7293 | 308.1701 | Average of the hour | 2020-09-17 20:00 | 20:00 | 25.6931 | 33.7293 | 308.1701 |  | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.6934 | 37.2299 | 376.9257 | Average of the hour | 2020-09-17 20:00 | 20:00 | 23.6934 | 37.2299 | 376.9257 |  | caution | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.455 | 46.2554 | 610.75 | Average of the hour | 2020-09-17 20:00 | 20:00 | 21.455 | 46.2554 | 610.75 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.65 | 45.3117 | 405 | Average of the hour | 2020-09-17 20:00 | 20:00 | 20.65 | 45.3117 | 405 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.6908 | 49.8875 | 412 | Average of the hour | 2020-09-17 20:00 | 20:00 | 20.6908 | 49.8875 | 412 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 21.85 | 37.875 | 438.1667 | Average of the hour | 2020-09-17 20:00 | 20:00 | 21.85 | 37.875 | 438.1667 |  | caution | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 21.9583 | 40.4583 | 421.625 | Average of the hour | 2020-09-17 20:00 | 20:00 | 21.9583 | 40.4583 | 421.625 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 22.9083 |  |  | Average of the hour | 2020-09-17 20:00 | 20:00 | 22.9083 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 17.3 |  |  | Average of the hour | 2020-09-17 20:00 | 20:00 | 17.3 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 17.588 |  | 438.3167 | Average of the hour | 2020-09-17 20:00 | 20:00 | 17.588 |  | 438.3167 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 17.5843 |  | 379.3333 | Average of the hour | 2020-09-17 20:00 | 20:00 | 17.5843 |  | 379.3333 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-17 20:00 | 20:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-17 20:00 | 20:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.036 | 23.6583 | 434.8072 | Average of the hour | 2020-09-17 20:00 | 20:00 | 22.036 | 23.6583 | 434.8072 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 44.012 | 688.2184 | Average of the hour | 2020-09-17 20:00 | 20:00 |  | 44.012 | 688.2184 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.1589 | 33.2238 |  | Average of the hour | 2020-09-17 20:00 | 20:00 | 21.1589 | 33.2238 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 20:00
2020-09-17 | 20:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 20:00 | 20:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 20:00
2020-09-17 | 21:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 16.4167 | 45.9583 | 430.7917 | Average of the hour | 2020-09-17 21:00 | 21:00 | 16.4167 | 45.9583 | 430.7917 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 12.7917 | 55.375 | 529.7917 | Average of the hour | 2020-09-17 21:00 | 21:00 | 12.7917 | 55.375 | 529.7917 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 21.2425 | 47.4192 | 401.3333 | Average of the hour | 2020-09-17 21:00 | 21:00 | 21.2425 | 47.4192 | 401.3333 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.5158 | 45.1025 | 393.5833 | Average of the hour | 2020-09-17 21:00 | 21:00 | 22.5158 | 45.1025 | 393.5833 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 19.67 | 54.1975 | 430.9167 | Average of the hour | 2020-09-17 21:00 | 21:00 | 19.67 | 54.1975 | 430.9167 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.1567 | 47.0125 | 467.25 | Average of the hour | 2020-09-17 21:00 | 21:00 | 22.1567 | 47.0125 | 467.25 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.1433 | 37.3283 | 433.1667 | Average of the hour | 2020-09-17 21:00 | 21:00 | 24.1433 | 37.3283 | 433.1667 |  | caution | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.7225 | 45.1421 | 417.5 | Average of the hour | 2020-09-17 21:00 | 21:00 | 22.7225 | 45.1421 | 417.5 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.4313 | 39.4051 | 482.3578 | Average of the hour | 2020-09-17 21:00 | 21:00 | 22.4313 | 39.4051 | 482.3578 |  | caution | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 26.0574 | 32.7231 | 307.4258 | Average of the hour | 2020-09-17 21:00 | 21:00 | 26.0574 | 32.7231 | 307.4258 | caution | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 24.0034 | 36.8277 | 377.6725 | Average of the hour | 2020-09-17 21:00 | 21:00 | 24.0034 | 36.8277 | 377.6725 |  | caution | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.4075 | 45.6721 | 613.0833 | Average of the hour | 2020-09-17 21:00 | 21:00 | 21.4075 | 45.6721 | 613.0833 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.76 | 44.7567 | 401.6667 | Average of the hour | 2020-09-17 21:00 | 21:00 | 20.76 | 44.7567 | 401.6667 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.7892 | 49.0688 | 413.4167 | Average of the hour | 2020-09-17 21:00 | 21:00 | 20.7892 | 49.0688 | 413.4167 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 18.5917 | 34.3333 | 449.1667 | Average of the hour | 2020-09-17 21:00 | 21:00 | 18.5917 | 34.3333 | 449.1667 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 16.65 | 41.1242 | 419.1333 | Average of the hour | 2020-09-17 21:00 | 21:00 | 16.65 | 41.1242 | 419.1333 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 13.3083 |  |  | Average of the hour | 2020-09-17 21:00 | 21:00 | 13.3083 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 14.4417 |  |  | Average of the hour | 2020-09-17 21:00 | 21:00 | 14.4417 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 13.9234 |  | 448.7583 | Average of the hour | 2020-09-17 21:00 | 21:00 | 13.9234 |  | 448.7583 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 13.8811 |  | 380 | Average of the hour | 2020-09-17 21:00 | 21:00 | 13.8811 |  | 380 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-17 21:00 | 21:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-17 21:00 | 21:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.1049 | 24.5836 | 437.7628 | Average of the hour | 2020-09-17 21:00 | 21:00 | 22.1049 | 24.5836 | 437.7628 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 42.6203 | 688.204 | Average of the hour | 2020-09-17 21:00 | 21:00 |  | 42.6203 | 688.204 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.0662 | 30.8919 |  | Average of the hour | 2020-09-17 21:00 | 21:00 | 21.0662 | 30.8919 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 21:00
2020-09-17 | 21:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 21:00 | 21:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 21:00
2020-09-17 | 22:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 15.9917 | 46.8333 | 449.7583 | Average of the hour | 2020-09-17 22:00 | 22:00 | 15.9917 | 46.8333 | 449.7583 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 13.5333 | 51.1667 | 535.9167 | Average of the hour | 2020-09-17 22:00 | 22:00 | 13.5333 | 51.1667 | 535.9167 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 19.0358 | 48.3525 | 402 | Average of the hour | 2020-09-17 22:00 | 22:00 | 19.0358 | 48.3525 | 402 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 22.43 | 41.9175 | 388 | Average of the hour | 2020-09-17 22:00 | 22:00 | 22.43 | 41.9175 | 388 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 18.8825 | 54.1492 | 430.8333 | Average of the hour | 2020-09-17 22:00 | 22:00 | 18.8825 | 54.1492 | 430.8333 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.3525 | 47.1675 | 467.4167 | Average of the hour | 2020-09-17 22:00 | 22:00 | 22.3525 | 47.1675 | 467.4167 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.1975 | 36.7946 | 430 | Average of the hour | 2020-09-17 22:00 | 22:00 | 24.1975 | 36.7946 | 430 |  | caution | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.8033 | 44.9187 | 418 | Average of the hour | 2020-09-17 22:00 | 22:00 | 22.8033 | 44.9187 | 418 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.5139 | 39.6886 | 484.0687 | Average of the hour | 2020-09-17 22:00 | 22:00 | 22.5139 | 39.6886 | 484.0687 |  | caution | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 26.1973 | 31.6154 | 305.1551 | Average of the hour | 2020-09-17 22:00 | 22:00 | 26.1973 | 31.6154 | 305.1551 | caution | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 24.1456 | 32.5889 | 380.2131 | Average of the hour | 2020-09-17 22:00 | 22:00 | 24.1456 | 32.5889 | 380.2131 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.34 | 44.6967 | 615.5 | Average of the hour | 2020-09-17 22:00 | 22:00 | 21.34 | 44.6967 | 615.5 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.805 | 44.0496 | 401.75 | Average of the hour | 2020-09-17 22:00 | 22:00 | 20.805 | 44.0496 | 401.75 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 20.98 | 50.6542 | 411 | Average of the hour | 2020-09-17 22:00 | 22:00 | 20.98 | 50.6542 | 411 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 16.0917 | 33.1667 | 449.0917 | Average of the hour | 2020-09-17 22:00 | 22:00 | 16.0917 | 33.1667 | 449.0917 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 13.6333 | 40.5517 | 416.0833 | Average of the hour | 2020-09-17 22:00 | 22:00 | 13.6333 | 40.5517 | 416.0833 |  |  | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 11.2 |  |  | Average of the hour | 2020-09-17 22:00 | 22:00 | 11.2 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 13.6917 |  |  | Average of the hour | 2020-09-17 22:00 | 22:00 | 13.6917 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 12.4945 |  | 449.15 | Average of the hour | 2020-09-17 22:00 | 22:00 | 12.4945 |  | 449.15 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 12.3147 |  | 380 | Average of the hour | 2020-09-17 22:00 | 22:00 | 12.3147 |  | 380 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-17 22:00 | 22:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-17 22:00 | 22:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.1251 | 25.343 | 438.2321 | Average of the hour | 2020-09-17 22:00 | 22:00 | 22.1251 | 25.343 | 438.2321 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 42.002 | 688.2103 | Average of the hour | 2020-09-17 22:00 | 22:00 |  | 42.002 | 688.2103 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.069 | 29.754 |  | Average of the hour | 2020-09-17 22:00 | 22:00 | 21.069 | 29.754 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 22:00
2020-09-17 | 22:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 22:00 | 22:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 22:00
2020-09-17 | 23:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 01 Return | [5 empty] | 14.8833 | 47.7083 | 441.2333 | Average of the hour | 2020-09-17 23:00 | 23:00 | 14.8833 | 47.7083 | 441.2333 |  |  | 2020-09-14 | B10991¦AHU 01 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B10991 | B10991 - 440 Kent St W - Lindsay | AHU 02 Return | [5 empty] | 11.3833 | 55 | 538.75 | Average of the hour | 2020-09-17 23:00 | 23:00 | 11.3833 | 55 | 538.75 |  |  | 2020-09-14 | B10991¦AHU 02 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 04 Return | [5 empty] | 17.4858 | 50.8925 | 393.25 | Average of the hour | 2020-09-17 23:00 | 23:00 | 17.4858 | 50.8925 | 393.25 |  |  | 2020-09-14 | B15646¦AHU 04 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 05 Return | [5 empty] | 21.7717 | 42.2008 | 388.3333 | Average of the hour | 2020-09-17 23:00 | 23:00 | 21.7717 | 42.2008 | 388.3333 |  |  | 2020-09-14 | B15646¦AHU 05 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 06 Return | [5 empty] | 18.4125 | 54.6575 | 431.0833 | Average of the hour | 2020-09-17 23:00 | 23:00 | 18.4125 | 54.6575 | 431.0833 |  |  | 2020-09-14 | B15646¦AHU 06 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B15646 | B15646 - 245 Windsor Ave - Windsor | AHU 07 Return | [5 empty] | 22.7217 | 47.2783 | 463.0833 | Average of the hour | 2020-09-17 23:00 | 23:00 | 22.7217 | 47.2783 | 463.0833 |  |  | 2020-09-14 | B15646¦AHU 07 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S01 Return | [5 empty] | 24.4 | 36.3708 | 432.6667 | Average of the hour | 2020-09-17 23:00 | 23:00 | 24.4 | 36.3708 | 432.6667 |  | caution | 2020-09-14 | B18343¦AHU S01 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S02 Return | [5 empty] | 22.6733 | 45.0371 | 417.8333 | Average of the hour | 2020-09-17 23:00 | 23:00 | 22.6733 | 45.0371 | 417.8333 |  |  | 2020-09-14 | B18343¦AHU S02 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S03 Return | [5 empty] | 22.5222 | 39.8993 | 483.0402 | Average of the hour | 2020-09-17 23:00 | 23:00 | 22.5222 | 39.8993 | 483.0402 |  | caution | 2020-09-14 | B18343¦AHU S03 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S04 Return | [5 empty] | 26.2224 | 29.6996 | 304.7881 | Average of the hour | 2020-09-17 23:00 | 23:00 | 26.2224 | 29.6996 | 304.7881 | caution | low | 2020-09-14 | B18343¦AHU S04 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S05 Return | [5 empty] | 23.1737 | 31.0538 | 378.0933 | Average of the hour | 2020-09-17 23:00 | 23:00 | 23.1737 | 31.0538 | 378.0933 |  | low | 2020-09-14 | B18343¦AHU S05 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S09 Return | [5 empty] | 21.36 | 44.1442 | 613.4167 | Average of the hour | 2020-09-17 23:00 | 23:00 | 21.36 | 44.1442 | 613.4167 |  |  | 2020-09-14 | B18343¦AHU S09 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S10 Return | [5 empty] | 20.9958 | 45.4842 | 408.9167 | Average of the hour | 2020-09-17 23:00 | 23:00 | 20.9958 | 45.4842 | 408.9167 |  |  | 2020-09-14 | B18343¦AHU S10 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18343 | B18343 - 80 Dundas Street East - London | AHU S11 Return | [5 empty] | 21.1775 | 49.9467 | 411.6667 | Average of the hour | 2020-09-17 23:00 | 23:00 | 21.1775 | 49.9467 | 411.6667 |  |  | 2020-09-14 | B18343¦AHU S11 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 01 Return | [5 empty] | 15.1583 | 30.5417 | 443.175 | Average of the hour | 2020-09-17 23:00 | 23:00 | 15.1583 | 30.5417 | 443.175 |  | low | 2020-09-14 | B18784¦AHU 01 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | AHU 02 Return | [5 empty] | 12.75 | 37.8025 | 417.8 | Average of the hour | 2020-09-17 23:00 | 23:00 | 12.75 | 37.8025 | 417.8 |  | caution | 2020-09-14 | B18784¦AHU 02 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 01 Return | [5 empty] | 10.5583 |  |  | Average of the hour | 2020-09-17 23:00 | 23:00 | 10.5583 |  |  |  |  | 2020-09-14 | B18784¦RTU 01 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 03 Return | [5 empty] | 13.2417 |  |  | Average of the hour | 2020-09-17 23:00 | 23:00 | 13.2417 |  |  |  |  | 2020-09-14 | B18784¦RTU 03 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 04 Return | [5 empty] | 11.828 |  | 443.0417 | Average of the hour | 2020-09-17 23:00 | 23:00 | 11.828 |  | 443.0417 |  |  | 2020-09-14 | B18784¦RTU 04 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | RTU 05 Return | [5 empty] | 11.626 |  | 379.6667 | Average of the hour | 2020-09-17 23:00 | 23:00 | 11.626 |  | 379.6667 |  |  | 2020-09-14 | B18784¦RTU 05 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND01 Zone | [8 empty] | Average of the hour | 2020-09-17 23:00 | 23:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND01 Zone¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B18784 | B18784 - 491 Steeles Ave E - Milton | VAV ZND02 Zone | [8 empty] | Average of the hour | 2020-09-17 23:00 | 23:00 | [5 empty] | 2020-09-14 | B18784¦VAV ZND02 Zone¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B24968 | B24968 - 159 Cedar St - Sudbury | AHU 01 Return | [5 empty] | 22.1707 | 25.5849 | 435.2849 | Average of the hour | 2020-09-17 23:00 | 23:00 | 22.1707 | 25.5849 | 435.2849 |  | low | 2020-09-14 | B24968¦AHU 01 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 03, 04, 05 Group GSF Return | [6 empty] | 41.5375 | 688.182 | Average of the hour | 2020-09-17 23:00 | 23:00 |  | 41.5375 | 688.182 |  |  | 2020-09-14 | B90009¦AHU 03, 04, 05 Group GSF Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | AHU 06 Return | [5 empty] | 21.0067 | 28.9941 |  | Average of the hour | 2020-09-17 23:00 | 23:00 | 21.0067 | 28.9941 |  |  | low | 2020-09-14 | B90009¦AHU 06 Return¦¦Sep-17-2020 23:00
2020-09-17 | 23:00 | CBRE ESI | B90009 | B90009 - 7755 HURONTARIO ST - Brampton | VAV 142 Zone | [8 empty] | Average of the hour | 2020-09-17 23:00 | 23:00 | [5 empty] | 2020-09-14 | B90009¦VAV 142 Zone¦¦Sep-17-2020 23:00
2020-09-21 08:18 | 44095.3455 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 128 |  | 0 | 11 | 68 | 391 | 16.7 | 49.4 | 397 | No | 2020-09-21 08:18 | 44095.3455 | 16.7 | 49.4 | 397 |  |  | 2020-09-21 | B14660¦128¦¦Sep-21-2020 08:17
2020-09-21 08:21 | 44095.348 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 001 |  | 0 | 11 | 68 | 391 | 19.1 | 43.7 | 413 | No | 2020-09-21 08:21 | 44095.348 | 19.1 | 43.7 | 413 |  |  | 2020-09-21 | B14660¦001¦¦Sep-21-2020 08:21
2020-09-21 08:25 | 44095.3507 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 028 |  | 0 | 11 | 68 | 391 | 21.6 | 37 | 405 | No | 2020-09-21 08:25 | 44095.3507 | 21.6 | 37 | 405 |  | caution | 2020-09-21 | B14660¦028¦¦Sep-21-2020 08:25
2020-09-21 08:26 | 44095.3512 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 waiting area |  | 1 | 13 | 48 | 460 | 19 | 34 | 441 |  | 2020-09-21 08:26 | 44095.3512 | 19 | 34 | 441 |  | low | 2020-09-21 | B20772¦H9 waiting area¦¦Sep-21-2020 08:25
2020-09-21 08:26 | 44095.3516 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 rear left |  | 1 | 13 | 48 | 460 | 20 | 33 | 452 |  | 2020-09-21 08:26 | 44095.3516 | 20 | 33 | 452 |  | low | 2020-09-21 | B20772¦H9 rear left¦¦Sep-21-2020 08:26
2020-09-21 08:27 | 44095.3524 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 rear right |  | 1 | 13 | 48 | 460 | 20 | 32 | 447 |  | 2020-09-21 08:27 | 44095.3524 | 20 | 32 | 447 |  | low | 2020-09-21 | B20772¦H9 rear right¦¦Sep-21-2020 08:27
2020-09-21 08:27 | 44095.3524 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 019 |  | 0 | 11 | 68 | 391 | 22.1 | 35.8 | 400 | No | 2020-09-21 08:27 | 44095.3524 | 22.1 | 35.8 | 400 |  | caution | 2020-09-21 | B14660¦019¦¦Sep-21-2020 08:27
2020-09-21 08:28 | 44095.3531 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 defendant |  | 1 | 13 | 48 | 460 | 20 | 32 | 446 |  | 2020-09-21 08:28 | 44095.3531 | 20 | 32 | 446 |  | low | 2020-09-21 | B20772¦H9 defendant ¦¦Sep-21-2020 08:28
2020-09-21 08:30 | 44095.3541 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 plaintiff |  | 1 | 13 | 48 | 460 | 20 | 32 | 447 |  | 2020-09-21 08:30 | 44095.3541 | 20 | 32 | 447 |  | low | 2020-09-21 | B20772¦H9 plaintiff¦¦Sep-21-2020 08:29
2020-09-21 08:31 | 44095.3548 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H9 judge |  | 1 | 13 | 48 | 460 | 20 | 32 | 446 |  | 2020-09-21 08:31 | 44095.3548 | 20 | 32 | 446 |  | low | 2020-09-21 | B20772¦H9 judge¦¦Sep-21-2020 08:30
2020-09-21 08:32 | 44095.3557 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 judge |  | 1 | 13 | 48 | 460 | 20 | 32 | 447 |  | 2020-09-21 08:32 | 44095.3557 | 20 | 32 | 447 |  | low | 2020-09-21 | B20772¦H15 judge¦¦Sep-21-2020 08:32
2020-09-21 08:33 | 44095.3565 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 plaintiff |  | 1 | 13 | 48 | 460 | 19 | 33 | 446 |  | 2020-09-21 08:33 | 44095.3565 | 19 | 33 | 446 |  | low | 2020-09-21 | B20772¦H15 plaintiff¦¦Sep-21-2020 08:33
2020-09-21 08:33 | 44095.3566 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 011 |  | 1 | 11 | 68 | 391 | 22.6 | 34.3 | 453 | No | 2020-09-21 08:33 | 44095.3566 | 22.6 | 34.3 | 453 |  | low | 2020-09-21 | B14660¦011¦¦Sep-21-2020 08:33
2020-09-21 08:34 | 44095.3571 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 defendant’s |  | 1 | 13 | 48 | 460 | 19 | 33 | 443 |  | 2020-09-21 08:34 | 44095.3571 | 19 | 33 | 443 |  | low | 2020-09-21 | B20772¦H15 defendant’s ¦¦Sep-21-2020 08:34
2020-09-21 08:34 | 44095.3571 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Security area |  | 1 | 5.5 | 91.9 | 429 | 14.3 | 52.5 | 496 |  | 2020-09-21 08:34 | 44095.3571 | 14.3 | 52.5 | 496 |  |  | 2020-09-21 | B17477¦Security area¦¦Sep-21-2020 08:34
2020-09-21 08:35 | 44095.3578 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 rear right |  | 1 | 13 | 48 | 460 | 19 | 34 | 445 |  | 2020-09-21 08:35 | 44095.3578 | 19 | 34 | 445 |  | low | 2020-09-21 | B20772¦H15 rear right¦¦Sep-21-2020 08:35
2020-09-21 08:36 | 44095.3585 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 rear left |  | 1 | 13 | 48 | 460 | 19 | 34 | 449 |  | 2020-09-21 08:36 | 44095.3585 | 19 | 34 | 449 |  | low | 2020-09-21 | B20772¦H15 rear left¦¦Sep-21-2020 08:36
2020-09-21 08:37 | 44095.3589 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 118 |  | 0 | 11 | 68 | 391 | 24.3 | 32.7 | 415 | No | 2020-09-21 08:37 | 44095.3589 | 24.3 | 32.7 | 415 |  | low | 2020-09-21 | B14660¦118¦¦Sep-21-2020 08:36
2020-09-21 08:37 | 44095.3591 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H15 waiting area |  | 1 | 13 | 48 | 460 | 19 | 33 | 447 |  | 2020-09-21 08:37 | 44095.3591 | 19 | 33 | 447 |  | low | 2020-09-21 | B20772¦H15 waiting area¦¦Sep-21-2020 08:37
2020-09-21 08:37 | 44095.3592 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 3 waiting area N |  | 0 | 5.5 | 91.9 | 429 | 17.5 | 45.5 | 457 |  | 2020-09-21 08:37 | 44095.3592 | 17.5 | 45.5 | 457 |  |  | 2020-09-21 | B17477¦LVL 3 waiting area N¦¦Sep-21-2020 08:37
2020-09-21 08:38 | 44095.3595 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | OPP office |  | 1 | 10 | 59 | 438 | 16 | 52 | 510 |  | 2020-09-21 08:38 | 44095.3595 | 16 | 52 | 510 |  |  | 2020-09-21 | B70235¦OPP office ¦¦Sep-21-2020 08:37
2020-09-21 08:38 | 44095.3599 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 3 waiting area S |  | 0 | 5.5 | 91.9 | 429 | 19.1 | 41.9 | 454 |  | 2020-09-21 08:38 | 44095.3599 | 19.1 | 41.9 | 454 |  |  | 2020-09-21 | B17477¦LVL 3 waiting area S¦¦Sep-21-2020 08:38
2020-09-21 08:38 | 44095.36 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 115 |  | 0 | 11 | 68 | 391 | 24.5 | 30.2 | 414 | No | 2020-09-21 08:38 | 44095.36 | 24.5 | 30.2 | 414 |  | low | 2020-09-21 | B14660¦115¦¦Sep-21-2020 08:38
2020-09-21 08:39 | 44095.3606 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 3 waiting area S |  | 0 | 5.5 | 91.9 | 429 | 19.1 | 41.9 | 454 |  | 2020-09-21 08:39 | 44095.3606 | 19.1 | 41.9 | 454 |  |  | 2020-09-21 | B17477¦LVL 3 waiting area S¦¦Sep-21-2020 08:39
2020-09-21 08:39 | 44095.3607 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 3 waiting area S |  | 0 | 5.5 | 91.9 | 429 | 19.1 | 41.9 | 454 |  | 2020-09-21 08:39 | 44095.3607 | 19.1 | 41.9 | 454 |  |  | 2020-09-21 | B17477¦LVL 3 waiting area S¦¦Sep-21-2020 08:39
2020-09-21 08:40 | 44095.3609 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom A chairs |  | 0 | 12.7 | 53.2 | 542 | 21.6 | 28.7 | 495 |  | 2020-09-21 08:40 | 44095.3609 | 21.6 | 28.7 | 495 |  | low | 2020-09-21 | B20603¦Courtroom A chairs¦¦Sep-21-2020 08:39
2020-09-21 08:40 | 44095.361 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office E |  | 3 | 10 | 59 | 438 | 19 | 41 | 488 |  | 2020-09-21 08:40 | 44095.361 | 19 | 41 | 488 |  |  | 2020-09-21 | B70235¦Main office E¦¦Sep-21-2020 08:39
2020-09-21 08:41 | 44095.3618 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom A bench |  | 0 | 12.7 | 53.2 | 542 | 21.8 | 28.4 | 491 |  | 2020-09-21 08:41 | 44095.3618 | 21.8 | 28.4 | 491 |  | low | 2020-09-21 | B20603¦Courtroom A bench¦¦Sep-21-2020 08:40
2020-09-21 08:41 | 44095.3618 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office C |  | 3 | 10 | 59 | 438 | 20 | 38 | 493 |  | 2020-09-21 08:41 | 44095.3618 | 20 | 38 | 493 |  | caution | 2020-09-21 | B70235¦Main office C ¦¦Sep-21-2020 08:41
2020-09-21 08:41 | 44095.3621 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 107 |  | 2 | 11 | 68 | 391 | 20.1 | 39.9 | 445 | No | 2020-09-21 08:41 | 44095.3621 | 20.1 | 39.9 | 445 |  | caution | 2020-09-21 | B14660¦107¦¦Sep-21-2020 08:41
2020-09-21 08:41 | 44095.3621 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 3 waiting area S |  | 0 | 5.5 | 91.9 | 429 | 20.4 | 36.5 | 484 |  | 2020-09-21 08:41 | 44095.3621 | 20.4 | 36.5 | 484 |  | caution | 2020-09-21 | B17477¦LVL 3 waiting area S¦¦Sep-21-2020 08:41
2020-09-21 08:42 | 44095.3628 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Main office W |  | 3 | 10 | 59 | 438 | 20 | 36 | 474 |  | 2020-09-21 08:42 | 44095.3628 | 20 | 36 | 474 |  | caution | 2020-09-21 | B70235¦Main office W¦¦Sep-21-2020 08:42
2020-09-21 08:43 | 44095.363 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area north |  | 1 | 13 | 48 | 460 | 21 | 29 | 435 |  | 2020-09-21 08:43 | 44095.363 | 21 | 29 | 435 |  | low | 2020-09-21 | B20772¦Courtroom waiting area north¦¦Sep-21-2020 08:42
2020-09-21 08:43 | 44095.363 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Robing corridor |  | 1 | 12.2 | 55.2 | 456 | 21.6 | 37.8 | 576 |  | 2020-09-21 08:43 | 44095.363 | 21.6 | 37.8 | 576 |  | caution | 2020-09-21 | B20474¦Robing corridor¦¦Sep-21-2020 08:42
2020-09-21 08:43 | 44095.363 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom B chairs |  | 0 | 12.7 | 53.2 | 542 | 21.2 | 28.7 | 490 |  | 2020-09-21 08:43 | 44095.363 | 21.2 | 28.7 | 490 |  | low | 2020-09-21 | B20603¦Courtroom B chairs ¦¦Sep-21-2020 08:42
2020-09-21 08:43 | 44095.3633 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 113 |  | 0 | 11 | 68 | 391 | 22 | 36 | 408 | No | 2020-09-21 08:43 | 44095.3633 | 22 | 36 | 408 |  | caution | 2020-09-21 | B14660¦113¦¦Sep-21-2020 08:43
2020-09-21 08:43 | 44095.3635 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | Courtroom waiting area south |  | 1 | 13 | 48 | 460 | 21 | 30 | 437 |  | 2020-09-21 08:43 | 44095.3635 | 21 | 30 | 437 |  | low | 2020-09-21 | B20772¦Courtroom waiting area south ¦¦Sep-21-2020 08:43
2020-09-21 08:44 | 44095.3636 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 waiting area |  | 0 | 5.5 | 91.9 | 429 | 20.8 | 35.8 | 441 |  | 2020-09-21 08:44 | 44095.3636 | 20.8 | 35.8 | 441 |  | caution | 2020-09-21 | B17477¦Courtroom 300 waiting area¦¦Sep-21-2020 08:43
2020-09-21 08:44 | 44095.3639 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Courtroom B bench |  | 0 | 12.7 | 53.2 | 542 | 21 | 29 | 484 |  | 2020-09-21 08:44 | 44095.3639 | 21 | 29 | 484 |  | low | 2020-09-21 | B20603¦Courtroom B bench ¦¦Sep-21-2020 08:43
2020-09-21 08:44 | 44095.3641 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Trial office |  | 0 | 10 | 59 | 438 | 21 | 34 | 478 |  | 2020-09-21 08:44 | 44095.3641 | 21 | 34 | 478 |  | low | 2020-09-21 | B70235¦Trial office ¦¦Sep-21-2020 08:44
2020-09-21 08:45 | 44095.3643 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 rear right |  | 1 | 13 | 48 | 460 | 21 | 30 | 445 |  | 2020-09-21 08:45 | 44095.3643 | 21 | 30 | 445 |  | low | 2020-09-21 | B20772¦H12 rear right¦¦Sep-21-2020 08:44
2020-09-21 08:45 | 44095.3643 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NW Hall |  | 0 | 13 | 48 | 460 | 18 | 44 | 590 |  | 2020-09-21 08:45 | 44095.3643 | 18 | 44 | 590 |  |  | 2020-09-21 | B25548¦NW Hall¦¦Sep-21-2020 08:44
2020-09-21 08:45 | 44095.3645 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Bsmt waiting area at mens washroom |  | 1 | 12.2 | 55.2 | 456 | 22.6 | 32.5 | 576 |  | 2020-09-21 08:45 | 44095.3645 | 22.6 | 32.5 | 576 |  | low | 2020-09-21 | B20474¦Bsmt waiting area at mens washroom¦¦Sep-21-2020 08:44
2020-09-21 08:45 | 44095.3648 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 114 |  | 0 | 11 | 68 | 391 | 21.8 | 36.2 | 393 | No | 2020-09-21 08:45 | 44095.3648 | 21.8 | 36.2 | 393 |  | caution | 2020-09-21 | B14660¦114¦¦Sep-21-2020 08:45
2020-09-21 08:45 | 44095.3649 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center |  | 0 | 12.7 | 53.2 | 542 | 21.1 | 29.4 | 489 |  | 2020-09-21 08:45 | 44095.3649 | 21.1 | 29.4 | 489 |  | low | 2020-09-21 | B20603¦Prep center ¦¦Sep-21-2020 08:45
2020-09-21 08:45 | 44095.3649 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jason Mariasine |  | 0 | 10 | 59 | 438 | 22 | 32 | 467 |  | 2020-09-21 08:45 | 44095.3649 | 22 | 32 | 467 |  | low | 2020-09-21 | B70235¦Jason Mariasine ¦¦Sep-21-2020 08:45
2020-09-21 08:46 | 44095.365 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 rear left |  | 1 | 13 | 48 | 460 | 20 | 30 | 446 |  | 2020-09-21 08:46 | 44095.365 | 20 | 30 | 446 |  | low | 2020-09-21 | B20772¦H12 rear left¦¦Sep-21-2020 08:45
2020-09-21 08:46 | 44095.3651 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 W |  | 0 | 5.5 | 91.9 | 429 | 21.7 | 35.2 | 444 |  | 2020-09-21 08:46 | 44095.3651 | 21.7 | 35.2 | 444 |  | caution | 2020-09-21 | B17477¦Courtroom 300 W ¦¦Sep-21-2020 08:45
2020-09-21 08:46 | 44095.3653 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | NE hall |  | 0 | 13 | 48 | 460 | 20 | 43 | 590 |  | 2020-09-21 08:46 | 44095.3653 | 20 | 43 | 590 |  |  | 2020-09-21 | B25548¦NE hall¦¦Sep-21-2020 08:46
2020-09-21 08:47 | 44095.3657 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 pleintiff |  | 1 | 13 | 48 | 460 | 21 | 30 | 442 |  | 2020-09-21 08:47 | 44095.3657 | 21 | 30 | 442 |  | low | 2020-09-21 | B20772¦H12 pleintiff¦¦Sep-21-2020 08:46
2020-09-21 08:47 | 44095.3658 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jennifer Mumby |  | 0 | 10 | 59 | 438 | 22 | 32 | 459 |  | 2020-09-21 08:47 | 44095.3658 | 22 | 32 | 459 |  | low | 2020-09-21 | B70235¦Jennifer Mumby ¦¦Sep-21-2020 08:46
2020-09-21 08:47 | 44095.3658 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center 2 |  | 0 | 12.7 | 53.2 | 542 | 21.3 | 29.1 | 500 |  | 2020-09-21 08:47 | 44095.3658 | 21.3 | 29.1 | 500 |  | low | 2020-09-21 | B20603¦Prep center 2¦¦Sep-21-2020 08:46
2020-09-21 08:47 | 44095.3658 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 300 E |  | 0 | 5.5 | 91.9 | 429 | 22 | 34.3 | 443 |  | 2020-09-21 08:47 | 44095.3658 | 22 | 34.3 | 443 |  | low | 2020-09-21 | B17477¦Courtroom 300 E¦¦Sep-21-2020 08:46
2020-09-21 08:47 | 44095.3661 | AINSWORTH | B25548 | B25548 - 301 St. Paul St - St. Catharines | E hall |  | 0 | 13 | 48 | 595 | 20 | 40 | 590 |  | 2020-09-21 08:47 | 44095.3661 | 20 | 40 | 590 |  | caution | 2020-09-21 | B25548¦E hall¦¦Sep-21-2020 08:47
2020-09-21 08:48 | 44095.3663 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Basmt waiting area inside dbl doors |  | 1 | 12.2 | 55.2 | 456 | 22.3 | 32.1 | 572 |  | 2020-09-21 08:48 | 44095.3663 | 22.3 | 32.1 | 572 |  | low | 2020-09-21 | B20474¦Basmt waiting area inside dbl doors¦¦Sep-21-2020 08:47
2020-09-21 08:48 | 44095.3664 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 defendant |  | 1 | 13 | 48 | 460 | 21 | 30 | 444 |  | 2020-09-21 08:48 | 44095.3664 | 21 | 30 | 444 |  | low | 2020-09-21 | B20772¦H12 defendant ¦¦Sep-21-2020 08:47
2020-09-21 08:48 | 44095.3665 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center 3 |  | 0 | 12.7 | 53.2 | 542 | 21.5 | 29.1 | 514 |  | 2020-09-21 08:48 | 44095.3665 | 21.5 | 29.1 | 514 |  | low | 2020-09-21 | B20603¦Prep center 3¦¦Sep-21-2020 08:47
2020-09-21 08:48 | 44095.3667 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Jennifer Broderick office |  | 0 | 10 | 59 | 438 | 22 | 32 | 468 |  | 2020-09-21 08:48 | 44095.3667 | 22 | 32 | 468 |  | low | 2020-09-21 | B70235¦Jennifer Broderick office ¦¦Sep-21-2020 08:47
2020-09-21 08:48 | 44095.3669 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 104 |  | 0 | 11 | 68 | 391 | 21.8 | 35.8 | 417 | No | 2020-09-21 08:48 | 44095.3669 | 21.8 | 35.8 | 417 |  | caution | 2020-09-21 | B14660¦104¦¦Sep-21-2020 08:48
2020-09-21 08:49 | 44095.3671 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Court services |  | 0 | 5.5 | 91.9 | 429 | 22.3 | 32.8 | 453 |  | 2020-09-21 08:49 | 44095.3671 | 22.3 | 32.8 | 453 |  | low | 2020-09-21 | B17477¦Court services¦¦Sep-21-2020 08:48
2020-09-21 08:49 | 44095.3671 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 judge |  | 1 | 13 | 48 | 460 | 21 | 30 | 450 |  | 2020-09-21 08:49 | 44095.3671 | 21 | 30 | 450 |  | low | 2020-09-21 | B20772¦H12 judge¦¦Sep-21-2020 08:48
2020-09-21 08:49 | 44095.3677 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 3 interview room |  | 0 | 5.5 | 91.9 | 429 | 22.3 | 32.4 | 450 |  | 2020-09-21 08:50 | 44095.3677 | 22.3 | 32.4 | 450 |  | low | 2020-09-21 | B17477¦LVL 3 interview room¦¦Sep-21-2020 08:49
2020-09-21 08:50 | 44095.3678 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom D |  | 0 | 7.9 | 77.7 | 443 | 18.5 | 46.4 | 476 | No | 2020-09-21 08:50 | 44095.3678 | 18.5 | 46.4 | 476 |  |  | 2020-09-21 | B20478¦Courtroom D¦¦Sep-21-2020 08:49
2020-09-21 08:50 | 44095.3679 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H12 retiring room |  | 1 | 13 | 48 | 460 | 21 | 30 | 450 |  | 2020-09-21 08:50 | 44095.3679 | 21 | 30 | 450 |  | low | 2020-09-21 | B20772¦H12 retiring room¦¦Sep-21-2020 08:49
2020-09-21 08:50 | 44095.3681 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Robert Beninger office |  | 0 | 10 | 59 | 438 | 22 | 32 | 471 |  | 2020-09-21 08:50 | 44095.3681 | 22 | 32 | 471 |  | low | 2020-09-21 | B70235¦Robert Beninger office ¦¦Sep-21-2020 08:50
2020-09-21 08:50 | 44095.3681 | AINSWORTH | B20474 | B20474 - 74 Woolwich St - Guelph | Courtroom3 waiting area |  | 1 | 12.2 | 55.2 | 456 | 22.3 | 32.1 | 572 |  | 2020-09-21 08:50 | 44095.3681 | 22.3 | 32.1 | 572 |  | low | 2020-09-21 | B20474¦Courtroom3 waiting area¦¦Sep-21-2020 08:50
2020-09-21 08:50 | 44095.3682 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center office 1 |  | 0 | 12.7 | 53.2 | 542 | 21.6 | 28.8 | 533 |  | 2020-09-21 08:50 | 44095.3682 | 21.6 | 28.8 | 533 |  | low | 2020-09-21 | B20603¦Prep center office 1¦¦Sep-21-2020 08:50
2020-09-21 08:51 | 44095.3685 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 101 |  | 0 | 11 | 68 | 391 | 21.8 | 36.4 | 398 | No | 2020-09-21 08:51 | 44095.3685 | 21.8 | 36.4 | 398 |  | caution | 2020-09-21 | B14660¦101¦¦Sep-21-2020 08:50
2020-09-21 08:51 | 44095.3686 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 2 waiting area |  | 0 | 5.5 | 91.9 | 429 | 22 | 31.9 | 446 |  | 2020-09-21 08:51 | 44095.3686 | 22 | 31.9 | 446 |  | low | 2020-09-21 | B17477¦LVL 2 waiting area¦¦Sep-21-2020 08:50
2020-09-21 08:51 | 44095.3686 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Stuart Konyer office |  | 0 | 10 | 59 | 438 | 22 | 32 | 478 |  | 2020-09-21 08:51 | 44095.3686 | 22 | 32 | 478 |  | low | 2020-09-21 | B70235¦Stuart Konyer office ¦¦Sep-21-2020 08:50
2020-09-21 08:51 | 44095.3687 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 retiring room |  | 1 | 13 | 48 | 460 | 21 | 30 | 445 |  | 2020-09-21 08:51 | 44095.3687 | 21 | 30 | 445 |  | low | 2020-09-21 | B20772¦H11 retiring room ¦¦Sep-21-2020 08:50
2020-09-21 08:51 | 44095.369 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom B |  | 0 | 7.9 | 77.7 | 443 | 20 | 43.3 | 478 | No | 2020-09-21 08:51 | 44095.369 | 20 | 43.3 | 478 |  |  | 2020-09-21 | B20478¦Courtroom B¦¦Sep-21-2020 08:51
2020-09-21 08:51 | 44095.369 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Administrative office |  | 7 | 11.7 | 59.3 | 440 | 15.8 | 52.1 | 478 |  | 2020-09-21 08:51 | 44095.369 | 15.8 | 52.1 | 478 |  |  | 2020-09-21 | B90558¦Administrative office¦¦Sep-21-2020 08:51
2020-09-21 08:52 | 44095.3691 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center office 610 |  | 0 | 12.7 | 53.2 | 542 | 21.8 | 28.3 | 529 |  | 2020-09-21 08:52 | 44095.3691 | 21.8 | 28.3 | 529 |  | low | 2020-09-21 | B20603¦Prep center office 610¦¦Sep-21-2020 08:51
2020-09-21 08:52 | 44095.3694 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 judge |  | 1 | 13 | 48 | 460 | 21 | 30 | 443 |  | 2020-09-21 08:52 | 44095.3694 | 21 | 30 | 443 |  | low | 2020-09-21 | B20772¦H11 judge¦¦Sep-21-2020 08:51
2020-09-21 08:52 | 44095.3695 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Lunch room |  | 0 | 10 | 59 | 438 | 23 | 32 | 471 |  | 2020-09-21 08:52 | 44095.3695 | 23 | 32 | 471 |  | low | 2020-09-21 | B70235¦Lunch room ¦¦Sep-21-2020 08:52
2020-09-21 08:53 | 44095.37 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom 2 |  | 0 | 11.7 | 59.3 | 440 | 18.1 | 42.4 | 434 |  | 2020-09-21 08:53 | 44095.37 | 18.1 | 42.4 | 434 |  |  | 2020-09-21 | B90558¦Courtroom 2¦¦Sep-21-2020 08:52
2020-09-21 08:53 | 44095.37 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 plsintiff |  | 1 | 13 | 48 | 460 | 21 | 30 | 443 |  | 2020-09-21 08:53 | 44095.37 | 21 | 30 | 443 |  | low | 2020-09-21 | B20772¦H11 plsintiff¦¦Sep-21-2020 08:52
2020-09-21 08:53 | 44095.3701 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom C |  | 0 | 7.9 | 46.4 | 443 | 21.5 | 37.8 | 470 | No | 2020-09-21 08:53 | 44095.3701 | 21.5 | 37.8 | 470 |  | caution | 2020-09-21 | B20478¦Courtroom C¦¦Sep-21-2020 08:52
2020-09-21 08:53 | 44095.3703 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court support office |  | 0 | 10 | 59 | 438 | 22 | 31 | 468 |  | 2020-09-21 08:53 | 44095.3703 | 22 | 31 | 468 |  | low | 2020-09-21 | B70235¦Court support office ¦¦Sep-21-2020 08:53
2020-09-21 08:54 | 44095.3707 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 134 |  | 0 | 11 | 68 | 391 | 22.8 | 34.4 | 403 | No | 2020-09-21 08:54 | 44095.3707 | 22.8 | 34.4 | 403 |  | low | 2020-09-21 | B14660¦134¦¦Sep-21-2020 08:53
2020-09-21 08:54 | 44095.3708 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 defendant’s |  | 1 | 14 | 48 | 460 | 21 | 29 | 444 |  | 2020-09-21 08:54 | 44095.3708 | 21 | 29 | 444 |  | low | 2020-09-21 | B20772¦H11 defendant’s ¦¦Sep-21-2020 08:53
2020-09-21 08:54 | 44095.3708 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Prep center office 618 |  | 1 | 12.7 | 53.2 | 542 | 22 | 28.8 | 567 |  | 2020-09-21 08:54 | 44095.3708 | 22 | 28.8 | 567 |  | low | 2020-09-21 | B20603¦Prep center office 618¦¦Sep-21-2020 08:53
2020-09-21 08:54 | 44095.3708 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom 3 |  | 0 | 11.7 | 59.3 | 440 | 18.8 | 40 | 430 |  | 2020-09-21 08:54 | 44095.3708 | 18.8 | 40 | 430 |  | caution | 2020-09-21 | B90558¦Courtroom 3¦¦Sep-21-2020 08:54
2020-09-21 08:54 | 44095.371 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 1 waiting area N |  | 0 | 5.5 | 91.9 | 429 | 21 | 34.8 | 443 |  | 2020-09-21 08:54 | 44095.371 | 21 | 34.8 | 443 |  | low | 2020-09-21 | B17477¦LVL 1 waiting area N¦¦Sep-21-2020 08:54
2020-09-21 08:55 | 44095.3713 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Crown staff office |  | 1 | 10 | 59 | 438 | 22 | 31 | 500 |  | 2020-09-21 08:55 | 44095.3713 | 22 | 31 | 500 |  | low | 2020-09-21 | B70235¦Crown staff office ¦¦Sep-21-2020 08:54
2020-09-21 08:55 | 44095.3715 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Courtroom A |  | 0 | 7.9 | 77.7 | 455 | 22 | 33.5 | 455 | No | 2020-09-21 08:55 | 44095.3715 | 22 | 33.5 | 455 |  | low | 2020-09-21 | B20478¦Courtroom A¦¦Sep-21-2020 08:54
2020-09-21 08:55 | 44095.3715 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 1 waiting area S |  | 0 | 5.5 | 91.9 | 429 | 21.2 | 33.9 | 442 |  | 2020-09-21 08:55 | 44095.3715 | 21.2 | 33.9 | 442 |  | low | 2020-09-21 | B17477¦LVL 1 waiting area S¦¦Sep-21-2020 08:54
2020-09-21 08:55 | 44095.3716 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 rear right |  | 1 | 13 | 48 | 460 | 21 | 30 | 446 |  | 2020-09-21 08:55 | 44095.3716 | 21 | 30 | 446 |  | low | 2020-09-21 | B20772¦H11 rear right¦¦Sep-21-2020 08:55
2020-09-21 08:55 | 44095.3717 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 138 |  | 5 | 11 | 68 | 391 | 23 | 34 | 431 | No | 2020-09-21 08:55 | 44095.3717 | 23 | 34 | 431 |  | low | 2020-09-21 | B14660¦138¦¦Sep-21-2020 08:55
2020-09-21 08:55 | 44095.3719 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | office 647 |  | 0 | 12.7 | 53.2 | 542 | 21.4 | 28.3 | 498 |  | 2020-09-21 08:55 | 44095.3719 | 21.4 | 28.3 | 498 |  | low | 2020-09-21 | B20603¦office 647¦¦Sep-21-2020 08:55
2020-09-21 08:56 | 44095.3719 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Peterborough Police |  | 1 | 10 | 59 | 438 | 22 | 32 | 510 |  | 2020-09-21 08:56 | 44095.3719 | 22 | 32 | 510 |  | low | 2020-09-21 | B70235¦Peterborough Police ¦¦Sep-21-2020 08:55
2020-09-21 08:56 | 44095.3724 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H11 rear left |  | 1 | 13 | 48 | 460 | 21 | 30 | 454 |  | 2020-09-21 08:56 | 44095.3724 | 21 | 30 | 454 |  | low | 2020-09-21 | B20772¦H11 rear left¦¦Sep-21-2020 08:56
2020-09-21 08:56 | 44095.3725 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 waiting area |  | 0 | 5.5 | 91.9 | 429 | 21.5 | 34.5 | 442 |  | 2020-09-21 08:56 | 44095.3725 | 21.5 | 34.5 | 442 |  | low | 2020-09-21 | B17477¦Courtroom 100 waiting area¦¦Sep-21-2020 08:56
2020-09-21 08:57 | 44095.3726 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Courtroom 1 |  | 1 | 11.7 | 59.3 | 440 | 19.6 | 38.3 | 443 | 2 air purifiers running front and back | 2020-09-21 08:57 | 44095.3726 | 19.6 | 38.3 | 443 |  | caution | 2020-09-21 | B90558¦Courtroom 1¦¦Sep-21-2020 08:56
2020-09-21 08:57 | 44095.3727 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | office 2 |  | 0 | 12.7 | 53.2 | 542 | 21.8 | 28.3 | 496 |  | 2020-09-21 08:57 | 44095.3727 | 21.8 | 28.3 | 496 |  | low | 2020-09-21 | B20603¦office 2¦¦Sep-21-2020 08:56
2020-09-21 08:57 | 44095.3728 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 144 |  | 0 | 11 | 68 | 391 | 23 | 33.4 | 441 | No | 2020-09-21 08:57 | 44095.3728 | 23 | 33.4 | 441 |  | low | 2020-09-21 | B14660¦144¦¦Sep-21-2020 08:56
2020-09-21 08:57 | 44095.3729 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Common area beside Courtroom A |  | 0 | 7.9 | 77.7 | 443 | 22.1 | 34.6 | 453 | No | 2020-09-21 08:57 | 44095.3729 | 22.1 | 34.6 | 453 |  | low | 2020-09-21 | B20478¦Common area beside Courtroom A¦¦Sep-21-2020 08:56
2020-09-21 08:57 | 44095.373 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 judge |  | 0 | 10 | 59 | 438 | 22 | 32 | 456 |  | 2020-09-21 08:57 | 44095.373 | 22 | 32 | 456 |  | low | 2020-09-21 | B70235¦Court #4 judge ¦¦Sep-21-2020 08:57
2020-09-21 08:58 | 44095.3734 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Lvl 1 interview room |  | 0 | 5.5 | 91.9 | 429 | 21.7 | 34.7 | 439 |  | 2020-09-21 08:58 | 44095.3734 | 21.7 | 34.7 | 439 |  | low | 2020-09-21 | B17477¦Lvl 1 interview room¦¦Sep-21-2020 08:57
2020-09-21 08:58 | 44095.3737 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 lawyer |  | 0 | 10 | 59 | 438 | 22 | 32 | 456 |  | 2020-09-21 08:58 | 44095.3737 | 22 | 32 | 456 |  | low | 2020-09-21 | B70235¦Court #4 lawyer ¦¦Sep-21-2020 08:58
2020-09-21 08:58 | 44095.3738 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | office 3 |  | 0 | 12.7 | 53.2 | 542 | 21.2 | 28.6 | 492 |  | 2020-09-21 08:58 | 44095.3738 | 21.2 | 28.6 | 492 |  | low | 2020-09-21 | B20603¦office 3 ¦¦Sep-21-2020 08:58
2020-09-21 08:58 | 44095.3738 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice O'Brien office |  | 0 | 11.7 | 59.3 | 440 | 19.5 | 39 | 450 | Dehumidifier running set at 17 | 2020-09-21 08:58 | 44095.3738 | 19.5 | 39 | 450 |  | caution | 2020-09-21 | B90558¦Justice O'Brien office¦¦Sep-21-2020 08:58
2020-09-21 08:58 | 44095.374 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | Law library |  | 0 | 7.9 | 77.7 | 443 | 21.6 | 35.1 | 452 | No | 2020-09-21 08:58 | 44095.374 | 21.6 | 35.1 | 452 |  | caution | 2020-09-21 | B20478¦Law library ¦¦Sep-21-2020 08:58
2020-09-21 08:59 | 44095.3741 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | LVL 1 interview room 2 |  | 0 | 5.5 | 91.9 | 429 | 21.7 | 34.4 | 439 |  | 2020-09-21 08:59 | 44095.3741 | 21.7 | 34.4 | 439 |  | low | 2020-09-21 | B17477¦LVL 1 interview room 2¦¦Sep-21-2020 08:58
2020-09-21 08:59 | 44095.3742 | AINSWORTH | B14660 | B14660 - 700 Memorial Ave - Orillia | 122 |  | 0 | 11 | 68 | 391 | 23.1 | 33 | 429 | No | 2020-09-21 08:59 | 44095.3742 | 23.1 | 33 | 429 |  | low | 2020-09-21 | B14660¦122¦¦Sep-21-2020 08:58
2020-09-21 08:59 | 44095.3742 | AINSWORTH | B20489 | B20489 - 1 Huron St - Stratford | 2nd floor hallway |  | 2 | 10 | 65 | 400 | 18 | 44.1 | 415 | No | 2020-09-21 08:59 | 44095.3742 | 18 | 44.1 | 415 |  |  | 2020-09-21 | B20489¦2nd floor hallway ¦¦Sep-21-2020 08:58
2020-09-21 08:59 | 44095.3743 | AINSWORTH | B70235 | B70235 - 70-110 Simcoe St - Peterborough | Court #4 vestibule |  | 0 | 10 | 59 | 438 | 22 | 31 | 467 |  | 2020-09-21 08:59 | 44095.3743 | 22 | 31 | 467 |  | low | 2020-09-21 | B70235¦Court #4 vestibule ¦¦Sep-21-2020 08:58
2020-09-21 09:00 | 44095.3747 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice Wheeler office |  | 0 | 11.7 | 59.3 | 440 | 19.3 | 38.9 | 453 |  | 2020-09-21 09:00 | 44095.3747 | 19.3 | 38.9 | 453 |  | caution | 2020-09-21 | B90558¦Justice Wheeler office¦¦Sep-21-2020 08:59
2020-09-21 09:00 | 44095.3749 | AINSWORTH | B20772 | B20772 - 7765 Hurontario St - Brampton | H14 exit entrance |  | 1 | 13 | 48 | 460 | 21 | 29 | 441 |  | 2020-09-21 09:00 | 44095.3749 | 21 | 29 | 441 |  | low | 2020-09-21 | B20772¦H14 exit entrance¦¦Sep-21-2020 08:59
2020-09-21 09:00 | 44095.375 | AINSWORTH | B20478 | B20478 - 5 Court St - Kingston | East Stairwell |  | 0 | 7.9 | 77.7 | 443 | 24.6 | 32.1 | 523 | No | 2020-09-21 09:00 | 44095.375 | 24.6 | 32.1 | 523 |  | low | 2020-09-21 | B20478¦East Stairwell ¦¦Sep-21-2020 08:59
2020-09-21 09:01 | 44095.3754 | AINSWORTH | B17477 | B17477 - 50 Frederick Hobson VC Dr - Simcoe | Courtroom 100 W |  | 0 | 5.5 | 91.9 | 429 | 21.5 | 35.3 | 439 |  | 2020-09-21 09:01 | 44095.3754 | 21.5 | 35.3 | 439 |  | caution | 2020-09-21 | B17477¦Courtroom 100 W¦¦Sep-21-2020 09:00
2020-09-21 09:01 | 44095.3754 | AINSWORTH | B20603 | B20603 - 119 King St W - Hamilton | Office 4 |  | 0 | 12.7 | 53.2 | 542 | 21.2 | 28.6 | 499 |  | 2020-09-21 09:01 | 44095.3754 | 21.2 | 28.6 | 499 |  | low | 2020-09-21 | B20603¦Office 4¦¦Sep-21-2020 09:00
2020-09-21 09:01 | 44095.3754 | AINSWORTH | B90558 | B90558 - 49 Place D'Armes - Kingston | Justice Letourneau office |  | 0 | 11.7 | 59.3 | 440 | 19.5 | 38.5 | 446 |  | 2020-09-21 09:01 | 44095.3754 | 19.5 | 38.5 | 446 |  | caution | 2020-09-21 | B90558¦Justice Letourneau office¦¦Sep-21-2020 09:00